## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-23 | Wednesday
|  |  | Date (day): | 2022-03-23 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13164.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13755 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-22 | 2022-03-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 250 | 250 | 250 | 115 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 95 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 240 | 240 | 240 | 210 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 |  | 185 | GT-2 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 43 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 217 | 213 | 220 | 220 | 115 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 53 | 52 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 296 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 129 | 306 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 100 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 97 | 99 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 116 | 133 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 70 | 70 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 91 | 90 | 91 |  | 13 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 25 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 2936 | 3058 | 3070 | 3144 | 701 | 1828
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 12 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 48 | 45 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 71 | 70 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 131 | 131 | 130 | 130 |  | 95 | ST Under S/D
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 0 | 24
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 26 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 281 | 290 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 77 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1328 | 1484 | 1483 | 1497 | 132 | 668
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 152 | 217 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 270 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 260 | 300 | 300 | 60 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 30 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 147 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 41 | 32 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 137 | 130 | 137 |  | 26 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 129 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 160 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 41 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 20 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 99 | 98 | 99 |  | 15 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 99 | 105 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 20 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 97 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1883 | 2213 | 2190 | 2341 | 586 | 69
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 68 | 81 | 80 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 173 | 180 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 108 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 20 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 428 | 406 | 485.6 | 454 | 102 | 13
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 264 | 279 | 265 | 280 |  | 50 | Engine problem
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 60 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 22 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 404 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 396 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1647 | 1659 | 1664 | 1681 | 251 | 413
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 712 | 715 | 729 | 729
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 40 |  | 14 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 155 | 158 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 220 | 235 | 300 | 300 | 110 |  | Engine problem
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 3 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1253 | 1345 | 1442 | 1529 | 110 | 93
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 80
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 30 | 25 | 30
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 65 | 65 | 65 | 129 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 650 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 190 | 220 | 180 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 731 | 965 | 930 | 1055 | 129 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 34 |  | 18 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 6 | 36 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 42 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint.
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 143 | 135 | 170 | 180 | 40 |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 162 | 170 | 180 | 40 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 393 | 414 | 414 | 414
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 25 | 31 |  | 19 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 54 | 90 | 90 | 90 |  | 14 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 177 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 93 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 95 | 95 |  | 18 | Engine problem
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1088 | 1443 | 1384 | 1545 | 251 | 327
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 81 | 80 | 81
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 96 | 110 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 100 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 479 | 523 | 516 | 509 | 74 | 125
|  | Total |  |  |  |  | 22291 | 21215 | 11773 | 13096 | 13164.6 | 13755 | 2336 | 3536
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11305.5321 | 12576 | 12641.8761 | 13208.8332
| A. |  | 2022-03-22 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13096 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9683 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13096 | MW
| 3 | Day peak Generation : |  |  | 11773 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12576 | MW
| 4 | Evening peak Generation : |  |  | 13096 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 286.3817 | MKWHr | By Solar | 1.3102 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 134.6091 | MKWHr |  | By Oil: | 106.92 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 21.2213 | MKWHr |  | By Hydro: | 1.7554 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2336 | MW | Dhaka | 4617 | 4617 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3536 | MW | Chittagong | 1390 | 1390 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5872 | MW | Khulna | 1470 | 1470 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1072.12 | MMCFD |  |  | Rajshahi | 1426 | 1426 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 135080801.21 | ii) Oil : | Taka | 943548820.76 | Comilla | 1100 | 1100 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 101238111.89 | Total | Taka | 1179867733.86 | Mymensingh | 940 | 940 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.052 | MKWHr. | Sylhet | 452 | 452 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -12 | MW (E to W) at | 21:00 | hrs | Barisal | 336 | 336 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -20 | MW at | 22:00 | hrs | Rangpur | 845 | 845 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 12576 | 12576 |  | 0
| B. |  | 2022-03-23 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13755 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11900 | MW
| 4 | Reserve(Generation end) |  |  |  | 255 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 295.2163 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10247 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2691 | MKWHr. | ii) HVDC Flow at Peak Time |  | 715 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2966 | MKWHr. | iii) Maximum HVDC Flow : |  | 716 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.28 |  | (b) Today: | 86.94 |  | (c) Rule Curve: |  | 89.64
.

## YesterdayGen
2022-03-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 270 | 91 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 190 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 0 | 32 | 0 | 0 | 0 |  | 18 | 0 | 0 | 50 | 0 | 50 | 0 | 39 | 0 | 0 | 0 | 270 | 275 | 184 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 33 | 43 | 19 | 11 | 33 | 21 | 134 | 86 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 265 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 22 | 11 | 80 | 298 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 200 | 138 | 400 | 109 | 90 | 105 | 0 | 281 | 54 | 110 | 82 | 101 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 89 | 55 |  | 714 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 142 | 0 | 395 | 105 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 550 | 214 | 0 | 0 | 0 | 0 | 54 |  | 7806 | 3375 | 11181 | 3695 | 714 | 1722 | 80 | 3632 | 831 | 70 | 120 | 183 | 134 | 0 | 0 | 87.33
2:00 | 0 | 0 | 200 | 0 | 270 | 93 | 0 | 0 | 0 |  | 0 | 310 | 150 | 0 | 0 | 55 | 194 | 0 | 0 | 0 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 36 | 35 | 0 | 150 | 0 | 31 | 0 | 0 | 0 |  | 20 | 0 | 0 | 10 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 280 | 275 | 185 | 8 | 72 | 29 | 30 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 132 | 86 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 275 | 22 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 17 | 142 | 400 | 108 | 90 | 105 | 0 | 265 | 54 | 110 | 34 | 101 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 25 | 55 |  | 713 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 137 | 0 | 414 | 105 | 0 | 113 | 0 | 103 | 0 | 0 | 113 | 520 | 224 | 0 | 0 | 0 | 0 | 17 |  | 7300 | 3331 | 10631 | 3711 | 713 | 1779 | 0 | 3189 | 801 | 71 | 120 | 115 | 132 | 0 | 0 | 87.32
3:00 | 0 | 0 | 200 | 0 | 270 | 95 | 0 | 0 | 0 |  | 0 | 320 | 150 | 0 | 0 | 15 | 200 | 0 | 0 | 0 | 50 | 84 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 36 | 35 | 0 | 150 | 0 | 31 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 0 | 39 | 0 | 0 | 0 | 290 | 285 | 193 | 8 | 72 | 29 | 30 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 126 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 142 | 0 | 90 | 0 | 132 | 401 | 108 | 51 | 105 | 0 | 265 | 54 | 110 | 2 | 99 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 137 | 0 | 414 | 105 | 0 | 113 | 0 | 110 | 0 | 0 | 70 | 520 | 202 | 0 | 0 | 0 | 0 | 17 |  | 6963 | 3258 | 10221 | 3778 | 714 | 1792 | 0 | 2735 | 801 | 71 | 120 | 84 | 126 | 0 | 0 | 87.31
4:00 | 0 | 0 | 200 | 0 | 270 | 96 | 0 | 0 | 0 |  | 0 | 320 | 150 | 0 | 0 | 15 | 209 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 33 | 33 | 34 | 0 | 35 | 35 | 0 | 150 | 0 | 31 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 39 | 0 | 0 | 0 | 285 | 275 | 188 | 8 | 72 | 29 | 30 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 30 | 21 | 122 | 98 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 124 | 0 | 90 | 0 | 130 | 401 | 109 | 0 | 105 | 0 | 265 | 54 | 110 | 0 | 102 | 100 | 400 | 92 | 0 | 141 | 113 | 0 | 17 | 0 | 0 | 55 |  | 713 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 137 | 0 | 420 | 105 | 0 | 113 | 0 | 35 | 0 | 0 | 70 | 520 | 182 | 0 | 0 | 0 | 0 | 17 |  | 6738 | 3156 | 9894 | 3763 | 713 | 1778 | 0 | 2463 | 801 | 70 | 120 | 64 | 122 | 0 | 0 | 87.3
5:00 | 0 | 0 | 200 | 0 | 270 | 99 | 0 | 0 | 0 |  | 0 | 320 | 150 | 0 | 0 | 15 | 215 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 34 | 0 | 33 | 35 | 0 | 150 | 0 | 30 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 34 | 0 | 0 | 0 | 275 | 275 | 183 | 8 | 72 | 26 | 30 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 30 | 21 | 116 | 101 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 268 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 285 | 22 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 100 | 0 | 90 | 0 | 139 | 397 | 109 | 0 | 97 | 0 | 265 | 47 | 110 | 0 | 102 | 100 | 345 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 138 | 0 | 383 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 520 | 150 | 0 | 0 | 0 | 0 | 17 |  | 6600 | 3083 | 9683 | 3697 | 714 | 1698 | 0 | 2406 | 800 | 68 | 120 | 64 | 116 | 0 | 0 | 87.29
6:00 | 0 | 0 | 200 | 0 | 270 | 99 | 0 | 0 | 0 |  | 0 | 320 | 150 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 22 | 33 | 33 | 34 | 0 | 33 | 35 | 0 | 150 | 0 | 60 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 0 | 0 | 280 | 275 | 183 | 8 | 72 | 26 | 57 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 30 | 21 | 114 | 98 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 265 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 23 | 11 | 0 | 45 | 0 | 0 | 184 | 0 | 102 | 0 | 90 | 0 | 140 | 363 | 109 | 0 | 105 | 0 | 265 | 35 | 110 | 0 | 107 | 100 | 360 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 49 |  | 714 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 138 | 0 | 383 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 520 | 150 | 0 | 0 | 0 | 0 | 17 |  | 6613 | 3087 | 9700 | 3711 | 714 | 1715 | 0 | 2395 | 799 | 68 | 120 | 64 | 114 | 0 | 0 | 87.28
7:00 | 0 | 0 | 199 | 0 | 270 | 99 | 0 | 0 | 0 |  | 0 | 310 | 150 | 0 | 0 | 15 | 221 | 0 | 0 | 0 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 22 | 33 | 33 | 34 | 0 | 35 | 35 | 0 | 150 | 0 | 141 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 12 | 0 | 37 | 0 | 0 | 0 | 310 | 305 | 203 | 8 | 72 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 30 | 21 | 112 | 98 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 268 | 30 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 184 | 0 | 105 | 1 | 90 | 0 | 138 | 363 | 109 | 45 | 105 | 0 | 264 | 35 | 110 | 0 | 106 | 50 | 250 | 91 | 4 | 144 | 113 | 0 | 17 | 2 | 1 | 55 |  | 714 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 66 | 0 | 200 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 134 | 0 | 383 | 105 | 0 | 113 | 0 | 72 | 0 | 0 | 70 | 520 | 150 | 0 | 0 | 0 | 9 | 17 |  | 6694 | 3126 | 9820 | 3763 | 714 | 1722 | 0 | 2453 | 786 | 70 | 120 | 64 | 112 | 16 | 0 | 87.27
8:00 | 0 | 0 | 200 | 0 | 270 | 98 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 22 | 33 | 33 | 0 | 0 | 35 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 12 | 0 | 11 | 0 | 0 | 0 | 275 | 275 | 183 | 8 | 73 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 16 | 11 | 30 | 21 | 112 | 89 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 84 | 0 | 0 | 191 | 0 | 116 | 5 | 90 | 15 | 127 | 362 | 109 | 66 | 105 | 1 | 264 | 35 | 110 | 51 | 107 | 50 | 280 | 91 | 13 | 144 | 113 | 0 | 17 | 7 | 24 | 55 |  | 716 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 129 | 0 | 382 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 95 | 520 | 152 | 0 | 0 | 0 | 31 | 52 |  | 6796 | 3269 | 10065 | 3716 | 716 | 1675 | 0 | 2735 | 800 | 70 | 120 | 64 | 112 | 57 | 0 | 87.26
9:00 | 0 | 0 | 200 | 0 | 270 | 97 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 30 | 223 | 0 | 0 | 0 | 66 | 84 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 23 | 33 | 33 | 36 | 0 | 35 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 12 | 0 | 10 | 0 | 0 | 0 | 290 | 290 | 219 | 8 | 72 | 26 | 53 | 0 | 51 | 0 | 0 | 43 | 16 | 11 | 30 | 20 | 118 | 81 | 0 | 17 | 1 | 30 | 30 | 50 | 0 | 0 | 268 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 174 | 0 | 116 | 14 | 90 | 17 | 135 | 364 | 108 | 70 | 105 | 3 | 264 | 35 | 110 | 51 | 107 | 60 | 400 | 91 | 25 | 144 | 113 | 0 | 17 | 9 | 51 | 55 |  | 714 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 134 | 0 | 384 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 95 | 520 | 152 | 0 | 0 | 1 | 45 | 72 |  | 7240 | 3322 | 10562 | 3907 | 714 | 1680 | 0 | 2972 | 799 | 70 | 120 | 84 | 118 | 98 | 0 | 87.25
10:00 | 0 | 0 | 200 | 0 | 270 | 97 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 30 | 222 | 0 | 0 | 0 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 29 | 33 | 33 | 50 | 0 | 35 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 31 | 0 | 10 | 0 | 0 | 0 | 280 | 275 | 217 | 8 | 72 | 26 | 51 | 0 | 51 | 0 | 0 | 43 | 16 | 11 | 28 | 20 | 126 | 71 | 0 | 17 | 1 | 30 | 30 | 47 | 0 | 0 | 269 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 250 | 0 | 0 | 174 | 0 | 117 | 10 | 90 | 17 | 140 | 364 | 108 | 70 | 105 | 4 | 270 | 35 | 110 | 51 | 102 | 90 | 400 | 91 | 34 | 144 | 95 | 0 | 17 | 25 | 51 | 55 |  | 715 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 52 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 158 | 0 | 383 | 105 | 0 | 74 | 0 | 100 | 0 | 2 | 95 | 520 | 132 | 0 | 0 | 4 | 74 | 72 |  | 7407 | 3354 | 10761 | 3889 | 715 | 1632 | 0 | 3077 | 799 | 70 | 120 | 179 | 126 | 154 | 0 | 87.24
11:00 | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 30 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 20 | 55 | 22 | 25 | 29 | 33 | 33 | 50 | 0 | 35 | 35 | 0 | 150 | 0 | 149 | 0 | 0 | 0 |  | 22 | 0 | 0 | 46 | 0 | 44 | 0 | 6 | 0 | 0 | 0 | 330 | 330 | 201 | 8 | 72 | 26 | 50 | 0 | 51 | 0 | 33 | 43 | 19 | 11 | 21 | 20 | 134 | 70 | 0 | 17 | 1 | 30 | 30 | 47 | 0 | 0 | 260 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 280 | 15 | 11 | 0 | 275 | 0 | 0 | 174 | 0 | 116 | 11 | 90 | 25 | 140 | 404 | 108 | 70 | 105 | 5 | 281 | 35 | 110 | 60 | 98 | 77 | 382 | 91 | 38 | 144 | 113 | 0 | 17 | 30 | 73 | 10 |  | 713 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 43 | 5 | 62 | 0 | 0 | 24 | 25 | 0 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 167 | 0 | 404 | 105 | 0 | 80 | 0 | 97 | 0 | 3 | 95 | 520 | 172 | 0 | 0 | 4 | 88 | 72 |  | 7643 | 3505 | 11148 | 3968 | 713 | 1703 | 0 | 3143 | 800 | 70 | 120 | 317 | 134 | 180 | 0 | 87.23
12:00 | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 43 | 217 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 50 | 0 | 36 | 35 | 0 | 150 | 12 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 48 | 0 | 5 | 0 | 0 | 0 | 290 | 290 | 152 | 8 | 136 | 26 | 51 | 0 | 51 | 0 | 36 | 41 | 19 | 11 | 25 | 21 | 142 | 68 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 264 | 55 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 14 | 8 | 20 | 275 | 129 | 100 | 173 | 97 | 114 | 15 | 90 | 129 | 140 | 403 | 108 | 70 | 105 | 5 | 281 | 35 | 110 | 80 | 99 | 77 | 400 | 91 | 38 | 144 | 113 | 0 | 20 | 32 | 96 | 25 |  | 712 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 34 | 6 | 54 | 0 | 0 | 24 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 3 | 162 | 0 | 393 | 105 | 0 | 93 | 0 | 96 | 0 | 5 | 95 | 520 | 190 | 0 | 0 | 4 | 93 | 100 |  | 8222 | 3551 | 11773 | 3885 | 712 | 1729 | 349 | 3469 | 798 | 71 | 120 | 304 | 142 | 194 | 0 | 87.22
13:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 50 | 0 | 35 | 35 | 0 | 150 | 17 | 140 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 280 | 260 | 147 | 8 | 136 | 26 | 51 | 0 | 51 | 0 | 35 | 33 | 19 | 11 | 25 | 21 | 144 | 68 | 0 | 17 | 2 | 30 | 30 | 44 | 0 | 0 | 265 | 55 | 85 | 0 | 0 | 0 | 0 | 10 | 275 | 14 | 8 | 50 | 275 | 30 | 100 | 182 | 100 | 116 | 7 | 90 | 200 | 138 | 404 | 108 | 70 | 105 | 4 | 281 | 35 | 110 | 80 | 105 | 77 | 375 | 91 | 41 | 144 | 113 | 0 | 35 | 30 | 98 | 37 |  | 713 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 34 | 15 | 52 | 0 | 0 | 25 | 52 | 0 | 17 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 58 | 162 | 0 | 391 | 105 | 100 | 109 | 0 | 95 | 0 | 6 | 95 | 520 | 213 | 0 | 0 | 5 | 89 | 115 |  | 8184 | 3767 | 11951 | 3821 | 713 | 1713 | 438 | 3637 | 800 | 70 | 120 | 311 | 144 | 184 | 0 | 87.21
14:00 | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 212 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 50 | 0 | 35 | 35 | 0 | 150 | 23 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 33 | 0 | 8 | 0 | 0 | 0 | 270 | 260 | 168 | 8 | 137 | 29 | 49 | 0 | 51 | 0 | 41 | 38 | 19 | 11 | 16 | 21 | 152 | 71 | 0 | 0 | 2 | 30 | 30 | 47 | 0 | 0 | 259 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 285 | 14 | 8 | 20 | 280 | 33 | 70 | 189 | 70 | 115 | 12 | 90 | 200 | 142 | 406 | 108 | 70 | 105 | 4 | 281 | 35 | 110 | 80 | 105 | 100 | 385 | 80 | 34 | 144 | 113 | 0 | 35 | 2 | 98 | 55 |  | 712 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 0 | 0 | 0 | 0 | 34 | 25 | 52 | 0 | 0 | 27 | 52 | 0 | 16 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 10 | 157 | 0 | 381 | 105 | 20 | 112 | 0 | 97 | 0 | 4 | 95 | 500 | 219 | 0 | 0 | 5 | 79 | 115 |  | 8111 | 3630 | 11741 | 3809 | 712 | 1722 | 223 | 3681 | 781 | 70 | 120 | 329 | 152 | 142 | 0 | 87.2
15:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 212 | 0 | 0 | 0 | 93 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 70 | 35 | 0 | 150 | 25 | 132 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 30 | 0 | 3 | 0 | 0 | 0 | 270 | 260 | 202 | 8 | 137 | 26 | 30 | 0 | 51 | 0 | 41 | 40 | 19 | 11 | 31 | 21 | 152 | 69 | 0 | 0 | 1 | 30 | 30 | 44 | 0 | 0 | 264 | 55 | 83 | 0 | 0 | 0 | 0 | 10 | 290 | 13 | 8 | 20 | 293 | 102 | 100 | 180 | 100 | 116 | 6 | 90 | 200 | 142 | 403 | 107 | 70 | 105 | 3 | 281 | 35 | 110 | 80 | 104 | 90 | 388 | 72 | 29 | 144 | 113 | 0 | 35 | 20 | 98 | 55 |  | 713 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 34 | 24 | 52 | 0 | 0 | 32 | 52 | 0 | 16 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 45 | 154 | 0 | 382 | 100 | 40 | 112 | 0 | 100 | 0 | 3 | 95 | 500 | 216 | 0 | 0 | 4 | 62 | 115 |  | 8223 | 3672 | 11895 | 3860 | 713 | 1685 | 407 | 3615 | 780 | 105 | 120 | 330 | 152 | 128 | 0 | 87.19
16:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 209 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 45 | 0 | 70 | 35 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 8 | 0 | 92 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 270 | 260 | 204 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 41 | 40 | 19 | 11 | 1 | 21 | 150 | 70 | 0 | 0 | 1 | 30 | 30 | 44 | 0 | 0 | 264 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 13 | 8 | 20 | 293 | 108 | 100 | 179 | 99 | 115 | 5 | 90 | 200 | 140 | 406 | 107 | 52 | 98 | 2 | 281 | 35 | 110 | 80 | 105 | 72 | 384 | 72 | 18 | 144 | 113 | 0 | 35 | 12 | 94 | 46 |  | 713 | 0 | 220 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 34 | 22 | 52 | 0 | 0 | 32 | 52 | 28 | 16 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 70 | 151 | 0 | 388 | 94 | 40 | 113 | 0 | 100 | 0 | 2 | 95 | 500 | 215 | 0 | 0 | 2 | 39 | 115 |  | 8199 | 3740 | 11939 | 3864 | 713 | 1693 | 437 | 3616 | 778 | 105 | 135 | 367 | 150 | 81 | 0 | 87.17
17:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 270 | 150 | 0 | 0 | 55 | 211 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 8 | 0 | 92 | 0 | 50 | 0 | 9 | 0 | 0 | 0 | 270 | 260 | 208 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 32 | 21 | 150 | 84 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 267 | 56 | 85 | 0 | 0 | 0 | 0 | 10 | 290 | 13 | 8 | 40 | 293 | 106 | 80 | 169 | 50 | 115 | 3 | 90 | 200 | 142 | 404 | 106 | 70 | 105 | 1 | 281 | 35 | 110 | 80 | 105 | 82 | 393 | 72 | 6 | 144 | 113 | 0 | 35 | 5 | 75 | 42 |  | 711 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 34 | 34 | 52 | 0 | 0 | 32 | 52 | 28 | 16 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 151 | 0 | 391 | 105 | 0 | 113 | 0 | 105 | 0 | 1 | 95 | 500 | 185 | 0 | 0 | 1 | 16 | 115 |  | 8185 | 3631 | 11816 | 3953 | 711 | 1664 | 276 | 3642 | 779 | 70 | 160 | 378 | 150 | 33 | 0 | 87.15
18:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 196 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 148 | 0 | 0 | 0 |  | 22 | 8 | 0 | 100 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 212 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 30 | 21 | 144 | 81 | 0 | 17 | 0 | 30 | 30 | 45 | 0 | 0 | 263 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 280 | 13 | 8 | 50 | 293 | 106 | 30 | 178 | 30 | 115 | 0 | 90 | 200 | 140 | 400 | 107 | 70 | 105 | 0 | 281 | 35 | 110 | 80 | 105 | 100 | 386 | 80 | 0 | 144 | 113 | 0 | 35 | 0 | 79 | 51 |  | 714 | 0 | 220 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 63 | 23 | 0 | 0 | 0 | 0 | 34 | 39 | 90 | 0 | 0 | 32 | 52 | 32 | 17 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 150 | 0 | 380 | 105 | 0 | 113 | 0 | 109 | 0 | 0 | 95 | 500 | 162 | 0 | 0 | 0 | 1 | 115 |  | 8121 | 3575 | 11696 | 3935 | 714 | 1602 | 216 | 3701 | 778 | 70 | 110 | 425 | 144 | 1 | 0 | 87.13
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 215 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 8 | 51 | 100 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 270 | 260 | 213 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 31 | 21 | 168 | 84 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 268 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 15 | 0 | 200 | 293 | 256 | 100 | 180 | 100 | 115 | 0 | 90 | 200 | 142 | 402 | 107 | 70 | 105 | 0 | 281 | 35 | 110 | 99 | 108 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 87 | 10 |  | 713 | 0 | 235 | 0 | 0 | 155 | 0 | 0 | 40 | 15 | 0 | 65 | 19 | 32 | 0 | 0 | 0 | 34 | 39 | 90 | 0 | 0 | 40 | 52 | 32 | 17 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 78 | 150 | 0 | 414 | 105 | 177 | 113 | 32 | 110 | 0 | 0 | 95 | 540 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8688 | 4146 | 12834 | 3974 | 713 | 1716 | 911 | 3770 | 818 | 70 | 155 | 539 | 168 | 0 | 0 | 87.07
19:30 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 250 | 150 | 0 | 0 | 55 | 216 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 8 | 51 | 100 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 270 | 260 | 216 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 38 | 43 | 19 | 11 | 32 | 21 | 160 | 84 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 270 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 15 | 5 | 200 | 297 | 305 | 100 | 181 | 100 | 116 | 0 | 90 | 200 | 142 | 402 | 107 | 70 | 105 | 0 | 281 | 35 | 110 | 99 | 106 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 98 | 55 |  | 713 | 0 | 235 | 0 | 0 | 155 | 0 | 0 | 40 | 15 | 0 | 65 | 28 | 32 | 0 | 0 | 0 | 34 | 42 | 90 | 0 | 34 | 40 | 52 | 34 | 17 | 0 | 8 | 79 | 0 | 200 | 15 | 0 | 0 | 0 | 133 | 0 | 0 | 100 | 151 | 0 | 414 | 105 | 179 | 113 | 1 | 110 | 0 | 0 | 95 | 600 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8773 | 4264 | 13037 | 3986 | 713 | 1699 | 984 | 3834 | 879 | 70 | 170 | 542 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 250 | 95 | 0 | 0 | 0 |  | 0 | 250 | 150 | 0 | 0 | 55 | 206 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 8 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 18 | 51 | 100 | 0 | 50 | 0 | 17 | 0 | 0 | 0 | 270 | 260 | 215 | 8 | 136 | 29 | 30 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 32 | 21 | 152 | 84 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 15 | 5 | 200 | 297 | 305 | 100 | 180 | 99 | 115 | 0 | 90 | 200 | 143 | 402 | 108 | 70 | 105 | 0 | 287 | 46 | 110 | 99 | 109 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 96 | 55 |  | 714 | 0 | 235 | 0 | 0 | 155 | 0 | 0 | 40 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 34 | 42 | 90 | 0 | 43 | 32 | 52 | 31 | 18 | 0 | 11 | 79 | 0 | 200 | 17 | 10 | 0 | 0 | 133 | 0 | 0 | 100 | 155 | 0 | 414 | 105 | 178 | 113 | 0 | 110 | 0 | 0 | 95 | 610 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8773 | 4245 | 13018 | 3960 | 714 | 1711 | 982 | 3828 | 889 | 70 | 182 | 530 | 152 | 0 | 0 | 87.09
21:00 | 0 | 0 | 200 | 0 | 250 | 95 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 20 | 24 | 51 | 100 | 0 | 45 | 0 | 26 | 0 | 0 | 0 | 270 | 260 | 217 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 160 | 81 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 279 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 200 | 296 | 306 | 100 | 180 | 99 | 116 | 0 | 90 | 200 | 147 | 404 | 108 | 70 | 105 | 0 | 290 | 54 | 110 | 99 | 105 | 100 | 396 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 97 | 55 |  | 715 | 0 | 235 | 0 | 0 | 155 | 0 | 0 | 35 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 34 | 36 | 90 | 0 | 43 | 32 | 52 | 31 | 18 | 0 | 11 | 81 | 0 | 200 | 17 | 0 | 0 | 0 | 135 | 0 | 0 | 100 | 162 | 0 | 414 | 105 | 177 | 113 | 0 | 110 | 0 | 0 | 95 | 650 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8820 | 4276 | 13096 | 4008 | 715 | 1721 | 982 | 3813 | 931 | 70 | 172 | 524 | 160 | 0 | 0 | 87.07
22:00 | 0 | 0 | 200 | 0 | 250 | 96 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 218 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 140 | 0 | 0 | 0 |  | 18 | 24 | 51 | 100 | 0 | 44 | 0 | 32 | 0 | 0 | 0 | 270 | 260 | 213 | 8 | 136 | 29 | 30 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 33 | 21 | 162 | 82 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 5 | 200 | 296 | 197 | 100 | 180 | 100 | 130 | 0 | 90 | 200 | 145 | 403 | 108 | 70 | 105 | 0 | 287 | 54 | 110 | 99 | 112 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 99 | 55 |  | 715 | 0 | 240 | 0 | 0 | 156 | 0 | 0 | 39 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 34 | 36 | 90 | 0 | 34 | 32 | 52 | 32 | 18 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 20 | 163 | 0 | 414 | 105 | 175 | 113 | 0 | 110 | 0 | 0 | 95 | 620 | 214 | 0 | 0 | 0 | 0 | 115 |  | 8728 | 4140 | 12868 | 4017 | 715 | 1712 | 792 | 3819 | 895 | 70 | 156 | 530 | 162 | 0 | 0 | 87.07
23:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 218 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 71 | 0 | 0 | 150 | 25 | 127 | 0 | 0 | 0 |  | 18 | 16 | 34 | 100 | 0 | 44 | 0 | 35 | 0 | 0 | 0 | 270 | 260 | 219 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 154 | 82 | 0 | 17 | 0 | 30 | 30 | 49 | 0 | 0 | 268 | 58 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 5 | 170 | 296 | 147 | 70 | 180 | 50 | 134 | 0 | 90 | 200 | 143 | 403 | 108 | 70 | 105 | 0 | 282 | 54 | 110 | 99 | 113 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 100 | 55 |  | 714 | 0 | 240 | 0 | 0 | 157 | 0 | 0 | 33 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 34 | 36 | 90 | 0 | 34 | 37 | 52 | 31 | 18 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 20 | 157 | 0 | 414 | 94 | 60 | 113 | 0 | 110 | 0 | 0 | 95 | 590 | 224 | 0 | 0 | 0 | 0 | 115 |  | 8559 | 3996 | 12555 | 4016 | 714 | 1725 | 517 | 3827 | 872 | 71 | 157 | 502 | 154 | 0 | 0 | 87.03
24:00 | 0 | 0 | 200 | 0 | 250 | 98 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 224 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 71 | 0 | 0 | 150 | 25 | 132 | 0 | 0 | 0 |  | 20 | 0 | 34 | 90 | 0 | 45 | 0 | 38 | 0 | 0 | 0 | 270 | 260 | 219 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 33 | 21 | 142 | 84 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 58 | 89 | 0 | 0 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 298 | 74 | 40 | 190 | 25 | 134 | 0 | 90 | 200 | 150 | 403 | 108 | 70 | 105 | 0 | 290 | 54 | 110 | 99 | 110 | 100 | 400 | 92 | 0 | 144 | 113 | 0 | 35 | 0 | 94 | 55 |  | 711 | 0 | 240 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 34 | 34 | 90 | 0 | 34 | 32 | 52 | 31 | 18 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 149 | 0 | 414 | 94 | 20 | 113 | 0 | 110 | 0 | 0 | 95 | 570 | 202 | 0 | 0 | 0 | 0 | 115 |  | 8278 | 3845 | 12123 | 4028 | 711 | 1720 | 159 | 3839 | 848 | 71 | 158 | 447 | 142 | 0 | 0 | 87.01
KWH | 0 | 0 | 4808000 | 0 | 6174682 | 2284318 | 0 | 0 | 0 |  | 0 | 6672500 | 3560902 | 0 | 0 | 1054492 | 5180857 | 0 | 0 | 0 | 1819872 | 3048480 | 0 | 0 | 0 | 0 | 1307520 | 842788 | 1252397 | 463392 | 600000 | 583920 | 813400 | 784400 | 1024800 | 0 | 1187362 | 568000 | 0 | 3600000 | 316776 | 2425454 | 0 | 0 | 0 |  | 514560 | 105152 | 328730 | 1356480 | 0 | 924000 | 0 | 484320 | 0 | 0 | 0 | 7100000 | 6764000 | 4793000 | 217454 | 2510700 | 640728 | 985920 | 0 | 1174026 | 0 | 593160 | 1025784 | 441756 | 234180 | 722100 | 522220 | 3296640 | 1932480 | 0 | 342504 | 11700 | 717000 | 697200 | 1163400 | 0 | 0 | 6058000 | 1409856 | 2106240 | 0 | 0 | 0 | 0 | 243000 | 7070500 | 413472 | 190800 | 1340928 | 5607816 | 2019075 | 1088642 | 4334400 | 10355227 | 2909660 | 87345 | 2105280 | 2946720 | 3362182 | 9446000 | 2546400 | 1494000 | 2524981 | 31320 | 6583855 | 1057213 | 2676352 | 1475160 | 2527560 | 2154240 | 9105000 | 2117760 | 282080 | 3493440 | 2693509 | 0 | 667080 | 199532 | 1553280 | 1200240 |  | 17269090 | 0 | 5668992 | 0 | 0 | 3247680 | 0 | 0 | 204000 | 18176 | 0 | 609000 | 578200 | 43200 | 0 | 0 | 0 | 477200 | 370638 | 1054680 | 0 | 183264 | 402260 | 970560 | 284529 | 406560 | 0 | 232290 | 1866763 | 0 | 4869200 | 25000 | 1200 | 0 | 0 | 3674364 | 0 | 0 | 649920 | 3823345 | 0 | 9538727 | 2570880 | 992262 | 2647296 | 36144 | 2249049 | 0 | 29854 | 2220768 | 14485300 | 4639936 | 0 | 0 | 31920 | 636480 | 1921335 |  | 197451651 | 88930062 | 286381713 | 93483092 | 17269090 | 41126003 | 16446054 | 80313093 | 21221263 | 1755362 | 3273880 | 6887005 | 3296640 | 1310231 | 0
Fuel Cost | 0 | 0 | 7019680 | 0 | 6853897.02 | 3015299.76 | 0 | 0 | 0 |  | 0 | 7273025 | 3952601.22 | 0 | 0 | 8921002.32 | 5388091.28 | 0 | 0 | 0 | 16597232.64 | 29997043.2 | 0 | 0 | 0 | 0 | 9544896 | 6514751.24 | 12348634.42 | 347544 | 450000 | 0 | 0 | 0 | 9909816 | 0 | 320587.74 | 153360 | 0 | 6516000 | 2942849.04 | 2643744.86 | 0 | 0 | 0 |  | 0 | 1016819.84 | 3188681 | 12954384 | 0 | 7318080 | 0 | 1438430.4 | 0 | 0 | 0 | 5254000 | 6764000 | 4409560 | 280515.66 | 2887305 | 724022.64 | 1380288 | 0 | 2007584.46 | 0 | 5990916 | 9796237.2 | 561030.12 | 175635 | 1263675 | 391665 | 24724800 | 2048428.8 | 0 | 434980.08 | 186498 | 1175880 | 1115520 | 2070852 | 0 | 0 | 6300320 | 2777416.32 | 4022918.4 | 0 | 0 | 0 | 0 | 495720 | 7141205 | 310104 | 145008 | 22809185.28 | 42395088.96 | 34283893.5 | 18202094.24 | 22538880 | 173139395.44 | 28631054.4 | 1021063.05 | 17158032 | 31971912 | 23703383.1 | 8784780 | 23223168 | 14118300 | 21992584.51 | 0 | 49773943.8 | 9208325.23 | 23525134.08 | 14722096.8 | 21661189.2 | 14347238.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99469958.4 | 0 | 5952441.6 | 0 | 0 | 45012844.8 | 0 | 0 | 2139960 | 190484.48 | 0 | 688170 | 896210 | 421632 | 0 | 0 | 0 | 4695648 | 3765682.08 | 9333918 | 0 | 2477729.28 | 3897899.4 | 9404726.4 | 2759931.3 | 780595.2 | 0 | 175843.53 | 11256580.89 | 0 | 26391064 | 866250 | 34236 | 0 | 0 | 4850160.48 | 0 | 0 | 11055139.2 | 4473313.65 | 0 | 9443339.73 | 26839987.2 | 16878376.62 | 25122839.04 | 341199.36 | 17452620.24 | 0 | 329886.7 | 16411475.52 | 63590467 | 0 | 0 | 0 | 0 | 0 | 0 |  | 878673277.65 | 427400610.1 | 1306073887.75 | 90882216.38 | 99469958.4 | 44198584.83 | 276368084.28 | 554290422.38 | 101238111.89 | 473947.74 | 45913330.8 | 66976983.3 | 24724800 | 1537447.75 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 43 | 217 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 50 | 0 | 36 | 35 | 0 | 150 | 12 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 48 | 0 | 5 | 0 | 0 | 0 | 290 | 290 | 152 | 8 | 136 | 26 | 51 | 0 | 51 | 0 | 36 | 41 | 19 | 11 | 25 | 21 | 142 | 68 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 264 | 55 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 14 | 8 | 20 | 275 | 129 | 100 | 173 | 97 | 114 | 15 | 90 | 129 | 140 | 403 | 108 | 70 | 105 | 5 | 281 | 35 | 110 | 80 | 99 | 77 | 400 | 91 | 38 | 144 | 113 | 0 | 20 | 32 | 96 | 25 |  | 712 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 34 | 6 | 54 | 0 | 0 | 24 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 3 | 162 | 0 | 393 | 105 | 0 | 93 | 0 | 96 | 0 | 5 | 95 | 520 | 190 | 0 | 0 | 4 | 93 | 100 |  | 11773 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 250 | 95 | 0 | 0 | 0 | 0 | 0 | 240 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 | 0 | 20 | 24 | 51 | 100 | 0 | 45 | 0 | 26 | 0 | 0 | 0 | 270 | 260 | 217 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 160 | 81 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 279 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 200 | 296 | 306 | 100 | 180 | 99 | 116 | 0 | 90 | 200 | 147 | 404 | 108 | 70 | 105 | 0 | 290 | 54 | 110 | 99 | 105 | 100 | 396 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 97 | 55 |  | 715 | 0 | 235 | 0 | 0 | 155 | 0 | 0 | 35 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 34 | 36 | 90 | 0 | 43 | 32 | 52 | 31 | 18 | 0 | 11 | 81 | 0 | 200 | 17 | 0 | 0 | 0 | 135 | 0 | 0 | 100 | 162 | 0 | 414 | 105 | 177 | 113 | 0 | 110 | 0 | 0 | 95 | 650 | 220 | 0 | 0 | 0 | 0 | 115 |  | 13096 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 | 0 | 0 | 240 | 150 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 | 0 | 22 | 24 | 51 | 100 | 0 | 50 | 0 | 25 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 137 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 22 | 163 | 100 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 280 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 133 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 99 | 113 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 |  | 100 | 55 |  | 729 | 0 | 300 | 0 | 0 | 225 | 0 | 0 | 40 | 30 | 0 | 65 | 30 | 80 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 43 | 40 | 52 | 31 | 22 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 100 | 180 | 0 | 414 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 95 | 660 | 220 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 200 | 0 | 250 | 100 | 0 | 0 | 0 | 0 | 0 | 240 | 150 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 130 | 29 | 55 | 0 | 51 | 0 | 32 | 43 | 22 | 11 | 33 | 22 | 138 | 80 | 0 | 17 | 1.6 | 30 | 30 | 50 | 0 | 0 | 265 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 133 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 90 | 50 | 144 | 113 | 0 | 35 | 30 | 100 | 55 |  | 729 | 0 | 300 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 42 | 0 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 414 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 95 | 660 | 180 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 | 0 | 0 | 240 | 150 | 0 | 0 | 33 | 180 | 0 | 0 | 0 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 36 | 0 | 69 | 0 | 0 | 150 | 0 | 130 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 70 | 0 | 37 | 0 | 11 | 0 | 0 | 0 | 270 | 305 | 219 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 15 | 20 | 124 | 104 | 0 | 17 | 1 | 30 | 30 | 49 | 0 | 0 | 266 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 215 | 0 | 0 | 193 | 0 | 133 | 6 | 90 | 37 | 142 | 381 | 109 | 70 | 105 | 1 | 300 | 35 | 110 | 99 | 106 | 100 | 170 | 91 | 14 | 144 | 113 | 0 | 35 | 11 | 32 | 55 | 0 | 711 | 0 | 250 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 142 | 0 | 370 | 94 | 0 | 113 | 0 | 103 | 0 | 1 | 95 | 460 | 173 | 0 | 0 | 1 | 30 | 115 | 0
199
| Minimum Generation |  | 9683 | 5:00
| Highest Generation |  | 13096 | 21:00
| Day Peak Generation |  | 11773 | 12:00
| Evening Peak Generation |  | 13096 | 21:00
| HVDC Max Flow |  | 716 | 8:00
| HVDC EvPeak Flow |  | 715 | 21:00
| Load factor L.F |  | 91.12%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-23
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11773 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 10247 | MW
Evening Peak Generation : |  | 13096 | MW Hour : | 21:00 | Available Max Generation : |  | 13755 | MW
E.P. Demand (at gen end) : |  | 13096 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13096 | MW Hour : | 21:00 | Reserve(Generation end) |  | 255 | MW
Total Gen. (MKWH) : |  | 286.3817 | System Load Factor : | 91.12% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -20 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-23
Actual : | 86.94 | Ft.(MSL) , | Rule curve : | 89.64 | Ft.( MSL )
Gas Consumed : | Total = | 1072.12 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 135080801.21
: |  | Coal : | 101238111.89 | Oil : | 943548820.76 | Total : | 1179867733.86
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4814.7554 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1643.5677 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1473.702 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1332.0117 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1203.5004 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 971.1981 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 534.9591 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 249.8434 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 749.0749 |  |  | 0 | 0%
Total | 0 |  | 12972.6128 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-100 MW & 71 MW
5) Raozan unit- 1
6) Kushiara 163 MW.
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mirpur-Uttara 132 kV Ckt was under shut down from 08:40 to 16:42 for C/M.
b) Benapole-Jashore 132 kV Ckt-1 was under shut down from 08:23 to 16:29 for C/M.
c) Aminbazar-Megnaghat 230 kV Ckt-1 was under shut down from 09:48 to 16:11 for A/M.
d) Faridpur 132 kV bus-A & T-3 transformer were under shut down from 09:34 to 16:38 for C/M.
e) Jhenidah(O)-Jhenidah(N) 132 kV Ckt-1 was under shut down from 09:43 to 10:32 for C/M.
f) Ghorasal 230 kV 953 CB was under shut down from 10:16 to 14:35 for C/M.
g) Ghorasal-Ashuganj 230 kV Ckt-2 tripped at 10:30 due to DC system problem and was switched on at 10:45.
h) Jhenidah-Bottail 132 kV Ckt-1 was under shut down from 10:53 to 11:42 for C/M.
i) Jhenidah 132/33 kV T-2 transformer was under shut down from 12:02 to 13:13 for C/M.
k) Baroaulia-KSRM 132 kV Ckt tripped at 13:09 showing O/C,E/F relays and was switched on at 15:38.
l) Sitakkha 132/33 kV T-1 transformer was under shut down from 13:04 to 15:51 for C/M.
m) Goalpara 132/33 kV T-6 transformer tripped at 13:45 showing differential 3-phase.
n) Pabna-Shahjadpur 132 kV Ckt was under shut down from 13:24 to 13:58 for D/W.
o) Narail 132/33 kV T-1 & T-2 transformer tripped at 18:17 due to CT burst of 33 kV Feeder and were | [5 empty] | About 28 MW power interruption occurred
switched on at 22:35 & 19:25 respectively. | [5 empty] | under Narail S/S from 18:17 to 19:25.
p) B.Baria 132/33 kV T-1 & T-2 transformer tripped at 18:17 due to 33 kV Feeder fault and were switched | [5 empty] | About 120 MW power interruption occurred
on at 17:41. | [5 empty] | under B.Baria S/S from 17:35 to 17:41.
q) Khulna-225 MW CCPP STG tripped at 17:12 due to tripping of 0.4 kV supply CB and was synchronized at 07:12(23/3/22).
r) Payra Unit-2 was shut down at 22:46.
s) Haripur 230/132 kV T-2 transformer was shut down at 22:16 due to red hot maintenance and was
switched on at 00:26(23/3/22).
t) Rampura 230/132 kV T-3 transformer was under shut down from 07:19 to 08:09(23/3/22) for C/M.
u) Jashore-Benapole 132 kV Ckt-2 is under shut down since 07:54(23/3/22) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4808000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6174682 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2284318 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 6672500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3560902 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1054492
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 463392
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 213 | 5180857 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1819872 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1307520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3048480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 842788
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 1252397 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1183920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 813400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1024800 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 5607816
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 306 | 2019075
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 1088642
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 10355227
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 2909660 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1494000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 2117760 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3493440 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 199532
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1200240
| Dhaka area Total |  |  |  | 5696 | 3058 | 72762112
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3600000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 316776
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 87345
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 924000
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1755362 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 131 | 2425454 | ST under S/D
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2524981
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 105152 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 328730 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1356480
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2105280 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 484320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31320
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 290 | 6583855 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1057213
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2676352
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2154240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2693509
| Chattogram area Total |  |  |  | 2382 | 1484 | 31210369
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4793000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7100000
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6764000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 640728 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 985920 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1174026
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 3362182 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 593160 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 2510700 | Gas shortage
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2946720
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 441756 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 234180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3296640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 722100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1025784 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 522220 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1340928
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 1475160 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 2527560 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 667080 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 1553280 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2213 | 44894578
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 81 | 1932480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 342504 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 4334400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2546400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 282080
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 20 | 514560
| Mymensingh Area Total |  |  |  | 622 | 406 | 9964124
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 697200 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 279 | 6058000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1163400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 190800
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1409856
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2106240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 413472
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7070500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9446000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 9105000
| Sylhet Area Total |  |  |  | 2377 | 1659 | 38620468
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 715 | 17269090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 204000 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 155 | 3247680
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 18176 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 5668992 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 649920
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2570880
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 36144 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 636480
| Khulna Area Total |  |  |  | 2229 | 1345 | 30301362
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 43200 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 578200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 609000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 650 | 14485300
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4639936
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 965 | 20355636
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 477200 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 36 | 370638 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 183264 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 402260 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 135 | 3674364 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 3823345 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9538727
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 284529 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 406560 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232290
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 970560
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 1054680 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 177 | 992262
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2647296
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 2220768 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31920
| Rajshahi Area Total |  |  |  | 2129 | 1443 | 27310663
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1866763
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4869200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 25000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 1200
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 2249049
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29854
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1921335
| Rangpur Area Total |  |  |  | 720 | 523 | 10962401
| Total |  |  |  | 21215 | 13096 | 286381713
| Eastern Grid Total |  |  |  | 14091 | 8820 | 197451651
| Western Grid Total |  |  |  | 7124 | 4276 | 88930062
| National Grid Total |  |  |  | 21215 | 13096 | 286381713
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-22
(a) ENTIRE EASTERN GRID : |  | 8499 | MW | (b) ENTIRE WESTERN GRID : |  | 4077 | MW
i) Dhaka area |  | 4617 | MW | i) Khulna area |  | 1470 | MW
ii) Chittagong area |  | 1390 | MW | ii) Rajshahi area |  | 1426 | MW
iii) Comilla area |  | 1100 | MW | iii) Barisal area |  | 336 | MW
iv) Mymensingh area |  | 940 | MW | iv) Rangpur area |  | 845 | MW
v) Sylhet area |  | 452 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12576 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 17:00 | Valuka | 114 | 8:00 | Central S/S | 89 | 21:00
Munsiganj | 94 | 19:00 | Tangail | 199 | 7:00 | Noapara | 44 | 20:00
Sonargaon | 95 | 0:00 | Mymensing | 224 | 18:30 | Jessore | 126 | 20:00
Bhulta | 220 | 23:00 | Kishoreganj | 112 | 1:00 | Benapol | 52 | 21:00
Madanganj | 40 | 15:00 | Netrokona | 126 | 8:00 | Jhenida(Old) | 112 | 21:00
Rahim steel | 28 | 15:00 | Jamalpur | 133 | 8:00 | Bottail | 122 | 20:00
Ghorasal | 82 | 22:00 | Sherpur | 135 | 7:00 | G.K Project | 52 | 21:00
Narsingdi | 177 | 20:00 | Srimongal | 47 | 21:00 | Faridpur | 136 | 19:00
Haripur(SBU) | 104 | 1:00 | Shahjibazar | 114 | 23:00 | Rajbari | 60 | 19:00
Sreenagar | 40 | 20:00 | Fenchuganj | 38 | 18:00 | Madaripur | 95 | 19:30
Shyampur | 204 | 12:00 | Kulawara | 34 | 20:00 | Sariatpur | 56 | 20:00
Shitalakhya | 118 | 12:00 | Sylhet | 144 | 19:00 | Gopalganj | 91 | 19:30
Matuail | 78 | 10:00 | Chatak | 22 | 24:00 | Bagerhat | 93 | 19:00
Char Saidpur | 45 | 23:00 | Sunamganj | 38 | 24:00 | Mongla | 42 | 12:00
Ullon | 47 | 20:00 | Biani Bazar | 49 | 18:30 | Satkhira | 112 | 21:00
Hasnabad | 80 | 19:30 | Comilla (S) | 170 | 18:30 | Gallamari | 54 | 19:00
Magbazar | 114 | 15:00 | Comilla(N) | 148 | 20:00 | Magura | 48 | 19:00
Maniknagar | 70 | 13:00 | Chandpur | 59 | 22:00 | Norail | 28 | 14:00
Bangabhaban | 11 | 11:00 | Feni | 1:00 | 21:00 | Chuadanga | 96 | 21:00
Motijheel | 37 | 13:00 | Chowmuhani | 175 | 22:00 | Barisal(N) | 56 | 18:30
Narinda | 64 | 13:00 | Ashuganj | 38 | 1:00 | Barisal (S) | 92 | 19:30
Kazla | 87 | 18:00 | Daudkandi | 124 | 21:00 | Patuakhali | 101 | 21:00
Dhanmondi | 198 | 13:00 | B.Baria | 158 | 22:00 | Bhandaria | 48 | 19:00
Lalbag | 95 | 12:00 | Ramganj | 74 | 18:30 | Borguna | 14 | 18:30
Madartek | 80 | 22:00 | Chaddagram | 44 | 20:00 | Borhan Uddin | 38 | 20:00
Dhaka University | 40 | 13:00 | PHP | 10 | 19:00 | Ishurdi | 69 | 20:00
Aftabnagar | 30 | 18:00 | Kochua | 58 | 20:00 | Ruppur Paromanobik | 4 | 9:00
Fatullah | 67 | 19:00 | Madunaghat | 55 | 19:00 | Natore | 142 | 21:00
Nawabganj | 47 | 20:00 | Hathazari | 83 | 19:30 | Bogra | 168 | 21:00
Keraniganj | 74 | 19:00 | Khulshi | 189 | 10:00 | Naogaon | 124 | 22:00
Banani | 56 | 15:00 | Halishahar | 88.5 | 15:00 | Rajshahi | 145 | 22:00
Mirpur | 120 | 16:00 | Baraulia | 125 | 2:00 | Rajshahi New | 38 | 1:00
Kalyanpur | 90 | 18:30 | Sikalbaha | 28 | 18:30 | C.Nawabganj | 68 | 22:00
Gulshan | 112 | 15:00 | Dohazari | 78 | 19:00 | Amnura | 65 | 21:00
Uttara | 118 | 13:00 | Cox'sbazar | 106 | 19:30 | Pabna | 67 | 22:00
Uttara New | 32 | 12:00 | Chandraghona | 30 | 19:00 | Shahjadpur | 99 | 20:00
Kamrangirchar | 68 | 18:30 | Kaptai | 0 | 1:00 | Serajganj | 114 | 19:30
Savar | 173 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 105 | 21:00
Bhasantec | 122 | 18:30 | Bakulia | 115 | 18:30 | Joypurhat | 64 | 20:00
Agargaon | 88 | 14:00 | Julda | 28 | 23:00 | Sherpur(Bogura) | 60 | 19:30
Satmosjid | 87 | 18:30 | TK chemical | 26 | 18:00 | Mohastangor | 66 | 19:30
Old Tongi | 124 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 34 | 19:00
Kabirpur | 292 | 18:30 | Shahmirpur | 38.1 | 2:00 | Rangpur | 145 | 19:30
Manikgonj | 101 | 13:00 | Khagrachhari | 24 | 18:30 | Lalmonirhat | 50 | 19:00
Joydevpur | 192 | 18:00 | Matarbari | 39 | 18:30 | Saidpur | 108 | 8:00
New Tongi | 82 | 11:00 | Baroiar Hat | 58 | 19:00 | Purbasadipur | 111 | 20:00
Kodda | 316 | 15:00 | Rangamati | 12 | 18:30 | Thakurgaon | 95 | 19:00
Dhamrai | 90 | 21:00 | Agrabad | 76 | 18:00 | Palashbari | 114 | 19:00
Rajendrapur | 98 | 21:00 | Rampur | 11 | 1:00 | Barapukuria | 58 | 10:00
Bashundara | 93 | 14:00 | Abul Khair 230 | 29 | 15:00 | Panchagar | 67 | 21:00
Purbachal | 18 | 21:00 | BSRM | 156 | 5:00 | Joldhaka | 66 | 19:30
Tongi Millgate | 52 | 17:00 | GPH Ispat | 82 | 6:00 | Kurigram | 66 | 18:30
Bashundhara Cement |  |  | Goalpara | 25 | 19:30 | Mithapukur | 39 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 1:00 | 398 | 13:00 | Kaliakoir | 383 | 0.25 | 362 | 0.58333
| Bheramara | 402 | 1:00 | 394 | 19:30 | Bhulta | 403 | 0.041667 | 389 | 0.66667
| Ashuganj(N) | 409 | 6:00 | 394 | 11:00 | Gopalganj | 410 | 0.625 | 395 | 0.83333
| Payra | 418 | 2:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 239 | 6:00 | 232 | 9:00
| Ishurdi | 236 | 5:00 | 228 | 21:00 | Megnaghat | 232 | 13:00 | 220 | 10:00
| Ashuganj | 240 | 1:00 | 234 | 11:00 | Fenchuganj | 245 | 1:00 | 231 | 15:00
| Serajganj | 236 | 3:00 | 232 | 21:00 | Siddhirganj | 228 | 6:00 | 218 | 15:00
| Baghabari | 235 | 1:00 | 231 | 7:00 | Maniknagar | 227 | 6:00 | 216 | 11:00
| Barapukuria | 232 | 10:00 | 225 | 4:00 | Agargaon | 226 | 5:00 | 213 | 11:00
| Bogra | 231 | 3:00 | 225 | 20:00 | Barisal | 245 | 8:00 | 238 | 21:00
| Rajshahi | 232 | 17:00 | 222 | 21:00 | Bhola 225 MW | 248 | 6:00 | 242 | 21:00
| Khulna South | 239 | 3:00 | 228 | 21:00 | AKSML | 239 | 8:00 | 229 | 11:00
| Rampura | 227 | 1:00 | 217 | 11:00 | BSRM | 236 | 8:00 | 228 | 11:00
| Haripur | 227 | 7:00 | 215 | 11:00 | Bibiyana | 236 | 1:00 | 231 | 6:00
| Hasnabad | 226 | 1:00 | 212 | 11:00 | Bhulta | 229 | 1:00 | 221 | 12:00
| Shyampur | 226 | 2:00 | 214 | 11:00 | Ashuganj (S) | 238 | 1:00 | 231 | 11:00
| Aminbazar | 228 | 1:00 | 215 | 2:00 | Kaliakoir | 226 | 1:00 | 214 | 10:00
| Tongi | 233 | 4:00 | 215 | 11:00 | GPH | 237 | 8:00 | 225 | 5:00
| Comilla (N) | 232 | 1:00 | 225 | 11:00 | Jhenaidah | 235 | 5:00 | 222 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 22:00 | 124 | 11:00 | PHP | 137 | 1:00 | 128 | 16:00
| Munsiganj | 135 | 22:00 | 124 | 11:00 | Kachua | 139 | 23:00 | 132 | 3:00
| Sonargaon | 133 | 19:30 | 125 | 11:00 | Madanhat | 139 | 22:00 | 133 | 12:00
| Bhulta | 128 | 22:00 | 116 | 11:00 | Hathazari | 139 | 6:00 | 135 | 16:00
| Madanganj | 132 | 19:30 | 127 | 10:00 | Khulshi | 137 | 7:00 | 132 | 11:00
| Rahim steel | 134 | 22:00 | 124 | 11:00 | Halishahar | 138 | 7:00 | 131 | 14:00
| Ghorasal | 138 | 1:00 | 135 | 15:00 | Baraulia | 140 | 7:00 | 134 | 16:00
| Narsingdi | 124 | 5:00 | 125 | 14:00 | Sikalbaha | 138 | 1:00 | 133 | 14:00
| Haripur(SBU) | 133 | 20:00 | 124 | 11:00 | Dohazari | 135 | 7:00 | 127 | 14:00
| Sreenagar | 136 | 22:00 | 126 | 10:00 | Cox'sbazar | 129 | 6:00 | 109 | 11:00
| Shyampur | 134 | 22:00 | 123 | 10:00 | Chandraghona | 139 | 7:00 | 135 | 11:00
| Shitalakhya | 136 | 22:00 | 124 | 11:00 | Kaptai | 130 | 1:00 | 127 | 13:00
| Matuail | 134 | 22:00 | 124 | 11:00 | A. Khaer Stl. | 137 | 1:00 | 132 | 14:00
| Char Saidpur | 136 | 22:00 | 124 | 11:00 | Bakulia | 139 | 7:00 | 131 | 15:00
| Ullon | 137 | 20:00 | 124 | 11:00 | Julda | 138 | 8:00 | 133 | 14:00
| Hasnabad | 135 | 19:00 | 125 | 11:00 | TK Chemical | 137 | 7:00 | 133 | 10:00
| Magbazar | 137 | 22:00 | 129 | 10:00 | Modern Steel | 137 | 6:00 | 133 | 15:00
| Maniknagar | 132 | 5:00 | 124 | 11:00 | Shahmirpur | 138 | 7:00 | 133 | 10:00
| Bangabhaban | 132 | 5:00 | 124 | 11:00 | Khagrachhari | 138 | 21:00 | 133 | 11:00
| Motijheel | 132 | 5:00 | 124 | 11:00 | Matarbari | 126 | 19:00 | 115 | 11:00
| Narinda | 132 | 5:00 | 124 | 11:00 | Baroiar Hat | 136 | 8:00 | 129 | 16:00
| Kazla | 132 | 5:00 | 124 | 11:00 | Rangamati | 138 | 7:00 | 134 | 11:00
| Dhanmondi | 134 | 22:00 | 123 | 11:00 | Agrabad | 138 | 7:00 | 132 | 11:00
| Lalbag | 136 | 22:00 | 122 | 11:00 | Rampur | 137 | 7:00 | 132 | 13:00
| Madartek | 136 | 21:00 | 123 | 11:00 | Goalpara S/S | 138 | 5:00 | 132 | 21:00
| Dhaka University | 137 | 22:00 | 124 | 11:00 | Khulna Central S/S | 138 | 5:00 | 132 | 21:00
| Aftabnagar | 137 | 20:00 | 125 | 10:00 | Noapara | 137 | 4:00 | 131 | 18:00
| Fatullah | 134 | 20:00 | 123 | 10:00 | Jessore | 132 | 1:00 | 125 | 21:00
| Nawabganj | 135 | 22:00 | 122 | 11:00 | Benapol | 135 | 3:00 | 126 | 14:00
| Keraniganj | 136 | 22:00 | 123 | 11:00 | Jhenida(Old) | 133 | 2:00 | 125 | 21:00
| Banani | 136 | 20:00 | 123 | 11:00 | Bottail | 136 | 5:00 | 130 | 20:00
| Mirpur | 134 | 1:00 | 131 | 7:00 | G.K Project | 139 | 1:00 | 135 | 21:00
| Kalyanpur | 135 | 3:00 | 127 | 11:00 | Faridpur | 136 | 4:00 | 130 | 19:30
| Gulshan | 136 | 19:30 | 123 | 11:00 | Rajbari | 136 | 5:00 | 128 | 19:30
| Uttara | 134 | 1:00 | 122 | 12:00 | Madaripur | 142 | 5:00 | 134 | 19:30
| Uttara New | 135 | 1:00 | 126 | 11:00 | Shariyatpur S/S | 140 | 4:00 | 133 | 21:00
| Kamrangirchar | 136 | 22:00 | 122 | 11:00 | Gopalganj | 140 | 6:00 | 131 | 20:00
| Savar | 135 | 7:00 | 127 | 18:00 | Bagerhat | 136 | 4:00 | 128 | 20:00
| Bhasantec | 132 | 1:00 | 123 | 11:00 | Mongla | 135 | 3:00 | 128 | 20:00
| Agargaon | 134 | 2:00 | 125 | 11:00 | Satkhira | 136 | 6:00 | 126 | 20:00
| Satmosjid | 136 | 16:00 | 124 | 11:00 | Gallamari | 139 | 6:00 | 130 | 19:30
| Old Tongi | 136 | 1:00 | 126 | 11:00 | Magura | 135 | 4:00 | 124 | 20:00
| Kabirpur | 137 | 2:00 | 125 | 11:00 | Narail | 132 | 5:00 | 123 | 20:00
| Manikgonj | 132 | 3:00 | 126 | 10:00 | Chuadanga | 128 | 6:00 | 115 | 21:00
| Joydevpur | 139 | 1:00 | 133 | 8:00 | Barisal(N) | 143 | 5:00 | 137 | 21:00
| New Tongi | 136 | 2:00 | 125 | 11:00 | Barisal (S) | 143 | 5:00 | 136 | 11:00
| Kodda | 135 | 1:00 | 122 | 11:00 | Patuakhali(S) | 137 | 5:00 | 131 | 20:00
| Dhamrai | 134 | 1:00 | 125 | 11:00 | Bhandaria | 141 | 5:00 | 134 | 19:30
| Rajendrapur | 135 | 2:00 | 119 | 16:00 | Barguna | 139 | 6:00 | 132 | 19:30
| Bashundara | 135 | 1:00 | 123 | 14:00 | Jhenida(New) | 135 | 5:00 | 130 | 11:00
| Purbachal | 137 | 20:00 | 128 | 10:00 | Ishurdi | 137 | 5:00 | 132 | 21:00
| Tongi Millgate | 135 | 1:00 | 127 | 14:00 | Ruppur Paromanobik | 136 | 5:00 | 132 | 21:00
| Bashundhara Cement |  |  |  |  | Natore | 134 | 2:00 | 129 | 21:00
| Valuka | 119 | 7:00 | 108 | 15:00 | Bogra | 135 | 4:00 | 129 | 21:00
| Tangail | 130 | 4:00 | 123 | 11:00 | Noagaon | 130 | 17:00 | 119 | 21:00
| Mymensing | 119 | 3:00 | 113 | 8:00 | Rajshahi | 132 | 17:00 | 127 | 21:00
| Kishorganj | 123 | 4:00 | 119 | 15:00 | Rajshahi New | 133 | 10:00 | 126 | 21:00
| Netrokona | 117 | 7:00 | 107 | 8:00 | C.Nawabganj | 130 | 10:00 | 123 | 21:00
| Jamalpur | 130 | 5:00 | 121 | 8:00 | Amnura | 130 | 10:00 | 124 | 21:00
| Sherpur | 128 | 19:00 | 119 | 8:00 | Pabna | 136 | 3:00 | 129 | 21:00
| Srimongal | 137 | 4:00 | 132 | 15:00 | Shahjadpur | 141 | 2:00 | 133 | 21:00
| Shahjibazar | 135 | 5:00 | 130 | 15:00 | Serajganj | 134 | 2:00 | 133 | 21:00
| Fenchuganj | 137 | 6:00 | 130 | 15:00 | Niyamatpur | 126 | 18:00 | 113 | 21:00
| Khulawara | 135 | 4:00 | 129 | 15:00 | Joypurhat | 126 | 17:00 | 116 | 21:00
| Sylhet | 131 | 5:00 | 123 | 18:00 | Sherpur(Bogura) | 134 | 4:00 | 127 | 21:00
| Chatak | 131 | 5:00 | 122 | 16:00 | Mohastangor | 133 | 5:00 | 126 | 21:00
| Sunamganj | 129 | 6:00 | 120 | 15:00 | Bhangura | 136 | 2:00 | 131 | 21:00
| Biani Bazar | 131 | 5:00 | 122 | 15:00 | Rangpur | 130 | 2:00 | 122 | 21:00
| Comilla(s) | 131 | 5:00 | 125 | 18:30 | Lalmonirhat | 128 | 4:00 | 120 | 18:30
| Comilla(n) | 137 | 1:00 | 131 | 11:00 | Saidpur | 131 | 2:00 | 122 | 21:00
| Chandpur | 142 | 22:00 | 132 | 6:00 | Purbasadipur | 132 | 17:00 | 122 | 7:00
| Feni | 136 | 1:00 | 130 | 14:00 | Thakurgaon | 135 | 17:00 | 121 | 7:00
| Chowmuhani | 135 | 12:00 | 129 | 16:00 | Palashbari | 130 | 2:00 | 122 | 21:00
| Ashuganj | 136 | 5:00 | 134 | 1:00 | Barapukuria | 132 | 10:00 | 128 | 7:00
| Daudkandi | 137 | 22:00 | 127 | 11:00 | Panchagar | 135 | 10:00 | 124 | 7:00
| B.Baria | 132 | 6:00 | 127 | 21:00 | Joldhaka | 129 | 4:00 | 120 | 22:00
| Ramganj | 138 | 12:00 | 132 | 6:00 | Kurigram | 128 | 4:00 | 117 | 21:00
| Chaddagram | 136 | 8:00 | 131 | 15:00 | Mithapukur | 131 | 4:00 | 125 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 36 | 8278 | 3845 | 12123 |  |  |  | QF-LDC-11
0:30 | 20 | 8042 | 3610 | 11652 | Date: | 2022-03-22
1:00 | 4 | 7806 | 3375 | 11181
1:30 | 74 | 7553 | 3353 | 10906
2:00 | 144 | 7300 | 3331 | 10631
2:30 | 148 | 7131.5 | 3294.5 | 10426 | [5 empty] | Gen. at Eve. Peak | 13096 | 13096 MW (21:00 )
3:00 | 152 | 6963 | 3258 | 10221 | [6 empty] | 21:00
3:30 | 192 | 6850.5 | 3207 | 10057.5 | [5 empty] | Gen. at Day Peak | 11773 | 11773 MW (12:00 )
4:00 | 232 | 6738 | 3156 | 9894 | [6 empty] | 12:00
4:30 | 231 | 6669 | 3119.5 | 9788.5 | [5 empty] | Highest Generation | 13096
5:00 | 230 | 6600 | 3083 | 9683 | [6 empty] | 21:00
5:30 | 206 | 6606.5 | 3085 | 9691.5
6:00 | 182 | 6613 | 3087 | 9700
6:30 | 119 | 6653.5 | 3106.5 | 9760
7:00 | 56 | 6694 | 3126 | 9820
7:30 | 51 | 6745 | 3197.5 | 9942.5
8:00 | 46 | 6796 | 3269 | 10065
8:30 | 123 | 7018 | 3295.5 | 10313.5
9:00 | 200 | 7240 | 3322 | 10562
9:30 | 277 | 7323.5 | 3338 | 10661.5
10:00 | 354 | 7407 | 3354 | 10761
10:30 | 371 | 7525 | 3429.5 | 10954.5
11:00 | 388 | 7643 | 3505 | 11148
11:30 | 315 | 7932.5 | 3528 | 11460.5
12:00 | 242 | 8222 | 3551 | 11773
12:30 | 234 | 8203 | 3659 | 11862
13:00 | 226 | 8184 | 3767 | 11951
13:30 | 211 | 8147.5 | 3698.5 | 11846
14:00 | 196 | 8111 | 3630 | 11741
14:30 | 233 | 8167 | 3651 | 11818
15:00 | 270 | 8223 | 3672 | 11895
15:30 | 303 | 8211 | 3706 | 11917
16:00 | 336 | 8199 | 3740 | 11939
16:30 | 337 | 8192 | 3685.5 | 11877.5
17:00 | 338 | 8185 | 3631 | 11816
17:30 | 317 | 8153 | 3603 | 11756
18:00 | 296 | 8121 | 3575 | 11696
18:30 | 209 | 8404.5 | 3860.5 | 12265
19:00 | 122 | 8688 | 4146 | 12834
19:30 | 122 | 8773 | 4264 | 13037
20:00 | 80 | 8773 | 4245 | 13018 |  |  |  | Executive Engineer
20:30 | 46 | 8796.5 | 4260.5 | 13057 |  |  |  | Network Operation Division
21:00 | 12 | 8820 | 4276 | 13096
21:30 | 16 | 8774 | 4208 | 12982
22:00 | 20 | 8728 | 4140 | 12868 |  |  |  |  | Page 6 of 7
22:30 | 12 | 8643.5 | 4068 | 12711.5
23:00 | 4 | 8559 | 3996 | 12555
23:30 | 20 | 8418.5 | 3920.5 | 12339
24:00 | 36 | 8278 | 3845 | 12123
13096 MW (21:00 )
11773 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-22 |  | Energy |  | 286381713
[13 empty] | 2022-03-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4028 | 711 | 1720 | 159 | 3839 | 848 | 71 | 158 | 447 | 142 | 0 | 0
0:30 | 3861.5 | 712.5 | 1721 | 119.5 | 3735.5 | 839.5 | 70.5 | 139 | 315 | 138 | 0 | 0 | Date: | 2022-03-22
1:00 | 3695 | 714 | 1722 | 80 | 3632 | 831 | 70 | 120 | 183 | 134 | 0 | 0
1:30 | 3703 | 713.5 | 1750.5 | 40 | 3410.5 | 816 | 70.5 | 120 | 149 | 133 | 0 | 0 | [8 empty] | Total Energy | 286.3817 | Total Energy Gen 286.382 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 286.382 MKWHr
2:00 | 3711 | 713 | 1779 | 0 | 3189 | 801 | 71 | 120 | 115 | 132 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3744.5 | 713.5 | 1785.5 | 0 | 2962 | 801 | 71 | 120 | 99.5 | 129 | 0 | 0 | [8 empty] | Energy Requirement | 286.3817
3:00 | 3778 | 714 | 1792 | 0 | 2735 | 801 | 71 | 120 | 84 | 126 | 0 | 0
3:30 | 3770.5 | 713.5 | 1785 | 0 | 2599 | 801 | 70.5 | 120 | 74 | 124 | 0 | 0 | [6 empty] | Shortage
4:00 | 3763 | 713 | 1778 | 0 | 2463 | 801 | 70 | 120 | 64 | 122 | 0 | 0
4:30 | 3730 | 713.5 | 1738 | 0 | 2434.5 | 800.5 | 69 | 120 | 64 | 119 | 0 | 0
5:00 | 3697 | 714 | 1698 | 0 | 2406 | 800 | 68 | 120 | 64 | 116 | 0 | 0
5:30 | 3704 | 714 | 1706.5 | 0 | 2400.5 | 799.5 | 68 | 120 | 64 | 115 | 0 | 0
6:00 | 3711 | 714 | 1715 | 0 | 2395 | 799 | 68 | 120 | 64 | 114 | 0 | 0
6:30 | 3737 | 714 | 1718.5 | 0 | 2424 | 792.5 | 69 | 120 | 64 | 113 | 8 | 0 |  |  |  |  | Coal
7:00 | 3763 | 714 | 1722 | 0 | 2453 | 786 | 70 | 120 | 64 | 112 | 16 | 0
7:30 | 3739.5 | 715 | 1698.5 | 0 | 2594 | 793 | 70 | 120 | 64 | 112 | 36.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3716 | 716 | 1675 | 0 | 2735 | 800 | 70 | 120 | 64 | 112 | 57 | 0
8:30 | 3811.5 | 715 | 1677.5 | 0 | 2853.5 | 799.5 | 70 | 120 | 74 | 115 | 77.5 | 0
9:00 | 3907 | 714 | 1680 | 0 | 2972 | 799 | 70 | 120 | 84 | 118 | 98 | 0
9:30 | 3898 | 714.5 | 1656 | 0 | 3024.5 | 799 | 70 | 120 | 131.5 | 122 | 126 | 0
10:00 | 3889 | 715 | 1632 | 0 | 3077 | 799 | 70 | 120 | 179 | 126 | 154 | 0
10:30 | 3928.5 | 714 | 1667.5 | 0 | 3110 | 799.5 | 70 | 120 | 248 | 130 | 167 | 0
11:00 | 3968 | 713 | 1703 | 0 | 3143 | 800 | 70 | 120 | 317 | 134 | 180 | 0
11:30 | 3926.5 | 712.5 | 1716 | 174.5 | 3306 | 799 | 70.5 | 120 | 310.5 | 138 | 187 | 0
12:00 | 3885 | 712 | 1729 | 349 | 3469 | 798 | 71 | 120 | 304 | 142 | 194 | 0
12:30 | 3853 | 712.5 | 1721 | 393.5 | 3553 | 799 | 70.5 | 120 | 307.5 | 143 | 189 | 0
13:00 | 3821 | 713 | 1713 | 438 | 3637 | 800 | 70 | 120 | 311 | 144 | 184 | 0
13:30 | 3821 | 713 | 1713 | 438 | 3637 | 800 | 70 | 120 | 311 | 144 | 184 | 0
14:00 | 3821 | 713 | 1713 | 438 | 3637 | 800 | 70 | 120 | 311 | 144 | 184 | 0
14:30 | 3840.5 | 713 | 1699 | 422.5 | 3626 | 790 | 87.5 | 120 | 320.5 | 148 | 156 | 0
15:00 | 3860 | 713 | 1685 | 407 | 3615 | 780 | 105 | 120 | 330 | 152 | 128 | 0
15:30 | 3862 | 713 | 1689 | 422 | 3615.5 | 779 | 105 | 127.5 | 348.5 | 151 | 104.5 | 0
16:00 | 3864 | 713 | 1693 | 437 | 3616 | 778 | 105 | 135 | 367 | 150 | 81 | 0
16:30 | 3953 | 712 | 1678.5 | 356.5 | 3629 | 778.5 | 87.5 | 147.5 | 372.5 | 150 | 57 | 0
17:00 | 3953 | 711 | 1664 | 276 | 3642 | 779 | 70 | 160 | 378 | 150 | 33 | 0
17:30 | 3944 | 712.5 | 1633 | 246 | 3671.5 | 778.5 | 70 | 135 | 401.5 | 147 | 17 | 0
18:00 | 3935 | 714 | 1602 | 216 | 3701 | 778 | 70 | 110 | 425 | 144 | 1 | 0
18:30 | 3954.5 | 713.5 | 1659 | 563.5 | 3735.5 | 798 | 70 | 132.5 | 482 | 156 | 0.5 | 0
19:00 | 3974 | 713 | 1716 | 911 | 3770 | 818 | 70 | 155 | 539 | 168 | 0 | 0
19:30 | 3986 | 713 | 1699 | 984 | 3834 | 879 | 70 | 170 | 542 | 160 | 0 | 0
20:00 | 3960 | 714 | 1711 | 982 | 3828 | 889 | 70 | 182 | 530 | 152 | 0 | 0
20:30 | 3984 | 714.5 | 1716 | 982 | 3820.5 | 910 | 70 | 177 | 527 | 156 | 0 | 0
21:00 | 4008 | 715 | 1721 | 982 | 3813 | 931 | 70 | 172 | 524 | 160 | 0 | 0
21:30 | 4012.5 | 715 | 1716.5 | 887 | 3816 | 913 | 70 | 164 | 527 | 161 | 0 | 0
22:00 | 4017 | 715 | 1712 | 792 | 3819 | 895 | 70 | 156 | 530 | 162 | 0 | 0
22:30 | 4016.5 | 714.5 | 1718.5 | 654.5 | 3823 | 883.5 | 70.5 | 156.5 | 516 | 158 | 0 | 0
23:00 | 4016 | 714 | 1725 | 517 | 3827 | 872 | 71 | 157 | 502 | 154 | 0 | 0
23:30 | 4022 | 712.5 | 1722.5 | 338 | 3833 | 860 | 71 | 157.5 | 474.5 | 148 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.1° C
24:00 | 4028 | 711 | 1720 | 159 | 3839 | 848 | 71 | 158 | 447 | 142 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 286.382 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 286.382 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 36 | 36 | 35 | 33 | 33 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 71 | 71 | 1187362
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [10 empty] | 568000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3600000
5 | Raozan 25 MW PP | [10 empty] | 0 | 12 | 17 | 23 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 316776
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 14 | 10 | 11 | 15 | 7 | 12 | 6 | 5 | 3 | [9 empty] | 87345
6 | Sikalbaha 225MW CCPP (Gas) | 32 | 31 | 31 | 31 | 30 | 60 | 141 | 131 | 131 | 131 | 149 | 131 | 140 | 131 | 132 | 131 | 131 | 148 |  | 131 | 131 | 131 | 131 | 140 | 127 | 132 | 2425454
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 34 | 34 | 328730
12 | Hathazari 100 MW peaking PP | [15 empty] | 8 | 8 | 8 |  | 8 | 8 | 18 | 24 | 24 | 16 |  | 105152
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 98 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2524981
| Daudkandi 200 MW PP (B.Trac) | 80 | [10 empty] | 20 | 50 | 20 | 20 | 20 | 40 | 50 |  | 200 | 200 | 200 | 200 | 200 | 170 |  | 1340928
14 | Titas 50 MW Peaking PP | 33 | [9 empty] | 33 | 36 | 35 | 41 | 41 | 41 | 40 | 40 |  | 40 | 38 | 42 | 41 | 42 | 41 | 42 | 593160
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 190 | 194 | 200 | 209 | 215 | 219 | 221 | 223 | 223 | 222 | 213 | 217 | 213 | 212 | 212 | 209 | 211 | 196 |  | 215 | 216 | 206 | 213 | 218 | 218 | 224 | 5180857
18 | Kodda 300 MW PP Unit-2 (Summit) | 298 | 245 | 95 | 45 | 45 | 45 | 45 | 84 | 195 | 250 | 275 | 275 | 275 | 280 | 293 | 293 | 293 | 293 |  | 293 | 297 | 297 | 296 | 296 | 296 | 298 | 5607816
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4808000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6174682
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 26 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 640728
33 | Ashuganj 225 MW CCPP | 184 | 185 | 193 | 188 | 183 | 183 | 203 | 183 | 219 | 217 | 201 | 152 | 147 | 168 | 202 | 204 | 208 | 212 |  | 213 | 216 | 215 | 217 | 213 | 219 | 219 | 4793000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 285 | 275 | 275 | 275 | 305 | 275 | 290 | 275 | 330 | 290 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6764000
| Ashuganj 450 MW CCPP(North) | 270 | 280 | 290 | 285 | 275 | 280 | 310 | 275 | 290 | 280 | 330 | 290 | 280 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7100000
35 | Ashuganj 55 MW PP (Precision) | 20 | 30 | 30 | 30 | 30 | 57 | 56 | 56 | 53 | 51 | 50 | 51 | 51 | 49 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 985920
36 | Chandpur 150 MW CCPP | 73 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 72 | 72 | 72 | 136 | 136 | 137 | 137 | 137 | 137 | 137 |  | 137 | 137 | 136 | 137 | 136 | 136 | 136 | 2510700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 310 | 320 | 320 | 320 | 320 | 310 | 300 | 300 | 300 | 300 | 300 | 290 | 290 | 280 | 280 | 270 | 260 |  | 260 | 250 | 250 | 240 | 240 | 240 | 240 | 6672500
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 86 | 86 | 105 | 98 | 101 | 98 | 98 | 89 | 81 | 71 | 70 | 68 | 68 | 71 | 69 | 70 | 84 | 81 |  | 84 | 84 | 84 | 81 | 82 | 82 | 84 | 1932480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 13 | 25 | 34 | 38 | 38 | 41 | 34 | 29 | 18 | 6 | 0 | [8 empty] | 282080
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 697200
46 | Shajibazar 330 MW CCPP | 265 | 266 | 266 | 267 | 268 | 265 | 268 | 266 | 268 | 269 | 260 | 264 | 265 | 259 | 264 | 264 | 267 | 263 |  | 268 | 270 | 267 | 279 | 267 | 268 | 266 | 6058000
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 56 | 60 |  | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 1409856
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 87 | 86 | 85 | 84 | 83 | 84 | 85 | 87 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2106240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243000
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 5 | 5 | 5 | 5 | 5 | 8 | 190800
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 44 | 47 | 44 | 44 | 47 | 45 |  | 50 | 50 | 50 | 50 | 50 | 49 | 50 | 1163400
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 23 | 16 | 16 | 16 | 16 | 15 | 14 | 14 | 14 | 13 | 13 | 13 | 13 |  | 15 | 15 | 15 | 16 | 16 | 24 | 24 | 413472
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 275 | 290 | 290 | 285 | 270 | 290 | 290 | 290 | 270 | 280 | 300 | 275 | 285 | 290 | 290 | 290 | 280 |  | 290 | 270 | 280 | 290 | 280 | 270 | 285 | 7070500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 345 | 360 | 250 | 280 | 400 | 400 | 382 | 400 | 375 | 385 | 388 | 384 | 393 | 386 |  | 400 | 400 | 400 | 396 | 400 | 400 | 400 | 9105000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 1252397
59 | Tangail Palli Power Gen 22 MW | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 20 | 18 | 18 | 20 | 514560
60 | Barabkunda 22 MW PP (Regent) | [25 empty] | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 463392
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 342504
63 | Impoprt (Tripura) | 134 | 132 | 126 | 122 | 116 | 114 | 112 | 112 | 118 | 126 | 134 | 142 | 144 | 152 | 152 | 150 | 150 | 144 |  | 168 | 160 | 152 | 160 | 162 | 154 | 142 | 3296640
64 | Malancha, Ctg. EPZ (United) | 39 | 30 | 39 | 39 | 34 | 40 | 37 | 11 | 10 | 10 | 6 | 5 | 8 | 8 | 3 | 5 | 9 | 2 |  | 11 | 15 | 17 | 26 | 32 | 35 | 38 | 484320
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 441756
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 21 | 25 | 25 | 16 | 31 | 1 | 32 | 30 |  | 31 | 32 | 32 | 33 | 33 | 33 | 33 | 722100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 522220
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 29 | 22 | 22 | 22 | 23 | 29 | 29 | 29 | 29 | 27 | 24 | 27 | 28 | 27 |  | 27 | 26 | 8 | 28 | 28 | 28 | 28 | 583920
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 784400
73 | Ghorashal 108MW PP (Regent) | 91 | 93 | 95 | 96 | 99 | 99 | 99 | 98 | 97 | 97 | 100 | 100 | 97 | 100 | 97 | 97 | 97 | 97 |  | 97 | 97 | 95 | 95 | 96 | 99 | 98 | 2284318
| Feni Lanka Power | 82 | 34 | 2 |  |  |  |  | 51 | 51 | 51 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1475160
| Chowmuhani 113 MW | 101 | 101 | 99 | 102 | 102 | 107 | 106 | 107 | 107 | 102 | 98 | 99 | 105 | 105 | 104 | 105 | 105 | 105 |  | 108 | 106 | 109 | 105 | 112 | 113 | 110 | 2527560
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 141 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3493440
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 42 | 42 | 42 | 34 | 34 | 34 | 34 | 0 | 36 | 50 | 50 | 50 | 50 | 50 |  | 45 | 49 | 49 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 1024800
79 | Kodda 150MW PP | 150 | 115 | 84 | 64 | 64 | 64 | 64 | 64 | 84 | 150 | 150 | 150 | 150 | 150 | 147 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3048480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 33 | 38 | 40 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025784
| Gazipur 100 MW PP | 90 | 90 | 51 |  |  |  | 45 | 66 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 52 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1494000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 31320
| Jodiac Power | 54 | 54 | 54 | 54 | 47 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 46 | 54 | 54 | 54 | 54 | 1057213
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2676352
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3560902
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 91 | 91 | 92 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 80 | 72 | 72 | 72 | 80 |  | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 2117760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 10 | 0 |  |  | 0 | 10 | 10 | 10 | 10 | 46 | 80 | 92 | 92 | 92 | 92 | 92 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 1356480
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1174026
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 50 | 7 | 7 | 7 | 16 | 48 | 66 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1819872
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 41 | 12 | 12 | 12 | 12 | 12 | 31 | 44 | 48 | 50 | 33 | 30 | 50 | 50 | 50 |  | 50 | 50 | 50 | 45 | 44 | 44 | 45 | 924000
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 17 | 30 | 30 | 30 | 43 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1054492
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | [5 empty] | 17 | 17 | 17 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 842788
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 |  | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 11700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1307520
104 | Keranigonj 300 MW PP (APR) | [11 empty] | 129 | 30 | 33 | 102 | 108 | 106 | 106 |  | 256 | 305 | 305 | 306 | 197 | 147 | 74 | 2019075
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 100 | 100 | 70 | 100 | 100 | 80 | 30 |  | 100 | 100 | 100 | 100 | 100 | 70 | 40 | 1088642
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 192 | 184 | 184 | 191 | 174 | 174 | 174 | 173 | 182 | 189 | 180 | 179 | 169 | 178 |  | 180 | 181 | 180 | 180 | 180 | 180 | 190 | 4334400
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 97 | 100 | 70 | 100 | 99 | 50 | 30 |  | 100 | 100 | 99 | 99 | 100 | 50 | 25 | 10355227
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 142 | 124 | 100 | 102 | 105 | 116 | 116 | 117 | 116 | 114 | 116 | 115 | 116 | 115 | 115 | 115 |  | 115 | 116 | 115 | 116 | 130 | 134 | 134 | 2909660
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2105280
116 | Chandpur 200MW (Desh energy) | 200 | 17 | 0 |  |  |  |  | 15 | 17 | 17 | 25 | 129 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2946720
117 | Ashuganj 150MW PP (Midland) | 138 | 142 | 132 | 130 | 139 | 140 | 138 | 127 | 135 | 140 | 140 | 140 | 138 | 142 | 142 | 140 | 142 | 140 |  | 142 | 142 | 143 | 147 | 145 | 143 | 150 | 3362182
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 401 | 401 | 397 | 363 | 363 | 362 | 364 | 364 | 404 | 403 | 404 | 406 | 403 | 406 | 404 | 400 |  | 402 | 402 | 402 | 404 | 403 | 403 | 403 | 9446000
| Jamalpur 115 MW PP (United) | 109 | 108 | 108 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 107 | 106 | 107 |  | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 2546400
| Anwara 300 MW PP (United) | 281 | 265 | 265 | 265 | 265 | 265 | 264 | 264 | 264 | 270 | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 281 |  | 281 | 281 | 287 | 290 | 287 | 282 | 290 | 6583855
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 60 | 90 | 77 | 77 | 77 | 100 | 90 | 72 | 82 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2154240
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2693509
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 667080
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 7 | 9 | 25 | 30 | 32 | 30 | 2 | 20 | 12 | 5 | [9 empty] | 199532
| Chandpur 115(Doreen) | 89 | 25 |  |  |  |  | 1 | 24 | 51 | 51 | 73 | 96 | 98 | 98 | 98 | 94 | 75 | 79 |  | 87 | 98 | 96 | 97 | 99 | 100 | 94 | 1553280
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 49 | 55 | 55 | 55 | 55 | 10 | 25 | 37 | 55 | 55 | 46 | 42 | 51 |  | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 1200240
120 | Eastern Zone Total | 7806 | 7300 | 6963 | 6738 | 6600 | 6613 | 6694 | 6796 | 7240 | 7407 | 7643 | 8222 | 8184 | 8111 | 8223 | 8199 | 8185 | 8121 |  | 8688 | 8773 | 8773 | 8820 | 8728 | 8559 | 8278 | 197451651
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 40 | 40 | 40 | 35 | 39 | 33 |  | 204000
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 135 | 160 | 110 |  | 155 | 155 | 155 | 155 | 156 | 157 | 158 | 3247680
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 100 | 94 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 94 | 94 | 2570880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 31 | 45 | 74 | 88 | 93 | 89 | 79 | 62 | 39 | 16 | 1 | [8 empty] | 636480
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 214 | 224 | 202 | 182 | 150 | 150 | 150 | 152 | 152 | 132 | 172 | 190 | 213 | 219 | 216 | 215 | 185 | 162 |  | 220 | 220 | 220 | 220 | 214 | 224 | 202 | 4639936
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 32 | 32 | [5 empty] | 43200
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [13 empty] | 15 | 30 | 65 | 65 | 63 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 609000
140 | Bhola 33 MW PP (Venture) | 27 | 27 | 26 | 25 | 21 | 20 | 21 | 18 | 21 | 19 | 20 | 21 | 23 | 24 | 25 | 25 | 25 | 23 |  | 19 | 28 | 29 | 30 | 30 | 28 | 27 | 578200
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 |  | 3 | 58 | 10 | 45 | 70 |  |  |  | 78 | 100 | 100 | 100 | 20 | 20 | 0 | 649920
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 15 | 15 | [5 empty] | 18176
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 32 | 1 |  |  |  |  | 0 | 36144
146 | Bheramara HVDC | 714 | 713 | 714 | 713 | 714 | 714 | 714 | 716 | 714 | 715 | 713 | 712 | 713 | 712 | 713 | 713 | 711 | 714 |  | 713 | 713 | 714 | 715 | 715 | 714 | 711 | 17269090
147 | Bheramara 410 MW CCPP | 220 | 220 | 230 | 235 | 235 | 235 | 240 | 240 | 240 | 230 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 235 | 235 | 235 | 235 | 240 | 240 | 240 | 5668992
148 | Payra 1320 MW | 550 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 500 | 500 | 500 | 500 | 500 |  | 540 | 600 | 610 | 650 | 620 | 590 | 570 | 14485300
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 81 | 81 | 80 | 79 | 66 | 80 | 79 | 79 | 80 | 78 | 80 | 81 | 80 | 78 | 79 | 78 |  | 78 | 79 | 79 | 81 | 75 | 82 | 78 | 1866763
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4869200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [10 empty] | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 477200
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 4 | 4 | 4 | 5 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 31920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 136 | 143 | 146 | 146 | 146 | 152 | 155 | 159 | 164 | 162 | 157 | 143 | 142 | 142 | 135 | 133 | 134 | 133 |  | 133 | 133 | 133 | 135 | 137 | 142 | 148 | 3674364
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 142 | 137 | 137 | 137 | 138 | 138 | 134 | 129 | 134 | 158 | 167 | 162 | 162 | 157 | 154 | 151 | 151 | 150 |  | 150 | 151 | 155 | 162 | 163 | 157 | 149 | 3823345
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 414 | 414 | 420 | 383 | 383 | 383 | 382 | 384 | 383 | 404 | 393 | 391 | 381 | 382 | 388 | 391 | 380 |  | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 9538727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [9 empty] | 5 | 5 | 6 | 15 | 25 | 24 | 22 | 34 | 39 |  | 39 | 42 | 42 | 36 | 36 | 36 | 34 | 370638
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 16 | 16 | 16 | 16 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 406560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 232290
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [20 empty] | 34 | 43 | 43 | 34 | 34 | 34 | 183264
167 | Katakhali 50 MW Peaking PP | [9 empty] | 24 | 24 | 24 | 25 | 27 | 32 | 32 | 32 | 32 |  | 40 | 40 | 32 | 32 | 32 | 37 | 32 | 402260
168 | Santahar 50 MW Peaking PP | [15 empty] | 28 | 28 | 32 |  | 32 | 34 | 31 | 31 | 32 | 31 | 31 | 284529
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 24 | 8 | 8 | 8 | 8 | 24 | 30 | 52 | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 970560
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 62 | 54 | 52 | 52 | 52 | 52 | 52 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1054680
171 | Baghabari 200 MW PP (Paramount) | [12 empty] | 100 | 20 | 40 | 40 |  |  |  | 177 | 179 | 178 | 177 | 175 | 60 | 20 | 992262
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 74 | 80 | 93 | 109 | 112 | 112 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2647296
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | 70 | 70 | 70 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2220768
173 | Rangpur 20 MW GTPP | [20 empty] | 15 | 17 | 17 |  |  |  | 25000
175 | Saidpur 20 MW GTPP | [21 empty] | 10 |  |  |  |  | 1200
176 | Rangpur 113 MW PP (Confidence) | 110 | 103 | 110 | 35 | 34 | 34 | 72 | 104 | 104 | 100 | 97 | 96 | 95 | 97 | 100 | 100 | 105 | 109 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2249049
177 | Sympa Solar Power 8MW | [9 empty] | 2 | 3 | 5 | 6 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 29854
178 | Energypac Power Venture Thakurgaon Ltd. | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 72 | 72 | 72 | 100 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1921335
178