## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-24 | Thursday
|  |  | Date (day): | 2022-03-24 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13248.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13801 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-23 | 2022-03-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 250 | 250 | 250 | 115 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 99 | 105 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 280 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 |  | 185 | GT-2 under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 64 | 100
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 208 | 213 | 220 | 220 | 115 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 52 | 52 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 283 | 268 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 298 | 300 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 100 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 97 | 99 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 134 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 70 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 91 | 90 | 91 |  | 13 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 3082 | 3146 | 3215 | 3325 | 641 | 1812
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 47 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 71 | 70 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 131 | 131 | 130 | 130 |  | 95 | ST Under S/D
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 17 | 0 | 40 |  | 58 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 25 | 6 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 65 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 94 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1264 | 1488 | 1479 | 1508 | 183 | 675
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 215 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 355 | 320 | 340 | 20 |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 335 | 320 | 340 | 20 |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 40 | 52 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 18 | 36 | 36 | 159 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 145 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 40 | 32 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 137 | 137 | 137 |  | 26 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 195 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 156 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 15 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 200 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 99 | 99 | 98 | 99 |  | 15 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 115 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 56 | 92 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 2114 | 2401 | 2265 | 2449 | 478 | 69
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 82 | 99 | 68 | 68 | 134 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 191 | 200 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 97 | 107 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 452 | 441 | 473.6 | 422 | 134 | 13
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 221 | 220 | 220 |  | 110 | Engine problem
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 87 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 22 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 380 | 403 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 382 | 390 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1358 | 1616 | 1619 | 1621 | 251 | 473
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 713 | 711 | 728 | 728
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 34 | 35 | 0 | 40 |  | 14 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 195 | 215 | 225 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 220 | 235 | 225 | 225 | 185 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 90 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1433 | 1401 | 1433 | 1453 | 185 | 93
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 26 | 0 | 80
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 31 | 25 | 30
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 60 | 65 | 65 | 129 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 270 | 622 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 180 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 578 | 961 | 930 | 1055 | 129 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 34 |  | 18 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 43 | 42 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 7 | 3 | 88 | 88 | 122 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 128 | 121 | 124 | 124 | 96 |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 158 | 146 | 126 | 126 | 94 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 416 | 350 | 350 | 64 |  | Gas shortage
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 31 |  | 19 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 91 | 90 | 90 |  | 14 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 176 | 175 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 112 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 95 | 95 |  | 18 | Engine problem
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1225 | 1454 | 1318 | 1459 | 547 | 117
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 79 | 80 | 81
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 102 | 110 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 497 | 504 | 516 | 509 | 74 | 125
|  | Total |  |  |  |  | 22291 | 21215 | 12003 | 13412 | 13248.6 | 13801 | 2622 | 3377
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11509.0531 | 12860.07 | 12703.3942 | 13233.0619
| A. |  | 2022-03-23 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13412 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10247 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13412 | MW
| 3 | Day peak Generation : |  |  | 12003 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12860.07 | MW
| 4 | Evening peak Generation : |  |  | 13412 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 285.3849 | MKWHr | By Solar | 1.3093 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 134.6377 | MKWHr |  | By Oil: | 108.9511 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 18.1323 | MKWHr |  | By Hydro: | 1.6915 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2622 | MW | Dhaka | 4852.77 | 4852.77 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3377 | MW | Chittagong | 1301 | 1301 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5999 | MW | Khulna | 1194 | 1194 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1083.39 | MMCFD |  |  | Rajshahi | 1011 | 1011 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 135734819.703 | ii) Oil : | Taka | 923358947.75 | Comilla | 485 | 485 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 87722122.27 | Total | Taka | 1146815889.723 | Mymensingh | 1538.1 | 1538.1 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.09 | MKWHr. | Sylhet | 363 | 363 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 104 | MW (E to W) at | 21:00 | hrs | Barisal | 1373.2 | 1373.2 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -78 | MW at | 7:00 | hrs | Rangpur | 742 | 742 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.5° C |  |  | Total | 12860.07 | 12860.07 |  | 0
| B. |  | 2022-03-24 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 38.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13801 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 293.6409 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10558 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2262 | MKWHr. | ii) HVDC Flow at Peak Time |  | 711 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4368 | MKWHr. | iii) Maximum HVDC Flow : |  | 714 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.94 |  | (b) Today: | 86.73 |  | (c) Rule Curve: |  | 89.32
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 71 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 |  | 20 | 0 | 0 | 90 | 0 | 45 | 0 | 37 | 0 | 0 | 0 | 300 | 260 | 222 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 33 | 21 | 138 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 265 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 296 | 0 | 25 | 190 | 0 | 123 | 0 | 90 | 200 | 150 | 401 | 108 | 70 | 93 | 0 | 281 | 54 | 110 | 99 | 110 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 85 | 55 |  | 711 | 0 | 240 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 34 | 31 | 90 | 0 | 34 | 30 | 52 | 32 | 18 | 0 | 11 | 77 | 0 | 200 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 149 | 0 | 414 | 94 | 0 | 113 | 0 | 110 | 0 | 0 | 95 | 540 | 192 | 0 | 0 | 0 | 0 | 115 |  | 8122 | 3696 | 11818 | 4073 | 711 | 1704 | 25 | 3795 | 817 | 71 | 75 | 409 | 138 | 0 | 0 | 86.99
2:00 | 0 | 0 | 200 | 0 | 250 | 101 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 30 | 222 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 70 | 0 | 0 | 150 | 8 | 130 | 0 | 0 | 0 |  | 18 | 0 | 0 | 40 | 0 | 45 | 0 | 38 | 0 | 0 | 0 | 300 | 260 | 222 | 8 | 137 | 29 | 40 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 33 | 21 | 136 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 260 | 24 | 8 | 0 | 298 | 0 | 0 | 190 | 0 | 135 | 0 | 90 | 120 | 150 | 402 | 108 | 70 | 102 | 0 | 294 | 54 | 110 | 70 | 111 | 100 | 360 | 92 | 0 | 144 | 113 | 0 | 35 | 0 | 93 | 55 |  | 711 | 0 | 240 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 34 | 29 | 90 | 0 | 0 | 30 | 52 | 32 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 140 | 0 | 414 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 95 | 520 | 202 | 0 | 0 | 0 | 0 | 72 |  | 7833 | 3538 | 11371 | 4036 | 711 | 1695 | 0 | 3500 | 801 | 70 | 15 | 407 | 136 | 0 | 0 | 86.98
3:00 | 0 | 0 | 200 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 70 | 0 | 0 | 150 | 8 | 132 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 0 | 41 | 0 | 38 | 0 | 0 | 0 | 300 | 260 | 222 | 8 | 137 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 134 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 269 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 275 | 24 | 8 | 0 | 298 | 0 | 0 | 191 | 0 | 135 | 0 | 90 | 17 | 150 | 401 | 108 | 70 | 105 | 0 | 292 | 54 | 110 | 70 | 112 | 100 | 300 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 35 | 55 |  | 711 | 0 | 245 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 34 | 0 | 46 | 0 | 0 | 0 | 24 | 30 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 137 | 0 | 414 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 95 | 500 | 201 | 0 | 0 | 0 | 0 | 34 |  | 7538 | 3346 | 10884 | 3979 | 711 | 1710 | 0 | 3226 | 779 | 70 | 15 | 260 | 134 | 0 | 0 | 86.97
4:00 | 0 | 0 | 200 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 15 | 223 | 0 | 0 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 69 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 300 | 260 | 219 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 130 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 268 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 230 | 0 | 0 | 191 | 0 | 135 | 0 | 90 | 17 | 150 | 401 | 109 | 70 | 105 | 0 | 292 | 44 | 110 | 70 | 109 | 100 | 311 | 93 | 0 | 129 | 113 | 0 | 35 | 0 | 40 | 55 |  | 711 | 0 | 250 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 73 | 0 | 200 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 132 | 0 | 414 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 95 | 500 | 172 | 0 | 0 | 0 | 0 | 36 |  | 7401 | 3196 | 10597 | 3988 | 711 | 1686 | 0 | 3080 | 773 | 69 | 10 | 150 | 130 | 0 | 0 | 86.96
5:00 | 0 | 0 | 200 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 15 | 200 | 0 | 0 | 0 | 40 | 100 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 69 | 0 | 0 | 150 | 0 | 142 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 300 | 260 | 217 | 8 | 135 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 126 | 104 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 200 | 0 | 133 | 0 | 90 | 17 | 150 | 376 | 109 | 70 | 105 | 0 | 300 | 47 | 110 | 34 | 105 | 100 | 235 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 23 | 55 |  | 710 | 0 | 250 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 131 | 0 | 386 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 70 | 470 | 172 | 0 | 0 | 0 | 0 | 17 |  | 7134 | 3113 | 10247 | 3849 | 710 | 1667 | 0 | 2951 | 745 | 69 | 30 | 100 | 126 | 0 | 0 | 86.95
6:00 | 0 | 0 | 203 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 15 | 200 | 0 | 0 | 0 | 40 | 100 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 29 | 33 | 33 | 34 | 0 | 68 | 0 | 0 | 150 | 0 | 132 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 0 | 18 | 0 | 40 | 0 | 0 | 0 | 275 | 305 | 218 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 120 | 105 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 269 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 195 | 0 | 0 | 192 | 0 | 135 | 0 | 90 | 17 | 142 | 399 | 109 | 70 | 105 | 0 | 300 | 35 | 110 | 34 | 107 | 100 | 195 | 92 | 0 | 144 | 113 | 0 | 35 | 0 | 17 | 55 |  | 711 | 0 | 250 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 131 | 0 | 383 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 70 | 470 | 172 | 0 | 0 | 0 | 0 | 17 |  | 7102 | 3149 | 10251 | 3844 | 711 | 1673 | 0 | 2922 | 748 | 68 | 65 | 100 | 120 | 0 | 0 | 86.94
7:00 | 0 | 0 | 200 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 15 | 220 | 0 | 0 | 0 | 40 | 100 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 29 | 33 | 33 | 34 | 0 | 69 | 0 | 0 | 150 | 0 | 142 | 0 | 0 | 0 |  | 19 | 0 | 0 | 20 | 0 | 18 | 0 | 35 | 0 | 0 | 0 | 310 | 335 | 217 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 118 | 102 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 195 | 0 | 0 | 192 | 0 | 124 | 2 | 90 | 17 | 137 | 400 | 109 | 70 | 105 | 1 | 300 | 35 | 110 | 34 | 109 | 100 | 175 | 92 | 5 | 144 | 113 | 0 | 35 | 4 | 17 | 55 |  | 710 | 0 | 260 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 18 | 0 | 11 | 76 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 133 | 0 | 420 | 94 | 0 | 113 | 0 | 103 | 0 | 0 | 95 | 470 | 170 | 0 | 0 | 0 | 9 | 17 |  | 7200 | 3225 | 10425 | 3956 | 710 | 1701 | 0 | 2949 | 746 | 69 | 55 | 100 | 118 | 21 | 0 | 86.93
8:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 33 | 180 | 0 | 0 | 0 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 36 | 0 | 69 | 0 | 0 | 150 | 0 | 130 | 0 | 0 | 0 |  | 22 | 0 | 0 | 70 | 0 | 37 | 0 | 11 | 0 | 0 | 0 | 270 | 305 | 219 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 15 | 20 | 124 | 104 | 0 | 17 | 1 | 30 | 30 | 49 | 0 | 0 | 266 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 215 | 0 | 0 | 193 | 0 | 133 | 6 | 90 | 37 | 142 | 381 | 109 | 70 | 105 | 1 | 300 | 35 | 110 | 99 | 106 | 100 | 170 | 91 | 14 | 144 | 113 | 0 | 35 | 11 | 32 | 55 |  | 711 | 0 | 250 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 142 | 0 | 370 | 94 | 0 | 113 | 0 | 103 | 0 | 1 | 95 | 460 | 173 | 0 | 0 | 1 | 30 | 115 |  | 7345 | 3311 | 10656 | 3765 | 711 | 1604 | 0 | 3376 | 737 | 69 | 55 | 150 | 124 | 65 | 0 | 86.92
9:00 | 0 | 0 | 200 | 0 | 250 | 96 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 70 | 0 | 46 | 0 | 5 | 0 | 0 | 0 | 270 | 305 | 193 | 8 | 137 | 26 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 16 | 20 | 128 | 93 | 0 | 17 | 1 | 30 | 30 | 47 | 0 | 0 | 268 | 30 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 23 | 8 | 0 | 265 | 25 | 100 | 192 | 25 | 134 | 7 | 90 | 57 | 140 | 399 | 108 | 70 | 105 | 3 | 300 | 35 | 110 | 99 | 108 | 100 | 265 | 90 | 26 | 144 | 113 | 0 | 35 | 17 | 62 | 55 |  | 712 | 0 | 245 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 84 | 0 | 199 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 156 | 0 | 415 | 94 | 0 | 113 | 0 | 103 | 0 | 2 | 95 | 300 | 134 | 0 | 0 | 2 | 52 | 115 |  | 7745 | 3233 | 10978 | 3829 | 712 | 1617 | 150 | 3519 | 583 | 70 | 110 | 150 | 128 | 110 | 0 | 86.91
10:00 | 0 | 0 | 200 | 0 | 250 | 96 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 20 | 33 | 33 | 42 | 0 | 70 | 0 | 0 | 150 | 20 | 132 | 0 | 0 | 0 |  | 22 | 0 | 0 | 70 | 0 | 43 | 0 | 5 | 0 | 0 | 0 | 300 | 260 | 171 | 8 | 137 | 26 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 16 | 20 | 140 | 79 | 0 | 0 | 2 | 30 | 30 | 47 | 0 | 0 | 267 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 305 | 23 | 8 | 0 | 280 | 167 | 100 | 192 | 64 | 135 | 4 | 76 | 87 | 142 | 401 | 108 | 70 | 105 | 3 | 300 | 35 | 110 | 99 | 105 | 90 | 380 | 91 | 35 | 144 | 113 | 0 | 35 | 23 | 71 | 55 |  | 712 | 0 | 235 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 77 | 0 | 199 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 167 | 0 | 415 | 94 | 0 | 112 | 0 | 103 | 0 | 5 | 95 | 250 | 224 | 0 | 0 | 3 | 71 | 115 |  | 8118 | 3318 | 11436 | 3905 | 712 | 1735 | 331 | 3566 | 526 | 70 | 140 | 165 | 140 | 146 | 0 | 86.91
11:00 | 0 | 0 | 200 | 0 | 250 | 97 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 42 | 0 | 70 | 0 | 0 | 150 | 25 | 140 | 0 | 0 | 0 |  | 23 | 0 | 0 | 70 | 0 | 45 | 0 | 5 | 0 | 0 | 0 | 270 | 260 | 195 | 8 | 137 | 29 | 40 | 0 | 51 | 0 | 21 | 43 | 19 | 11 | 16 | 20 | 148 | 82 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 209 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 8 | 0 | 283 | 109 | 100 | 191 | 97 | 133 | 17 | 76 | 150 | 142 | 404 | 97 | 70 | 105 | 4 | 300 | 35 | 110 | 99 | 107 | 65 | 380 | 91 | 42 | 144 | 113 | 0 | 35 | 28 | 62 | 45 |  | 712 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 30 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 2 | 0 | 148 | 0 | 0 | 50 | 167 | 0 | 388 | 94 | 176 | 112 | 0 | 102 | 0 | 5 | 95 | 250 | 224 | 0 | 0 | 4 | 82 | 115 |  | 8107 | 3650 | 11757 | 3887 | 712 | 1691 | 532 | 3583 | 527 | 70 | 180 | 243 | 148 | 184 | 0 | 86.9
12:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 208 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 71 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 21 | 0 | 0 | 70 | 0 | 44 | 0 | 5 | 0 | 0 | 0 | 270 | 260 | 206 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 30 | 43 | 19 | 11 | 15 | 18 | 148 | 82 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 0 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 305 | 22 | 8 | 200 | 283 | 298 | 100 | 191 | 97 | 134 | 19 | 76 | 195 | 137 | 380 | 97 | 70 | 90 | 4 | 300 | 35 | 110 | 99 | 108 | 65 | 382 | 91 | 42 | 144 | 94 | 0 | 35 | 30 | 56 | 54 |  | 713 | 0 | 220 | 0 | 0 | 195 | 0 | 0 | 34 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 52 | 0 | 15 | 0 | 11 | 76 | 0 | 199 | 0 | 0 | 7 | 0 | 128 | 0 | 0 | 90 | 158 | 0 | 388 | 94 | 176 | 112 | 0 | 102 | 0 | 5 | 95 | 270 | 220 | 0 | 0 | 4 | 87 | 115 |  | 8270 | 3733 | 12003 | 3614 | 713 | 1705 | 961 | 3599 | 545 | 71 | 195 | 259 | 148 | 193 | 0 | 86.9
13:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 250 | 150 | 0 | 0 | 55 | 202 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 20 | 33 | 33 | 41 | 0 | 71 | 0 | 0 | 150 | 14 | 142 | 0 | 0 | 0 |  | 6 | 0 | 0 | 80 | 0 | 45 | 0 | 8 | 0 | 0 | 0 | 270 | 260 | 208 | 8 | 137 | 29 | 40 | 0 | 51 | 0 | 36 | 43 | 19 | 11 | 15 | 18 | 154 | 82 | 0 | 17 | 2 | 30 | 30 | 44 | 0 | 0 | 0 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 200 | 281 | 303 | 100 | 190 | 98 | 130 | 18 | 90 | 200 | 133 | 376 | 97 | 70 | 105 | 4 | 282 | 35 | 110 | 99 | 105 | 65 | 375 | 91 | 39 | 144 | 92 | 0 | 35 | 30 | 63 | 46 |  | 713 | 0 | 195 | 0 | 0 | 210 | 0 | 0 | 34 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 34 | 0 | 45 | 0 | 34 | 0 | 52 | 0 | 15 | 0 | 11 | 77 | 0 | 199 | 0 | 0 | 2 | 0 | 124 | 0 | 0 | 99 | 149 | 0 | 365 | 94 | 176 | 111 | 0 | 102 | 0 | 5 | 95 | 300 | 220 | 0 | 0 | 4 | 83 | 115 |  | 8286 | 3751 | 12037 | 3589 | 713 | 1657 | 976 | 3607 | 576 | 71 | 210 | 299 | 154 | 185 | 0 | 86.89
14:00 | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 250 | 150 | 0 | 0 | 55 | 202 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 20 | 33 | 33 | 40 | 0 | 71 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 12 | 0 | 0 | 80 | 0 | 45 | 0 | 5 | 0 | 0 | 0 | 270 | 260 | 206 | 8 | 138 | 29 | 40 | 0 | 51 | 0 | 40 | 46 | 19 | 11 | 16 | 18 | 164 | 81 | 0 | 17 | 2 | 30 | 30 | 50 | 0 | 0 | 0 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 200 | 280 | 306 | 100 | 189 | 100 | 133 | 16 | 90 | 200 | 130 | 404 | 106 | 70 | 105 | 4 | 284 | 35 | 110 | 99 | 105 | 70 | 387 | 91 | 34 | 144 | 92 | 0 | 12 | 25 | 63 | 0 |  | 712 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 34 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 0 | 34 | 0 | 45 | 0 | 34 | 24 | 52 | 0 | 14 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 3 | 0 | 118 | 0 | 0 | 100 | 139 | 0 | 362 | 105 | 176 | 110 | 0 | 101 | 0 | 5 | 113 | 320 | 213 | 0 | 0 | 4 | 74 | 115 |  | 8288 | 3782 | 12070 | 3602 | 712 | 1648 | 982 | 3598 | 597 | 71 | 205 | 327 | 164 | 164 | 0 | 86.89
15:00 | 0 | 0 | 200 | 0 | 250 | 95 | 0 | 0 | 0 |  | 0 | 240 | 150 | 0 | 0 | 55 | 205 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 20 | 33 | 23 | 40 | 0 | 71 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 13 | 0 | 0 | 80 | 0 | 46 | 0 | 3 | 0 | 0 | 0 | 270 | 270 | 213 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 33 | 18 | 162 | 81 | 0 | 17 | 2 | 30 | 30 | 44 | 0 | 0 | 0 | 60 | 83 | 0 | 0 | 0 | 0 | 10 | 300 | 20 | 11 | 200 | 281 | 300 | 96 | 178 | 95 | 132 | 13 | 90 | 200 | 120 | 363 | 96 | 90 | 105 | 3 | 267 | 35 | 98 | 99 | 105 | 100 | 380 | 91 | 28 | 144 | 92 | 0 | 34 | 18 | 63 | 0 |  | 712 | 0 | 195 | 0 | 0 | 206 | 0 | 0 | 31 | 0 | 0 | 62 | 27 | 0 | 0 | 0 | 0 | 34 | 6 | 45 | 0 | 34 | 24 | 52 | 32 | 15 | 0 | 11 | 76 | 0 | 199 | 0 | 9 | 3 | 0 | 118 | 0 | 0 | 100 | 138 | 0 | 362 | 94 | 176 | 110 | 27 | 99 | 0 | 4 | 113 | 320 | 214 | 0 | 0 | 3 | 55 | 115 |  | 8229 | 3821 | 12050 | 3575 | 712 | 1642 | 967 | 3623 | 595 | 71 | 215 | 362 | 162 | 126 | 0 | 86.88
16:00 | 0 | 0 | 0 | 0 | 250 | 98 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 207 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 20 | 33 | 23 | 40 | 0 | 71 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 13 | 0 | 9 | 86 | 0 | 46 | 0 | 3 | 0 | 0 | 0 | 357 | 340 | 214 | 8 | 137 | 29 | 45 | 0 | 51 | 0 | 40 | 34 | 19 | 11 | 33 | 18 | 160 | 97 | 0 | 17 | 1 | 30 | 30 | 44 | 0 | 0 | 0 | 58 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 20 | 11 | 200 | 278 | 304 | 100 | 177 | 99 | 131 | 7 | 90 | 200 | 120 | 402 | 96 | 70 | 105 | 1 | 260 | 35 | 92 | 99 | 103 | 100 | 390 | 91 | 15 | 144 | 109 | 0 | 35 | 12 | 69 | 14 |  | 712 | 0 | 215 | 0 | 0 | 208 | 0 | 0 | 33 | 0 | 0 | 62 | 24 | 0 | 0 | 0 | 0 | 34 | 37 | 48 | 0 | 34 | 24 | 52 | 32 | 16 | 0 | 11 | 77 | 0 | 200 | 12 | 8 | 3 | 0 | 118 | 0 | 0 | 100 | 144 | 0 | 362 | 100 | 173 | 110 | 50 | 99 | 0 | 3 | 113 | 320 | 195 | 0 | 0 | 2 | 35 | 115 |  | 8268 | 3881 | 12149 | 3625 | 712 | 1650 | 976 | 3647 | 597 | 71 | 228 | 407 | 160 | 76 | 0 | 86.87
17:00 | 0 | 0 | 0 | 0 | 250 | 103 | 0 | 0 | 0 |  | 0 | 270 | 150 | 0 | 0 | 55 | 207 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 20 | 33 | 25 | 49 | 0 | 71 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 10 | 17 | 90 | 0 | 46 | 0 | 6 | 0 | 0 | 0 | 330 | 335 | 180 | 8 | 137 | 29 | 49 | 0 | 51 | 0 | 40 | 38 | 19 | 11 | 33 | 18 | 156 | 97 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 0 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 20 | 11 | 150 | 280 | 210 | 70 | 177 | 70 | 132 | 2 | 90 | 200 | 125 | 404 | 97 | 90 | 105 | 0 | 281 | 35 | 92 | 99 | 113 | 90 | 390 | 91 | 6 | 144 | 113 | 0 | 35 | 4 | 63 | 34 |  | 713 | 0 | 215 | 0 | 0 | 210 | 0 | 0 | 33 | 0 | 0 | 63 | 24 | 0 | 0 | 0 | 0 | 42 | 39 | 53 | 0 | 43 | 24 | 52 | 32 | 15 | 0 | 11 | 78 | 0 | 200 | 14 | 8 | 2 | 0 | 118 | 0 | 0 | 50 | 144 | 0 | 362 | 105 | 130 | 110 | 50 | 99 | 0 | 1 | 113 | 320 | 197 | 0 | 0 | 1 | 14 | 115 |  | 8075 | 3800 | 11875 | 3560 | 713 | 1646 | 680 | 3751 | 598 | 71 | 232 | 440 | 156 | 28 | 0 | 86.86
18:00 | 0 | 0 | 200 | 0 | 250 | 104 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 206 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 24 | 51 | 92 | 0 | 45 | 0 | 8 | 0 | 0 | 0 | 320 | 330 | 213 | 8 | 137 | 29 | 51 | 0 | 51 | 0 | 41 | 40 | 19 | 11 | 33 | 18 | 166 | 96 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 40 | 55 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 13 | 11 | 50 | 280 | 24 | 40 | 187 | 40 | 132 | 0 | 90 | 200 | 138 | 402 | 96 | 90 | 105 | 0 | 281 | 35 | 97 | 99 | 112 | 100 | 379 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 69 | 55 |  | 712 | 0 | 215 | 0 | 0 | 210 | 0 | 0 | 33 | 0 | 0 | 60 | 28 | 0 | 0 | 0 | 0 | 43 | 37 | 90 | 0 | 43 | 24 | 52 | 32 | 16 | 0 | 11 | 80 | 0 | 200 | 12 | 8 | 3 | 0 | 118 | 0 | 0 | 50 | 144 | 0 | 360 | 105 | 50 | 113 | 50 | 103 | 0 | 0 | 113 | 300 | 184 | 0 | 0 | 0 | 1 | 115 |  | 8105 | 3715 | 11820 | 3802 | 712 | 1656 | 254 | 3824 | 580 | 70 | 230 | 525 | 166 | 1 | 0 | 86.85
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 250 | 104 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 206 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 141 | 0 | 0 | 0 |  | 18 | 32 | 51 | 100 | 0 | 48 | 0 | 11 | 0 | 0 | 0 | 320 | 330 | 212 | 8 | 137 | 29 | 52 | 0 | 51 | 0 | 41 | 38 | 19 | 11 | 33 | 20 | 162 | 98 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 110 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 200 | 281 | 204 | 100 | 198 | 100 | 134 | 0 | 90 | 200 | 142 | 405 | 106 | 90 | 105 | 0 | 281 | 35 | 98 | 99 | 113 | 100 | 385 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 82 | 55 |  | 713 | 0 | 220 | 0 | 0 | 211 | 0 | 0 | 40 | 0 | 0 | 63 | 31 | 0 | 0 | 0 | 0 | 43 | 37 | 90 | 0 | 43 | 32 | 52 | 32 | 19 | 0 | 11 | 80 | 0 | 200 | 15 | 8 | 2 | 0 | 118 | 0 | 0 | 80 | 144 | 0 | 359 | 105 | 176 | 113 | 50 | 109 | 0 | 0 | 113 | 370 | 218 | 0 | 0 | 0 | 0 | 115 |  | 8742 | 4012 | 12754 | 3916 | 713 | 1719 | 860 | 3882 | 650 | 70 | 234 | 548 | 162 | 0 | 0 | 86.82
19:30 | 0 | 0 | 200 | 0 | 250 | 104 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 206 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 40 | 51 | 100 | 0 | 48 | 0 | 16 | 0 | 0 | 0 | 350 | 335 | 215 | 8 | 137 | 29 | 52 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 20 | 154 | 98 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 200 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 200 | 281 | 303 | 100 | 198 | 100 | 149 | 0 | 90 | 200 | 142 | 402 | 107 | 90 | 105 | 0 | 281 | 40 | 110 | 99 | 113 | 100 | 395 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 96 | 55 |  | 712 | 0 | 235 | 0 | 0 | 212 | 0 | 0 | 36 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 37 | 52 | 34 | 20 | 0 | 11 | 80 | 0 | 200 | 16 | 8 | 2 | 0 | 119 | 0 | 0 | 100 | 144 | 0 | 359 | 105 | 176 | 113 | 56 | 110 | 0 | 0 | 113 | 520 | 218 | 0 | 0 | 0 | 0 | 115 |  | 9030 | 4213 | 13243 | 4066 | 712 | 1725 | 979 | 3941 | 800 | 70 | 236 | 560 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 212 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 40 | 51 | 100 | 0 | 50 | 0 | 7 | 0 | 0 | 0 | 358 | 345 | 216 | 8 | 137 | 29 | 52 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 33 | 21 | 154 | 99 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 200 | 281 | 304 | 100 | 198 | 100 | 149 | 0 | 90 | 200 | 142 | 402 | 107 | 90 | 105 | 0 | 300 | 46 | 110 | 99 | 114 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 88 | 55 |  | 712 | 0 | 235 | 0 | 0 | 214 | 0 | 0 | 31 | 0 | 0 | 65 | 32 | 16 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 32 | 20 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 2 | 0 | 121 | 0 | 0 | 90 | 144 | 0 | 415 | 105 | 176 | 113 | 22 | 110 | 0 | 0 | 113 | 560 | 220 | 0 | 0 | 0 | 0 | 115 |  | 9097 | 4259 | 13356 | 4122 | 712 | 1777 | 970 | 3943 | 839 | 70 | 214 | 555 | 154 | 0 | 0 | 86.83
21:00 | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 17 | 51 | 100 | 0 | 47 | 0 | 25 | 0 | 0 | 0 | 355 | 335 | 215 | 18 | 137 | 29 | 52 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 33 | 21 | 156 | 99 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 200 | 268 | 300 | 100 | 200 | 99 | 149 | 0 | 90 | 200 | 145 | 403 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 99 | 115 | 100 | 390 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 92 | 55 |  | 711 | 0 | 235 | 0 | 0 | 215 | 0 | 0 | 35 | 0 | 0 | 60 | 31 | 26 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 28 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 3 | 0 | 121 | 0 | 0 | 100 | 146 | 0 | 416 | 105 | 175 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 222 | 0 | 0 | 0 | 0 | 115 |  | 9092 | 4320 | 13412 | 4100 | 711 | 1819 | 974 | 3934 | 901 | 70 | 215 | 532 | 156 | 0 | 0 | 86.82
22:00 | 0 | 0 | 200 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 216 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 17 | 51 | 100 | 0 | 44 | 0 | 33 | 0 | 0 | 0 | 360 | 345 | 211 | 36 | 138 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 160 | 100 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 218 | 58 | 87 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 200 | 260 | 301 | 100 | 191 | 98 | 149 | 0 | 90 | 200 | 150 | 402 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 99 | 115 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 97 | 55 |  | 712 | 0 | 235 | 0 | 0 | 217 | 0 | 0 | 35 | 0 | 0 | 38 | 32 | 32 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 3 | 0 | 121 | 0 | 0 | 50 | 147 | 0 | 415 | 105 | 100 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 220 | 0 | 0 | 0 | 0 | 115 |  | 9113 | 4182 | 13295 | 4099 | 712 | 1823 | 849 | 3930 | 902 | 70 | 217 | 533 | 160 | 0 | 0 | 86.81
23:00 | 0 | 0 | 200 | 0 | 250 | 104 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 0 | 55 | 215 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 71 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 18 | 17 | 51 | 100 | 0 | 47 | 0 | 35 | 0 | 0 | 0 | 355 | 345 | 196 | 36 | 137 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 156 | 101 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 50 | 87 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 200 | 275 | 127 | 100 | 191 | 50 | 149 | 0 | 90 | 200 | 150 | 402 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 99 | 115 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 97 | 55 |  | 712 | 0 | 235 | 0 | 0 | 218 | 0 | 0 | 35 | 0 | 0 | 65 | 31 | 32 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 3 | 0 | 121 | 0 | 0 | 0 | 145 | 0 | 414 | 105 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 580 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8894 | 4014 | 12908 | 4098 | 712 | 1835 | 477 | 3948 | 860 | 71 | 218 | 533 | 156 | 0 | 0 | 86.8
24:00 | 0 | 0 | 200 | 0 | 250 | 101 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 216 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 71 | 0 | 0 | 150 | 25 | 145 | 0 | 0 | 0 |  | 18 | 17 | 51 | 100 | 0 | 50 | 0 | 36 | 0 | 0 | 0 | 350 | 335 | 186 | 36 | 135 | 29 | 55 | 0 | 51 | 0 | 25 | 42 | 19 | 11 | 25 | 21 | 154 | 100 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 50 | 88 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 283 | 53 | 100 | 191 | 0 | 149 | 0 | 90 | 200 | 143 | 402 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 99 | 110 | 90 | 390 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 96 | 55 |  | 714 | 0 | 235 | 0 | 0 | 218 | 0 | 0 | 35 | 0 | 0 | 65 | 31 | 32 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 28 | 22 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 3 | 0 | 121 | 0 | 0 | 0 | 133 | 0 | 414 | 105 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 560 | 222 | 0 | 0 | 0 | 0 | 115 |  | 8517 | 3987 | 12504 | 4055 | 714 | 1846 | 153 | 3935 | 841 | 71 | 218 | 517 | 154 | 0 | 0 | 86.79
KWH | 0 | 0 | 4413000 | 0 | 5973036 | 2371090 | 0 | 0 | 0 |  | 0 | 6031750 | 3584320 | 0 | 0 | 1113022 | 5169984 | 0 | 0 | 0 | 2062512 | 3413760 | 0 | 0 | 0 | 0 | 1294920 | 1133427 | 1323604 | 413172 | 600000 | 580860 | 762480 | 776900 | 1020000 | 0 | 1691471 | 0 | 0 | 3700000 | 403650 | 3118805 | 0 | 0 | 0 |  | 440160 | 164649 | 371947 | 1525560 | 0 | 1007040 | 0 | 488160 | 0 | 0 | 0 | 7698700 | 7273000 | 5032000 | 317818 | 3247460 | 654912 | 1084800 | 0 | 1174293 | 0 | 614152 | 1016904 | 439740 | 230040 | 677700 | 528660 | 3436800 | 2220480 | 0 | 369144 | 12700 | 715000 | 696152 | 1167600 | 0 | 0 | 3947000 | 1357152 | 2073600 | 0 | 0 | 0 | 0 | 244260 | 7099500 | 506784 | 228096 | 2222592 | 6440834 | 3435537 | 1470234 | 4521600 | 1299492 | 3287950 | 116910 | 2057280 | 3384000 | 3353818 | 9541000 | 2491200 | 1869600 | 2509927 | 27330 | 6879927 | 1060111 | 2599407 | 2112420 | 2633400 | 2227200 | 8159300 | 2182080 | 284360 | 3490560 | 2627018 | 0 | 862560 | 196264 | 1598400 | 1162080 |  | 17226181 | 2700 | 5712192 | 0 | 0 | 3525120 | 0 | 0 | 434880 | 0 | 0 | 1455000 | 578200 | 119232 | 0 | 0 | 0 | 543264 | 388880 | 1168808 | 0 | 503104 | 383139 | 1127520 | 391268 | 402480 | 0 | 252729 | 1906909 | 0 | 4848500 | 62000 | 40000 | 142500 | 0 | 3478391 | 0 | 0 | 1061760 | 3686327 | 0 | 9470982 | 2407680 | 1897835 | 2716800 | 263232 | 2519788 | 0 | 39417 | 2423904 | 11376900 | 4791109 | 0 | 0 | 31860 | 600480 | 2285688 |  | 195118117 | 90266759 | 285384876 | 93757696 | 17226181 | 40879962 | 11387450 | 86059119 | 18132309 | 1691471 | 3629820 | 7874747 | 3436800 | 1309321 | 0
Fuel Cost | 0 | 0 | 6442980 | 0 | 6630069.96 | 3129838.8 | 0 | 0 | 0 |  | 0 | 6574607.5 | 3978595.2 | 0 | 0 | 9416166.12 | 5376783.36 | 0 | 0 | 0 | 18810109.44 | 33591398.4 | 0 | 0 | 0 | 0 | 9452916 | 8761390.71 | 13050735.44 | 309879 | 450000 | 0 | 0 | 0 | 9863400 | 0 | 456697.17 | 0 | 0 | 6697000 | 3749908.5 | 3399497.45 | 0 | 0 | 0 |  | 0 | 1592155.83 | 3607885.9 | 14569098 | 0 | 7975756.8 | 0 | 1449835.2 | 0 | 0 | 0 | 5697038 | 7273000 | 4629440 | 409985.22 | 3734579 | 740050.56 | 1518720 | 0 | 2008041.03 | 0 | 6202935.2 | 9711433.2 | 558469.8 | 172530 | 1185975 | 396495 | 25776000 | 2353708.8 | 0 | 468812.88 | 202438 | 1172600 | 1113843.2 | 2078328 | 0 | 0 | 4104880 | 2673589.44 | 3960576 | 0 | 0 | 0 | 0 | 498290.4 | 7170495 | 380088 | 173352.96 | 37806289.92 | 48692705.04 | 58335418.26 | 24582312.48 | 23512320 | 21727506.24 | 32353428 | 1366677.9 | 16766832 | 36716400 | 23644416.9 | 8873130 | 22719744 | 17667720 | 21861464.17 | 0 | 52012248.12 | 9233566.81 | 22848787.53 | 21081951.6 | 22568238 | 14833152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99222802.56 | 77220 | 5997801.6 | 0 | 0 | 48858163.2 | 0 | 0 | 4561891.2 | 0 | 0 | 1644150 | 896210 | 1163704.32 | 0 | 0 | 0 | 5345717.76 | 3951020.8 | 10343950.8 | 0 | 6801966.08 | 3712616.91 | 10925668.8 | 3795299.6 | 772761.6 | 0 | 191315.853 | 11498661.27 | 0 | 26278870 | 2148300 | 1141200 | 166725 | 0 | 4591476.12 | 0 | 0 | 18060537.6 | 4313002.59 | 0 | 9376272.18 | 25136179.2 | 32282173.35 | 25782432 | 2484910.08 | 19553554.88 | 0 | 435557.85 | 17912650.56 | 49944591 | 0 | 0 | 0 | 0 | 0 | 0 |  | 814906708.44 | 459369354.763 | 1274276063.203 | 91912263.573 | 99222802.56 | 43822556.13 | 192794237.85 | 601634954.3 | 87722122.27 | 456697.17 | 52224883.2 | 76704872.4 | 25776000 | 2004673.75 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 260 | 150 | 0 | 0 | 55 | 208 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 71 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 21 | 0 | 0 | 70 | 0 | 44 | 0 | 5 | 0 | 0 | 0 | 270 | 260 | 206 | 8 | 136 | 29 | 40 | 0 | 51 | 0 | 30 | 43 | 19 | 11 | 15 | 18 | 148 | 82 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 0 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 305 | 22 | 8 | 200 | 283 | 298 | 100 | 191 | 97 | 134 | 19 | 76 | 195 | 137 | 380 | 97 | 70 | 90 | 4 | 300 | 35 | 110 | 99 | 108 | 65 | 382 | 91 | 42 | 144 | 94 | 0 | 35 | 30 | 56 | 54 |  | 713 | 0 | 220 | 0 | 0 | 195 | 0 | 0 | 34 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 52 | 0 | 15 | 0 | 11 | 76 | 0 | 199 | 0 | 0 | 7 | 0 | 128 | 0 | 0 | 90 | 158 | 0 | 388 | 94 | 176 | 112 | 0 | 102 | 0 | 5 | 95 | 270 | 220 | 0 | 0 | 4 | 87 | 115 |  | 12003 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 | 0 | 0 | 280 | 150 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 25 | 131 | 0 | 0 | 0 | 0 | 18 | 17 | 51 | 100 | 0 | 47 | 0 | 25 | 0 | 0 | 0 | 355 | 335 | 215 | 18 | 137 | 29 | 52 | 0 | 51 | 0 | 40 | 43 | 19 | 11 | 33 | 21 | 156 | 99 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 200 | 268 | 300 | 100 | 200 | 99 | 149 | 0 | 90 | 200 | 145 | 403 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 99 | 115 | 100 | 390 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 92 | 55 |  | 711 | 0 | 235 | 0 | 0 | 215 | 0 | 0 | 35 | 0 | 0 | 60 | 31 | 26 | 0 | 0 | 0 | 43 | 37 | 91 | 0 | 43 | 40 | 52 | 28 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 3 | 0 | 121 | 0 | 0 | 100 | 146 | 0 | 416 | 105 | 175 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 222 | 0 | 0 | 0 | 0 | 115 |  | 13412 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 100 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 | 0 | 22 | 40 | 51 | 100 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 340 | 340 | 220 | 36 | 137 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 22 | 163 | 68 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 99 | 113 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 |  | 100 | 55 |  | 728 | 0 | 225 | 0 | 0 | 225 | 0 | 0 | 40 | 30 | 0 | 65 | 30 | 80 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 43 | 40 | 52 | 31 | 22 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 88 | 0 | 124 | 0 | 0 | 100 | 126 | 0 | 350 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 95 | 660 | 220 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 64 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 6 | 0 | 0 | 0 | 320 | 320 | 220 | 36 | 137 | 29 | 55 | 0 | 51 | 0 | 32 | 43 | 22 | 11 | 33 | 22 | 138 | 68 | 0 | 17 | 1.6 | 30 | 30 | 50 | 0 | 0 | 220 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 90 | 50 | 144 | 113 | 0 | 35 | 30 | 100 | 55 |  | 728 | 0 | 225 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 42 | 0 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 88 | 0 | 124 | 0 | 0 | 100 | 126 | 0 | 350 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 95 | 660 | 180 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 250 | 105 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 16 | 55 | 150 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 69 | 0 | 0 | 150 | 25 | 130 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 50 | 0 | 45 | 0 | 6 | 0 | 0 | 0 | 275 | 275 | 182 | 36 | 137 | 29 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 0 | 21 | 18 | 74 | 88 | 0 | 14 | 0 | 30 | 30 | 44 | 0 | 0 | 225 | 40 | 88 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 281 | 0 | 0 | 183 | 0 | 149 | 6 | 90 | 100 | 142 | 352 | 98 | 90 | 105 | 2 | 281 | 54 | 93 | 82 | 106 | 100 | 220 | 91 | 11 | 144 | 101 | 0 | 35 | 5 | 96 | 55 | 0 | 714 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 40 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 54 | 0 | 121 | 0 | 0 | 0 | 126 | 0 | 284 | 105 | 0 | 113 | 0 | 110 | 0 | 1 | 95 | 270 | 153 | 0 | 0 | 0 | 29 | 115 | 0
199
| Minimum Generation |  | 10247 | 5:00
| Highest Generation |  | 13412 | 21:00
| Day Peak Generation |  | 12003 | 12:00
| Evening Peak Generation |  | 13412 | 21:00
| HVDC Max Flow |  | 714 | 24:00
| HVDC EvPeak Flow |  | 711 | 21:00
| Load factor L.F |  | 88.66%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-24
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12003 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10558 | MW
Evening Peak Generation : |  | 13412 | MW Hour : | 21:00 | Available Max Generation : |  | 13801 | MW
E.P. Demand (at gen end) : |  | 13412 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 13412 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1 | MW
Total Gen. (MKWH) : |  | 285.3849 | System Load Factor : | 88.66% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -78 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-24
Actual : | 86.73 | Ft.(MSL) , | Rule curve : | 89.32 | Ft.( MSL )
Gas Consumed : | Total = | 1083.39 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 135734819.703
: |  | Coal : | 87722122.27 | Oil : | 923358947.75 | Total : | 1146815889.723
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4913.4045 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1677.8291 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1504.5265 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1359.9094 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1228.6863 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 991.524 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 545.404 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 255.0524 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 764.7556 |  |  | 0 | 0%
Total | 0 |  | 13241.0918 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-100 MW & 71 MW
5) Raozan unit- 1
6) Kushiara 163 MW.
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bhaluka 132/33 kV T-1 transformer was under shut down from 08:09 to 10:00 for C/M. | [5 empty] | About 30 MW power interruption occurred under
Bhaluka S/S area from 08:09 to 10:00.
b) Meghnaghat-Aminbazar 230 kV Ckt-1 was under shut down from 09:03 to 16:11 for A/M.
c) Rangamati-Chandraghona 132 kV Ckt-2 was under shut down from 09:27 to 13:01 C/M.
d) Shahjibazar 330 MW was shut down at 11:37 due to problem with air compressor and GT-2 was
synchronized at 17:53.
e) Baraulia-KSRM 132 kV Ckt tripped at 11:06 from both sides showing O/C relay and was switched on at | [5 empty] | About 11 MW power interruption occurred under
11:23. | [5 empty] | KSRM S/S area from 11:06 to 11:23.
f) Madunaghat 132/33 kV T-1 transformer tripped at 11:07 showing Inst. E/F relay and was switched on at | [5 empty] | About 35 MW power interruption occurred under
11:51. | [5 empty] | Madunaghat S/S area from 11:07 to 11:51.
g) Barishal 132 kV Bus-A was under shut down from 10:35 to 11:20 for C/M.
h) Faridpur-Gopalganj(N) 132 kV Ckt-1 was under shut down from 09:07 to 17:35 for D/W.
i) Faridpur-Gopalganj(N) 132 kV Ckt-2 was under shut down from 09:21 to 17:36 for D/W.
j) Haripur 132 kV Reserve Bus was under shut down from 09:02 to 20:50 for C/M.
k) Kabirpur 132/33 kV T-1,T-2 & T-3 transformer tripped at 12:04 At LT side due to CT burst and T2 , T1 were | [5 empty] | About 227 MW power interruption occurred under
switched on at 12:40, 12:59 respectively. | [5 empty] | Kabirpur S/S area from 12:04 to 12:59.
l) Bheramara GK 132/33 kV T-1 transformer was under shut down from 13:01 to 14:46 for C/M.
m) Tongi 132/33 kV T-1 transformer tripped at 14:02 showing O/C relay and was switched on at 14:30.
n) Mithapukur 132/33 kV T-1 transformer was under shut down from 15:38 to 16:50 for C/M. | [5 empty] | About 1111 MW power interruption occurred under
Mithapukur S/S area from 15:38 to 16:50.
o) Bheramara-GK 132 kV Ckt-2 was under shut down from 15:34 to 21:18 for C/M.
p) Madanganj-Char Saidpur 132 kV Ckt was switched on at 19:39.
q) Ghorashal unit-4 tripped at 15:12 due to exciter tripping and was synchronized at 17:01.
r) Sirajganj unit-1 CCPP ST was synchronized at 00:20(24/2/2022).
s) After renewal contract, Madanganj Summit 102 MW was synchronized at 00:36(24/3/2022).
t) Keraniganj-Nawabganj 132 kV Ckt-2 tripped at 04:40(24/3/2022) from both sides showing Dist. Z1,E/F
relay and was switched on at 06:47.
u) Hasnabad 33 kV main Bus under 132/33 kV transformer tripped at 06:06(24/3/2022) showing master trip | [5 empty] | About 60 MW power interruption occurred under
and was switched on at 06:32. | [5 empty] | Hasnabad S/S area from 06:06(24/3/2022) to 06:32.
v) Narshingdi 132/33 kV T-1 transformer tripped at 06:41(24/3/20220 from 33 kV side showing O/C relay due
to 33 kV Raipur feeder fault and was switched on at 06:49.
w) Gopalganj(N)-Faridpur 132 kV Ckt-1 & 2 were shut down at 06:29(24/3/2022) for D/W.
x) Norail 132/33 kV T-1 transformer was under shut down from 06:47(24/3/20220 to 08:35 for R/H maint. | [5 empty] | About 15 MW power interruption occurred under
Norail S/S area from 06:47(24/3/20220 to 08:35.
y) Chattak 132/33 kV T-1 transformer was shut down at 07:14(24/3/2022) for C/M.
z) Haripur 230/132 kV T-2 transformer was shut down at 07:35(24/3/2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4413000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 5973036 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2371090
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6031750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3584320 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1113022
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 413172
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 213 | 5169984 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2062512 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1294920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3413760
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1133427
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1323604
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1180860 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 762480
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 776900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1020000 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 268 | 6440834 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 3435537
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 1470234
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 1299492
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3287950
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 1869600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 2182080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3490560 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 196264
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1162080
| Dhaka area Total |  |  |  | 5696 | 3146 | 66872468
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 403650
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 116910
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 1007040
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1691471 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 131 | 3118805 | ST under S/D
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2509927
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 17 | 164649 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 371947 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1525560
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2057280 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 488160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27330
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6879927
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1060111
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2599407
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2227200
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2627018
| Chattogram area Total |  |  |  | 2382 | 1488 | 32576392
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 5032000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 355 | 7698700
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 335 | 7273000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 654912 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1084800
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 18 | 317818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1174293
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 3353818
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 614152 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 3247460 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3384000
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439740
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 230040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3436800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 677700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1016904 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 528660 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2222592
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 2112420 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2633400
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 862560 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1598400 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2401 | 49594169
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 2220480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 369144 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 4521600
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 2491200
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 284360
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 440160 | Engine problem
| Mymensingh Area Total |  |  |  | 622 | 441 | 10339644
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 696152 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 221 | 3947000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1167600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 228096
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1357152
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 87 | 2073600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 506784
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7099500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9541000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244260
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 390 | 8159300
| Sylhet Area Total |  |  |  | 2377 | 1616 | 35735444
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 2700 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 711 | 17226181
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 434880 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 215 | 3525120
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 5712192 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 1061760
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2407680
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 263232 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 600480
| Khulna Area Total |  |  |  | 2229 | 1401 | 31234225
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 26 | 119232 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 578200
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1455000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 11376900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4791109
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 961 | 18320441
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 543264 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 37 | 388880 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 503104 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 383139 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 3 | 142500 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 121 | 3478391 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 146 | 3686327 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 9470982
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 391268 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 402480
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252729
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1127520
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 1168808 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 175 | 1897835 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2716800
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2423904
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31860
| Rajshahi Area Total |  |  |  | 2129 | 1454 | 29009791
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4848500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 62000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 40000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 2519788
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39417
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2285688
| Rangpur Area Total |  |  |  | 720 | 504 | 11702302
| Total |  |  |  | 21215 | 13412 | 285384876
| Eastern Grid Total |  |  |  | 14091 | 9092 | 195118117
| Western Grid Total |  |  |  | 7124 | 4320 | 90266759
| National Grid Total |  |  |  | 21215 | 13412 | 285384876
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-23
(a) ENTIRE EASTERN GRID : |  | 8539.87 | MW | (b) ENTIRE WESTERN GRID : |  | 4320.2 | MW
i) Dhaka area |  | 4852.77 | MW | i) Khulna area |  | 1194 | MW
ii) Chittagong area |  | 1301 | MW | ii) Rajshahi area |  | 1011 | MW
iii) Comilla area |  | 485 | MW | iii) Barisal area |  | 1373.2 | MW
iv) Mymensingh area |  | 1538.1 | MW | iv) Rangpur area |  | 742 | MW
v) Sylhet area |  | 363 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12860.07 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 125 | 19:30 | Valuka | 112 | 18:30 | Central S/S | 94 | 19:30
Munsiganj | 98 | 21:00 | Tangail | 218 | 0:00 | Noapara | 49 | 19:30
Sonargaon | 115 | 12:00 | Mymensing | 230 | 20:00 | Jessore | 122 | 21:00
Bhulta | 228 | 15:00 | Kishoreganj | 124 | 1:00 | Benapol | 56 | 20:00
Madanganj | 98 | 0:00 | Netrokona | 126 | 6:00 | Jhenida(Old) | 114 | 19:30
Rahim steel | 28 | 12:00 | Jamalpur | 139 | 9:00 | Bottail | 130 | 19:30
Ghorasal | 126 | 19:30 | Sherpur | 138 | 7:00 | G.K Project | 59 | 20:00
Narsingdi | 179 | 20:00 | Srimongal | 56 | 21:00 | Faridpur | 134 | 19:00
Haripur(SBU) | 103 | 22:00 | Shahjibazar | 119 | 22:00 | Rajbari | 64 | 19:00
Sreenagar | 56 | 21:00 | Fenchuganj | 40 | 18:00 | Madaripur | 97 | 21:00
Shyampur | 200 | 11:00 | Kulawara | 34 | 18:30 | Sariatpur | 48 | 18:30
Shitalakhya | 119 | 15:00 | Sylhet | 155 | 19:00 | Gopalganj | 94 | 19:00
Matuail | 60 | 9:00 | Chatak | 26 | 18:30 | Bagerhat | 96 | 20:00
Char Saidpur | 44 | 0:00 | Sunamganj | 38 | 18:30 | Mongla | 46 | 12:00
Ullon | 49 | 20:00 | Biani Bazar | 55 | 18:30 | Satkhira | 116 | 20:00
Hasnabad | 80 | 11:00 | Comilla (S) | 182 | 18:30 | Gallamari | 55 | 19:00
Magbazar | 121 | 16:00 | Comilla(N) | 154 | 21:00 | Magura | 54 | 19:00
Maniknagar | 74 | 13:00 | Chandpur | 71 | 19:00 | Norail | 51 | 19:30
Bangabhaban | 24 | 10:00 | Feni | 126 | 19:30 | Chuadanga | 100 | 20:00
Motijheel | 28 | 12:00 | Chowmuhani | 194 | 21:00 | Barisal(N) | 54 | 19:00
Narinda | 58 | 12:00 | Ashuganj | 39 | 14:00 | Barisal (S) | 100 | 21:00
Kazla | 88 | 23:00 | Daudkandi | 140 | 22:00 | Patuakhali | 105 | 20:00
Dhanmondi | 203 | 14:00 | B.Baria | 142 | 1:00 | Bhandaria | 50 | 19:30
Lalbag | 96 | 14:00 | Ramganj | 84 | 19:30 | Borguna | 16 | 19:00
Madartek | 45 | 8:00 | Chaddagram | 50 | 18:30 | Borhan Uddin | 41 | 19:00
Dhaka University | 36 | 11:00 | PHP | 9 | 16:00 | Ishurdi | 71 | 19:30
Aftabnagar | 32 | 18:30 | Kochua | 64 | 19:00 | Ruppur Paromanobik | 4 | 11:00
Fatullah | 134 | 19:00 | Madunaghat | 59 | 21:00 | Natore | 143 | 20:00
Nawabganj | 49.8 | 21:00 | Hathazari | 95 | 18:30 | Bogra | 172 | 22:00
Keraniganj | 74 | 19:30 | Khulshi | 185 | 20:00 | Naogaon | 118 | 22:00
Banani | 57 | 14:00 | Halishahar | 93 | 15:00 | Rajshahi | 128 | 23:00
Mirpur | 128 | 19:00 | Baraulia | 101 | 0:00 | Rajshahi New | 46 | 22:00
Kalyanpur | 99 | 18:30 | Sikalbaha | 35 | 18:30 | C.Nawabganj | 66 | 21:00
Gulshan | 90 | 2:00 | Dohazari | 112 | 19:30 | Amnura | 64 | 0:00
Uttara | 67 | 15:00 | Cox'sbazar | 116 | 13:00 | Pabna | 105 | 20:00
Uttara New | 34 | 14:00 | Chandraghona | 28 | 19:00 | Shahjadpur | 112 | 21:00
Kamrangirchar | 73 | 18:30 | Kaptai | 5 | 18:30 | Serajganj | 120 | 21:00
Savar | 175 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 100 | 0:00
Bhasantec | 136 | 18:30 | Bakulia | 126 | 18:30 | Joypurhat | 59 | 0:00
Agargaon | 91 | 13:00 | Hasnabad | 28 | 12:00 | Sherpur(Bogura) | 60 | 22:00
Satmosjid | 90 | 13:00 | TK chemical | 21 | 18:00 | Mohastangor | 70 | 20:00
Old Tongi | 128 | 17:00 | Modern Steel | 0 | 1:00 | Bhangura | 38 | 20:00
Kabirpur | 272 | 10:00 | Shahmirpur | 32 | 0:00 | Rangpur | 128 | 13:00
Manikgonj | 97 | 20:00 | Khagrachhari | 28 | 18:30 | Lalmonirhat | 45 | 8:00
Joydevpur | 185 | 17:00 | Matarbari | 39 | 21:00 | Saidpur | 109 | 8:00
New Tongi | 84.7 | 16:00 | Baroiar Hat | 52 | 20:00 | Purbasadipur | 112 | 14:00
Kodda | 317 | 18:00 | Rangamati | 12 | 19:00 | Thakurgaon | 88 | 21:00
Dhamrai | 102 | 18:30 | Agrabad | 80 | 15:00 | Palashbari | 102 | 13:00
Rajendrapur | 108 | 20:00 | Rampur | 13 | 15:00 | Barapukuria | 54 | 8:00
Bashundara | 174 | 18:30 | Abul Khair 230 | 135 | 16:00 | Panchagar | 56 | 19:00
Purbachal | 19 | 19:00 | BSRM | 162 | 5:00 | Joldhaka | 57 | 20:00
Tongi Millgate | 52 | 18:30 | GPH Ispat | 90 | 2:00 | Kurigram | 60 | 18:00
Bashundhara Cement | 13 | 0:00 | Goalpara | 79 | 0:00 | Mithapukur | 40 | 21:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 20:00 | 399 | 12:00 | Kaliakoir | 390 | 0.75 | 376 | 0.45833
| Bheramara | 404 | 7:00 | 394 | 12:00 | Bhulta | 404 | 0.83333 | 387 | 0.45833
| Ashuganj(N) | 411 | 4:00 | 395 | 11:00 | Gopalganj | 420 | 0.625 | 390 | 0.875
| Payra | 420 | 22:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 238 | 14:00 | Hathazari | 238 | 4:00 | 233 | 24:00
| Ishurdi | 237 | 16:00 | 231 | 7:00 | Megnaghat | 232 | 8:00 | 228 | 10:00
| Ashuganj | 242 | 3:00 | 235 | 18:00 | Fenchuganj | 238 | 21:00 | 230 | 18:00
| Serajganj | 237 | 16:00 | 232 | 7:00 | Siddhirganj | 227 | 4:00 | 221 | 10:00
| Baghabari | 237 | 18:00 | 231 | 6:00 | Maniknagar | 228 | 4:00 | 217 | 11:00
| Barapukuria | 233 | 18:00 | 220 | 7:00 | Agargaon | 228 | 9:00 | 216 | 11:00
| Bogra | 235 | 18:30 | 223 | 7:00 | Barisal | 245 | 3:00 | 233 | 20:00
| Rajshahi | 236 | 16:00 | 226 | 7:00 | Bhola 225 MW | 247 | 9:00 | 241 | 21:00
| Khulna South | 242 | 16:00 | 231 | 20:00 | AKSML | 238 | 3:00 | 230 | 12:00
| Rampura | 233 | 14:00 | 219 | 11:00 | BSRM | 235 | 1:00 | 229 | 10:00
| Haripur | 227 | 7:00 | 219 | 10:00 | Bibiyana | 237 | 7:00 | 230 | 18:00
| Hasnabad | 228 | 22:00 | 220 | 9:00 | Bhulta | 231 | 4:00 | 219 | 11:00
| Shyampur | 228 | 22:00 | 217 | 11:00 | Ashuganj (S) | 239 | 1:00 | 232 | 11:00
| Aminbazar | 228 | 1:00 | 219 | 2:00 | Kaliakoir | 230 | 3:00 | 219 | 11:00
| Tongi | 230 | 4:00 | 217 | 15:00 | GPH | 237 | 8:00 | 230 | 12:00
| Comilla (N) | 233 | 8:00 | 226 | 11:00 | Jhenaidah | 237 | 7:00 | 224 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 127 | 11:00 | PHP | 138 | 1:00 | 130 | 19:30
| Munsiganj | 136 | 2:00 | 129 | 11:00 | Kachua | 139 | 1:00 | 133 | 19:30
| Sonargaon | 134 | 3:00 | 128 | 10:00 | Madanhat | 138 | 2:00 | 133 | 11:00
| Bhulta | 130 | 6:00 | 123 | 11:00 | Hathazari | 140 | 2:00 | 134 | 12:00
| Madanganj | 135 | 7:00 | 128 | 11:00 | Khulshi | 137 | 1:00 | 131 | 12:00
| Rahim steel | 135 | 4:00 | 129 | 10:00 | Halishahar | 138 | 8:00 | 132 | 12:00
| Ghorasal | 139 | 1:00 | 134 | 15:00 | Baraulia | 138 | 4:00 | 133 | 17:00
| Narsingdi | 131 | 5:00 | 124 | 11:00 | Sikalbaha | 138 | 7:00 | 133 | 12:00
| Haripur(SBU) | 135 | 5:00 | 129 | 10:00 | Dohazari | 133 | 15:00 | 127 | 12:00
| Sreenagar | 138 | 22:00 | 131 | 10:00 | Cox'sbazar | 123 | 7:00 | 116 | 20:00
| Shyampur | 134 | 20:00 | 126 | 11:00 | Chandraghona | 139 | 8:00 | 134 | 12:00
| Shitalakhya | 137 | 8:00 | 130 | 11:00 | Kaptai | 135 | 13:00 | 130 | 1:00
| Matuail | 133 | 1:00 | 127 | 11:00 | A. Khaer Stl. | 136 | 4:00 | 134 | 10:00
| Char Saidpur | 136 | 2:00 | 129 | 11:00 | Bakulia | 137 | 1:00 | 131 | 12:00
| Ullon | 138 | 1:00 | 128 | 11:00 | Julda | 138 | 1:00 | 133 | 12:00
| Hasnabad | 136 | 20:00 | 132 | 18:00 | TK Chemical | 139 | 7:00 | 134 | 4:00
| Magbazar | 139 | 1:00 | 130 | 12:00 | Modern Steel | 138 | 8:00 | 133 | 11:00
| Maniknagar | 133 | 4:00 | 124 | 11:00 | Shahmirpur | 138 | 8:00 | 132 | 12:00
| Bangabhaban | 132 | 1:00 | 124 | 11:00 | Khagrachhari | 138 | 21:00 | 131 | 12:00
| Motijheel | 132 | 1:00 | 124 | 10:00 | 0 | 127 | 15:00 | 118 | 19:30
| Narinda | N/A | N/A | N/A | N/A | Baroiar Hat | 138 | 8:00 | 132 | 11:00
| Kazla | 132 | 4:00 | 125 | 12:00 | Rangamati | 138 | 8:00 | 132 | 12:00
| Dhanmondi | 136 | 6:00 | 126 | 11:00 | Agrabad | 137 | 7:00 | 132 | 11:00
| Lalbag | 137 | 4:00 | 130 | 11:00 | Rampur | 137 | 7:00 | 132 | 3:00
| Madartek | 138 | 1:00 | 130 | 15:00 | Goalpara S/S | 139 | 16:00 | 135 | 2:00
| Dhaka University | 138 | 3:00 | 129 | 14:00 | Khulna Central S/S | 138 | 16:00 | 133 | 20:00
| Aftabnagar | 138 | 2:00 | 128 | 11:00 | Noapara | 139 | 16:00 | 133 | 20:00
| Fatullah | 137 | 22:00 | 129 | 11:00 | Jessore | 135 | 16:00 | 129 | 20:00
| Nawabganj | 137 | 3:00 | 130 | 11:00 | Benapol | 134 | 14:00 | 128 | 20:00
| Keraniganj | 137 | 3:00 | 130 | 11:00 | Jhenida(Old) | 134 | 16:00 | 128 | 21:00
| Banani | 138 | 2:00 | 129 | 11:00 | Bottail | 136 | 16:00 | 130 | 20:00
| Mirpur | 135 | 7:00 | 126 | 11:00 | G.K Project | 140 | 16:00 | 135 | 20:00
| Kalyanpur | 135 | 3:00 | 127 | 11:00 | Faridpur | 138 | 9:00 | 125 | 14:00
| Gulshan | 137 | 3:00 | 128 | 11:00 | Rajbari | 134 | 4:00 | 127 | 13:00
| Uttara | 135 | 4:00 | 127 | 10:00 | Madaripur | 143 | 9:00 | 130 | 20:00
| Uttara New | 135 | 3:00 | 126 | 11:00 | Shariyatpur S/S | 142 | 14:00 | 130 | 20:00
| Kamrangirchar | 136 | 3:00 | 131 | 10:00 | Gopalganj | 142 | 16:00 | 128 | 20:00
| Savar | 136 | 1:00 | 127 | 11:00 | Bagerhat | 137 | 15:00 | 129 | 20:00
| Bhasantec | 134 | 4:00 | 125 | 11:00 | Mongla | 136 | 15:00 | 129 | 20:00
| Agargaon | 135 | 4:00 | 122 | 16:00 | Satkhira | 135 | 15:00 | 128 | 20:00
| Satmosjid | 134 | 3:00 | 126 | 11:00 | Gallamari | 139 | 9:00 | 126 | 20:00
| Old Tongi | 137 | 4:00 | 123 | 22:00 | Magura | 132 | 10:00 | 125 | 20:00
| Kabirpur | 138 | 19:00 | 124 | 16:00 | Narail | 131 | 5:00 | 123 | 20:00
| Manikgonj | 135 | 13:00 | 123 | 6:00 | Chuadanga | 128 | 8:00 | 116 | 20:00
| Joydevpur | 140 | 18:00 | 135 | 10:00 | Barisal(N) | 143 | 10:00 | 135 | 21:00
| New Tongi | 137 | 19:30 | 128 | 11:00 | Barisal (S) | 143 | 9:00 | 136 | 19:30
| Kodda | 140 | 18:30 | 122 | 15:00 | Patuakhali(S) | 138 | 6:00 | 131 | 19:30
| Dhamrai | 137 | 3:00 | 129 | 11:00 | Bhandaria | 141 | 5:00 | 131 | 20:00
| Rajendrapur | 136 | 4:00 | 122 | 16:00 | Barguna | 138 | 9:00 | 131 | 19:00
| Bashundara | 136 | 2:00 | 124 | 16:00 | Jhenida(New) | 134 | 16:00 | 127 | 20:00
| Purbachal | 138 | 1:00 | 128 | 11:00 | Ishurdi | 138 | 16:00 | 134 | 7:00
| Tongi Millgate | 136 | 1:00 | 127 | 17:00 | Ruppur Paromanobik | 137 | 14:00 | 134 | 7:00
| Bashundhara Cement | 135 | 7:00 | 128 | 11:00 | Natore | 137 | 18:00 | 130 | 7:00
| Valuka | 117 | 5:00 | 108 | 7:00 | Bogra | 137 | 18:00 | 129 | 7:00
| Tangail | 129 | 12:00 | 124 | 9:00 | Noagaon | 134 | 18:00 | 119 | 7:00
| Mymensing | 119 | 18:30 | 112 | 7:00 | Rajshahi | 135 | 16:00 | 127 | 7:00
| Kishorganj | 124 | 5:00 | 118 | 1:00 | Rajshahi New | 135 | 18:00 | 128 | 7:00
| Netrokona | 115 | 4:00 | 109 | 7:00 | C.Nawabganj | 132 | 17:00 | 125 | 7:00
| Jamalpur | 128 | 6:00 | 120 | 7:00 | Amnura | 133 | 18:00 | 122 | 7:00
| Sherpur | 125 | 6:00 | 114 | 21:00 | Pabna | 136 | 18:30 | 131 | 7:00
| Srimongal | 138 | 8:00 | 132 | 18:00 | Shahjadpur | 142 | 4:00 | 135 | 7:00
| Shahjibazar | 135 | 6:00 | 130 | 22:00 | Serajganj | 134 | 3:00 | 128 | 7:00
| Fenchuganj | 136 | 6:00 | 129 | 18:00 | Niyamatpur | 124 | 2:00 | 113 | 7:00
| Khulawara | 135 | 6:00 | 129 | 14:00 | Joypurhat | 135 | 17:00 | 116 | 7:00
| Sylhet | 131 | 6:00 | 123 | 18:00 | Sherpur(Bogura) | 136 | 18:30 | 130 | 13:00
| Chatak | 131 | 6:00 | 123 | 18:30 | Mohastangor | 137 | 18:00 | 127 | 7:00
| Sunamganj | 128 | 6:00 | 119 | 18:00 | Bhangura | 137 | 18:30 | 132 | 8:00
| Biani Bazar | 131 | 7:00 | 119 | 18:30 | Rangpur | 133 | 17:00 | 122 | 13:00
| Comilla(s) | 131 | 4:00 | 123 | 18:30 | Lalmonirhat | 132 | 19:00 | 120 | 7:00
| Comilla(n) | 138 | 8:00 | 132 | 11:00 | Saidpur | 133 | 17:00 | 119 | 7:00
| Chandpur | 142 | 3:00 | 136 | 19:30 | Purbasadipur | 135 | 17:00 | 115 | 7:00
| Feni | 139 | 7:00 | 131 | 19:30 | Thakurgaon | 136 | 17:00 | 115 | 7:00
| Chowmuhani | 138 | 8:00 | 131 | 22:00 | Palashbari | 134 | 18:00 | 122 | 7:00
| Ashuganj | 135 | 4:00 | 133 | 0:00 | Barapukuria | 132 | 18:00 | 124 | 7:00
| Daudkandi | 135 | 19:00 | 127 | 11:00 | Panchagar | 137 | 17:00 | 115 | 7:00
| B.Baria | 133 | 7:00 | 127 | 23:00 | Joldhaka | 132 | 17:00 | 115 | 7:00
| Ramganj | 138 | 2:00 | 131 | 19:30 | Kurigram | 132 | 17:00 | 115 | 7:00
| Chaddagram | 139 | 7:00 | 132 | 19:30 | Mithapukur | 136 | 18:00 | 125 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 168 | 8517 | 3987 | 12504 |  |  |  | QF-LDC-11
0:30 | 93 | 8319.5 | 3841.5 | 12161 | Date: | 2022-03-23
1:00 | 18 | 8122 | 3696 | 11818
1:30 | 31 | 7977.5 | 3617 | 11594.5
2:00 | 44 | 7833 | 3538 | 11371
2:30 | 52 | 7685.5 | 3442 | 11127.5 | [5 empty] | Gen. at Eve. Peak | 13412 | 13412 MW (21:00 )
3:00 | 60 | 7538 | 3346 | 10884 | [6 empty] | 21:00
3:30 | 49 | 7469.5 | 3271 | 10740.5 | [5 empty] | Gen. at Day Peak | 12003 | 12003 MW (12:00 )
4:00 | 38 | 7401 | 3196 | 10597 | [6 empty] | 12:00
4:30 | 40 | 7267.5 | 3154.5 | 10422 | [5 empty] | Highest Generation | 13412
5:00 | 42 | 7134 | 3113 | 10247 | [6 empty] | 21:00
5:30 | 53 | 7118 | 3131 | 10249
6:00 | 64 | 7102 | 3149 | 10251
6:30 | 71 | 7151 | 3187 | 10338
7:00 | 78 | 7200 | 3225 | 10425
7:30 | 76 | 7272.5 | 3268 | 10540.5
8:00 | 74 | 7345 | 3311 | 10656
8:30 | 45 | 7545 | 3272 | 10817
9:00 | 16 | 7745 | 3233 | 10978
9:30 | 47 | 7931.5 | 3275.5 | 11207
10:00 | 78 | 8118 | 3318 | 11436
10:30 | 135 | 8112.5 | 3484 | 11596.5
11:00 | 192 | 8107 | 3650 | 11757
11:30 | 261 | 8188.5 | 3691.5 | 11880
12:00 | 330 | 8270 | 3733 | 12003
12:30 | 235 | 8278 | 3742 | 12020
13:00 | 140 | 8286 | 3751 | 12037
13:30 | 193 | 8287 | 3766.5 | 12053.5
14:00 | 246 | 8288 | 3782 | 12070
14:30 | 310 | 8258.5 | 3801.5 | 12060
15:00 | 374 | 8229 | 3821 | 12050
15:30 | 398 | 8248.5 | 3851 | 12099.5
16:00 | 422 | 8268 | 3881 | 12149
16:30 | 559 | 8171.5 | 3840.5 | 12012
17:00 | 696 | 8075 | 3800 | 11875
17:30 | 710 | 8090 | 3757.5 | 11847.5
18:00 | 724 | 8105 | 3715 | 11820
18:30 | 511 | 8423.5 | 3863.5 | 12287
19:00 | 298 | 8742 | 4012 | 12754
19:30 | 246 | 9030 | 4213 | 13243
20:00 | 136 | 9097 | 4259 | 13356 |  |  |  | Executive Engineer
20:30 | 120 | 9094.5 | 4289.5 | 13384 |  |  |  | Network Operation Division
21:00 | 104 | 9092 | 4320 | 13412
21:30 | 88 | 9102.5 | 4251 | 13353.5
22:00 | 72 | 9113 | 4182 | 13295 |  |  |  |  | Page 6 of 7
22:30 | 51 | 9003.5 | 4098 | 13101.5
23:00 | 30 | 8894 | 4014 | 12908
23:30 | 99 | 8705.5 | 4000.5 | 12706
24:00 | 168 | 8517 | 3987 | 12504
13412 MW (21:00 )
12003 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-23 |  | Energy |  | 285384876
[13 empty] | 2022-03-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4055 | 714 | 1846 | 153 | 3935 | 841 | 71 | 218 | 517 | 154 | 0 | 0
0:30 | 4064 | 712.5 | 1775 | 89 | 3865 | 829 | 71 | 146.5 | 463 | 146 | 0 | 0 | Date: | 2022-03-23
1:00 | 4073 | 711 | 1704 | 25 | 3795 | 817 | 71 | 75 | 409 | 138 | 0 | 0
1:30 | 4054.5 | 711 | 1699.5 | 12.5 | 3647.5 | 809 | 70.5 | 45 | 408 | 137 | 0 | 0 | [8 empty] | Total Energy | 285.3849 | Total Energy Gen 285.385 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 285.385 MKWHr
2:00 | 4036 | 711 | 1695 | 0 | 3500 | 801 | 70 | 15 | 407 | 136 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4007.5 | 711 | 1702.5 | 0 | 3363 | 790 | 70 | 15 | 333.5 | 135 | 0 | 0 | [8 empty] | Energy Requirement | 285.3849
3:00 | 3979 | 711 | 1710 | 0 | 3226 | 779 | 70 | 15 | 260 | 134 | 0 | 0
3:30 | 3983.5 | 711 | 1698 | 0 | 3153 | 776 | 69.5 | 12.5 | 205 | 132 | 0 | 0 | [6 empty] | Shortage
4:00 | 3988 | 711 | 1686 | 0 | 3080 | 773 | 69 | 10 | 150 | 130 | 0 | 0
4:30 | 3918.5 | 710.5 | 1676.5 | 0 | 3015.5 | 759 | 69 | 20 | 125 | 128 | 0 | 0
5:00 | 3849 | 710 | 1667 | 0 | 2951 | 745 | 69 | 30 | 100 | 126 | 0 | 0
5:30 | 3846.5 | 710.5 | 1670 | 0 | 2936.5 | 746.5 | 68.5 | 47.5 | 100 | 123 | 0 | 0
6:00 | 3844 | 711 | 1673 | 0 | 2922 | 748 | 68 | 65 | 100 | 120 | 0 | 0
6:30 | 3900 | 710.5 | 1687 | 0 | 2935.5 | 747 | 68.5 | 60 | 100 | 119 | 10.5 | 0 |  |  |  |  | Coal
7:00 | 3956 | 710 | 1701 | 0 | 2949 | 746 | 69 | 55 | 100 | 118 | 21 | 0
7:30 | 3860.5 | 710.5 | 1652.5 | 0 | 3162.5 | 741.5 | 69 | 55 | 125 | 121 | 43 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3765 | 711 | 1604 | 0 | 3376 | 737 | 69 | 55 | 150 | 124 | 65 | 0
8:30 | 3797 | 711.5 | 1610.5 | 75 | 3447.5 | 660 | 69.5 | 82.5 | 150 | 126 | 87.5 | 0
9:00 | 3829 | 712 | 1617 | 150 | 3519 | 583 | 70 | 110 | 150 | 128 | 110 | 0
9:30 | 3867 | 712 | 1676 | 240.5 | 3542.5 | 554.5 | 70 | 125 | 157.5 | 134 | 128 | 0
10:00 | 3905 | 712 | 1735 | 331 | 3566 | 526 | 70 | 140 | 165 | 140 | 146 | 0
10:30 | 3896 | 712 | 1713 | 431.5 | 3574.5 | 526.5 | 70 | 160 | 204 | 144 | 165 | 0
11:00 | 3887 | 712 | 1691 | 532 | 3583 | 527 | 70 | 180 | 243 | 148 | 184 | 0
11:30 | 3750.5 | 712.5 | 1698 | 746.5 | 3591 | 536 | 70.5 | 187.5 | 251 | 148 | 188.5 | 0
12:00 | 3614 | 713 | 1705 | 961 | 3599 | 545 | 71 | 195 | 259 | 148 | 193 | 0
12:30 | 3601.5 | 713 | 1681 | 968.5 | 3603 | 560.5 | 71 | 202.5 | 279 | 151 | 189 | 0
13:00 | 3589 | 713 | 1657 | 976 | 3607 | 576 | 71 | 210 | 299 | 154 | 185 | 0
13:30 | 3589 | 713 | 1657 | 976 | 3607 | 576 | 71 | 210 | 299 | 154 | 185 | 0
14:00 | 3589 | 713 | 1657 | 976 | 3607 | 576 | 71 | 210 | 299 | 154 | 185 | 0
14:30 | 3582 | 712.5 | 1649.5 | 971.5 | 3615 | 585.5 | 71 | 212.5 | 330.5 | 158 | 155.5 | 0
15:00 | 3575 | 712 | 1642 | 967 | 3623 | 595 | 71 | 215 | 362 | 162 | 126 | 0
15:30 | 3600 | 712 | 1646 | 971.5 | 3635 | 596 | 71 | 221.5 | 384.5 | 161 | 101 | 0
16:00 | 3625 | 712 | 1650 | 976 | 3647 | 597 | 71 | 228 | 407 | 160 | 76 | 0
16:30 | 3560 | 712.5 | 1648 | 828 | 3699 | 597.5 | 71 | 230 | 423.5 | 158 | 52 | 0
17:00 | 3560 | 713 | 1646 | 680 | 3751 | 598 | 71 | 232 | 440 | 156 | 28 | 0
17:30 | 3681 | 712.5 | 1651 | 467 | 3787.5 | 589 | 70.5 | 231 | 482.5 | 161 | 14.5 | 0
18:00 | 3802 | 712 | 1656 | 254 | 3824 | 580 | 70 | 230 | 525 | 166 | 1 | 0
18:30 | 3859 | 712.5 | 1687.5 | 557 | 3853 | 615 | 70 | 232 | 536.5 | 164 | 0.5 | 0
19:00 | 3916 | 713 | 1719 | 860 | 3882 | 650 | 70 | 234 | 548 | 162 | 0 | 0
19:30 | 4066 | 712 | 1725 | 979 | 3941 | 800 | 70 | 236 | 560 | 154 | 0 | 0
20:00 | 4122 | 712 | 1777 | 970 | 3943 | 839 | 70 | 214 | 555 | 154 | 0 | 0
20:30 | 4111 | 711.5 | 1798 | 972 | 3938.5 | 870 | 70 | 214.5 | 543.5 | 155 | 0 | 0
21:00 | 4100 | 711 | 1819 | 974 | 3934 | 901 | 70 | 215 | 532 | 156 | 0 | 0
21:30 | 4099.5 | 711.5 | 1821 | 911.5 | 3932 | 901.5 | 70 | 216 | 532.5 | 158 | 0 | 0
22:00 | 4099 | 712 | 1823 | 849 | 3930 | 902 | 70 | 217 | 533 | 160 | 0 | 0
22:30 | 4098.5 | 712 | 1829 | 663 | 3939 | 881 | 70.5 | 217.5 | 533 | 158 | 0 | 0
23:00 | 4098 | 712 | 1835 | 477 | 3948 | 860 | 71 | 218 | 533 | 156 | 0 | 0
23:30 | 4076.5 | 713 | 1840.5 | 315 | 3941.5 | 850.5 | 71 | 218 | 525 | 155 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 36.5° C
24:00 | 4055 | 714 | 1846 | 153 | 3935 | 841 | 71 | 218 | 517 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 285.385 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 285.385 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 71 | 70 | 70 | 69 | 69 | 68 | 69 | 69 | 70 | 70 | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 70 |  | 70 | 70 | 70 | 70 | 70 | 71 | 71 | 1691471
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | 25 | 8 | 8 | [6 empty] | 20 | 25 | 0 | 14 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 403650
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 6 | 7 | 4 | 17 | 19 | 18 | 16 | 13 | 7 | 2 | [9 empty] | 116910
6 | Sikalbaha 225MW CCPP (Gas) | 130 | 130 | 132 | 131 | 142 | 132 | 142 | 130 | 131 | 132 | 140 | 131 | 142 | 131 | 131 | 131 | 131 | 131 |  | 141 | 131 | 131 | 131 | 131 | 131 | 145 | 3118805
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 9 | 17 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 371947
12 | Hathazari 100 MW peaking PP | [16 empty] | 10 | 24 |  | 32 | 40 | 40 | 17 | 17 | 17 | 17 | 164649
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 93 | 102 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2509927
| Daudkandi 200 MW PP (B.Trac) | [11 empty] | 200 | 200 | 200 | 200 | 200 | 150 | 50 |  | 200 | 200 | 200 | 200 | 200 | 200 |  | 2222592
14 | Titas 50 MW Peaking PP | 42 | 42 | [8 empty] | 21 | 30 | 36 | 40 | 40 | 40 | 40 | 41 |  | 41 | 41 | 40 | 40 | 41 | 41 | 25 | 614152
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 220 | 222 | 219 | 223 | 200 | 200 | 220 | 180 | 214 | 214 | 213 | 208 | 202 | 202 | 205 | 207 | 207 | 206 |  | 206 | 206 | 212 | 213 | 216 | 215 | 216 | 5169984
18 | Kodda 300 MW PP Unit-2 (Summit) | 296 | 298 | 298 | 230 | 195 | 195 | 195 | 215 | 265 | 280 | 283 | 283 | 281 | 280 | 281 | 278 | 280 | 280 |  | 281 | 281 | 281 | 268 | 260 | 275 | 283 | 6440834
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 18 | 36 | 36 | 36 | 317818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 203 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  |  | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4413000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5973036
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 654912
33 | Ashuganj 225 MW CCPP | 222 | 222 | 222 | 219 | 217 | 218 | 217 | 219 | 193 | 171 | 195 | 206 | 208 | 206 | 213 | 214 | 180 | 213 |  | 212 | 215 | 216 | 215 | 211 | 196 | 186 | 5032000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 305 | 335 | 305 | 305 | 260 | 260 | 260 | 260 | 260 | 270 | 340 | 335 | 330 |  | 330 | 335 | 345 | 335 | 345 | 345 | 335 | 7273000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 275 | 310 | 270 | 270 | 300 | 270 | 270 | 270 | 270 | 270 | 357 | 330 | 320 |  | 320 | 350 | 358 | 355 | 360 | 355 | 350 | 7698700
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 45 | 49 | 51 |  | 52 | 52 | 52 | 52 | 55 | 55 | 55 | 1084800
36 | Chandpur 150 MW CCPP | 136 | 137 | 137 | 136 | 135 | 136 | 136 | 136 | 137 | 137 | 137 | 136 | 137 | 138 | 136 | 137 | 137 | 137 |  | 137 | 137 | 137 | 137 | 138 | 137 | 135 | 3247460
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 260 | 260 | 260 | 260 | 250 | 250 | 240 | 260 | 270 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 290 | 6031750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 105 | 105 | 105 | 105 | 104 | 105 | 102 | 104 | 93 | 79 | 82 | 82 | 82 | 81 | 81 | 97 | 97 | 96 |  | 98 | 98 | 99 | 99 | 100 | 101 | 100 | 2220480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 14 | 26 | 35 | 42 | 42 | 39 | 34 | 28 | 15 | 6 | 0 | [8 empty] | 284360
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 696152
46 | Shajibazar 330 MW CCPP | 265 | 266 | 269 | 268 | 267 | 269 | 267 | 266 | 268 | 267 | 209 | 0 | [5 empty] | 40 |  | 110 | 200 | 220 | 221 | 218 | 221 | 221 | 3947000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 40 | 40 | 60 | 60 | 30 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 55 | 55 |  | 60 | 60 | 60 | 60 | 58 | 50 | 50 | 1357152
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 84 | 84 | 84 | 84 | 83 | 84 | 84 | 86 |  | 86 | 86 | 87 | 87 | 87 | 87 | 88 | 2073600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244260
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228096
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 47 | 47 | 47 | 47 | 44 | 50 | 44 | 44 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1167600
56 | Shahjahanulla 25 MW PP | 22 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 23 | 23 | 23 | 22 | 22 | 22 | 20 | 20 | 20 | 13 |  | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 506784
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 260 | 275 | 280 | 290 | 300 | 300 | 280 | 280 | 305 | 290 | 305 | 290 | 290 | 300 | 300 | 270 | 270 |  | 290 | 290 | 290 | 300 | 280 | 290 | 290 | 7099500
| Bibiyana South 400 MW | 400 | 360 | 300 | 311 | 235 | 195 | 175 | 170 | 265 | 380 | 380 | 382 | 375 | 387 | 380 | 390 | 390 | 379 |  | 385 | 395 | 400 | 390 | 400 | 400 | 390 | 8159300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1323604
59 | Tangail Palli Power Gen 22 MW | 20 | 18 | 18 | 18 | 18 | 18 | 19 | 22 | 22 | 22 | 23 | 21 | 6 | 12 | 13 | 13 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 440160
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 | 18 |  | 0 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 413172
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 369144
63 | Impoprt (Tripura) | 138 | 136 | 134 | 130 | 126 | 120 | 118 | 124 | 128 | 140 | 148 | 148 | 154 | 164 | 162 | 160 | 156 | 166 |  | 162 | 154 | 154 | 156 | 160 | 156 | 154 | 3436800
64 | Malancha, Ctg. EPZ (United) | 37 | 38 | 38 | 40 | 40 | 40 | 35 | 11 | 5 | 5 | 5 | 5 | 8 | 5 | 3 | 3 | 6 | 8 |  | 11 | 16 | 7 | 25 | 33 | 35 | 36 | 488160
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439740
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 8 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 230040
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 15 | 16 | 16 | 16 | 15 | 15 | 16 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 677700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 528660
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 27 | 27 | 27 | 27 | 27 | 27 | 580860
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 762480
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 23 | 23 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 776900
73 | Ghorashal 108MW PP (Regent) | 99 | 101 | 102 | 102 | 102 | 102 | 102 | 99 | 96 | 96 | 97 | 99 | 99 | 99 | 95 | 98 | 103 | 104 |  | 104 | 104 | 105 | 105 | 102 | 104 | 101 | 2371090
| Feni Lanka Power | 99 | 70 | 70 | 70 | 34 | 34 | 34 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2112420
| Chowmuhani 113 MW | 110 | 111 | 112 | 109 | 105 | 107 | 109 | 106 | 108 | 105 | 107 | 108 | 105 | 105 | 105 | 103 | 113 | 112 |  | 113 | 113 | 114 | 115 | 115 | 115 | 110 | 2633400
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 129 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3490560
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 50 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 42 | 42 | 42 | 41 | 41 | 40 | 40 | 40 | 49 | 49 |  | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 1020000
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 100 | 100 | 100 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3413760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 46 | 43 | 34 | 38 | 40 |  | 38 | 43 | 43 | 43 | 43 | 43 | 42 | 1016904
| Gazipur 100 MW PP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 70 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1869600
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 27330
| Jodiac Power | 54 | 54 | 54 | 44 | 47 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 40 | 46 | 54 | 54 | 54 | 54 | 1060111
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 98 | 92 | 92 | 97 |  | 98 | 110 | 110 | 110 | 110 | 110 | 110 | 2599407
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3584320
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 92 | 91 | 93 | 91 | 92 | 92 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2182080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 40 | 10 | 10 | 10 | 10 | 20 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 86 | 90 | 92 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1525560
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1174293
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 64 | 40 | 40 | 40 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2062512
95 | Patenga 50MW PP (Baraka) | 45 | 45 | 41 | 18 | 18 | 18 | 18 | 37 | 46 | 43 | 45 | 44 | 45 | 45 | 46 | 46 | 46 | 45 |  | 48 | 48 | 50 | 47 | 44 | 47 | 50 | 1007040
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [6 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 15 | 15 | 15 | 15 | 15 | 33 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1113022
100 | Manikganj 55 MW PP (Northern) | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1133427
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 12700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1294920
104 | Keranigonj 300 MW PP (APR) | [8 empty] | 25 | 167 | 109 | 298 | 303 | 306 | 300 | 304 | 210 | 24 |  | 204 | 303 | 304 | 300 | 301 | 127 | 53 | 3435537
105 | Bramhangoan 100 MW PP (Aggreko) | 25 | [7 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 100 | 70 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1470234
106 | Mymensingh 200 MW PP (United) | 190 | 190 | 191 | 191 | 200 | 192 | 192 | 193 | 192 | 192 | 191 | 191 | 190 | 189 | 178 | 177 | 177 | 187 |  | 198 | 198 | 198 | 200 | 191 | 191 | 191 | 4521600
112 | Aurahati 100MW PP (Aggreko) | [8 empty] | 25 | 64 | 97 | 97 | 98 | 100 | 95 | 99 | 70 | 40 |  | 100 | 100 | 100 | 99 | 98 | 50 | 0 | 1299492
114 | Kodda 149 MW PP Unit-1 (Summit) | 123 | 135 | 135 | 135 | 133 | 135 | 124 | 133 | 134 | 135 | 133 | 134 | 130 | 133 | 132 | 131 | 132 | 132 |  | 134 | 149 | 149 | 149 | 149 | 149 | 149 | 3287950
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2057280
116 | Chandpur 200MW (Desh energy) | 200 | 120 | 17 | 17 | 17 | 17 | 17 | 37 | 57 | 87 | 150 | 195 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3384000
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 150 | 150 | 142 | 137 | 142 | 140 | 142 | 142 | 137 | 133 | 130 | 120 | 120 | 125 | 138 |  | 142 | 142 | 142 | 145 | 150 | 150 | 143 | 3353818
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 401 | 401 | 376 | 399 | 400 | 381 | 399 | 401 | 404 | 380 | 376 | 404 | 363 | 402 | 404 | 402 |  | 405 | 402 | 402 | 403 | 402 | 402 | 402 | 9541000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 97 | 97 | 97 | 106 | 96 | 96 | 97 | 96 |  | 106 | 107 | 107 | 107 | 107 | 107 | 107 | 2491200
| Anwara 300 MW PP (United) | 281 | 294 | 292 | 292 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 282 | 284 | 267 | 260 | 281 | 281 |  | 281 | 281 | 300 | 300 | 300 | 300 | 300 | 6879927
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 65 | 65 | 65 | 70 | 100 | 100 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 2227200
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 94 | 92 | 92 | 92 | 109 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2627018
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 12 | 34 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 862560
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 11 | 17 | 23 | 28 | 30 | 30 | 25 | 18 | 12 | 4 | 0 | [8 empty] | 196264
| Chandpur 115(Doreen) | 85 | 93 | 35 | 40 | 23 | 17 | 17 | 32 | 62 | 71 | 62 | 56 | 63 | 63 | 63 | 69 | 63 | 69 |  | 82 | 96 | 88 | 92 | 97 | 97 | 96 | 1598400
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 54 | 46 |  |  | 14 | 34 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1162080
120 | Eastern Zone Total | 8122 | 7833 | 7538 | 7401 | 7134 | 7102 | 7200 | 7345 | 7745 | 8118 | 8107 | 8270 | 8286 | 8288 | 8229 | 8268 | 8075 | 8105 |  | 8742 | 9030 | 9097 | 9092 | 9113 | 8894 | 8517 | 195118117
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [10 empty] | 30 | 34 | 34 | 34 | 31 | 33 | 33 | 33 |  | 40 | 36 | 31 | 35 | 35 | 35 | 35 | 434880
| Khulna 225 MW CCPP | 75 | 15 | 15 | 10 | 30 | 65 | 55 | 55 | 110 | 140 | 180 | 195 | 210 | 205 | 206 | 208 | 210 | 210 |  | 211 | 212 | 214 | 215 | 217 | 218 | 218 | 3525120
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 105 | 94 | 100 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2407680
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 30 | 52 | 71 | 82 | 87 | 83 | 74 | 55 | 35 | 14 | 1 | [8 empty] | 600480
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 192 | 202 | 201 | 172 | 172 | 172 | 170 | 173 | 134 | 224 | 224 | 220 | 220 | 213 | 214 | 195 | 197 | 184 |  | 218 | 218 | 220 | 222 | 220 | 220 | 222 | 4791109
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [21 empty] | 16 | 26 | 32 | 32 | 32 | 119232
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 45 | 30 | 65 | 65 | 65 | 60 | 62 | 62 | 63 | 60 |  | 63 | 65 | 65 | 60 | 38 | 65 | 65 | 1455000
140 | Bhola 33 MW PP (Venture) | 26 | 24 | 24 | 22 | 21 | 20 | 18 | 16 | 17 | 20 | 21 | 23 | 23 | 22 | 27 | 24 | 24 | 28 |  | 31 | 31 | 32 | 31 | 32 | 31 | 31 | 578200
141 | Noapara 100 MW PP (Bangla Trac) | [10 empty] | 50 | 90 | 99 | 100 | 100 | 100 | 50 | 50 |  | 80 | 100 | 90 | 100 | 50 |  |  | 1061760
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3 | [26 empty] | 2700
145 | Madhumati 100 MW PP | [14 empty] | 27 | 50 | 50 | 50 |  | 50 | 56 | 22 |  |  |  |  | 263232
146 | Bheramara HVDC | 711 | 711 | 711 | 711 | 710 | 711 | 710 | 711 | 712 | 712 | 712 | 713 | 713 | 712 | 712 | 712 | 713 | 712 |  | 713 | 712 | 712 | 711 | 712 | 712 | 714 | 17226181
147 | Bheramara 410 MW CCPP | 240 | 240 | 245 | 250 | 250 | 250 | 260 | 250 | 245 | 235 | 230 | 220 | 195 | 200 | 195 | 215 | 215 | 215 |  | 220 | 235 | 235 | 235 | 235 | 235 | 235 | 5712192
148 | Payra 1320 MW | 540 | 520 | 500 | 500 | 470 | 470 | 470 | 460 | 300 | 250 | 250 | 270 | 300 | 320 | 320 | 320 | 320 | 300 |  | 370 | 520 | 560 | 622 | 622 | 580 | 560 | 11376900
149
150 | Barapukuria TPP Unit-1 | 77 | 81 | 79 | 73 | 75 | 78 | 76 | 78 | 84 | 77 | 78 | 76 | 77 | 78 | 76 | 77 | 78 | 80 |  | 80 | 80 | 80 | 79 | 80 | 80 | 81 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 |  | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 4848500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | [8 empty] | 0 | 34 | 34 | 34 | 34 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 543264
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 31860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [10 empty] | 2 | 7 | 2 | 3 | 3 | 3 | 2 | 3 |  | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 142500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 148 | 153 | 153 | 153 | 153 | 154 | 159 | 159 | 159 | 155 | 148 | 128 | 124 | 118 | 118 | 118 | 118 | 118 |  | 118 | 119 | 121 | 121 | 121 | 121 | 121 | 3478391
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | [11 empty] | 0
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 149 | 140 | 137 | 132 | 131 | 131 | 133 | 142 | 156 | 167 | 167 | 158 | 149 | 139 | 138 | 144 | 144 | 144 |  | 144 | 144 | 144 | 146 | 147 | 145 | 133 | 3686327
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 386 | 383 | 420 | 370 | 415 | 415 | 388 | 388 | 365 | 362 | 362 | 362 | 362 | 360 |  | 359 | 359 | 415 | 416 | 415 | 414 | 414 | 9470982
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 29 | [12 empty] | 6 | 37 | 39 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 388880
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 15 | 15 | 14 | 15 | 16 | 15 | 16 |  | 19 | 20 | 20 | 22 | 22 | 22 | 22 | 402480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252729
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | [10 empty] | 34 | 34 | 34 | 34 | 34 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 503104
167 | Katakhali 50 MW Peaking PP | 30 | 30 | [11 empty] | 24 | 24 | 24 | 24 | 24 |  | 32 | 37 | 40 | 40 | 40 | 40 | 40 | 383139
168 | Santahar 50 MW Peaking PP | 32 | 32 | 30 | [11 empty] | 32 | 32 | 32 | 32 |  | 32 | 34 | 32 | 28 | 28 | 28 | 28 | 391268
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 24 | 24 | 24 | 24 | 29 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1127520
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 46 | [6 empty] | 15 | 42 | 45 | 45 | 45 | 45 | 48 | 53 | 90 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 1168808
171 | Baghabari 200 MW PP (Paramount) | [10 empty] | 176 | 176 | 176 | 176 | 176 | 173 | 130 | 50 |  | 176 | 176 | 176 | 175 | 100 |  |  | 1897835
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 112 | 112 | 112 | 111 | 110 | 110 | 110 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2716800
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 70 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2423904
173 | Rangpur 20 MW GTPP | [15 empty] | 12 | 14 | 12 |  | 15 | 16 | [5 empty] | 62000
175 | Saidpur 20 MW GTPP | [14 empty] | 9 | 8 | 8 | 8 |  | 8 | 8 | [5 empty] | 40000
176 | Rangpur 113 MW PP (Confidence) | 110 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 102 | 102 | 102 | 101 | 99 | 99 | 99 | 103 |  | 109 | 110 | 110 | 110 | 110 | 110 | 110 | 2519788
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 5 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [8 empty] | 39417
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 72 | 34 | 36 | 17 | 17 | 17 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2285688
178