## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-30 | Wednesday
|  |  | Date (day): | 2022-03-30 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13897.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14560 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-29 | 2022-03-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 210 | 210 | 210 | 210
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | ST under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 93 | 91 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 57 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 148 | 130 | 150 | 150 |  | 185 | GT-2 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 67 | 65 | 80 | 80
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 38 | 55 | 50 | 60 | 150 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 60 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 214 | 228 | 220 | 220 |  | 115 | ST under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 84 | 85 | 90 |  | 12 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 50 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 45 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 5 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 28 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 281 | 281 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 154 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 50 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 138 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 88 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 126 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 50 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 2773 | 3085 | 3386 | 3471 | 381 | 2011
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | 33 kV BPDB feeder problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 200 | 200
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 0 | 50 |  | 58 | On test
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 86 | 95 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 94 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1406 | 1532 | 1528 | 1563 | 81 | 605
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 185 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 300 | 300 | 60 |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 270 | 300 | 300 | 60 |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 15 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 32 | 42 |  | 10 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 136 | 135 | 136 |  | 27 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 116 | 157 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 178 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 14 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 72 | 98 | 98 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 103 | 113 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 33 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 99 | 99 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1741 | 2012 | 2126 | 2262 | 636 | 104
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 73 | 107 | 110 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 183 | 200 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 107 | 106 | 107
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 383 | 458 | 509.6 | 459 | 92 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 |  | 90 | Under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 270 | 270 | 270 | 270 | 60 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 50 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 23 | 29 | 30 | 30
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 60 | 66
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 145 | 140 | 145 | 86 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 20 | 20 | 20 | 20
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 24 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 375 | 400 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1501 | 1605 | 1594 | 1606 | 166 | 613
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 897 | 892 | 915 | 915
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 83 | 100 | 100
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42 |  | 12 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 225 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 280 | 280 | 300 | 110 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 32 | 32 | 32
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 95 | 95 | 95 |  | 10 | Engine problem
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 12 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1431 | 1616 | 1797 | 1839 | 110 | 101
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 32 | 80
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 35 | 25 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 67 | 65 | 67 | 127 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 490 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 205 | 214 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 100
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 708 | 838 | 1002 | 1162 | 127 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 45 | 40 | 45 |  | 26 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 40 | 40 |  | 10 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 32 | 0 | 33 |  | 17 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 174 | 186 | 130 | 150 | 60 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 151 | 220 | 220 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 147 | 188 | 170 | 180 | 40 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 287 | 0 | 300 | 350 | 64 |  | Gas shortage
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 30 | 36 |  | 14 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 35 | 43 | 43 |  | 9 | Engine problem
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 93 | 90 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 40 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 100 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 95 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1058 | 1129 | 1444 | 1692 | 335 | 96
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 78 | 75 | 78
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 110 | 102 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 506 | 494 | 511 | 506 | 74 | 125
|  | Total |  |  |  |  | 22291 | 21215 | 11507 | 12769 | 13897.6 | 14560 | 2002 | 3663
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11136.7376 | 12358.13 | 13450.4149 | 14091.5007
| A. |  | 2022-03-29 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12769 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 10314 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12769 | MW
| 3 | Day peak Generation : |  |  | 11507 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12358.13 | MW
| 4 | Evening peak Generation : |  |  | 12769 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 278.5639 | MKWHr | By Solar | 1.0985 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 132.4338 | MKWHr |  | By Oil: | 98.811 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.593 | MKWHr |  | By Hydro: | 1.6698 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2002 | MW | Dhaka | 4273.3 | 4273.3 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3663 | MW | Chittagong | 1284.23 | 1284.23 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5665 | MW | Khulna | 1600.4 | 1600.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1059.89 | MMCFD |  |  | Rajshahi | 1480.2 | 1480.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145475917.188 | ii) Oil : | Taka | 766659942.17 | Comilla | 1030 | 1030 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 94141044.16 | Total | Taka | 1006276903.518 | Mymensingh | 1090 | 1090 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.3825 | MKWHr. | Sylhet | 367 | 367 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -268 | MW (E to W) at | 19:00 | hrs | Barisal | 369 | 369 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -268 | MW at | 19:00 | hrs | Rangpur | 864 | 864 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 12358.13 | 12358.13 |  | 0
| B. |  | 2022-03-30 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14560 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11700 | MW
| 4 | Reserve(Generation end) |  |  |  | 1160 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 292.3295 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10068 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6938 | MKWHr. | ii) HVDC Flow at Peak Time |  | 892 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.264 | MKWHr. | iii) Maximum HVDC Flow : |  | 903 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.55 |  | (b) Today: | 85.32 |  | (c) Rule Curve: |  | 88.51
.

## YesterdayGen
2022-03-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 224 | 0 | 37 | 0 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 26 | 51 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 91 | 25 | 0 | 27 | 0 | 0 | 0 | 270 | 265 | 148 | 8 | 137 | 29 | 37 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 15 | 124 | 104 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 269 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 290 | 24 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 128 | 400 | 48 | 105 | 105 | 0 | 300 | 54 | 110 | 99 | 110 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 | 0 | 99 | 55 |  | 897 | 0 | 285 | 0 | 14 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 43 | 17 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 118 | 0 | 333 | 93 | 0 | 113 | 0 | 110 | 0 | 0 | 95 | 580 | 222 | 0 | 0 | 0 | 0 | 0 |  | 7828 | 3826 | 11654 | 3742 | 897 | 1906 | 0 | 3673 | 860 | 68 | 250 | 264 | 124 | 0 | 0 | 85.6
2:00 | 0 | 0 | 212 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 221 | 0 | 40 | 0 | 93 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 26 | 51 | 0 | 67 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 95 | 25 | 0 | 36 | 0 | 0 | 0 | 270 | 265 | 150 | 8 | 136 | 29 | 37 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 15 | 116 | 104 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 269 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 275 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 34 | 142 | 400 | 48 | 105 | 105 | 0 | 300 | 54 | 102 | 99 | 108 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 | 0 | 50 | 55 |  | 895 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 134 | 0 | 333 | 93 | 0 | 113 | 0 | 110 | 0 | 0 | 95 | 570 | 209 | 0 | 0 | 0 | 0 | 0 |  | 7532 | 3737 | 11269 | 3762 | 895 | 1882 | 0 | 3384 | 849 | 67 | 250 | 194 | 116 | 0 | 0 | 85.59
3:00 | 0 | 0 | 212 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 15 | 219 | 0 | 40 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 28 | 51 | 0 | 68 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 102 | 25 | 0 | 36 | 0 | 0 | 0 | 270 | 265 | 154 | 8 | 137 | 29 | 37 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 15 | 114 | 104 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 268 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 17 | 135 | 400 | 48 | 105 | 105 | 0 | 300 | 54 | 102 | 53 | 109 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 | 0 | 0 | 55 |  | 896 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 143 | 0 | 343 | 93 | 0 | 113 | 0 | 110 | 0 | 0 | 95 | 550 | 222 | 0 | 0 | 0 | 0 | 0 |  | 7104 | 3712 | 10816 | 3700 | 896 | 1919 | 0 | 2992 | 829 | 68 | 250 | 178 | 114 | 0 | 0 | 85.58
4:00 | 0 | 0 | 212 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 15 | 220 | 0 | 40 | 0 | 42 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 28 | 51 | 0 | 69 | 0 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 36 | 0 | 0 | 0 | 270 | 265 | 150 | 8 | 137 | 29 | 37 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 15 | 108 | 105 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 267 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 295 | 24 | 11 | 0 | 15 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 17 | 133 | 400 | 48 | 70 | 105 | 0 | 300 | 54 | 110 | 34 | 105 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 | 0 | 0 | 55 |  | 898 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 161 | 0 | 344 | 93 | 0 | 113 | 0 | 40 | 0 | 0 | 35 | 520 | 222 | 0 | 0 | 0 | 0 | 0 |  | 6928 | 3573 | 10501 | 3715 | 898 | 1936 | 0 | 2693 | 800 | 69 | 250 | 162 | 108 | 0 | 0 | 85.57
5:00 | 0 | 0 | 215 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 15 | 223 | 0 | 41 | 0 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 25 | 51 | 0 | 70 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 38 | 0 | 0 | 0 | 270 | 265 | 189 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 0 | 0 | 15 | 106 | 107 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 268 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 17 | 128 | 400 | 28 | 70 | 105 | 0 | 300 | 54 | 110 | 17 | 105 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 | 0 | 0 | 55 |  | 897 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 168 | 0 | 344 | 94 | 0 | 113 | 0 | 40 | 0 | 0 | 35 | 500 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6979 | 3549 | 10528 | 3825 | 897 | 1894 | 0 | 2674 | 780 | 70 | 250 | 162 | 106 | 0 | 0 | 85.56
6:00 | 0 | 0 | 210 | 0 | 200 | 96 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 15 | 181 | 0 | 41 | 0 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 0 | 16 | 51 | 0 | 70 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 39 | 0 | 0 | 0 | 270 | 265 | 208 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 0 | 0 | 15 | 100 | 112 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 270 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 295 | 24 | 11 | 0 | 15 | 0 | 0 | 195 | 0 | 149 | 0 | 90 | 17 | 137 | 362 | 48 | 70 | 105 | 0 | 300 | 54 | 110 | 17 | 105 | 90 | 0 | 74 | 0 | 144 | 113 | 0 | 35 | 0 | 0 | 55 |  | 897 | 0 | 275 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 167 | 0 | 344 | 94 | 0 | 70 | 0 | 40 | 0 | 0 | 35 | 470 | 185 | 0 | 0 | 0 | 0 | 0 |  | 6879 | 3435 | 10314 | 3719 | 897 | 1867 | 0 | 2629 | 750 | 70 | 250 | 162 | 100 | 0 | 0 | 85.55
7:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 15 | 200 | 0 | 62 | 0 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 33 | 16 | 51 | 0 | 70 | 0 | 0 | 150 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 35 | 0 | 0 | 0 | 270 | 265 | 220 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 15 | 98 | 113 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 163 | 270 | 60 | 89 | 0 | 100 | 0 | 19 | 10 | 310 | 24 | 11 | 0 | 15 | 0 | 0 | 195 | 0 | 149 | 3 | 90 | 17 | 132 | 352 | 48 | 70 | 102 | 1 | 300 | 54 | 110 | 17 | 106 | 60 | 0 | 87 | 3 | 144 | 113 | 0 | 35 | 0 | 0 | 55 |  | 897 | 0 | 272 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 344 | 94 | 0 | 70 | 0 | 70 | 0 | 0 | 60 | 440 | 221 | 0 | 0 | 0 | 9 | 17 |  | 6957 | 3513 | 10470 | 3811 | 897 | 1898 | 0 | 2677 | 721 | 70 | 250 | 162 | 98 | 16 | 0 | 85.54
8:00 | 0 | 0 | 205 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 5 | 20 | 160 | 0 | 62 | 2 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 29 | 33 | 16 | 50 | 0 | 70 | 0 | 0 | 150 | 5 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 10 | 0 | 0 | 0 | 270 | 265 | 222 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 7 | 104 | 109 | 0 | 19 | 0 | 30 | 30 | 47 | 23 | 110 | 266 | 40 | 89 | 0 | 100 | 0 | 19 | 10 | 270 | 24 | 8 | 0 | 80 | 0 | 0 | 195 | 0 | 149 | 7 | 90 | 17 | 129 | 352 | 48 | 70 | 87 | 2 | 300 | 54 | 110 | 52 | 105 | 60 | 0 | 90 | 6 | 144 | 113 | 0 | 35 | 7 | 11 | 55 |  | 897 | 0 | 265 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 163 | 0 | 343 | 94 | 0 | 96 | 0 | 75 | 0 | 0 | 95 | 400 | 221 | 0 | 0 | 0 | 32 | 52 |  | 6861 | 3589 | 10450 | 3690 | 897 | 1767 | 0 | 2906 | 680 | 70 | 250 | 162 | 104 | 54 | 0 | 85.53
9:00 | 0 | 0 | 210 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 280 | 150 | 0 | 30 | 40 | 220 | 0 | 37 | 7 | 64 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 70 | 0 | 0 | 150 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 265 | 219 | 8 | 137 | 29 | 10 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 13 | 122 | 74 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 163 | 266 | 50 | 89 | 0 | 100 | 0 | 19 | 10 | 275 | 24 | 8 | 0 | 100 | 0 | 0 | 195 | 0 | 149 | 13 | 90 | 23 | 130 | 352 | 49 | 70 | 87 | 2 | 300 | 54 | 110 | 52 | 105 | 85 | 0 | 90 | 10 | 144 | 113 | 0 | 16 | 17 | 24 | 55 |  | 897 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 151 | 0 | 344 | 94 | 0 | 113 | 0 | 110 | 0 | 0 | 95 | 400 | 211 | 0 | 0 | 0 | 41 | 52 |  | 7151 | 3608 | 10759 | 3685 | 897 | 1814 | 0 | 3076 | 679 | 70 | 250 | 212 | 122 | 84 | 0 | 85.53
10:00 | 0 | 0 | 210 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 280 | 155 | 0 | 24 | 40 | 180 | 0 | 37 | 7 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 29 | 25 | 25 | 50 | 0 | 70 | 0 | 0 | 150 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 87 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 186 | 8 | 136 | 29 | 10 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 13 | 132 | 73 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 130 | 269 | 60 | 89 | 0 | 100 | 0 | 18 | 10 | 280 | 24 | 5 | 0 | 188 | 0 | 0 | 195 | 0 | 149 | 15 | 90 | 34 | 133 | 328 | 48 | 90 | 87 | 1 | 300 | 54 | 110 | 52 | 101 | 90 | 0 | 89 | 14 | 144 | 113 | 0 | 17 | 20 | 51 | 55 |  | 898 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 138 | 0 | 288 | 94 | 0 | 113 | 0 | 110 | 0 | 1 | 95 | 380 | 154 | 0 | 0 | 2 | 62 | 52 |  | 7256 | 3519 | 10775 | 3568 | 898 | 1677 | 0 | 3210 | 659 | 70 | 250 | 325 | 132 | 116 | 0 | 85.52
11:00 | 0 | 0 | 210 | 0 | 200 | 93 | 0 | 0 | 0 |  | 0 | 280 | 145 | 8 | 35 | 41 | 212 | 0 | 38 | 12 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 25 | 46 | 0 | 70 | 0 | 0 | 150 | 8 | 214 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 87 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 194 | 8 | 136 | 29 | 15 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 13 | 142 | 73 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 130 | 270 | 60 | 89 | 0 | 100 | 0 | 18 | 10 | 310 | 24 | 5 | 0 | 265 | 0 | 0 | 184 | 0 | 137 | 15 | 90 | 48 | 132 | 375 | 48 | 90 | 87 | 4 | 300 | 54 | 93 | 72 | 101 | 100 | 0 | 88 | 15 | 144 | 113 | 0 | 17 | 20 | 69 | 55 |  | 903 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 5 | 36 | 0 | 21 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 147 | 0 | 288 | 94 | 0 | 94 | 0 | 110 | 0 | 0 | 95 | 390 | 170 | 0 | 0 | 2 | 79 | 115 |  | 7553 | 3630 | 11183 | 3671 | 903 | 1720 | 0 | 3424 | 667 | 70 | 250 | 330 | 142 | 136 | 0 | 85.5
12:00 | 0 | 0 | 210 | 0 | 200 | 93 | 0 | 0 | 0 |  | 0 | 270 | 148 | 57 | 67 | 40 | 214 | 0 | 38 | 60 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 25 | 16 | 50 | 0 | 70 | 0 | 0 | 150 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 86 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 300 | 183 | 8 | 137 | 26 | 15 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 13 | 144 | 73 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 130 | 270 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 290 | 22 | 5 | 0 | 281 | 0 | 0 | 183 | 0 | 138 | 19 | 90 | 116 | 125 | 375 | 48 | 90 | 87 | 5 | 300 | 54 | 93 | 72 | 103 | 100 | 0 | 88 | 35 | 144 | 113 | 0 | 33 | 30 | 99 | 50 |  | 897 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 16 | 34 | 0 | 21 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 174 | 0 | 0 | 130 | 0 | 0 | 147 | 0 | 287 | 94 | 0 | 94 | 0 | 110 | 0 | 2 | 95 | 400 | 205 | 0 | 0 | 4 | 95 | 115 |  | 7804 | 3703 | 11507 | 3678 | 897 | 1724 | 0 | 3663 | 679 | 70 | 250 | 341 | 144 | 191 | 0 | 85.49
13:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 140 | 100 | 80 | 40 | 214 | 0 | 38 | 85 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 25 | 16 | 45 | 0 | 70 | 0 | 0 | 150 | 25 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 86 | 25 | 0 | 6 | 0 | 0 | 0 | 270 | 300 | 187 | 8 | 137 | 29 | 20 | 0 | 43 | 0 | 2 | 43 | 0 | 11 | 0 | 13 | 154 | 71 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 163 | 265 | 60 | 88 | 0 | 115 | 0 | 20 | 10 | 305 | 22 | 5 | 0 | 281 | 109 | 0 | 184 | 0 | 138 | 18 | 90 | 195 | 125 | 400 | 48 | 90 | 87 | 5 | 300 | 54 | 110 | 80 | 106 | 90 | 0 | 90 | 35 | 140 | 113 | 0 | 35 | 28 | 98 | 45 |  | 895 | 0 | 220 | 0 | 17 | 125 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 16 | 34 | 0 | 21 | 0 | 11 | 82 | 0 | 199 | 0 | 0 | 177 | 0 | 0 | 135 | 0 | 0 | 146 | 0 | 287 | 94 | 0 | 102 | 0 | 106 | 0 | 5 | 95 | 420 | 105 | 0 | 0 | 1 | 95 | 115 |  | 8193 | 3654 | 11847 | 3716 | 895 | 1672 | 109 | 3869 | 701 | 70 | 260 | 348 | 154 | 188 | 0 | 85.48
14:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 130 | 100 | 79 | 40 | 180 | 0 | 38 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 27 | 25 | 25 | 48 | 0 | 69 | 0 | 0 | 150 | 25 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 93 | 25 | 0 | 3 | 0 | 0 | 0 | 270 | 270 | 177 | 8 | 137 | 29 | 20 | 0 | 43 | 0 | 20 | 43 | 0 | 11 | 21 | 15 | 158 | 72 | 0 | 19 | 1 | 30 | 0 | 44 | 23 | 163 | 271 | 60 | 88 | 0 | 145 | 0 | 18 | 10 | 270 | 22 | 5 | 0 | 283 | 0 | 0 | 194 | 0 | 134 | 15 | 90 | 200 | 127 | 390 | 48 | 90 | 95 | 1 | 300 | 54 | 110 | 80 | 105 | 90 | 0 | 90 | 16 | 54 | 113 | 0 | 35 | 15 | 99 | 55 |  | 894 | 0 | 210 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 24 | 64 | 26 | 32 | 0 | 0 | 0 | 43 | 5 | 45 | 0 | 0 | 16 | 43 | 0 | 21 | 0 | 11 | 83 | 0 | 199 | 0 | 0 | 169 | 0 | 0 | 181 | 0 | 0 | 140 | 0 | 200 | 94 | 0 | 113 | 0 | 110 | 0 | 5 | 95 | 450 | 205 | 0 | 0 | 1 | 61 | 115 |  | 7904 | 3854 | 11758 | 3620 | 894 | 1633 | 0 | 3927 | 732 | 69 | 331 | 460 | 158 | 115 | 0 | 85.47
15:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 142 | 100 | 77 | 40 | 210 | 0 | 38 | 94 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 27 | 25 | 25 | 40 | 0 | 68 | 0 | 0 | 150 | 25 | 205 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 94 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 178 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 24 | 43 | 0 | 11 | 25 | 15 | 160 | 100 | 0 | 19 | 0 | 30 | 0 | 44 | 23 | 163 | 271 | 60 | 88 | 0 | 145 | 0 | 18 | 10 | 300 | 22 | 5 | 30 | 281 | 64 | 25 | 192 | 25 | 149 | 10 | 90 | 200 | 123 | 402 | 48 | 90 | 105 | 3 | 300 | 54 | 110 | 85 | 105 | 100 | 0 | 90 | 23 | 54 | 113 | 0 | 35 | 17 | 99 | 55 |  | 896 | 0 | 205 | 0 | 49 | 205 | 0 | 0 | 0 | 0 | 32 | 64 | 27 | 32 | 0 | 0 | 0 | 43 | 15 | 45 | 0 | 0 | 21 | 43 | 0 | 21 | 0 | 11 | 79 | 0 | 199 | 0 | 0 | 170 | 0 | 0 | 201 | 0 | 0 | 152 | 0 | 0 | 94 | 0 | 94 | 0 | 110 | 0 | 4 | 95 | 480 | 214 | 0 | 0 | 0 | 20 | 115 |  | 8187 | 3736 | 11923 | 3705 | 896 | 1469 | 144 | 3942 | 758 | 68 | 406 | 499 | 160 | 77 | 0 | 85.46
16:00 | 0 | 0 | 209 | 0 | 200 | 90 | 0 | 0 | 0 |  | 0 | 270 | 130 | 100 | 77 | 40 | 209 | 0 | 54 | 96 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 28 | 25 | 26 | 42 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 33 | 0 | 0 | 94 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 192 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 31 | 34 | 0 | 11 | 25 | 14 | 156 | 99 | 0 | 19 | 1 | 30 | 0 | 44 | 23 | 163 | 267 | 40 | 89 | 0 | 145 | 0 | 18 | 10 | 270 | 22 | 5 | 0 | 281 | 0 | 0 | 192 | 0 | 149 | 7 | 76 | 198 | 132 | 401 | 48 | 90 | 105 | 2 | 300 | 54 | 110 | 98 | 105 | 100 | 0 | 73 | 10 | 54 | 113 | 0 | 35 | 10 | 99 | 0 |  | 897 | 0 | 215 | 0 | 49 | 180 | 0 | 0 | 5 | 0 | 32 | 66 | 27 | 32 | 0 | 0 | 0 | 43 | 43 | 45 | 0 | 8 | 24 | 43 | 37 | 21 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 210 | 0 | 0 | 177 | 0 | 0 | 94 | 0 | 94 | 0 | 109 | 0 | 3 | 95 | 480 | 200 | 0 | 0 | 1 | 41 | 115 |  | 7945 | 3872 | 11817 | 3772 | 897 | 1413 | 0 | 3878 | 757 | 68 | 390 | 621 | 156 | 75 | 0 | 85.45
17:00 | 0 | 0 | 200 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 132 | 100 | 65 | 40 | 180 | 0 | 37 | 96 | 64 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 25 | 28 | 25 | 17 | 0 | 0 | 69 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 25 | 0 | 0 | 95 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 202 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 41 | 34 | 0 | 11 | 25 | 14 | 152 | 104 | 0 | 20 | 0 | 30 | 0 | 44 | 24 | 130 | 271 | 40 | 89 | 0 | 145 | 0 | 21 | 10 | 280 | 23 | 5 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 2 | 50 | 136 | 130 | 364 | 57 | 90 | 105 | 1 | 300 | 54 | 110 | 51 | 113 | 50 | 0 | 82 | 5 | 54 | 113 | 0 | 35 | 4 | 99 | 55 |  | 896 | 0 | 235 | 0 | 49 | 140 | 0 | 0 | 26 | 0 | 8 | 65 | 26 | 32 | 0 | 0 | 0 | 43 | 44 | 45 | 0 | 8 | 24 | 24 | 36 | 21 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 205 | 0 | 0 | 151 | 0 | 0 | 189 | 0 | 0 | 70 | 0 | 70 | 0 | 75 | 0 | 1 | 50 | 450 | 181 | 0 | 0 | 1 | 14 | 72 |  | 7595 | 3541 | 11136 | 3730 | 896 | 1377 | 0 | 3465 | 729 | 69 | 291 | 550 | 152 | 28 | 0 | 85.44
18:00 | 0 | 0 | 211 | 0 | 200 | 90 | 0 | 0 | 0 |  | 0 | 270 | 147 | 100 | 65 | 50 | 150 | 0 | 40 | 98 | 64 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 24 | 33 | 8 | 2 | 0 | 70 | 0 | 0 | 150 | 25 | 204 | 0 | 0 | 0 |  | 24 | 30 | 26 | 0 | 98 | 25 | 0 | 5 | 0 | 0 | 0 | 270 | 270 | 182 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 40 | 34 | 19 | 11 | 25 | 14 | 156 | 105 | 0 | 20 | 0 | 30 | 0 | 47 | 24 | 110 | 269 | 40 | 89 | 0 | 145 | 0 | 21 | 10 | 270 | 24 | 5 | 0 | 281 | 0 | 0 | 200 | 0 | 125 | 0 | 50 | 136 | 145 | 364 | 105 | 70 | 105 | 0 | 300 | 54 | 110 | 51 | 113 | 50 | 0 | 90 | 1 | 64 | 113 | 0 | 23 | 0 | 99 | 12 |  | 896 | 0 | 260 | 0 | 77 | 140 | 0 | 0 | 33 | 0 | 8 | 65 | 31 | 32 | 0 | 0 | 0 | 43 | 45 | 56 | 0 | 8 | 27 | 24 | 36 | 22 | 0 | 11 | 77 | 0 | 199 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 70 | 0 | 70 | 0 | 75 | 0 | 0 | 50 | 450 | 154 | 0 | 0 | 0 | 0 | 72 |  | 7572 | 3501 | 11073 | 3669 | 896 | 1346 | 0 | 3511 | 726 | 70 | 280 | 558 | 156 | 1 | 0 | 85.43
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 130 | 100 | 65 | 55 | 228 | 0 | 55 | 100 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 50 | 0 | 25 | 20 | 33 | 5 | 28 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 51 | 0 | 95 | 25 | 0 | 15 | 0 | 0 | 0 | 270 | 270 | 185 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 14 | 178 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 29 | 163 | 270 | 61 | 89 | 0 | 145 | 0 | 20 | 10 | 300 | 24 | 11 | 100 | 281 | 154 | 50 | 200 | 100 | 131 | 0 | 90 | 157 | 150 | 400 | 107 | 90 | 105 | 0 | 300 | 54 | 94 | 98 | 113 | 100 | 0 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 99 | 55 |  | 892 | 0 | 280 | 0 | 83 | 180 | 0 | 0 | 42 | 0 | 32 | 67 | 35 | 32 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 34 | 32 | 35 | 36 | 22 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 186 | 0 | 0 | 151 | 0 | 0 | 188 | 0 | 0 | 95 | 40 | 100 | 12 | 102 | 0 | 0 | 113 | 490 | 214 | 0 | 0 | 0 | 0 | 115 |  | 8692 | 4077 | 12769 | 3888 | 892 | 1497 | 444 | 4126 | 767 | 70 | 331 | 727 | 178 | 0 | 0 | 85.4
19:30 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 135 | 100 | 65 | 55 | 229 | 0 | 34 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 28 | 33 | 25 | 25 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 51 | 0 | 95 | 25 | 0 | 12 | 0 | 0 | 0 | 270 | 270 | 188 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 14 | 170 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 29 | 163 | 267 | 60 | 89 | 0 | 145 | 0 | 22 | 10 | 265 | 24 | 11 | 0 | 281 | 10 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 150 | 400 | 105 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 0 | 90 | 0 | 145 | 113 | 0 | 17 | 0 | 99 | 55 |  | 893 | 0 | 285 | 0 | 96 | 213 | 0 | 0 | 38 | 0 | 32 | 66 | 36 | 32 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 25 | 32 | 43 | 38 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 210 | 0 | 0 | 195 | 0 | 0 | 215 | 0 | 0 | 94 | 0 | 113 | 15 | 102 | 0 | 0 | 113 | 600 | 214 | 0 | 0 | 0 | 0 | 115 |  | 8317 | 4309 | 12626 | 3951 | 893 | 1467 | 10 | 4203 | 880 | 70 | 408 | 769 | 170 | 0 | 0 | 0
20:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 134 | 100 | 60 | 40 | 227 | 0 | 34 | 100 | 58 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 28 | 33 | 25 | 25 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 51 | 0 | 98 | 0 | 0 | 15 | 0 | 0 | 0 | 270 | 270 | 194 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 10 | 168 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 263 | 60 | 89 | 0 | 145 | 0 | 25 | 10 | 270 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 150 | 400 | 106 | 90 | 105 | 0 | 300 | 54 | 103 | 98 | 113 | 100 | 0 | 90 | 0 | 145 | 113 | 0 | 17 | 0 | 99 | 55 |  | 894 | 0 | 285 | 0 | 96 | 180 | 0 | 0 | 38 | 0 | 32 | 66 | 36 | 32 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 25 | 32 | 43 | 36 | 22 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 195 | 0 | 0 | 215 | 0 | 0 | 95 | 0 | 113 | 15 | 110 | 0 | 0 | 113 | 610 | 223 | 0 | 0 | 0 | 0 | 115 |  | 8231 | 4308 | 12539 | 3951 | 894 | 1489 | 0 | 4129 | 891 | 70 | 375 | 767 | 168 | 0 | 0 | 85.41
21:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 150 | 100 | 30 | 40 | 224 | 0 | 37 | 100 | 58 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 10 | 22 | 25 | 28 | 33 | 25 | 45 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 51 | 0 | 98 | 0 | 0 | 25 | 0 | 0 | 0 | 270 | 270 | 200 | 8 | 137 | 27 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 10 | 148 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 271 | 60 | 89 | 0 | 145 | 0 | 24 | 10 | 280 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 150 | 401 | 97 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 0 | 90 | 0 | 138 | 113 | 0 | 17 | 0 | 99 | 55 |  | 893 | 0 | 300 | 0 | 94 | 180 | 0 | 0 | 38 | 5 | 32 | 66 | 36 | 32 | 0 | 0 | 0 | 43 | 45 | 91 | 0 | 25 | 32 | 43 | 36 | 22 | 0 | 11 | 81 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 180 | 0 | 0 | 215 | 0 | 0 | 95 | 0 | 113 | 15 | 110 | 0 | 0 | 113 | 600 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8272 | 4294 | 12566 | 4001 | 893 | 1521 | 0 | 4118 | 880 | 70 | 360 | 755 | 148 | 0 | 0 | 85.4
22:00 | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 |  | 0 | 270 | 140 | 100 | 30 | 40 | 224 | 0 | 37 | 100 | 58 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 51 | 0 | 102 | 0 | 0 | 34 | 0 | 0 | 0 | 270 | 270 | 203 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 14 | 134 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 272 | 60 | 89 | 0 | 145 | 0 | 24 | 10 | 290 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 148 | 401 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 0 | 90 | 0 | 54 | 113 | 0 | 27 | 0 | 99 | 55 |  | 893 | 0 | 305 | 0 | 94 | 170 | 0 | 0 | 38 | 0 | 32 | 67 | 36 | 32 | 0 | 0 | 0 | 43 | 45 | 91 | 0 | 25 | 32 | 43 | 36 | 22 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 157 | 0 | 0 | 213 | 0 | 0 | 95 | 0 | 113 | 15 | 110 | 0 | 0 | 113 | 600 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8228 | 4259 | 12487 | 4015 | 893 | 1530 | 0 | 4069 | 879 | 70 | 327 | 727 | 134 | 0 | 0 | 85.39
23:00 | 0 | 0 | 210 | 0 | 200 | 92 | 0 | 0 | 0 |  | 0 | 270 | 140 | 100 | 30 | 40 | 218 | 0 | 37 | 100 | 58 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 20 | 22 | 25 | 29 | 33 | 25 | 51 | 0 | 70 | 0 | 0 | 150 | 8 | 203 | 0 | 0 | 0 |  | 24 | 17 | 51 | 0 | 102 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 270 | 209 | 8 | 140 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 14 | 140 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 270 | 40 | 89 | 0 | 145 | 0 | 25 | 10 | 270 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 76 | 200 | 148 | 401 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 117 | 100 | 0 | 90 | 0 | 54 | 113 | 0 | 35 | 0 | 99 | 55 |  | 892 | 0 | 315 | 0 | 97 | 120 | 0 | 0 | 0 | 0 | 32 | 67 | 38 | 32 | 0 | 0 | 0 | 43 | 0 | 91 | 0 | 8 | 32 | 43 | 36 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 135 | 0 | 0 | 215 | 0 | 0 | 95 | 0 | 113 | 15 | 110 | 0 | 0 | 113 | 570 | 220 | 0 | 0 | 0 | 0 | 36 |  | 8119 | 3994 | 12113 | 4010 | 892 | 1517 | 0 | 3960 | 849 | 70 | 255 | 555 | 140 | 0 | 0 | 85.38
24:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 135 | 63 | 3 | 40 | 219 | 0 | 37 | 100 | 58 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 25 | 51 | 0 | 69 | 0 | 0 | 150 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 102 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 270 | 205 | 8 | 140 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 144 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 270 | 40 | 89 | 0 | 145 | 0 | 25 | 10 | 290 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 76 | 200 | 143 | 399 | 78 | 92 | 105 | 0 | 300 | 54 | 110 | 98 | 108 | 100 | 0 | 90 | 0 | 54 | 113 | 0 | 35 | 0 | 99 | 55 |  | 898 | 0 | 320 | 0 | 98 | 120 | 0 | 0 | 0 | 0 | 32 | 67 | 37 | 16 | 0 | 0 | 0 | 15 | 0 | 92 | 0 | 8 | 12 | 43 | 36 | 22 | 0 | 11 | 79 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 215 | 0 | 0 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 550 | 220 | 0 | 0 | 0 | 0 | 34 |  | 8003 | 3899 | 11902 | 4000 | 898 | 1533 | 0 | 3858 | 828 | 69 | 250 | 452 | 144 | 0 | 0 | 85.37
KWH | 0 | 0 | 5052000 | 0 | 4746300 | 2163045 | 0 | 0 | 0 |  | 0 | 6592300 | 3419724 | 1248960 | 856488 | 929299 | 5134439 | 0 | 1144000 | 1306560 | 1772784 | 2545440 | 0 | 0 | 0 | 0 | 1170000 | 885185 | 1111412 | 368064 | 600000 | 648000 | 689700 | 559200 | 1075680 | 0 | 1669762 | 0 | 0 | 3700000 | 354650 | 4906247 | 0 | 0 | 0 |  | 592320 | 281296 | 318051 | 0 | 2294400 | 497760 | 0 | 416640 | 0 | 0 | 0 | 6941700 | 6777000 | 4533000 | 200727 | 3247660 | 652968 | 367680 | 0 | 1036480 | 0 | 336440 | 1018906 | 278640 | 224820 | 250600 | 320550 | 3264000 | 2270400 | 0 | 404532 | 6300 | 715000 | 390000 | 1161000 | 624384 | 3739172 | 6167000 | 1327968 | 2135040 | 0 | 2887420 | 0 | 463320 | 249840 | 7055000 | 546288 | 208272 | 106560 | 5249016 | 255486 | 78911 | 4692000 | 115356 | 3512880 | 114210 | 2037120 | 2942880 | 3238400 | 9261000 | 1482000 | 2124000 | 2421272 | 27359 | 7048036 | 1344973 | 2607770 | 1690620 | 2598960 | 2184000 | 0 | 2114880 | 165130 | 2777760 | 2693509 | 0 | 747360 | 164555 | 1667520 | 1265040 |  | 21693818 | 0 | 6485184 | 0 | 829440 | 3450240 | 0 | 0 | 203040 | 3712 | 27225 | 1579000 | 719387 | 679008 | 0 | 0 | 0 | 481952 | 346180 | 954400 | 0 | 197511 | 290782 | 739397 | 340360 | 509280 | 0 | 252054 | 1896872 | 0 | 4870900 | 0 | 0 | 4645727 | 0 | 0 | 3769300 | 0 | 0 | 4297773 | 0 | 4586618 | 2231040 | 25530 | 2524416 | 75600 | 2311977 | 0 | 22905 | 2150016 | 12825200 | 4781700 | 0 | 0 | 16980 | 581040 | 1587915 |  | 185580376 | 92983479 | 278563855 | 92212506 | 21693818 | 40221337 | 581843 | 84907945 | 19592972 | 1669762 | 7219540 | 6101653 | 3264000 | 1098479 | 0
Fuel Cost | 0 | 0 | 7375920 | 0 | 5268393 | 2855219.4 | 0 | 0 | 0 |  | 0 | 7185607 | 3795893.64 | 9479606.4 | 5901202.32 | 7861869.54 | 5339816.56 | 0 | 1979120 | 9838396.8 | 16167790.08 | 25047129.6 | 0 | 0 | 0 | 0 | 8541000 | 6842480.05 | 10958522.32 | 276048 | 450000 | 0 | 0 | 0 | 10401825.6 | 0 | 450835.74 | 0 | 0 | 6697000 | 3294698.5 | 5347809.23 | 0 | 0 | 0 |  | 0 | 2720132.32 | 3085094.7 | 0 | 19961280 | 3942259.2 | 0 | 1237420.8 | 0 | 0 | 0 | 5136858 | 6777000 | 4170360 | 258937.83 | 3734809 | 737853.84 | 514752 | 0 | 1772380.8 | 0 | 3398044 | 9730552.3 | 353872.8 | 168615 | 438550 | 240412.5 | 24480000 | 2406624 | 0 | 513755.64 | 100422 | 1172600 | 624000 | 2066580 | 974039.04 | 4262656.08 | 6413680 | 2616096.96 | 4077926.4 | 0 | 4995236.6 | 0 | 542084.4 | 509673.6 | 7125550 | 409716 | 158286.72 | 1812585.6 | 39682560.96 | 4338152.28 | 1319391.92 | 24398400 | 1928752.32 | 34566739.2 | 1335114.9 | 16602528 | 31930248 | 22830720 | 8612730 | 13515840 | 20071800 | 21089279.12 | 0 | 53283152.16 | 11714714.83 | 22922298.3 | 16872387.6 | 22273087.2 | 14545440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 124956391.68 | 0 | 6809443.2 | 0 | 6519398.4 | 47820326.4 | 0 | 0 | 2129889.6 | 38901.76 | 283684.5 | 1784270 | 1115049.85 | 6627118.08 | 0 | 0 | 0 | 4742407.68 | 3517188.8 | 8446440 | 0 | 2670348.72 | 2817677.58 | 7164756.93 | 3301492 | 977817.6 | 0 | 190804.878 | 11438138.16 | 0 | 26400278 | 0 | 0 | 5435500.59 | 0 | 0 | 55484096 | 0 | 0 | 5028394.41 | 0 | 4540751.82 | 23292057.6 | 434265.3 | 23956707.84 | 713664 | 17940941.52 | 0 | 253100.25 | 15888618.24 | 56302628 | 0 | 0 | 0 | 0 | 0 | 0 |  | 678830218.7 | 479022549.388 | 1157852768.088 | 101663576.928 | 124956391.68 | 43812340.26 | 9833147.42 | 594277974.31 | 94141044.16 | 450835.74 | 103304422.4 | 59244398.04 | 24480000 | 1688637.15 | 0
Yesterday Day Peak | 0 | 0 | 210 | 0 | 200 | 93 | 0 | 0 | 0 |  | 0 | 270 | 148 | 57 | 67 | 40 | 214 | 0 | 38 | 60 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 25 | 16 | 50 | 0 | 70 | 0 | 0 | 150 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 86 | 25 | 0 | 2 | 0 | 0 | 0 | 270 | 300 | 183 | 8 | 137 | 26 | 15 | 0 | 43 | 0 | 0 | 43 | 0 | 11 | 0 | 13 | 144 | 73 | 0 | 19 | 1 | 30 | 30 | 47 | 23 | 130 | 270 | 60 | 89 | 0 | 100 | 0 | 20 | 10 | 290 | 22 | 5 | 0 | 281 | 0 | 0 | 183 | 0 | 138 | 19 | 90 | 116 | 125 | 375 | 48 | 90 | 87 | 5 | 300 | 54 | 93 | 72 | 103 | 100 | 0 | 88 | 35 | 144 | 113 | 0 | 33 | 30 | 99 | 50 |  | 897 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 16 | 34 | 0 | 21 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 174 | 0 | 0 | 130 | 0 | 0 | 147 | 0 | 287 | 94 | 0 | 94 | 0 | 110 | 0 | 2 | 95 | 400 | 205 | 0 | 0 | 4 | 95 | 115 |  | 11507 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 0 | 200 | 91 | 0 | 0 | 0 | 0 | 0 | 270 | 130 | 100 | 65 | 55 | 228 | 0 | 55 | 100 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 50 | 0 | 25 | 20 | 33 | 5 | 28 | 0 | 70 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 42 | 51 | 0 | 95 | 25 | 0 | 15 | 0 | 0 | 0 | 270 | 270 | 185 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 14 | 178 | 107 | 0 | 20 | 0 | 30 | 0 | 53 | 29 | 163 | 270 | 61 | 89 | 0 | 145 | 0 | 20 | 10 | 300 | 24 | 11 | 100 | 281 | 154 | 50 | 200 | 100 | 131 | 0 | 90 | 157 | 150 | 400 | 107 | 90 | 105 | 0 | 300 | 54 | 94 | 98 | 113 | 100 | 0 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 99 | 55 |  | 892 | 0 | 280 | 0 | 83 | 180 | 0 | 0 | 42 | 0 | 32 | 67 | 35 | 32 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 34 | 32 | 35 | 36 | 22 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 186 | 0 | 0 | 151 | 0 | 0 | 188 | 0 | 0 | 95 | 40 | 100 | 12 | 102 | 0 | 0 | 113 | 490 | 214 | 0 | 0 | 0 | 0 | 115 |  | 12769 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 0 | 200 | 100 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 100 | 80 | 55 | 220 | 0 | 60 | 100 | 90 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 200 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 0 | 100 | 25 | 0 | 20 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 22 | 163 | 110 | 0 | 20 | 0 | 30 | 0 | 51 | 30 | 163 | 270 | 66 | 86 | 0 | 145 | 0 | 20 | 10 | 300 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 107 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 0 | 90 | 0 | 144 | 113 | 0 | 35 |  | 100 | 55 |  | 915 | 0 | 300 | 0 | 100 | 225 | 0 | 0 | 42 | 30 | 32 | 67 | 35 | 80 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 40 | 33 | 43 | 36 | 22 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 100 | 180 | 0 | 350 | 95 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 660 | 220 |  | 100 |  |  | 115
Forecast for Day | 0 | 0 | 210 | 0 | 200 | 100 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 100 | 80 | 55 | 220 | 0 | 50 | 100 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 200 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 100 | 25 | 0 | 10 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 135 | 29 | 5 | 0 | 43 | 0 | 32 | 43 | 19 | 11 | 25 | 22 | 138 | 110 | 0 | 20 | 1.6 | 30 | 0 | 50 | 30 | 163 | 270 | 60 | 86 | 0 | 140 | 0 | 20 | 10 | 300 | 24 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 106 | 90 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 0 | 90 | 50 | 144 | 113 | 0 | 35 | 30 | 100 | 55 |  | 915 | 0 | 280 | 0 | 100 | 225 | 0 | 0 | 0 | 0 | 32 | 65 | 25 | 32 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 40 | 0 | 43 | 30 | 22 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 220 | 0 | 100 | 170 | 0 | 300 | 95 | 100 | 113 | 0 | 113 | 0 | 8 | 95 | 660 | 220 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 | 0 | 0 | 270 | 140 | 7 | 10 | 40 | 224 | 0 | 38 | 6 | 58 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 0 | 25 | 25 | 32 | 0 | 70 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 96 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 180 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 124 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 268 | 40 | 89 | 0 | 130 | 0 | 23 | 10 | 290 | 16 | 5 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 7 | 90 | 17 | 150 | 352 | 48 | 90 | 87 | 1 | 300 | 54 | 110 | 34 | 106 | 100 | 0 | 90 | 11 | 72 | 94 | 0 | 35 | 7 | 17 | 55 | 0 | 913 | 0 | 380 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 0 | 95 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 400 | 191 | 0 | 0 | 0 | 33 | 88 | 0 |  |  |  |  | 98810981 |  | 0
98810981
| Minimum Generation |  | 10314 | 6:00
| Highest Generation |  | 12769 | 19:00
| Day Peak Generation |  | 11507 | 12:00
| Evening Peak Generation |  | 12769 | 19:00
| HVDC Max Flow |  | 903 | 11:00
| HVDC EvPeak Flow |  | 892 | 19:00
| Load factor L.F |  | 90.9%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-30
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11507 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10068 | MW
Evening Peak Generation : |  | 12769 | MW Hour : | 19:00 | Available Max Generation : |  | 14560 | MW
E.P. Demand (at gen end) : |  | 12769 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13400 | MW
Maximum Generation : |  | 12769 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1160 | MW
Total Gen. (MKWH) : |  | 278.5639 | System Load Factor : | 90.9% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -268 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-30
Actual : | 85.32 | Ft.(MSL) , | Rule curve : | 88.51 | Ft.( MSL )
Gas Consumed : | Total = | 1059.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145475917.188
: |  | Coal : | 94141044.16 | Oil : | 766659942.17 | Total : | 1006276903.518
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4815.8522 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1643.9487 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1474.0447 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1332.3218 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1203.7805 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 971.4241 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 535.0753 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 249.9013 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 749.2492 |  |  | 0 | 0%
Total | 0 |  | 12975.5978 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1
6) Bibiyana South
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Baroirhat-Feni 132 kV Ckt-1 was under shut down from 07:04 to 08:49 for D/W.
b) Thakurgaon-Panchaghar 132 kV Ckt was under shut down from 06:10 to 09:15 for red hot maintenance. | [5 empty] | About 30 MW power interruption occurred under
Panchaghar S/S area from 07:04 to 08:49.
c) Jamalpur 132/33 kV T-2 transformer was under shut down from 07:10 to 08:44 due to red hot maintenance | [5 empty] | About 60 MW power interruption occurred under
at 33 kV T5 feeder DS. | [5 empty] | Jamalpur S/S area from 07:10 to 08:44.
d) Savar 33 kV Bus-A was under shut down from 08:06 to 21:35 for C/M.
e) Mirpur-Uttara 3rd phase 132 kV Ckt was under shut down at 07:43 for C/M.
f) Mirpur 132 kV main bus was under shut down from 09:30 to 07:32(30/3/22) for C/M.
g) Kabirpur-Manikganj 132 kV Ckt-1 was under shut down from 08:20 to 10:46 due to red maintenance | [5 empty] | About 20 MW power interruption occurred under
at B-phase T joint. | [5 empty] | Manikganj S/S area from 08:20 to 10:46.
h) Savar 33 kV capacitor bank-2 was under shut down at 08:05 for C/M.
i) Ghorasal-Norsingdi 132 kV Ckt-2 tripped at 08:15 showing dist.B-phase was switched on at 08:46.
j) Baroirhat-PHP 132 kV Ckt was under shut down from 09:03 to 10:10 for D/W.
k) Keraniganj 132/33 kV T-1 transformer was under shut down at 09:16 for D/W.
l) Srinagar 132/33 kV T-1 transformer along with 33 kV bus were shut down at 10:49 due to 33 kV feeder | [5 empty] | About 15 MW power interruption occurred under
maintenance and was switched on at 11:06. | [5 empty] | Srinagar S/S area from 10:49 to 11:06.
m) Munshiganj 132/33 kV T-2 transformer was under shut down from 10:35 to 15:12 for C/M.
n) Bagerhat 132/33 kV T-1 & T-2 transformers were under shut down from 07:03 to 08:42 for C/M. | [5 empty] | About 30 MW power interruption occurred under
Bagerhat S/S area from 07:03 to 08:42.
o) Khulna(S)-Satkhira 132 kV Ckt-2 was under shut down from 08:30 to 10:28 for C/M.
p) Cumilla(N) 132/33 kV T-4 transformer with 33 kV bus were under shut down from 11:11 to 13:13 due to | [5 empty] | About 20 MW power interruption occurred under
feeder CT change. | [5 empty] | Cumilla(N) S/S area from 11:11 to 13:13.
q) Ruppur 132/11 kV T-1 transformer was under shut down from 12:19 to 13:17 due to NESCO-2 feeder
maintenance.
r) Jholdhaka 132/33 kV T-2 transformer was under shut down at 12:25 due to red hot maintenance at 33 | [5 empty] | About 20 MW power interruption occurred under
kV bus and was switched on at 13:30. | [5 empty] | Jholdhaka S/S area from12:25 to 13:30.
s) Tongi-Kabirpur 132 kV Ckt-2 tripped at 16:20 showing dist.Z1,C-phase and was switched on at 16:46.
t) Sirajganj #4 was forced shut down at 14:12 due to maintenance work and was synchronized at 06:57
(30/3/22) and tripped at 07:10(30/3/22) and was synchronized at 09:30(30/3/22).
u) Maniknagar-Kazla 132 kV Ckt-1 was shut down at 20:02 due to red hot maintenance and was switched
on at 22:51.
v) Hathazari-Baraulia 132 kV Ckt-1 is under shut down since 05:58(30/3/22) for C/M.
w) Agargaon-Cantonment 132 kV Ckt-2 tripped at 05:58(30/3/22) showing diff. inter trip.
x) Kaliakoir-Aminbazar 230 kV Ckt-2 is under shut down since 06:21(30/3/22) for C/M.
y) Fenchuganj P/S-Sylhet 132 kV Ckt is under shut down since 06:40(30/3/22) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 5052000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4746300 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 2163045 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6592300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 100 | 1248960
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3419724 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 65 | 856488 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 929299
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 368064 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 55 | 1144000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 100 | 1306560
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 228 | 5134439 | ST under maint., Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1772784 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1170000
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2545440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 885185
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 50 | 1111412
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1248000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 689700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 5 | 559200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 28 | 1075680
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 5249016 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 154 | 255486 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 78911 | Low demand.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 115356
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 3512880 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2124000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2114880 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2777760 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 164555
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1265040
| Dhaka area Total |  |  |  | 5696 | 3085 | 61676464
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 354650
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 114210
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 497760 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1669762 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4906247
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2421272
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 281296 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 318051 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2037120 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 416640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 2294400 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27359
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 7048036
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1344973
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 94 | 2607770 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2184000 | 33 kV feeder fault.
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2693509
| Chattogram area Total |  |  |  | 2382 | 1532 | 34917055
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 185 | 4533000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 6941700 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6777000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 652968 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 367680 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1036480 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3238400
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 336440 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3247660 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 157 | 2942880 | Low demand.
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 278640
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 178 | 3264000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 250600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1018906 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 320550 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 106560 | Low demand.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1690620 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2598960
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 747360 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 1667520 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2012 | 42443471
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2270400 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 404532
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 4692000
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 1482000
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 165130
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 592320
| Mymensingh Area Total |  |  |  | 622 | 458 | 9612682
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 390000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3739172
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 270 | 6167000 | Machine problem
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1161000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 29 | 624384
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 208272
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1327968
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2135040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 2887420 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 20 | 463320
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 546288
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7055000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9261000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1605 | 36930704
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 892 | 21693818
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 83 | 829440 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 203040 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3450240 | Low demand.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 3712 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 280 | 6485184 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 32 | 27225
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 2231040 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 12 | 75600 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 581040
| Khulna Area Total |  |  |  | 2229 | 1616 | 35580339
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 679008 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 35 | 719387
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1579000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 490 | 12825200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 214 | 4781700
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 838 | 20584295
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 481952 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 45 | 346180 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 197511 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 290782 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 186 | 4645727 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 151 | 3769300 | Running on HSD
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4297773 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 4586618 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 340360 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 509280
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252054
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 35 | 739397 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 954400 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 40 | 25530 | Low demand.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 2524416 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2150016
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 16980
| Rajshahi Area Total |  |  |  | 2129 | 1129 | 26128276
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1896872
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4870900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 2311977 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22905
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1587915
| Rangpur Area Total |  |  |  | 720 | 494 | 10690569
| Total |  |  |  | 21215 | 12769 | 278563855
| Eastern Grid Total |  |  |  | 14091 | 8692 | 185580376
| Western Grid Total |  |  |  | 7124 | 4077 | 92983479
| National Grid Total |  |  |  | 21215 | 12769 | 278563855
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-29
(a) ENTIRE EASTERN GRID : |  | 8044.53 | MW | (b) ENTIRE WESTERN GRID : |  | 4313.6 | MW
i) Dhaka area |  | 4273.3 | MW | i) Khulna area |  | 1600.4 | MW
ii) Chittagong area |  | 1284.23 | MW | ii) Rajshahi area |  | 1480.2 | MW
iii) Comilla area |  | 1030 | MW | iii) Barisal area |  | 369 | MW
iv) Mymensingh area |  | 1090 | MW | iv) Rangpur area |  | 864 | MW
v) Sylhet area |  | 367 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12358.13 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 29 | 12:00 | Hasnabad | 95 | 18:30 | Palashbari | 122 | 19:30
Agargaon | 90 | 13:00 | Hathazari | 97 | 18:30 | Panchagarh | 61 | 19:00
Agrabad | 80 | 15:00 | Ishurdi | 72 | 19:00 | Patuakhali | 116 | 22:00
AKS | 11 | 22:00 | Jaldhaka | 54 | 18:30 | PHP | 8 | 18:00
AKSML | 130 | 07:00 | Jamalpur | 151 | 07:00 | Purbachal | 17 | 15:00
Amnura | 67 | 00:00 | Jashore | 123 | 19:30 | Purbasadipur | 109 | 19:00
Ashuganj | 35 | 11:00 | Jhenaidah | 122 | 19:00 | Rahim | 20 | 15:00
Bagerhat | 101 | 17:00 | Joydebpur | 198 | 21:00 | Rajbari | 66 | 19:30
Bakulia | 121 | 18:30 | Joypurhat | 63 | 22:00 | Rajendrapur | 110 | 19:00
Banani | 51 | 15:00 | Juldah | 26 | 23:00 | Rajshahi | 155 | 19:00
Bangabhaban | 22 | 11:00 | Kabirpur | 257 | 11:00 | Rajshahi | 45 | 22:00
Barapukuria | 57 | 18:30 | Kachua | 66 | 19:00 | Ramganj | 92 | 21:00
Barguna | 18 | 23:00 | Kallyanpur | 93 | 15:00 | Rampur | 16 | 18:00
Barishal | 102 | 19:00 | Kalurghat | N/A | N/A | Rangamati | 13 | 19:00
Barishal | 57 | 21:00 | Kamrangirchar | 75 | 13:00 | Rangpur | 144 | 19:00
Baroaulia | 79 | 11:00 | Kaptai | 4.2 | 18:30 | Ruppur | 5 | 10:00
Baroirhat | 50 | 19:00 | Kazla | 90 | 18:30 | Saidpur | 110 | 19:00
Bashundhara | 166 | 15:00 | Keranigonj | 64 | 00:00 | Satkhira | 111 | 22:00
BashundharaCement | 13 | 01:00 | Khagrachori | 24 | 18:30 | Satmasjid | 89 | 15:00
Beanibazar | 47 | 18:30 | Khulna | 83 | 19:00 | Savar | 161 | 19:30
Benapole | 68 | 15:00 | Khulshi | 177 | 20:00 | Shahjadpur | 117 | 19:30
Bhaluka | 118 | 19:00 | Kishoreganj | 124 | 19:00 | Shahjibazar | 85 | 19:30
Bhandaria | 52 | 21:00 | Kodda | 299 | 12:00 | Shahmirpur | 37.5 | 19:00
Bhangura | 38 | 19:00 | KSRM | 26.87 | 16:00 | Shariatpur | 66 | 19:30
Bheramara(GK) | 60 | 19:00 | Kulaura | 30 | 18:30 | Sherpur | 140 | 19:00
Bhulta | 233 | 16:00 | Kurigram | 60 | 20:00 | Shikalbaha | 30 | 01:00
Bog-Sherpur | 56 | 19:00 | Kushtia | 134 | 19:00 | Shitalakhya | 118 | 15:00
Bogura | 175 | 19:30 | Lalbag | 95 | 17:00 | Sholosohor | N/A | N/A
Borhanuddin | 45 | 21:00 | Lalmonirhat | 45 | 19:00 | Shyampur | 176 | 10:00
Brahmanbaria | 116 | 00:00 | Madanganj | 164 | 18:00 | Siddhirganj | 122 | 10:00
BSRM | 157 | 12:00 | Madaripur | 104 | 22:00 | Sirajganj | 126 | 20:00
Cantonment | 138 | 15:00 | Madartek | 73 | 18:30 | Sonargaon | 80 | 01:00
Chandpur | 70 | 19:00 | Madunaghat | 59 | 19:30 | Sreemongol | 43 | 18:30
Chandraghona | 30 | 18:30 | Magura | 62 | 19:30 | Srinagar | 42.31 | 18:30
Chapai | 69 | 00:00 | Mahasthangarh | 72 | 20:00 | SSM | 3 | 09:00
Charsaidpur | 47 | 10:00 | Manikganj | 89 | 20:00 | Sunamganj | 38 | 19:30
Chauddagram | 45 | 20:00 | Maniknagar | 71 | 13:00 | Sylhet | 119 | 18:30
Chhatak | 22 | 21:00 | Matarbari | 42 | 19:30 | Tangail | 225 | 20:00
Chowmuhani | 207 | 22:00 | Matuail | 62 | 09:00 | Thakurgaon | 80 | 19:00
Chuadanga | 101 | 20:00 | Millgate | 48 | 15:00 | TK | N/A | N/A
Coxsbazar | 116 | 19:00 | Mirpur | 112 | 14:00 | Tongi | 124 | 22:00
Cumilla(N) | 129 | 22:00 | Mirsorai | N/A | N/A | Ullon | 42 | 18:30
Cumilla(S) | 180 | 18:30 | Mithapukur | 41 | 13:00 | Uttara | 65 | 13:00
Daudkandi | 120 | 13:00 | Modern | 0 | 00:00 | UttaraNew | 33 | 15:00
Dhaka | 37 | 11:00 | Mogbazar | 115 | 15:00 | Zigatola | 42 | 18:30
Dhamrai | 122 | 15:00 | Mongla | 42 | 11:00
Dhanmondi | 192 | 14:00 | Motijheel | 31 | 13:00
Dohazari | 86 | 19:00 | Munshiganj | 95 | 00:00
Faridpur | 141 | 21:00 | Mymensingh | 231 | 19:30
Fatullah | 68 | 11:00 | Naogaon | 124 | 00:00
Fenchuganj | 28 | 18:30 | Narail | 53 | 20:00
Feni | 127 | 21:00 | Narinda | 59 | 12:00
Ghorashal | 75 | 11:00 | Narshingdi | 153 | 00:00
Goalpara | 27 | 19:00 | Natore | 144 | 21:00
Gollamari | 54 | 19:30 | Nawabganj | 49.6 | 20:00
Gopalganj | 99.6 | 19:30 | Netrakona | 116 | 20:00
GPH | 91 | 13:00 | New | 83.6 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 19:00 | 400 | 10:00 | Kaliakoir | 395 | 0.41667 | 379 | 0.45833
| Bheramara | 397 | 7:00 | 391 | 16:00 | Bhulta | 406 | 0.79167 | 388 | 0.41667
| Ashuganj(N) | 412 | 19:00 | 396 | 11:00 | Gopalganj | 412 | 0.625 | 395 | 0.041667
| Payra | 420 | 19:00 | 406 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 7:00 | Hathazari | 236 | 7:00 | 230 | 10:00
| Ishurdi | 234 | 10:00 | 227 | 19:30 | Megnaghat | 235 | 6:00 | 228 | 14:00
| Ashuganj | 243 | 19:00 | 236 | 16:00 | Fenchuganj | 244 | 19:00 | 232 | 17:00
| Serajganj | 236 | 17:00 | 230 | 19:30 | Siddhirganj | 232 | 5:00 | 216 | 13:00
| Baghabari | 233 | 14:00 | 227 | 20:00 | Maniknagar | 229 | 5:00 | 216 | 11:00
| Barapukuria | 230 | 16:00 | 219 | 19:00 | Agargaon | 228 | 10:00 | 216 | 11:00
| Bogra | 230 | 10:00 | 221 | 19:30 | Barisal | 241 | 8:00 | 230 | 24:00
| Rajshahi | 225 | 9:00 | 217 | 19:30 | Bhola 225 MW | 245 | 10:00 | 238 | 20:00
| Khulna South | 240 | 18:00 | 227 | 1:00 | AKSML | 236 | 8:00 | 230 | 11:00
| Rampura | 230 | 23:00 | 217 | 10:00 | BSRM | 236 | 19:00 | 228 | 11:00
| Haripur | 230 | 19:00 | 218 | 11:00 | Bibiyana | 240 | 19:00 | 235 | 2:00
| Hasnabad | 227 | 3:00 | 217 | 11:00 | Bhulta | 232 | 19:00 | 220 | 10:00
| Shyampur | 229 | 19:00 | 216 | 11:00 | Ashuganj (S) | 240 | 23:00 | 232 | 11:00
| Aminbazar | 228 | 1:00 | 215 | 2:00 | Kaliakoir | 230 | 1:00 | 219 | 12:00
| Tongi | 231 | 24:00 | 220 | 11:00 | GPH | 236 | 8:00 | 230 | 11:00
| Comilla (N) | 240 | 14:00 | 220 | 18:30 | Jhenaidah | 232 | 18:00 | 221 | 19:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 22:00 | 126 | 10:00 | Manikganj | 137 | 01:00 | 127 | 16:00
| Agargaon | 138 | 02:00 | 129 | 11:00 | Maniknagar | 133 | 03:00 | 124 | 11:00
| Agrabad | 135 | 00:00 | 130 | 12:00 | Matarbari | 137 | 04:00 | 115 | 00:00
| AKS | 134 | 00:00 | 131 | 01:00 | Matuail | 137 | 19:30 | 128 | 11:00
| Aminbazar | 136 | 00:00 | 126 | 16:00 | Millgate | 138 | 00:00 | 130 | 11:00
| Amnura | 135 | 17:00 | 127 | 05:00 | Mirpur | 133 | 00:00 | 127 | 12:00
| Ashuganj | 140 | 02:00 | 135 | 11:00 | Mithapukur | 132 | 16:00 | 122 | 19:00
| Bagerhat | 136 | 08:00 | 129 | 19:30 | Modern | 135 | 00:00 | 131 | 12:00
| Bakulia | 136 | 08:00 | 130 | 17:00 | Mogbazar | 137 | 22:00 | 125 | 12:00
| Banani | 138 | 00:00 | 130 | 11:00 | Mongla | 135 | 09:00 | 128 | 20:00
| Bangabhaban | 162 | 06:00 | 125 | 11:00 | Motijheel | 133 | 08:00 | 125 | 11:00
| Barapukuria | 133 | 16:00 | 126 | 18:30 | Munshiganj | 140 | 19:00 | 129 | 10:00
| Barguna | 138 | 07:00 | 129 | 22:00 | Mymensingh | 129 | 06:00 | 117 | 18:30
| Barishal | 139 | 06:00 | 128 | 22:00 | Naogaon | 128 | 16:00 | 118 | 19:00
| Barishal | 140 | 10:00 | 133 | 19:30 | Narail | 129 | 09:00 | 120 | 19:00
| Baroaulia | 137 | 08:00 | 131 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 08:00 | 129 | 04:00 | Narshingdi | 134 | 19:00 | 123 | 11:00
| Bashundhara | 138 | 00:00 | 129 | 11:00 | Natore | 135 | 10:00 | 130 | 07:00
| BashundharaCement | 139 | 19:00 | 130 | 11:00 | Nawabganj | 137 | 08:00 | 129 | 11:00
| Beanibazar | 135 | 04:00 | 132 | 14:00 | Netrakona | 126 | 06:00 | 115 | 11:00
| Benapole | 132 | 18:00 | 12 | 12:00 | New | 139 | 02:00 | 131 | 10:00
| Bhaluka | 129 | 04:00 | 116 | 11:00 | Niamatpur | 125 | 10:00 | 112 | 19:00
| Bhandaria | 139 | 08:00 | 128 | 22:00 | Noapara | 136 | 18:00 | 129 | 01:00
| Bhangura | 134 | 14:00 | 129 | 19:30 | Pabna | 133 | 10:00 | 128 | 19:30
| Bheramara | 135 | 10:00 | 131 | 19:30 | Palashbari | 128 | 10:00 | 120 | 19:00
| Bheramara(GK) | 138 | 17:00 | 133 | 19:30 | Panchagarh | 135 | 16:00 | 121 | 19:00
| Bhulta | 134 | 19:00 | 123 | 11:00 | Patuakhali | 136 | 05:00 | 130 | 22:00
| Bog-Sherpur | 133 | 10:00 | 125 | 19:30 | PHP | 134 | 23:00 | 129 | 03:00
| Bogura | 134 | 11:00 | 128 | 19:00 | Purbachal | 138 | 00:00 | 130 | 11:00
| Bogura | 135 | 10:00 | 127 | 19:00 | Purbasadipur | 134 | 16:00 | 122 | 07:00
| Brahmanbaria | 136 | 17:00 | 132 | 10:00 | Rahim | 138 | 19:00 | 128 | 11:00
| Cantonment | 137 | 03:00 | 128 | 11:00 | Rajbari | 135 | 10:00 | 126 | 20:00
| Chandpur | 140 | 23:00 | 130 | 04:00 | Rajendrapur | 137 | 01:00 | 129 | 12:00
| Chandraghona | 139 | 15:00 | 133 | 10:00 | Rajshahi | 136 | 17:00 | 130 | 19:30
| Chapai | 134 | 17:00 | 127 | 05:00 | Rajshahi | 137 | 17:00 | 130 | 19:30
| Charsaidpur | 142 | 19:00 | 130 | 10:00 | Ramganj | 135 | 09:00 | 126 | 05:00
| Chauddagram | 136 | 23:00 | 35 | 20:00 | Rampur | 135 | 06:00 | 131 | 20:00
| Chhatak | 139 | 03:00 | 130 | 14:00 | Rampura | 137 | 23:00 | 128 | 13:00
| Chowmuhani | 134 | 23:00 | 126 | 06:00 | Rangamati | 137 | 08:00 | 132 | 12:00
| Chuadanga | 126 | 09:00 | 112 | 19:00 | Rangpur | 130 | 09:00 | 118 | 19:00
| Coxsbazar | 124 | 08:00 | 111 | 22:00 | Ruppur | 135 | 09:00 | 131 | 19:30
| Cumilla(N) | 137 | 19:00 | 132 | 10:00 | Saidpur | 133 | 03:00 | 120 | 19:00
| Cumilla(S) | 137 | 20:00 | 124 | 14:00 | Satkhira | 136 | 18:00 | 127 | 01:00
| Daudkandi | 137 | 20:00 | 128 | 10:00 | Satmasjid | 137 | 00:00 | 129 | 11:00
| Dhaka | 136 | 19:00 | 125 | 10:00 | Savar | 136 | 18:30 | 123 | 16:00
| Dhamrai | 138 | 02:00 | 128 | 16:00 | Shahjadpur | 137 | 02:00 | 132 | 19:00
| Dhanmondi | 137 | 19:30 | 127 | 10:00 | Shahjibazar | 138 | 03:00 | 136 | 09:00
| Dohazari | 133 | 08:00 | 125 | 17:00 | Shahmirpur | 135 | 00:00 | 131 | 17:00
| Faridpur | 135 | 10:00 | 125 | 19:30 | Shariatpur | 137 | 09:00 | 128 | 20:00
| Fatullah | 137 | 19:00 | 128 | 11:00 | Sherpur | 131 | 04:00 | 120 | 09:00
| Fenchuganj | 139 | 06:00 | 133 | 01:00 | Shikalbaha | 135 | 06:00 | 132 | 11:00
| Feni | 136 | 23:00 | 129 | 06:00 | Shikalbaha | 135 | 08:00 | 132 | 13:00
| Ghorashal | 140 | 17:00 | 130 | 00:00 | Shitalakhya | 140 | 19:00 | 129 | 10:00
| Goalpara | 138 | 09:00 | 133 | 01:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 135 | 10:00 | 125 | 00:00 | Shyampur | 135 | 03:00 | 128 | 12:00
| Gopalganj | 136 | 10:00 | 128 | 00:00 | Shyampur | 136 | 19:00 | 128 | 11:00
| Gopalganj_I | 140 | 09:00 | 132 | 01:00 | Siddhirganj | 138 | 18:30 | 128 | 10:00
| Gulshan | 136 | 22:00 | 125 | 10:00 | Sirajganj | 132 | 03:00 | 126 | 19:00
| Halishahar | 136 | 08:00 | 130 | 12:00 | Sonargaon | 140 | 19:00 | 128 | 10:00
| Haripur | 138 | 19:00 | 128 | 11:00 | Sreemongol | 141 | 02:00 | 137 | 15:00
| HaripurSBU | 138 | 19:30 | 128 | 11:00 | Srinagar | 137 | 03:00 | 130 | 11:00
| Hasnabad | 136 | 00:00 | 130 | 11:00 | SSM | 136 | 00:00 | 131 | 17:00
| Hathazari | 137 | 00:00 | 134 | 10:00 | Sunamganj | 133 | 07:00 | 130 | 00:00
| Ishurdi | 136 | 18:00 | 132 | 07:00 | Sylhet | 134 | 04:00 | 132 | 15:00
| Jaldhaka | 130 | 13:00 | 117 | 19:00 | Tangail | 135 | 02:00 | 126 | 11:00
| Jamalpur | 132 | 01:00 | 122 | 11:00 | Thakurgaon | 135 | 16:00 | 121 | 01:00
| Jashore | 132 | 18:00 | 125 | 01:00 | TK | N/A | N/A | N/A | N/A
| Jhenaidah | 132 | 09:00 | 123 | 19:00 | Tongi | 138 | 22:00 | 133 | 11:00
| Jhenaidah | 132 | 09:00 | 124 | 19:00 | Ullon | 136 | 19:30 | 125 | 10:00
| Joydebpur | 141 | 17:00 | 134 | 11:00 | Uttara | 136 | 13:00 | 126 | 11:00
| Joypurhat | 125 | 10:00 | 115 | 19:00 | UttaraNew | 136 | 18:00 | 130 | 10:00
| Juldah | 134 | 01:00 | 131 | 12:00 | Zigatola | 136 | 02:00 | 36 | 03:00
| Kabirpur | 141 | 01:00 | 129 | 16:00
| Kachua | 137 | 22:00 | 130 | 02:00
| Kaliakoir | 140 | 18:00 | 36 | 18:30
| Kallyanpur | 135 | 00:00 | 127 | 13:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 137 | 01:00 | 129 | 12:00
| Kaptai | 135 | 00:00 | 131 | 15:00
Page 7 of 7

## L-Curve
Date | 2022-03-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 104 | 8003 | 3899 | 11902 |  |  |  | QF-LDC-11
0:30 | 68 | 7915.5 | 3862.5 | 11778 | Date: | 2022-03-29
1:00 | 32 | 7828 | 3826 | 11654
1:30 | 16 | 7680 | 3781.5 | 11461.5
2:00 | 0 | 7532 | 3737 | 11269
2:30 | 29 | 7318 | 3724.5 | 11042.5 | [5 empty] | Gen. at Eve. Peak | 12769 | 12769 MW (19:00 )
3:00 | 58 | 7104 | 3712 | 10816 | [6 empty] | 19:00
3:30 | 81 | 7016 | 3642.5 | 10658.5 | [5 empty] | Gen. at Day Peak | 11507 | 11507 MW (12:00 )
4:00 | 104 | 6928 | 3573 | 10501 | [6 empty] | 12:00
4:30 | 95 | 6953.5 | 3561 | 10514.5 | [5 empty] | Highest Generation | 12769
5:00 | 86 | 6979 | 3549 | 10528 | [6 empty] | 19:00
5:30 | 102 | 6929 | 3492 | 10421
6:00 | 118 | 6879 | 3435 | 10314
6:30 | 111 | 6918 | 3474 | 10392
7:00 | 104 | 6957 | 3513 | 10470
7:30 | 152 | 6909 | 3551 | 10460
8:00 | 200 | 6861 | 3589 | 10450
8:30 | 298 | 7006 | 3598.5 | 10604.5
9:00 | 396 | 7151 | 3608 | 10759
9:30 | 415 | 7203.5 | 3563.5 | 10767
10:00 | 434 | 7256 | 3519 | 10775
10:30 | 422 | 7404.5 | 3574.5 | 10979
11:00 | 410 | 7553 | 3630 | 11183
11:30 | 359 | 7678.5 | 3666.5 | 11345
12:00 | 308 | 7804 | 3703 | 11507
12:30 | 264 | 7998.5 | 3678.5 | 11677
13:00 | 220 | 8193 | 3654 | 11847
13:30 | 262 | 8048.5 | 3754 | 11802.5
14:00 | 304 | 7904 | 3854 | 11758
14:30 | 272 | 8045.5 | 3795 | 11840.5
15:00 | 240 | 8187 | 3736 | 11923
15:30 | 276 | 8066 | 3804 | 11870
16:00 | 312 | 7945 | 3872 | 11817
16:30 | 280 | 7770 | 3706.5 | 11476.5
17:00 | 248 | 7595 | 3541 | 11136
17:30 | 206 | 7583.5 | 3521 | 11104.5
18:00 | 164 | 7572 | 3501 | 11073
18:30 | 216 | 8132 | 3789 | 11921
19:00 | 268 | 8692 | 4077 | 12769
19:30 | 194 | 8317 | 4309 | 12626
20:00 | 160 | 8231 | 4308 | 12539 |  |  |  | Executive Engineer
20:30 | 152 | 8251.5 | 4301 | 12552.5 |  |  |  | Network Operation Division
21:00 | 144 | 8272 | 4294 | 12566
21:30 | 111 | 8250 | 4276.5 | 12526.5
22:00 | 78 | 8228 | 4259 | 12487 |  |  |  |  | Page 6 of 7
22:30 | 139 | 8173.5 | 4126.5 | 12300
23:00 | 200 | 8119 | 3994 | 12113
23:30 | 152 | 8061 | 3946.5 | 12007.5
24:00 | 104 | 8003 | 3899 | 11902
12769 MW (19:00 )
11507 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-29 |  | Energy |  | 278563855
[13 empty] | 2022-03-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4000 | 898 | 1533 | 0 | 3858 | 828 | 69 | 250 | 452 | 144 | 0 | 0
0:30 | 3871 | 897.5 | 1719.5 | 0 | 3765.5 | 844 | 68.5 | 250 | 358 | 134 | 0 | 0 | Date: | 2022-03-29
1:00 | 3742 | 897 | 1906 | 0 | 3673 | 860 | 68 | 250 | 264 | 124 | 0 | 0
1:30 | 3752 | 896 | 1894 | 0 | 3528.5 | 854.5 | 67.5 | 250 | 229 | 120 | 0 | 0 | [8 empty] | Total Energy | 278.5639 | Total Energy Gen 278.564 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 278.564 MKWHr
2:00 | 3762 | 895 | 1882 | 0 | 3384 | 849 | 67 | 250 | 194 | 116 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3731 | 895.5 | 1900.5 | 0 | 3188 | 839 | 67.5 | 250 | 186 | 115 | 0 | 0 | [8 empty] | Energy Requirement | 278.5639
3:00 | 3700 | 896 | 1919 | 0 | 2992 | 829 | 68 | 250 | 178 | 114 | 0 | 0
3:30 | 3707.5 | 897 | 1927.5 | 0 | 2842.5 | 814.5 | 68.5 | 250 | 170 | 111 | 0 | 0 | [6 empty] | Shortage
4:00 | 3715 | 898 | 1936 | 0 | 2693 | 800 | 69 | 250 | 162 | 108 | 0 | 0
4:30 | 3770 | 897.5 | 1915 | 0 | 2683.5 | 790 | 69.5 | 250 | 162 | 107 | 0 | 0
5:00 | 3825 | 897 | 1894 | 0 | 2674 | 780 | 70 | 250 | 162 | 106 | 0 | 0
5:30 | 3772 | 897 | 1880.5 | 0 | 2651.5 | 765 | 70 | 250 | 162 | 103 | 0 | 0
6:00 | 3719 | 897 | 1867 | 0 | 2629 | 750 | 70 | 250 | 162 | 100 | 0 | 0
6:30 | 3765 | 897 | 1882.5 | 0 | 2653 | 735.5 | 70 | 250 | 162 | 99 | 8 | 0 |  |  |  |  | Coal
7:00 | 3811 | 897 | 1898 | 0 | 2677 | 721 | 70 | 250 | 162 | 98 | 16 | 0
7:30 | 3750.5 | 897 | 1832.5 | 0 | 2791.5 | 700.5 | 70 | 250 | 162 | 101 | 35 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3690 | 897 | 1767 | 0 | 2906 | 680 | 70 | 250 | 162 | 104 | 54 | 0
8:30 | 3687.5 | 897 | 1790.5 | 0 | 2991 | 679.5 | 70 | 250 | 187 | 113 | 69 | 0
9:00 | 3685 | 897 | 1814 | 0 | 3076 | 679 | 70 | 250 | 212 | 122 | 84 | 0
9:30 | 3626.5 | 897.5 | 1745.5 | 0 | 3143 | 669 | 70 | 250 | 268.5 | 127 | 100 | 0
10:00 | 3568 | 898 | 1677 | 0 | 3210 | 659 | 70 | 250 | 325 | 132 | 116 | 0
10:30 | 3619.5 | 900.5 | 1698.5 | 0 | 3317 | 663 | 70 | 250 | 327.5 | 137 | 126 | 0
11:00 | 3671 | 903 | 1720 | 0 | 3424 | 667 | 70 | 250 | 330 | 142 | 136 | 0
11:30 | 3674.5 | 900 | 1722 | 0 | 3543.5 | 673 | 70 | 250 | 335.5 | 143 | 163.5 | 0
12:00 | 3678 | 897 | 1724 | 0 | 3663 | 679 | 70 | 250 | 341 | 144 | 191 | 0
12:30 | 3697 | 896 | 1698 | 54.5 | 3766 | 690 | 70 | 255 | 344.5 | 149 | 189.5 | 0
13:00 | 3716 | 895 | 1672 | 109 | 3869 | 701 | 70 | 260 | 348 | 154 | 188 | 0
13:30 | 3716 | 895 | 1672 | 109 | 3869 | 701 | 70 | 260 | 348 | 154 | 188 | 0
14:00 | 3716 | 895 | 1672 | 109 | 3869 | 701 | 70 | 260 | 348 | 154 | 188 | 0
14:30 | 3710.5 | 895.5 | 1570.5 | 126.5 | 3905.5 | 729.5 | 69 | 333 | 423.5 | 157 | 132.5 | 0
15:00 | 3705 | 896 | 1469 | 144 | 3942 | 758 | 68 | 406 | 499 | 160 | 77 | 0
15:30 | 3738.5 | 896.5 | 1441 | 72 | 3910 | 757.5 | 68 | 398 | 560 | 158 | 76 | 0
16:00 | 3772 | 897 | 1413 | 0 | 3878 | 757 | 68 | 390 | 621 | 156 | 75 | 0
16:30 | 3730 | 896.5 | 1395 | 0 | 3671.5 | 743 | 68.5 | 340.5 | 585.5 | 154 | 51.5 | 0
17:00 | 3730 | 896 | 1377 | 0 | 3465 | 729 | 69 | 291 | 550 | 152 | 28 | 0
17:30 | 3699.5 | 896 | 1361.5 | 0 | 3488 | 727.5 | 69.5 | 285.5 | 554 | 154 | 14.5 | 0
18:00 | 3669 | 896 | 1346 | 0 | 3511 | 726 | 70 | 280 | 558 | 156 | 1 | 0
18:30 | 3778.5 | 894 | 1421.5 | 222 | 3818.5 | 746.5 | 70 | 305.5 | 642.5 | 167 | 0.5 | 0
19:00 | 3888 | 892 | 1497 | 444 | 4126 | 767 | 70 | 331 | 727 | 178 | 0 | 0
19:30 | 3951 | 893 | 1467 | 10 | 4203 | 880 | 70 | 408 | 769 | 170 | 0 | 0
20:00 | 3951 | 894 | 1489 | 0 | 4129 | 891 | 70 | 375 | 767 | 168 | 0 | 0
20:30 | 3976 | 893.5 | 1505 | 0 | 4123.5 | 885.5 | 70 | 367.5 | 761 | 158 | 0 | 0
21:00 | 4001 | 893 | 1521 | 0 | 4118 | 880 | 70 | 360 | 755 | 148 | 0 | 0
21:30 | 4008 | 893 | 1525.5 | 0 | 4093.5 | 879.5 | 70 | 343.5 | 741 | 141 | 0 | 0
22:00 | 4015 | 893 | 1530 | 0 | 4069 | 879 | 70 | 327 | 727 | 134 | 0 | 0
22:30 | 4012.5 | 892.5 | 1523.5 | 0 | 4014.5 | 864 | 70 | 291 | 641 | 137 | 0 | 0
23:00 | 4010 | 892 | 1517 | 0 | 3960 | 849 | 70 | 255 | 555 | 140 | 0 | 0
23:30 | 4005 | 895 | 1525 | 0 | 3909 | 838.5 | 69.5 | 252.5 | 503.5 | 142 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.8° C
24:00 | 4000 | 898 | 1533 | 0 | 3858 | 828 | 69 | 250 | 452 | 144 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 278.564 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 278.564 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 68 | 67 | 68 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 68 | 68 | 69 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 1669762
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | 25 | [6 empty] | 5 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 354650
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0 | 3 | 7 | 13 | 15 | 15 | 19 | 18 | 15 | 10 | 7 | 2 | 0 | [8 empty] | 114210
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 204 | 131 | 131 | 203 | 204 | 216 | 203 | 203 | 204 | 214 | 204 | 204 | 202 | 205 | 203 | 203 | 204 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4906247
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [16 empty] | 26 |  | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 318051
12 | Hathazari 100 MW peaking PP | [15 empty] | 33 | 25 | 30 |  | 42 | 42 | 42 | 42 | 42 | 17 |  | 281296
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 102 | 87 | 87 | 87 | 87 | 87 | 87 | 95 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2421272
| Daudkandi 200 MW PP (B.Trac) | [14 empty] | 30 |  |  |  |  | 100 | [6 empty] | 106560
14 | Titas 50 MW Peaking PP | [12 empty] | 2 | 20 | 24 | 31 | 41 | 40 |  | 42 | 42 | 42 | 42 | 42 |  |  | 336440
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 40 | 40 | 40 | 41 | 41 | 62 | 62 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 54 | 37 | 40 |  | 55 | 34 | 34 | 37 | 37 | 37 | 37 | 1144000
17 | Siddhirganj 335 MW CCPP | 224 | 221 | 219 | 220 | 223 | 181 | 200 | 160 | 220 | 180 | 212 | 214 | 214 | 180 | 210 | 209 | 180 | 150 |  | 228 | 229 | 227 | 224 | 224 | 218 | 219 | 5134439
18 | Kodda 300 MW PP Unit-2 (Summit) | 280 | 281 | 145 | 15 | 15 | 15 | 15 | 80 | 100 | 188 | 265 | 281 | 281 | 283 | 281 | 281 | 281 | 281 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 5249016
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 212 | 212 | 212 | 215 | 210 | 210 | 205 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 209 | 200 | 211 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 5052000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4746300
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 27 | 29 | 29 | 29 | 652968
33 | Ashuganj 225 MW CCPP | 148 | 150 | 154 | 150 | 189 | 208 | 220 | 222 | 219 | 186 | 194 | 183 | 187 | 177 | 178 | 192 | 202 | 182 |  | 185 | 188 | 194 | 200 | 203 | 209 | 205 | 4533000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 270 | 270 | 300 | 300 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6777000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6941700
35 | Ashuganj 55 MW PP (Precision) | 37 | 37 | 37 | 37 | 5 | 5 | 5 | 5 | 10 | 10 | 15 | 15 | 20 | 20 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 367680
36 | Chandpur 150 MW CCPP | 137 | 136 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 137 | 137 | 137 | 136 | 137 | 137 | 136 |  | 136 | 137 | 137 | 137 | 137 | 140 | 140 | 3247660
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 290 | 290 | 300 | 300 | 300 | 290 | 280 | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6592300
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 104 | 104 | 104 | 105 | 107 | 112 | 113 | 109 | 74 | 73 | 73 | 73 | 71 | 72 | 100 | 99 | 104 | 105 |  | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 2270400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 6 | 10 | 14 | 15 | 35 | 35 | 16 | 23 | 10 | 5 | 1 | [8 empty] | 165130
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [13 empty] | 390000
46 | Shajibazar 330 MW CCPP | 269 | 269 | 268 | 267 | 268 | 270 | 270 | 266 | 266 | 269 | 270 | 270 | 265 | 271 | 271 | 267 | 271 | 269 |  | 270 | 267 | 263 | 271 | 272 | 270 | 270 | 6167000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 | 40 |  | 61 | 60 | 60 | 60 | 60 | 40 | 40 | 1327968
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 88 | 88 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2135040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 115 | 145 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 2887420
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 18 | 18 | 20 | 20 | 18 | 18 | 18 | 21 | 21 |  | 20 | 22 | 25 | 24 | 24 | 25 | 25 | 463320
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 208272
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 47 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1161000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 546288
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 290 | 295 | 290 | 295 | 310 | 270 | 275 | 280 | 310 | 290 | 305 | 270 | 300 | 270 | 280 | 270 |  | 300 | 265 | 270 | 280 | 290 | 270 | 290 | 7055000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 50 |  |  | 10 | 17 | 20 | 55 | 1111412
59 | Tangail Palli Power Gen 22 MW | 24 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 592320
60 | Barabkunda 22 MW PP (Regent) | [10 empty] | 0 | [15 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [7 empty] | 0 | 22 | 22 | 22 | 22 | 368064
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 404532
63 | Impoprt (Tripura) | 124 | 116 | 114 | 108 | 106 | 100 | 98 | 104 | 122 | 132 | 142 | 144 | 154 | 158 | 160 | 156 | 152 | 156 |  | 178 | 170 | 168 | 148 | 134 | 140 | 144 | 3264000
64 | Malancha, Ctg. EPZ (United) | 27 | 36 | 36 | 36 | 38 | 39 | 35 | 10 | 2 | 2 | 2 | 2 | 6 | 3 | 2 | 2 | 2 | 5 |  | 15 | 12 | 15 | 25 | 34 | 37 | 37 | 416640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | [7 empty] | 0 | 0 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 278640
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224820
67 | Jangalia 33MW PP (Summit) | [13 empty] | 21 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 250600
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 7 | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 14 | 14 | 14 |  | 14 | 14 | 10 | 10 | 14 | 14 | 12 | 320550
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 27 | 27 | 28 | 28 | 24 |  | 20 | 28 | 28 | 28 | 28 | 29 | 29 | 648000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 689700
72 | Rupganj 33 MW PP(Summit) | 26 | 26 | 28 | 28 | 25 | 16 | 16 | 16 | 33 | 25 | 25 | 16 | 16 | 25 | 25 | 26 | 17 | 8 |  | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 559200
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 94 | 94 | 96 | 94 | 91 | 92 | 92 | 93 | 93 | 91 | 91 | 91 | 90 | 91 | 90 |  | 91 | 91 | 91 | 91 | 91 | 92 | 94 | 2163045
| Feni Lanka Power | 99 | 99 | 53 | 34 | 17 | 17 | 17 | 52 | 52 | 52 | 72 | 72 | 80 | 80 | 85 | 98 | 51 | 51 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1690620
| Chowmuhani 113 MW | 110 | 108 | 109 | 105 | 105 | 105 | 106 | 105 | 105 | 101 | 101 | 103 | 106 | 105 | 105 | 105 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 117 | 108 | 2598960
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 140 | 54 | 54 | 54 | 54 | 64 |  | 126 | 145 | 145 | 138 | 54 | 54 | 54 | 2777760
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 2 | 7 | 7 | 12 | 60 | 85 | 91 | 94 | 96 | 96 | 98 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1306560
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 46 | 50 | 45 | 48 | 40 | 42 |  | 2 |  | 28 | 25 | 25 | 45 | 51 | 51 | 51 | 1075680
79 | Kodda 150MW PP | 100 | 64 | 48 | 32 | 32 | 32 | 32 | 32 | 82 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 115 | 82 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2545440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 34 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1018906
| Gazipur 100 MW PP | 105 | 105 | 105 | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 |  | 90 | 90 | 90 | 90 | 90 | 90 | 92 | 2124000
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 2 | 1 | 4 | 5 | 5 | 1 | 3 | 2 | 1 | [9 empty] | 27359
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1344973
| Karnaphuli Power Ltd. | 110 | 102 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 93 | 93 | 110 | 110 | 110 | 110 | 110 | 110 |  | 94 | 110 | 103 | 110 | 110 | 110 | 110 | 2607770
82 | Madanganj 102 PP(Summit) | [7 empty] | 5 | 30 | 24 | 35 | 67 | 80 | 79 | 77 | 77 | 65 | 65 |  | 65 | 65 | 60 | 30 | 30 | 30 | 3 | 856488
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 155 | 145 | 148 | 140 | 130 | 142 | 130 | 132 | 147 |  | 130 | 135 | 134 | 150 | 140 | 140 | 135 | 3419724
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 8 | 57 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 63 | 1248960
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 74 | 87 | 90 | 90 | 89 | 88 | 88 | 90 | 90 | 90 | 73 | 82 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2114880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 |  | 29 | 29 | 32 | 32 | 32 | 32 | 32 | 624384
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1036480
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 24 | 42 | 64 | 64 | 64 | 64 | 64 | 64 | 84 | 93 | 93 | 93 | 93 | 93 | 64 | 64 |  | 84 | 93 | 58 | 58 | 58 | 58 | 58 | 1772784
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | [5 empty] | 497760
96 | Chattogram 108 MW PP (ECPV) | 91 | 95 | 102 | 96 | 96 | 96 | 96 | 96 | 96 | 87 | 87 | 86 | 86 | 93 | 94 | 94 | 95 | 98 |  | 95 | 95 | 98 | 98 | 102 | 102 | 102 | 2294400
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 20 | 40 | 40 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 50 |  | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 929299
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 885185
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3739172
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | [8 empty] | 6300
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1170000
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 109 |  | 64 |  |  |  |  | 154 | 10 |  |  |  |  | 0 | 255486
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 25 |  |  |  |  | 50 | [5 empty] | 0 | 78911
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 195 | 195 | 195 | 184 | 183 | 184 | 194 | 192 | 192 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4692000
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 25 |  |  |  |  | 100 | [5 empty] | 0 | 115356
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 137 | 138 | 138 | 134 | 149 | 149 | 149 | 125 |  | 131 | 149 | 149 | 149 | 149 | 149 | 149 | 3512880
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 50 | 50 |  | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 2037120
116 | Chandpur 200MW (Desh energy) | 200 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 34 | 48 | 116 | 195 | 200 | 200 | 198 | 136 | 136 |  | 157 | 200 | 200 | 200 | 200 | 200 | 200 | 2942880
117 | Ashuganj 150MW PP (Midland) | 128 | 142 | 135 | 133 | 128 | 137 | 132 | 129 | 130 | 133 | 132 | 125 | 125 | 127 | 123 | 132 | 130 | 145 |  | 150 | 150 | 150 | 150 | 148 | 148 | 143 | 3238400
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 400 | 400 | 362 | 352 | 352 | 352 | 328 | 375 | 375 | 400 | 390 | 402 | 401 | 364 | 364 |  | 400 | 400 | 400 | 401 | 401 | 401 | 399 | 9261000
| Jamalpur 115 MW PP (United) | 48 | 48 | 48 | 48 | 28 | 48 | 48 | 48 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 57 | 105 |  | 107 | 105 | 106 | 97 | 107 | 107 | 78 | 1482000
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7048036
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 90 | 60 | 60 | 85 | 90 | 100 | 100 | 90 | 90 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2184000
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2693509
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 16 | 17 | 17 | 33 | 35 | 35 | 35 | 35 | 35 | 23 |  | 17 | 17 | 17 | 17 | 27 | 35 | 35 | 747360
| Spectra Solar Plant Ltd. | [7 empty] | 7 | 17 | 20 | 20 | 30 | 28 | 15 | 17 | 10 | 4 | 0 | [8 empty] | 164555
| Chandpur 115(Doreen) | 99 | 50 |  |  |  |  | 0 | 11 | 24 | 51 | 69 | 99 | 98 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1667520
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 45 | 55 | 55 |  | 55 | 12 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1265040
120 | Eastern Zone Total | 7828 | 7532 | 7104 | 6928 | 6979 | 6879 | 6957 | 6861 | 7151 | 7256 | 7553 | 7804 | 8193 | 7904 | 8187 | 7945 | 7595 | 7572 |  | 8692 | 8317 | 8231 | 8272 | 8228 | 8119 | 8003 | 185580376
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 14 | [11 empty] | 17 | 49 | 49 | 49 | 49 | 77 |  | 83 | 96 | 96 | 94 | 94 | 97 | 98 | 829440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 5 | 26 | 33 |  | 42 | 38 | 38 | 38 | 38 |  |  | 203040
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 125 | 150 | 205 | 180 | 140 | 140 |  | 180 | 213 | 180 | 180 | 170 | 120 | 120 | 3450240
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 70 | 70 |  | 95 | 94 | 95 | 95 | 95 | 95 | 95 | 2231040
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 32 | 41 | 62 | 79 | 95 | 95 | 61 | 20 | 41 | 14 | [9 empty] | 581040
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 209 | 222 | 222 | 220 | 185 | 221 | 221 | 211 | 154 | 170 | 205 | 105 | 205 | 214 | 200 | 181 | 154 |  | 214 | 214 | 223 | 220 | 220 | 220 | 220 | 4781700
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 679008
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 68 | 68 | 66 | 66 | 67 | 67 | 66 | 67 | 67 | 64 | 64 | 64 | 65 | 64 | 64 | 66 | 65 | 65 |  | 67 | 66 | 66 | 66 | 67 | 67 | 67 | 1579000
140 | Bhola 33 MW PP (Venture) | 40 | 35 | 34 | 33 | 28 | 28 | 25 | 26 | 26 | 26 | 28 | 23 | 25 | 26 | 27 | 27 | 26 | 31 |  | 35 | 36 | 36 | 36 | 36 | 38 | 37 | 719387
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 24 | 32 | 32 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 27225
143 | Gopalganj 100 MW Peaking PP | [22 empty] | 5 |  |  |  | 3712
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 12 | 15 | 15 | 15 | 15 | 15 |  | 75600
146 | Bheramara HVDC | 897 | 895 | 896 | 898 | 897 | 897 | 897 | 897 | 897 | 898 | 903 | 897 | 895 | 894 | 896 | 897 | 896 | 896 |  | 892 | 893 | 894 | 893 | 893 | 892 | 898 | 21693818
147 | Bheramara 410 MW CCPP | 285 | 285 | 285 | 285 | 280 | 275 | 272 | 265 | 245 | 235 | 230 | 225 | 220 | 210 | 205 | 215 | 235 | 260 |  | 280 | 285 | 285 | 300 | 305 | 315 | 320 | 6485184
148 | Payra 1320 MW | 580 | 570 | 550 | 520 | 500 | 470 | 440 | 400 | 400 | 380 | 390 | 400 | 420 | 450 | 480 | 480 | 450 | 450 |  | 490 | 600 | 610 | 600 | 600 | 570 | 550 | 12825200
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 80 | 80 | 80 | 78 | 80 | 82 | 83 | 79 | 78 | 80 | 77 |  | 78 | 80 | 81 | 81 | 80 | 79 | 79 | 1896872
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 200 | 200 | 199 | 199 | 200 | 199 | 4870900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 15 | 481952
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 2 | 2 | 4 | 1 | 1 | 0 | 1 | 1 | 0 | [8 empty] | 16980
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 174 | 177 | 169 | 170 | 198 | 205 | 170 |  | 186 | 210 | 214 | 214 | 214 | 214 | 214 | 4645727
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 135 | 181 | 201 | 210 | 151 | 140 |  | 151 | 195 | 195 | 180 | 157 | 135 | 130 | 3769300
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 118 | 134 | 143 | 161 | 168 | 167 | 164 | 163 | 151 | 138 | 147 | 147 | 146 | 140 | 152 | 177 | 189 | 160 |  | 188 | 215 | 215 | 215 | 213 | 215 | 215 | 4297773
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 333 | 333 | 343 | 344 | 344 | 344 | 344 | 343 | 344 | 288 | 288 | 287 | 287 | 200 | 0 | [11 empty] | 4586618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 5 | 15 | 43 | 44 | 45 |  | 45 | 45 | 45 | 45 | 45 | 0 |  | 346180
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252054
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | [14 empty] | 8 | 8 | 8 |  | 34 | 25 | 25 | 25 | 25 | 8 | 8 | 197511
167 | Katakhali 50 MW Peaking PP | [10 empty] | 5 | 16 | 16 | 16 | 21 | 24 | 24 | 27 |  | 32 | 32 | 32 | 32 | 32 | 32 | 12 | 290782
168 | Santahar 50 MW Peaking PP | 17 | [14 empty] | 37 | 36 | 36 |  | 36 | 38 | 36 | 36 | 36 | 36 | 36 | 340360
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 36 | 34 | 34 | 43 | 43 | 43 | 24 | 24 |  | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 739397
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 56 |  | 93 | 93 | 93 | 91 | 91 | 91 | 92 | 954400
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 40 | [5 empty] | 0 | 25530
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 96 | 113 | 113 | 94 | 94 | 102 | 113 | 94 | 94 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2524416
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 35 | 35 | 35 | 60 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 50 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2150016
173 | Rangpur 20 MW GTPP | [24 empty] | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 110 | 110 | 110 | 40 | 40 | 40 | 70 | 75 | 110 | 110 | 110 | 110 | 106 | 110 | 110 | 109 | 75 | 75 |  | 102 | 102 | 110 | 110 | 110 | 110 | 110 | 2311977
177 | Sympa Solar Power 8MW | [9 empty] | 1 |  | 2 | 5 | 5 | 4 | 3 | 1 | 0 | [8 empty] | 22905
178 | Energypac Power Venture Thakurgaon Ltd. | [6 empty] | 17 | 52 | 52 | 52 | 115 | 115 | 115 | 115 | 115 | 115 | 72 | 72 |  | 115 | 115 | 115 | 115 | 115 | 36 | 34 | 1587915
178