## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-31 | Thursday
|  |  | Date (day): | 2022-03-31 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13890.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14815 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-30 | 2022-03-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 141 | 210 | 210 | 210
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 200 | 200 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 99 | 99 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 38 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 125 | 150 | 150 |  | 185 | GT-2 Under maint.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 64 | 77 | 80 | 80
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 55 | 60 | 60 | 150 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 65 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 213 | 224 | 220 | 225 |  | 115 | ST under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 85 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 25 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 44 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 281 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 212 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 50 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 90 | 105 | 90 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 87 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 108 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 0 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 2525 | 3166 | 3401 | 3599 | 381 | 1893
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | 33 kV BPDB feeder problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 69 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 200 | 200
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 34 | 0 | 50 |  | 58 | On test
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 102 | 100 | 102
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1345 | 1523 | 1523 | 1565 | 81 | 605
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 194 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 300 | 300 | 60 |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 300 | 300 | 60 |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 43 | 43 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 150 | 142 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 32 | 42 |  | 10 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 137 | 0 | 90 |  | 73 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 60 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 156 | 170 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 34 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 15 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 98 | 98 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 102 | 103 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 98 | 99 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1719 | 2057 | 1991 | 2216 | 636 | 150
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 96 | 108 | 110 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 193 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 105 | 106 | 107
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 31 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 353 | 450 | 509.6 | 459 | 92 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 20 | 20 |  | 70 | Under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 270 | 269 | 270 | 270 | 60 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 29 | 32 | 30 | 30
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 66
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 77 | 150 | 220 | 220 | 11 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 21 | 25 | 20 | 20
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 401 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 50 |  | 333 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1487 | 1606 | 1694 | 1751 | 91 | 543
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 915 | 930 | 930
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 35 | 101 | 100 | 100
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 42 |  | 12 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 213 | 225 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 215 | 250 | 300 | 110 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 32 | 29 | 32 | 32
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 30 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 95 | 95 | 95 | 95 |  | 10 | Engine problem
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1616 | 1636 | 1782 | 1854 | 110 | 101
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 32 | 80
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 35 | 25 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 66 | 65 | 66 | 128 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 590 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 160 | 220 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 100
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 636 | 943 | 1002 | 1161 | 128 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 43 | 43 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 45 | 40 | 45 |  | 26 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 40 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 0 | 33 |  | 17 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 198 | 132 | 140 | 150 | 60 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 216 | 220 | 220 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 120 | 170 | 180 | 40 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 335 | 300 | 350 | 64 |  | Gas shortage
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 30 | 36 |  | 14 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 16 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 33 | 43 | 43 | 43 |  | 9 | Engine problem
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 92 | 90 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1330 | 1397 | 1472 | 1702 | 335 | 86
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 110 | 110 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 506 | 505 | 516 | 508 | 74 | 125
|  | Total |  |  |  |  | 22291 | 21215 | 11517 | 13283 | 13890.6 | 14815 | 1928 | 3511
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11023.8577 | 12714.24 | 13295.8234 | 14180.6418
| A. |  | 2022-03-30 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13283 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 10068 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13283 | MW
| 3 | Day peak Generation : |  |  | 11517 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12714.24 | MW
| 4 | Evening peak Generation : |  |  | 13283 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 280.1102 | MKWHr | By Solar | 1.0995 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 133.376 | MKWHr |  | By Oil: | 99.1608 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.2437 | MKWHr |  | By Hydro: | 1.6623 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1928 | MW | Dhaka | 4655.54 | 4655.54 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3511 | MW | Chittagong | 1294.5 | 1294.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5439 | MW | Khulna | 1624.8 | 1624.8 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1081.36 | MMCFD |  |  | Rajshahi | 1471.4 | 1471.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146945688.544 | ii) Oil : | Taka | 784663860.4 | Comilla | 1110 | 1110 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 92575459.43 | Total | Taka | 1024185008.374 | Mymensingh | 1034 | 1034 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.334 | MKWHr. | Sylhet | 385 | 385 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 58 | MW (E to W) at | 19:30 | hrs | Barisal | 365 | 365 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -134 | MW at | 1:00 | hrs | Rangpur | 774 | 774 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.1° C |  |  | Total | 12714.24 | 12714.24 |  | 0
| B. |  | 2022-03-31 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14815 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1315 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 284.6863 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10184 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0495 | MKWHr. | ii) HVDC Flow at Peak Time |  | 915 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5184 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.32 |  | (b) Today: | 85.08 |  | (c) Rule Curve: |  | 88.17
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 150 | 0 | 0 | 40 | 219 | 0 | 37 | 100 | 58 | 135 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 25 | 51 | 0 | 68 | 0 | 0 | 150 | 8 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 103 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 285 | 207 | 8 | 138 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 136 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 271 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 280 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 140 | 0 | 90 | 155 | 127 | 401 | 48 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 108 | 100 | 0 | 90 | 0 | 54 | 0 | 0 | 35 | 0 | 99 | 55 |  | 900 | 0 | 330 | 0 | 95 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 213 | 0 | 0 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 550 | 221 | 0 | 0 | 0 | 0 | 35 |  | 7727 | 3719 | 11446 | 4035 | 900 | 1536 | 0 | 3557 | 829 | 68 | 250 | 265 | 136 | 0 | 0 | 85.36
2:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 135 | 0 | 0 | 40 | 220 | 0 | 37 | 0 | 58 | 64 | 0 | 0 | 0 | 0 | 54 | 54 | 55 | 22 | 25 | 29 | 25 | 25 | 51 | 0 | 68 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 103 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 270 | 212 | 8 | 139 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 130 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 163 | 270 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 270 | 24 | 11 | 0 | 281 | 0 | 0 | 193 | 0 | 149 | 0 | 90 | 100 | 137 | 398 | 48 | 90 | 105 | 0 | 300 | 54 | 110 | 98 | 106 | 100 | 0 | 90 | 0 | 54 | 20 | 0 | 35 | 0 | 99 | 55 |  | 900 | 0 | 335 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 200 | 0 | 0 | 94 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 550 | 218 | 0 | 0 | 0 | 0 | 35 |  | 7469 | 3623 | 11092 | 3972 | 900 | 1510 | 0 | 3368 | 830 | 68 | 250 | 194 | 130 | 0 | 0 | 85.35
3:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 145 | 0 | 0 | 30 | 220 | 0 | 37 | 0 | 58 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 29 | 25 | 25 | 51 | 0 | 68 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 103 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 285 | 211 | 8 | 138 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 132 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 270 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 280 | 24 | 11 | 0 | 210 | 0 | 0 | 193 | 0 | 149 | 0 | 90 | 17 | 148 | 401 | 48 | 90 | 105 | 0 | 300 | 54 | 110 | 70 | 107 | 100 | 0 | 90 | 0 | 54 | 0 | 0 | 35 | 0 | 34 | 55 |  | 901 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 95 | 0 | 113 | 0 | 75 | 0 | 0 | 113 | 550 | 220 | 0 | 0 | 0 | 0 | 17 |  | 7134 | 3447 | 10581 | 3972 | 901 | 1468 | 0 | 2913 | 829 | 68 | 250 | 178 | 132 | 0 | 0 | 85.34
4:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 145 | 0 | 0 | 30 | 220 | 0 | 37 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 25 | 25 | 25 | 0 | 68 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 103 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 270 | 213 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 25 | 12 | 124 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 270 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 285 | 24 | 11 | 0 | 210 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 17 | 148 | 399 | 48 | 90 | 105 | 0 | 300 | 54 | 103 | 34 | 106 | 100 | 0 | 90 | 0 | 54 | 0 | 0 | 35 | 0 | 34 | 55 |  | 904 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 94 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 520 | 220 | 0 | 0 | 0 | 0 | 17 |  | 6977 | 3430 | 10407 | 3953 | 904 | 1476 | 0 | 2816 | 800 | 68 | 250 | 146 | 124 | 0 | 0 | 85.33
5:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 15 | 220 | 0 | 37 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 25 | 25 | 0 | 0 | 68 | 0 | 0 | 150 | 0 | 209 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 275 | 210 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 36 | 19 | 11 | 25 | 12 | 120 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 271 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 17 | 148 | 374 | 48 | 90 | 91 | 0 | 300 | 54 | 110 | 17 | 107 | 100 | 0 | 90 | 0 | 54 | 0 | 0 | 35 | 0 | 17 | 55 |  | 904 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 95 | 0 | 113 | 0 | 38 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 | 0 | 17 |  | 6772 | 3366 | 10138 | 3946 | 904 | 1467 | 0 | 2607 | 760 | 68 | 250 | 146 | 120 | 0 | 0 | 85.32
6:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 135 | 0 | 0 | 15 | 220 | 0 | 37 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 25 | 25 | 5 | 0 | 69 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 0 | 0 | 33 | 0 | 0 | 0 | 270 | 270 | 196 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 116 | 109 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 270 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 285 | 16 | 11 | 0 | 145 | 0 | 0 | 195 | 0 | 149 | 0 | 90 | 17 | 148 | 352 | 48 | 90 | 87 | 0 | 300 | 54 | 110 | 17 | 106 | 100 | 0 | 90 | 0 | 72 | 2 | 0 | 35 | 0 | 17 | 55 |  | 904 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 154 | 0 | 0 | 95 | 0 | 113 | 0 | 38 | 0 | 0 | 113 | 470 | 220 | 0 | 0 | 0 | 0 | 17 |  | 6733 | 3335 | 10068 | 3891 | 904 | 1440 | 0 | 2632 | 750 | 69 | 250 | 146 | 116 | 0 | 0 | 85.32
7:00 | 0 | 0 | 210 | 0 | 200 | 94 | 0 | 0 | 0 |  | 0 | 270 | 150 | 0 | 0 | 28 | 226 | 0 | 37 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 25 | 25 | 24 | 0 | 70 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 0 | 0 | 34 | 0 | 0 | 0 | 270 | 270 | 188 | 8 | 138 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 11 | 108 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 271 | 40 | 89 | 0 | 145 | 0 | 24 | 10 | 285 | 16 | 11 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 3 | 90 | 17 | 150 | 351 | 48 | 90 | 87 | 1 | 300 | 54 | 110 | 17 | 105 | 100 | 0 | 90 | 2 | 72 | 80 | 0 | 35 | 3 | 17 | 55 |  | 910 | 0 | 375 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 153 | 0 | 10 | 95 | 0 | 113 | 0 | 38 | 0 | 0 | 113 | 420 | 190 | 0 | 0 | 0 | 11 | 17 |  | 6866 | 3296 | 10162 | 3891 | 910 | 1448 | 0 | 2750 | 699 | 70 | 250 | 146 | 108 | 20 | 0 | 85.31
8:00 | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 |  | 0 | 270 | 140 | 7 | 10 | 40 | 224 | 0 | 38 | 6 | 58 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 0 | 25 | 25 | 32 | 0 | 70 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 180 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 124 | 108 | 0 | 20 | 0 | 30 | 0 | 53 | 32 | 110 | 268 | 40 | 89 | 0 | 130 | 0 | 23 | 10 | 290 | 16 | 5 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 7 | 90 | 17 | 150 | 352 | 48 | 90 | 87 | 1 | 300 | 54 | 110 | 34 | 106 | 100 | 0 | 90 | 11 | 72 | 94 | 0 | 35 | 7 | 17 | 55 |  | 913 | 0 | 380 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 0 | 95 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 400 | 191 | 0 | 0 | 0 | 33 | 88 |  | 6908 | 3441 | 10349 | 3827 | 913 | 1409 | 0 | 2987 | 678 | 70 | 250 | 162 | 124 | 59 | 0 | 85.3
9:00 | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 |  | 0 | 270 | 110 | 16 | 25 | 40 | 227 | 0 | 57 | 15 | 85 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 0 | 33 | 25 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 92 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 190 | 8 | 134 | 29 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 12 | 136 | 108 | 0 | 20 | 1 | 30 | 0 | 50 | 32 | 130 | 269 | 60 | 86 | 0 | 20 | 0 | 23 | 10 | 270 | 16 | 5 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 13 | 90 | 19 | 150 | 400 | 48 | 90 | 87 | 3 | 300 | 54 | 110 | 54 | 105 | 100 | 0 | 90 | 16 | 79 | 94 | 0 | 35 | 12 | 22 | 55 |  | 913 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 80 | 0 | 189 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 182 | 0 | 0 | 95 | 0 | 113 | 0 | 110 | 0 | 1 | 113 | 370 | 177 | 0 | 0 | 1 | 60 | 115 |  | 7049 | 3520 | 10569 | 3843 | 913 | 1359 | 0 | 3170 | 639 | 70 | 250 | 212 | 136 | 107 | 0 | 85.29
10:00 | 0 | 0 | 208 | 0 | 200 | 96 | 0 | 0 | 0 |  | 0 | 270 | 140 | 16 | 55 | 55 | 180 | 0 | 40 | 40 | 93 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 20 | 33 | 25 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 205 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 85 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 285 | 210 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 25 | 13 | 148 | 106 | 0 | 20 | 1 | 30 | 0 | 50 | 32 | 130 | 268 | 60 | 86 | 0 | 25 | 0 | 22 | 10 | 275 | 16 | 5 | 0 | 202 | 0 | 0 | 194 | 0 | 149 | 14 | 76 | 50 | 150 | 376 | 48 | 90 | 87 | 1 | 300 | 54 | 110 | 84 | 103 | 100 | 0 | 91 | 22 | 105 | 94 | 0 | 35 | 25 | 51 | 55 |  | 914 | 0 | 330 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 64 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 39 | 0 | 22 | 0 | 11 | 79 | 0 | 165 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 170 | 0 | 60 | 95 | 0 | 113 | 0 | 110 | 0 | 2 | 113 | 360 | 163 | 0 | 0 | 1 | 55 | 115 |  | 7331 | 3470 | 10801 | 3765 | 914 | 1437 | 0 | 3404 | 604 | 70 | 250 | 218 | 148 | 121 | 0 | 85.28
11:00 | 0 | 0 | 214 | 0 | 200 | 93 | 0 | 0 | 0 |  | 0 | 270 | 135 | 16 | 64 | 55 | 180 | 0 | 40 | 50 | 93 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 25 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 205 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 200 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 24 | 13 | 144 | 106 | 0 | 20 | 1 | 26 | 20 | 48 | 32 | 130 | 269 | 60 | 89 | 0 | 30 | 0 | 23 | 10 | 290 | 16 | 5 | 0 | 240 | 0 | 0 | 135 | 0 | 149 | 12 | 76 | 51 | 150 | 376 | 48 | 90 | 87 | 4 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 26 | 117 | 94 | 0 | 35 | 21 | 86 | 55 |  | 913 | 0 | 330 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 64 | 24 | 16 | 0 | 0 | 0 | 43 | 0 | 45 | 0 | 0 | 24 | 43 | 0 | 18 | 0 | 11 | 79 | 0 | 190 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 107 | 95 | 0 | 113 | 0 | 104 | 0 | 2 | 113 | 370 | 163 | 0 | 0 | 1 | 63 | 115 |  | 7460 | 3654 | 11114 | 3751 | 913 | 1490 | 0 | 3500 | 639 | 70 | 250 | 357 | 144 | 130 | 0 | 85.27
12:00 | 0 | 0 | 141 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 270 | 0 | 38 | 64 | 55 | 213 | 0 | 37 | 65 | 93 | 133 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 20 | 33 | 25 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 199 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 17 | 13 | 156 | 96 | 0 | 20 | 1 | 30 | 20 | 50 | 29 | 130 | 270 | 60 | 89 | 0 | 77 | 0 | 21 | 10 | 280 | 16 | 5 | 0 | 245 | 0 | 0 | 135 | 0 | 149 | 20 | 76 | 60 | 150 | 400 | 48 | 90 | 87 | 4 | 300 | 54 | 110 | 98 | 102 | 90 | 0 | 87 | 31 | 126 | 96 | 0 | 0 | 24 | 98 | 55 |  | 917 | 0 | 350 | 0 | 35 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 25 | 16 | 0 | 0 | 0 | 43 | 4 | 45 | 0 | 0 | 24 | 33 | 0 | 18 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 0 | 178 | 0 | 417 | 95 | 0 | 113 | 0 | 110 | 0 | 2 | 113 | 370 | 160 | 0 | 0 | 3 | 67 | 115 |  | 7429 | 4088 | 11517 | 3878 | 917 | 1656 | 0 | 3540 | 649 | 70 | 250 | 379 | 156 | 152 | 0 | 85.26
13:00 | 0 | 0 | 200 | 0 | 200 | 102 | 0 | 0 | 0 |  | 0 | 270 | 0 | 92 | 64 | 55 | 208 | 0 | 38 | 100 | 93 | 133 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 20 | 33 | 25 | 42 | 0 | 68 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 88 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 275 | 185 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 17 | 13 | 150 | 95 | 0 | 20 | 1 | 30 | 20 | 53 | 31 | 163 | 268 | 60 | 89 | 0 | 84 | 0 | 22 | 10 | 280 | 16 | 5 | 0 | 195 | 0 | 0 | 126 | 0 | 149 | 11 | 90 | 100 | 150 | 399 | 48 | 90 | 87 | 4 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 27 | 98 | 113 | 0 | 15 | 28 | 78 | 55 |  | 917 | 0 | 320 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 32 | 64 | 26 | 16 | 0 | 0 | 0 | 43 | 5 | 45 | 0 | 0 | 24 | 43 | 0 | 18 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 414 | 95 | 0 | 113 | 0 | 103 | 0 | 3 | 113 | 370 | 194 | 0 | 0 | 2 | 52 | 115 |  | 7557 | 4140 | 11697 | 3904 | 917 | 1734 | 0 | 3647 | 649 | 68 | 250 | 380 | 150 | 128 | 0 | 85.25
14:00 | 0 | 0 | 171 | 0 | 180 | 102 | 0 | 0 | 0 |  | 0 | 270 | 70 | 91 | 64 | 55 | 206 | 0 | 0 | 98 | 93 | 133 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 20 | 33 | 8 | 42 | 0 | 68 | 0 | 0 | 150 | 3 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 91 | 0 | 0 | 3 | 0 | 0 | 0 | 270 | 270 | 180 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 17 | 13 | 150 | 92 | 0 | 20 | 1 | 30 | 20 | 50 | 31 | 163 | 271 | 60 | 89 | 0 | 108 | 0 | 22 | 10 | 290 | 16 | 8 | 0 | 210 | 0 | 0 | 120 | 0 | 149 | 15 | 90 | 69 | 150 | 400 | 48 | 90 | 87 | 4 | 300 | 54 | 110 | 80 | 102 | 100 | 0 | 90 | 27 | 82 | 113 | 0 | 26 | 27 | 63 | 55 |  | 918 | 0 | 295 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 32 | 66 | 27 | 16 | 0 | 0 | 0 | 43 | 16 | 45 | 0 | 0 | 24 | 43 | 0 | 17 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 212 | 0 | 0 | 130 | 0 | 0 | 206 | 0 | 414 | 95 | 0 | 113 | 0 | 106 | 0 | 3 | 113 | 390 | 216 | 0 | 0 | 2 | 64 | 115 |  | 7481 | 4181 | 11662 | 3780 | 918 | 1830 | 0 | 3592 | 670 | 68 | 250 | 391 | 150 | 143 | 0 | 85.24
15:00 | 0 | 0 | 210 | 0 | 200 | 102 | 0 | 0 | 0 |  | 0 | 270 | 115 | 85 | 64 | 55 | 206 | 0 | 0 | 95 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 20 | 33 | 8 | 42 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 91 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 190 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 20 | 11 | 17 | 13 | 160 | 92 | 0 | 17 | 1 | 30 | 20 | 47 | 31 | 163 | 267 | 60 | 89 | 0 | 120 | 0 | 24 | 10 | 180 | 16 | 8 | 0 | 230 | 80 | 50 | 125 | 50 | 149 | 13 | 90 | 117 | 150 | 401 | 47 | 90 | 87 | 3 | 300 | 54 | 110 | 98 | 100 | 90 | 0 | 86 | 26 | 91 | 113 | 0 | 35 | 27 | 63 | 55 |  | 917 | 0 | 260 | 0 | 44 | 120 | 0 | 0 | 0 | 0 | 32 | 64 | 28 | 16 | 0 | 0 | 0 | 43 | 26 | 45 | 0 | 0 | 24 | 43 | 20 | 17 | 0 | 11 | 83 | 0 | 199 | 0 | 0 | 209 | 0 | 0 | 130 | 0 | 0 | 198 | 0 | 414 | 95 | 0 | 113 | 0 | 110 | 0 | 3 | 113 | 430 | 218 | 0 | 0 | 1 | 56 | 115 |  | 7815 | 4197 | 12012 | 3807 | 917 | 1766 | 180 | 3714 | 712 | 68 | 250 | 438 | 160 | 130 | 0 | 85.23
16:00 | 0 | 0 | 210 | 0 | 200 | 98 | 0 | 0 | 0 |  | 0 | 270 | 135 | 90 | 64 | 55 | 211 | 0 | 60 | 98 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 44 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 16 | 0 | 0 | 91 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 202 | 8 | 138 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 20 | 11 | 25 | 13 | 156 | 98 | 0 | 17 | 1 | 30 | 20 | 50 | 31 | 163 | 269 | 60 | 89 | 0 | 136 | 0 | 25 | 10 | 240 | 16 | 8 | 0 | 230 | 0 | 0 | 115 | 0 | 149 | 7 | 76 | 180 | 145 | 401 | 47 | 90 | 87 | 3 | 300 | 54 | 110 | 98 | 89 | 90 | 0 | 76 | 12 | 90 | 113 | 0 | 35 | 28 | 99 | 55 |  | 916 | 0 | 240 | 0 | 15 | 120 | 0 | 0 | 0 | 0 | 8 | 63 | 29 | 16 | 0 | 0 | 0 | 43 | 35 | 45 | 0 | 0 | 24 | 16 | 35 | 17 | 0 | 11 | 83 | 0 | 199 | 0 | 0 | 202 | 0 | 0 | 130 | 0 | 0 | 177 | 0 | 414 | 95 | 0 | 110 | 0 | 70 | 0 | 3 | 50 | 430 | 219 | 0 | 0 | 1 | 24 | 34 |  | 7893 | 3874 | 11767 | 3885 | 916 | 1848 | 0 | 3505 | 712 | 68 | 250 | 478 | 156 | 79 | 0 | 85.22
17:00 | 0 | 0 | 210 | 0 | 200 | 98 | 0 | 0 | 0 |  | 0 | 270 | 135 | 94 | 64 | 45 | 212 | 0 | 60 | 95 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 44 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 31 | 0 | 0 | 98 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 203 | 8 | 138 | 27 | 5 | 0 | 43 | 0 | 30 | 29 | 21 | 11 | 25 | 14 | 152 | 98 | 0 | 17 | 0 | 30 | 20 | 50 | 31 | 110 | 268 | 40 | 89 | 0 | 136 | 0 | 25 | 10 | 290 | 16 | 8 | 0 | 230 | 0 | 0 | 115 | 0 | 132 | 2 | 90 | 180 | 142 | 354 | 47 | 91 | 87 | 1 | 300 | 54 | 110 | 98 | 84 | 90 | 0 | 86 | 10 | 90 | 113 | 0 | 35 | 22 | 99 | 55 |  | 917 | 0 | 220 | 0 | 16 | 120 | 0 | 0 | 2 | 0 | 8 | 63 | 26 | 16 | 0 | 0 | 0 | 43 | 42 | 45 | 0 | 0 | 24 | 16 | 35 | 20 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 153 | 0 | 354 | 95 | 0 | 113 | 0 | 54 | 0 | 2 | 50 | 430 | 184 | 0 | 0 | 0 | 16 | 34 |  | 7861 | 3696 | 11557 | 3748 | 917 | 1750 | 0 | 3505 | 712 | 68 | 250 | 532 | 152 | 53 | 0 | 85.21
18:00 | 0 | 0 | 210 | 0 | 200 | 60 | 0 | 0 | 0 |  | 0 | 270 | 120 | 100 | 64 | 55 | 170 | 0 | 35 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 44 | 0 | 68 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 0 | 0 | 270 | 270 | 204 | 8 | 136 | 29 | 5 | 0 | 43 | 0 | 40 | 29 | 21 | 11 | 25 | 14 | 152 | 106 | 0 | 20 | 0 | 30 | 20 | 17 | 31 | 110 | 270 | 40 | 89 | 0 | 143 | 0 | 25 | 10 | 270 | 16 | 11 | 0 | 238 | 0 | 0 | 155 | 0 | 143 | 0 | 90 | 200 | 138 | 329 | 102 | 91 | 87 | 0 | 300 | 54 | 110 | 98 | 95 | 100 | 0 | 90 | 1 | 96 | 113 | 0 | 24 | 0 | 99 | 55 |  | 916 | 0 | 215 | 0 | 16 | 120 | 0 | 0 | 29 | 10 | 8 | 66 | 32 | 16 | 0 | 0 | 0 | 43 | 42 | 59 | 0 | 8 | 24 | 16 | 35 | 20 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 162 | 0 | 0 | 130 | 0 | 0 | 140 | 0 | 351 | 95 | 0 | 113 | 0 | 54 | 0 | 0 | 50 | 420 | 142 | 0 | 0 | 0 | 1 | 34 |  | 7831 | 3659 | 11490 | 3652 | 916 | 1608 | 0 | 3675 | 701 | 68 | 250 | 596 | 152 | 2 | 0 | 85.2
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 205 | 0 | 200 | 100 | 0 | 0 | 0 |  | 0 | 270 | 135 | 100 | 77 | 55 | 222 | 0 | 57 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 0 | 48 | 0 | 69 | 0 | 0 | 150 | 25 | 206 | 0 | 0 | 0 |  | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 20 | 0 | 0 | 0 | 270 | 270 | 180 | 8 | 137 | 29 | 5 | 0 | 51 | 0 | 40 | 34 | 21 | 11 | 25 | 15 | 172 | 105 | 0 | 20 | 0 | 30 | 20 | 50 | 32 | 163 | 269 | 60 | 89 | 0 | 150 | 0 | 25 | 10 | 290 | 16 | 11 | 100 | 281 | 220 | 50 | 182 | 100 | 149 | 0 | 90 | 200 | 142 | 401 | 105 | 105 | 95 | 0 | 300 | 54 | 110 | 98 | 102 | 100 | 0 | 90 | 0 | 108 | 113 | 0 | 17 | 0 | 99 | 0 |  | 915 | 0 | 210 | 0 | 70 | 190 | 0 | 0 | 40 | 5 | 32 | 65 | 35 | 32 | 0 | 0 | 0 | 43 | 42 | 92 | 0 | 50 | 31 | 43 | 36 | 0 | 0 | 11 | 84 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 161 | 0 | 2 | 127 | 0 | 335 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 500 | 221 | 0 | 0 | 0 | 0 | 115 |  | 8756 | 4263 | 13019 | 3718 | 915 | 1839 | 472 | 4135 | 784 | 69 | 351 | 725 | 172 | 0 | 0 | 85.17
19:30 | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 |  | 0 | 270 | 125 | 100 | 77 | 55 | 224 | 0 | 55 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 25 | 44 | 0 | 69 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 17 | 0 | 0 | 0 | 270 | 270 | 194 | 8 | 137 | 29 | 5 | 0 | 51 | 0 | 40 | 34 | 21 | 11 | 25 | 15 | 170 | 108 | 0 | 20 | 0 | 30 | 20 | 50 | 32 | 163 | 269 | 60 | 89 | 0 | 150 | 0 | 25 | 10 | 280 | 16 | 11 | 100 | 281 | 212 | 50 | 193 | 100 | 149 | 0 | 90 | 200 | 142 | 401 | 105 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 0 |  | 915 | 0 | 215 | 0 | 101 | 213 | 0 | 0 | 38 | 0 | 29 | 66 | 35 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 43 | 36 | 16 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 216 | 0 | 30 | 120 | 0 | 335 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 590 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8802 | 4481 | 13283 | 3748 | 915 | 1830 | 492 | 4199 | 870 | 69 | 429 | 777 | 170 | 0 | 0 | 0
20:00 | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 |  | 0 | 270 | 130 | 100 | 77 | 55 | 223 | 0 | 57 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 0 | 44 | 0 | 69 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 20 | 0 | 0 | 0 | 270 | 270 | 197 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 42 | 34 | 21 | 11 | 25 | 15 | 164 | 107 | 0 | 20 | 0 | 30 | 20 | 54 | 32 | 163 | 269 | 60 | 89 | 0 | 155 | 0 | 25 | 10 | 290 | 16 | 11 | 100 | 281 | 207 | 50 | 193 | 100 | 149 | 0 | 90 | 200 | 145 | 400 | 105 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 104 | 100 | 0 | 91 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 0 |  | 915 | 0 | 215 | 0 | 109 | 213 | 0 | 0 | 38 | 0 | 32 | 66 | 37 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 43 | 35 | 18 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 216 | 0 | 0 | 120 | 0 | 341 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 610 | 223 | 0 | 0 | 0 | 0 | 115 |  | 8665 | 4496 | 13161 | 3593 | 915 | 1865 | 457 | 4215 | 892 | 69 | 429 | 778 | 164 | 0 | 0 | 85.18
21:00 | 0 | 0 | 210 | 0 | 200 | 100 | 0 | 0 | 0 |  | 0 | 270 | 140 | 100 | 78 | 55 | 221 | 0 | 57 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 0 | 33 | 25 | 44 | 0 | 69 | 0 | 0 | 150 | 25 | 208 | 0 | 0 | 0 |  | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 24 | 0 | 0 | 0 | 290 | 290 | 205 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 41 | 34 | 21 | 11 | 25 | 15 | 160 | 107 | 0 | 20 | 0 | 30 | 20 | 53 | 32 | 163 | 269 | 60 | 89 | 0 | 163 | 0 | 25 | 10 | 285 | 17 | 11 | 30 | 281 | 80 | 50 | 194 | 70 | 149 | 0 | 90 | 200 | 145 | 401 | 107 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 0 |  | 916 | 0 | 215 | 0 | 111 | 215 | 0 | 0 | 38 | 0 | 32 | 66 | 38 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 52 | 35 | 22 | 0 | 11 | 83 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 218 | 0 | 0 | 120 | 0 | 340 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 620 | 222 | 0 | 0 | 0 | 0 | 115 |  | 8492 | 4536 | 13028 | 3689 | 916 | 1877 | 230 | 4190 | 903 | 69 | 433 | 779 | 160 | 0 | 0 | 85.17
22:00 | 0 | 0 | 210 | 0 | 200 | 100 | 0 | 0 | 0 |  | 0 | 270 | 125 | 100 | 79 | 55 | 219 | 0 | 57 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 0 | 33 | 25 | 51 | 0 | 69 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 33 | 0 | 0 | 0 | 270 | 270 | 210 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 42 | 34 | 21 | 11 | 25 | 15 | 162 | 107 | 0 | 20 | 0 | 30 | 20 | 53 | 32 | 163 | 271 | 60 | 86 | 0 | 163 | 0 | 24 | 10 | 300 | 19 | 11 | 0 | 281 | 0 | 50 | 194 | 30 | 149 | 0 | 90 | 200 | 147 | 400 | 107 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 0 |  | 916 | 0 | 215 | 0 | 111 | 215 | 0 | 0 | 38 | 0 | 32 | 66 | 39 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 218 | 0 | 0 | 120 | 0 | 340 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 222 | 0 | 0 | 0 | 0 | 115 |  | 8321 | 4540 | 12861 | 3655 | 916 | 1883 | 80 | 4200 | 901 | 69 | 433 | 780 | 162 | 0 | 0 | 85.16
23:00 | 0 | 0 | 210 | 0 | 200 | 101 | 0 | 0 | 0 |  | 0 | 270 | 130 | 100 | 79 | 55 | 219 | 0 | 56 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 30 | 22 | 25 | 9 | 33 | 25 | 51 | 0 | 71 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 31 | 51 | 0 | 103 | 0 | 0 | 36 | 0 | 0 | 0 | 270 | 270 | 212 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 42 | 34 | 21 | 11 | 25 | 15 | 160 | 109 | 0 | 20 | 0 | 30 | 20 | 53 | 32 | 163 | 270 | 60 | 86 | 0 | 163 | 0 | 25 | 10 | 270 | 20 | 11 | 0 | 281 | 0 | 0 | 194 | 0 | 149 | 0 | 90 | 200 | 142 | 400 | 107 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 104 | 100 | 0 | 90 | 0 | 108 | 112 | 0 | 35 | 0 | 99 | 0 |  | 916 | 0 | 215 | 0 | 112 | 120 | 0 | 0 | 38 | 0 | 32 | 67 | 38 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 166 | 0 | 0 | 118 | 0 | 340 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 215 | 0 | 0 | 0 | 0 | 115 |  | 8239 | 4386 | 12625 | 3666 | 916 | 1855 | 0 | 4210 | 902 | 71 | 286 | 725 | 160 | 0 | 0 | 85.15
24:00 | 0 | 0 | 210 | 0 | 200 | 100 | 0 | 0 | 0 |  | 0 | 270 | 132 | 72 | 0 | 55 | 218 | 0 | 59 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 9 | 33 | 25 | 51 | 0 | 71 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 103 | 0 | 0 | 37 | 0 | 0 | 0 | 270 | 270 | 217 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 42 | 40 | 21 | 11 | 25 | 15 | 154 | 109 | 0 | 20 | 0 | 30 | 20 | 53 | 32 | 163 | 271 | 60 | 86 | 0 | 162 | 0 | 24 | 10 | 270 | 21 | 11 | 0 | 281 | 0 | 0 | 194 | 0 | 149 | 0 | 90 | 200 | 147 | 400 | 77 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 0 | 108 | 0 | 0 | 35 | 0 | 99 | 0 |  | 898 | 0 | 210 | 0 | 83 | 120 | 0 | 0 | 38 | 0 | 16 | 66 | 38 | 32 | 0 | 0 | 0 | 43 | 44 | 92 | 0 | 0 | 32 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 0 | 118 | 0 | 330 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 622 | 220 | 0 | 0 | 0 | 0 | 115 |  | 7977 | 4224 | 12201 | 3668 | 898 | 1851 | 0 | 3881 | 901 | 71 | 250 | 657 | 154 | 0 | 0 | 85.14
KWH | 0 | 0 | 4882000 | 0 | 4795500 | 2236227 | 0 | 0 | 0 |  | 0 | 6389600 | 2937309 | 1261440 | 1084536 | 1127285 | 5161620 | 0 | 1134000 | 1541760 | 1874016 | 2532000 | 0 | 0 | 0 | 0 | 978120 | 914186 | 1208713 | 416556 | 600000 | 350820 | 737640 | 524100 | 987840 | 0 | 1662349 | 0 | 0 | 3700000 | 273749 | 4866079 | 0 | 0 | 0 |  | 586800 | 244848 | 292672 | 0 | 2333760 | 0 | 0 | 462240 | 0 | 0 | 0 | 6932000 | 6743000 | 4829000 | 217454 | 2684610 | 939792 | 144000 | 0 | 1090459 | 0 | 294656 | 903691 | 460116 | 235980 | 584500 | 316440 | 3518400 | 2460480 | 0 | 1327140 | 8100 | 714000 | 315000 | 1193400 | 752400 | 3502063 | 6185000 | 1246464 | 2130240 | 0 | 2919080 | 0 | 555940 | 250740 | 6833500 | 437928 | 218256 | 210048 | 5600289 | 578541 | 239150 | 4101600 | 364232 | 3588910 | 120150 | 2060160 | 2712000 | 3470909 | 9305000 | 1480800 | 2288400 | 2286618 | 26881 | 7083164 | 1344968 | 2665479 | 1836540 | 2469600 | 2403840 | 0 | 2147520 | 197200 | 2122560 | 2066236 | 0 | 815760 | 186220 | 1776000 | 1022400 |  | 22049454 | 0 | 7263360 | 0 | 1010880 | 3353280 | 0 | 0 | 226080 | 9088 | 34725 | 1571000 | 712749 | 484416 | 0 | 0 | 0 | 568544 | 409449 | 893880 | 0 | 267768 | 337480 | 736296 | 345390 | 449280 | 0 | 240462 | 1926981 | 0 | 4791700 | 0 | 0 | 4655690 | 0 | 0 | 3672218 | 0 | 20160 | 4129836 | 0 | 4758909 | 2248800 | 0 | 2732640 | 0 | 2175590 | 0 | 26056 | 2574240 | 12525000 | 4877045 | 0 | 0 | 20100 | 514800 | 1884099 |  | 185612769 | 94497445 | 280110214 | 93882449 | 22049454 | 39493555 | 1412131 | 84569103 | 19243681 | 1662349 | 7025498 | 6154087 | 3518400 | 1099507 | 0
Fuel Cost | 0 | 0 | 7127720 | 0 | 5323005 | 2951819.64 | 0 | 0 | 0 |  | 0 | 6964664 | 3260412.99 | 9574329.6 | 7472453.04 | 9536831.1 | 5368084.8 | 0 | 1961820 | 11609452.8 | 17091025.92 | 24914880 | 0 | 0 | 0 | 0 | 7140276 | 7066657.78 | 11917910.18 | 312417 | 450000 | 0 | 0 | 0 | 9552412.8 | 0 | 448834.23 | 0 | 0 | 6697000 | 2543128.21 | 5304026.11 | 0 | 0 | 0 |  | 0 | 2367680.16 | 2838918.4 | 0 | 20303712 | 0 | 0 | 1372852.8 | 0 | 0 | 0 | 5129680 | 6743000 | 4442680 | 280515.66 | 3087301.5 | 1061964.96 | 201600 | 0 | 1864684.89 | 0 | 2976025.6 | 8630249.05 | 584347.32 | 176985 | 1022875 | 237330 | 26388000 | 2608108.8 | 0 | 1685467.8 | 129114 | 1170960 | 504000 | 2124252 | 1173744 | 3992351.82 | 6432400 | 2455534.08 | 4068758.4 | 0 | 5050008.4 | 0 | 650449.8 | 511509.6 | 6901835 | 328446 | 165874.56 | 3572916.48 | 42338184.84 | 9823626.18 | 3998588 | 21328320 | 6089959.04 | 35314874.4 | 1404553.5 | 16790304 | 29425200 | 24469908.45 | 8653650 | 13504896 | 21625380 | 19916442.78 | 0 | 53548719.84 | 11714671.28 | 23429560.41 | 18328669.2 | 21164472 | 16009574.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127004855.04 | 0 | 7626528 | 0 | 7945516.8 | 46476460.8 | 0 | 0 | 2371579.2 | 95242.24 | 361834.5 | 1775230 | 1104760.95 | 4727900.16 | 0 | 0 | 0 | 5594472.96 | 4160001.84 | 7910838 | 0 | 3620223.36 | 3270181.2 | 7134708.24 | 3350283 | 862617.6 | 0 | 182029.734 | 11619695.43 | 0 | 25971014 | 0 | 0 | 5447157.3 | 0 | 0 | 54055048.96 | 0 | 342921.6 | 4831908.12 | 0 | 4711319.91 | 23477472 | 0 | 25932753.6 | 0 | 16882578.4 | 0 | 287918.8 | 19023633.6 | 54984750 | 0 | 0 | 0 | 0 | 0 | 0 |  | 696704848.6 | 483143435.344 | 1179848283.944 | 103947539.484 | 127004855.04 | 42998149.06 | 23828011.3 | 600454236.74 | 92575459.43 | 448834.23 | 100531509.76 | 59850102.6 | 26388000 | 1821586.3 | 0
Yesterday Day Peak | 0 | 0 | 141 | 0 | 250 | 99 | 0 | 0 | 0 |  | 0 | 270 | 0 | 38 | 64 | 55 | 213 | 0 | 37 | 65 | 93 | 133 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 20 | 33 | 25 | 42 | 0 | 70 | 0 | 0 | 150 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 0 | 0 | 2 | 0 | 0 | 0 | 270 | 270 | 199 | 8 | 137 | 29 | 5 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 17 | 13 | 156 | 96 | 0 | 20 | 1 | 30 | 20 | 50 | 29 | 130 | 270 | 60 | 89 | 0 | 77 | 0 | 21 | 10 | 280 | 16 | 5 | 0 | 245 | 0 | 0 | 135 | 0 | 149 | 20 | 76 | 60 | 150 | 400 | 48 | 90 | 87 | 4 | 300 | 54 | 110 | 98 | 102 | 90 | 0 | 87 | 31 | 126 | 96 | 0 | 0 | 24 | 98 | 55 |  | 917 | 0 | 350 | 0 | 35 | 120 | 0 | 0 | 0 | 0 | 32 | 65 | 25 | 16 | 0 | 0 | 0 | 43 | 4 | 45 | 0 | 0 | 24 | 33 | 0 | 18 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 0 | 178 | 0 | 417 | 95 | 0 | 113 | 0 | 110 | 0 | 2 | 113 | 370 | 160 | 0 | 0 | 3 | 67 | 115 |  | 11517 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 0 | 200 | 99 | 0 | 0 | 0 | 0 | 0 | 270 | 125 | 100 | 77 | 55 | 224 | 0 | 55 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 25 | 44 | 0 | 69 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 34 | 51 | 0 | 102 | 0 | 0 | 17 | 0 | 0 | 0 | 270 | 270 | 194 | 8 | 137 | 29 | 5 | 0 | 51 | 0 | 40 | 34 | 21 | 11 | 25 | 15 | 170 | 108 | 0 | 20 | 0 | 30 | 20 | 50 | 32 | 163 | 269 | 60 | 89 | 0 | 150 | 0 | 25 | 10 | 280 | 16 | 11 | 100 | 281 | 212 | 50 | 193 | 100 | 149 | 0 | 90 | 200 | 142 | 401 | 105 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 103 | 100 | 0 | 90 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 0 |  | 915 | 0 | 215 | 0 | 101 | 213 | 0 | 0 | 38 | 0 | 29 | 66 | 35 | 32 | 0 | 0 | 0 | 43 | 45 | 92 | 0 | 50 | 32 | 43 | 36 | 16 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 216 | 0 | 30 | 120 | 0 | 335 | 95 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 590 | 220 | 0 | 0 | 0 | 0 | 115 |  | 13283 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 0 | 300 | 105 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 100 | 80 | 55 | 225 | 0 | 60 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 200 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 0 | 102 | 25 | 0 | 20 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 90 | 29 | 5 | 0 | 43 | 0 | 42 | 43 | 19 | 11 | 25 | 22 | 163 | 110 | 0 | 20 | 0 | 30 | 20 | 51 | 30 | 163 | 270 | 66 | 86 | 0 | 220 | 0 | 20 | 10 | 300 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 107 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 50 | 90 | 0 | 144 | 113 | 0 | 35 |  | 100 | 55 |  | 930 | 0 | 300 | 0 | 100 | 225 | 0 | 0 | 42 | 30 | 32 | 66 | 35 | 80 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 50 | 33 | 43 | 36 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 100 | 180 | 0 | 350 | 95 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 660 | 220 |  | 100 |  |  | 115
Forecast for Day | 0 | 0 | 210 | 0 | 200 | 105 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 100 | 80 | 55 | 220 | 0 | 60 | 100 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 150 | 25 | 200 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 100 | 25 | 0 | 5 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 32 | 43 | 19 | 11 | 25 | 22 | 138 | 110 | 0 | 20 | 1.6 | 30 | 20 | 50 | 30 | 163 | 270 | 60 | 86 | 0 | 220 | 0 | 20 | 10 | 300 | 24 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 106 | 90 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 |  | 90 | 50 | 144 | 113 | 0 | 35 | 30 | 100 | 55 |  | 930 | 0 | 250 | 0 | 100 | 225 | 0 | 0 | 0 | 0 | 32 | 65 | 25 | 32 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 40 | 0 | 43 | 30 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 220 | 0 | 100 | 170 | 0 | 300 | 95 | 100 | 113 | 0 | 113 | 0 | 8 | 113 | 660 | 220 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 210 | 0 | 200 | 105 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 30 | 40 | 180 | 0 | 61 | 0 | 84 | 62 | 0 | 0 | 0 | 0 | 35 | 5 | 35 | 22 | 25 | 23 | 33 | 33 | 33 | 0 | 70 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 270 | 222 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 25 | 15 | 130 | 119 | 0 | 20 | 0 | 30 | 20 | 14 | 5 | 110 | 273 | 40 | 86 | 0 | 215 | 0 | 12 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 184 | 0 | 149 | 8 | 90 | 17 | 141 | 364 | 48 | 60 | 105 | 2 | 300 | 54 | 110 | 70 | 103 | 50 | 0 | 55 | 12 | 108 | 113 | 0 | 35 | 8 | 35 | 0 | 0 | 917 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 130 | 0 | 0 | 118 | 0 | 305 | 95 | 0 | 113 | 0 | 98 | 0 | 1 | 113 | 450 | 175 | 0 | 0 | 1 | 32 | 115 | 0 |  |  |  |  | 99160819 |  | 0
99160819
| Minimum Generation |  | 10068 | 6:00
| Highest Generation |  | 13283 | 19:30
| Day Peak Generation |  | 11517 | 12:00
| Evening Peak Generation |  | 13283 | 19:30
| HVDC Max Flow |  | 918 | 14:00
| HVDC EvPeak Flow |  | 915 | 19:30
| Load factor L.F |  | 87.87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-31
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11517 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10184 | MW
Evening Peak Generation : |  | 13283 | MW Hour : | 19:30 | Available Max Generation : |  | 14815 | MW
E.P. Demand (at gen end) : |  | 13283 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13283 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1315 | MW
Total Gen. (MKWH) : |  | 280.1102 | System Load Factor : | 87.87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -134 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-31
Actual : | 85.08 | Ft.(MSL) , | Rule curve : | 88.17 | Ft.( MSL )
Gas Consumed : | Total = | 1081.36 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146945688.544
: |  | Coal : | 92575459.43 | Oil : | 784663860.4 | Total : | 1024185008.374
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4799.6067 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1638.3065 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1468.9686 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1327.7276 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1199.6329 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 968.0768 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 533.3552 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 249.0435 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 746.6669 |  |  | 0 | 0%
Total | 0 |  | 12931.3847 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1
6) Bibiyana South
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Jashore-Benapole 132 kV Ckt-2 was under shut down from 07:58 to 16:11 for C/M.
b) Rampura-Bashundhara 132 kV Ckt-1 tripped at 09:37 from both end showing Dist. Z1, R-phase relays
and was switched on at 10:21.
c) Polashbari-Mohasthangarh 132 kV Ckt-1 was under shut down from 08:31 to 16:22 for C/M.
d) Kulshi 132 kV boy of Rampur was switched on at 12:12.
e) Halishahar 132 kV boy of Rampur was switched on at 12:14.
f) Sirajganj unit-4 GT was synchronized at 09:30.
g) Sirajganj unit-4 ST was synchronized at 10:53.
h) Sylhet CCPP ST was synchronized at 11:06.
i) Summit Meghnaghat GT-1 & ST tripped at 11:45 due to tripping of GBC and GT-1 was synchronized
at 13:37
j) Siddhirganj GT-1 tripped at 13:39 due to problem of control system.
k) Chandpur 150 MW CCPP GT tripped 19:32.
l) Halishar 132 kV main bus was shut down at 05:55 for C/M. | [5 empty] | About 55 MW power interruption occurred under
Halishar S/S area from 05:55(31-03-2022) to till.
m) Mymensing 33 kV bus sec of T2 transformer was shut down at 06:15(30-03-2022) to 08:06 for C/M. | [5 empty] | About 60 MW power interruption occurred under
Mymensing S/S area from 06:15 to 08:06.
n) Kodda-Kabirpur 132 kV Ckt-1 was under shut down since 07:15(31-03-2022) for D/W.
o) Sylhet-Fenchuganj 132 kV Ckt was under shut down since 07:14(31-03-2022) for D/W. | [5 empty] | About 35 MW power interruption occurred under
Sylhet S/S area from 07:14 to till
p) Ghorasal-Ashuganj(S) 230 kV Ckt-1 tripped at 05:52(31-03-2022) showing Dist. Z1 relays at Ghorasal
end & Dist. Z1, A-phase relays.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4882000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4795500 | ST under maint
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2236227
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6389600 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 100 | 1261440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 2937309 | GT-2 Under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 77 | 1084536 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1127285
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 416556
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 55 | 1134000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 100 | 1541760
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 224 | 5161620 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1874016 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 978120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2532000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 914186
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1208713
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 950820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 737640
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 524100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 44 | 987840 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 5600289 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 212 | 578541 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 239150 | Low demand.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 364232
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3588910
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2288400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2147520 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 2122560 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186220
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 1022400 | Engine problem
| Dhaka area Total |  |  |  | 5696 | 3166 | 61813490
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 273749
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120150
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 69 | 1662349 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4866079
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2286618
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 244848 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 292672 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2060160 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 462240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 102 | 2333760
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26881
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 7083164
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1344968
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2665479
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2403840 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2066236
| Chattogram area Total |  |  |  | 2382 | 1523 | 33893193
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 4829000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 6932000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6743000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 939792 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 144000 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1090459
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 3470909
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 294656 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 2684610 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2712000
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 460116
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3518400
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 584500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 903691 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 316440 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 210048 | Low demand.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1836540 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 103 | 2469600 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 815760 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 1776000 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2057 | 43184955
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 108 | 2460480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 1327140
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 193 | 4101600
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1480800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 197200
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 586800
| Mymensingh Area Total |  |  |  | 622 | 450 | 10162120
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 714000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 315000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3502063
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 269 | 6185000 | Machine problem
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1193400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 32 | 752400
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 218256
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1246464
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2130240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 2919080 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 25 | 555940
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 437928
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6833500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9305000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250740
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1606 | 36559011
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 915 | 22049454
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 101 | 1010880 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 226080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 213 | 3353280
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9088 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 7263360 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 29 | 34725
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 30 | 20160 | Low demand.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 2248800 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514800
| Khulna Area Total |  |  |  | 2229 | 1636 | 36730627
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 484416 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 35 | 712749
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 66 | 1571000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 12525000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4877045
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 943 | 20170210
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 568544 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 45 | 409449 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 267768
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 337480 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 132 | 4655690 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 216 | 3672218 | Running on HSD
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 120 | 4129836 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 335 | 4758909 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 345390 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 16 | 449280
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240462
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 736296 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 893880 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2732640
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2574240
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20100
| Rajshahi Area Total |  |  |  | 2129 | 1397 | 26792182
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1926981
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4791700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 2175590
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26056
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1884099
| Rangpur Area Total |  |  |  | 720 | 505 | 10804426
| Total |  |  |  | 21215 | 13283 | 280110214
| Eastern Grid Total |  |  |  | 14091 | 8802 | 185612769
| Western Grid Total |  |  |  | 7124 | 4481 | 94497445
| National Grid Total |  |  |  | 21215 | 13283 | 280110214
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-30
(a) ENTIRE EASTERN GRID : |  | 8479.04 | MW | (b) ENTIRE WESTERN GRID : |  | 4235.2 | MW
i) Dhaka area |  | 4655.54 | MW | i) Khulna area |  | 1624.8 | MW
ii) Chittagong area |  | 1294.5 | MW | ii) Rajshahi area |  | 1471.4 | MW
iii) Comilla area |  | 1110 | MW | iii) Barisal area |  | 365 | MW
iv) Mymensingh area |  | 1034 | MW | iv) Rangpur area |  | 774 | MW
v) Sylhet area |  | 385 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12714.24 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 30 | 18:30 | Hasnabad | 81 | 19:00 | Palashbari | 110 | 19:30
Agargaon | 85 | 16:00 | Hathazari | 101 | 19:00 | Panchagarh | 58 | 19:00
Agrabad | 82 | 18:00 | Ishurdi | 71 | 19:30 | Patuakhali | 116 | 23:00
AKS | 10 | 05:00 | Jaldhaka | 50 | 19:00 | PHP | 7 | 02:00
AKSML | 151 | 12:00 | Jamalpur | 155 | 08:00 | Purbachal | 17 | 15:00
Amnura | 64 | 00:00 | Jashore | 127 | 20:00 | Purbasadipur | 99 | 19:00
Ashuganj | 43 | 12:00 | Jhenaidah | 122 | 20:00 | Rahim | 25 | 20:00
Bagerhat | 107 | 20:00 | Joydebpur | 229 | 11:00 | Rajbari | 68 | 20:00
Bakulia | 124 | 19:00 | Joypurhat | 59 | 00:00 | Rajendrapur | 108 | 13:00
Banani | 49 | 15:00 | Juldah | 31 | 10:00 | Rajshahi | 161 | 21:00
Bangabhaban | 22 | 10:00 | Kabirpur | 279 | 15:00 | Rajshahi | 39 | 12:00
Barapukuria | 53 | 19:30 | Kachua | 62 | 16:00 | Ramganj | 92 | 22:00
Barguna | 18 | 22:00 | Kallyanpur | 96 | 18:30 | Rampur | 16 | 16:00
Barishal | 105 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 12 | 18:30
Barishal | 66 | 03:00 | Kamrangirchar | 75 | 18:30 | Rangpur | 128 | 19:00
Baroaulia | 77 | 00:00 | Kaptai | 4 | 18:00 | Ruppur | 4.6 | 16:00
Baroirhat | 50 | 21:00 | Kazla | 83 | 17:00 | Saidpur | 99 | 19:00
Bashundhara | 159 | 15:00 | Keranigonj | 72 | 18:30 | Satkhira | 120 | 21:00
BashundharaCement | 13 | 00:00 | Khagrachori | 26 | 21:00 | Satmasjid | 93 | 18:30
Beanibazar | 44 | 19:00 | Khulna | 86 | 19:00 | Savar | 179 | 18:30
Benapole | 56 | 19:00 | Khulshi | 178 | 18:30 | Shahjadpur | 119 | 19:00
Bhaluka | 118 | 19:30 | Kishoreganj | 122 | 22:00 | Shahjibazar | 85 | 21:00
Bhandaria | 54 | 19:30 | Kodda | 202 | 22:00 | Shahmirpur | 42 | 01:00
Bhangura | 41 | 19:00 | KSRM | 27 | 23:00 | Shariatpur | 68 | 20:00
Bheramara(GK) | 60 | 20:00 | Kulaura | 30 | 18:30 | Sherpur | 130 | 00:00
Bhulta | 210 | 17:00 | Kurigram | 52 | 19:30 | Shikalbaha | 38 | 12:00
Bog-Sherpur | 60 | 20:00 | Kushtia | 138 | 19:30 | Shitalakhya | 112 | 15:00
Bogura | 172 | 22:00 | Lalbag | 95 | 16:00 | Sholosohor | N/A | N/A
Borhanuddin | 45 | 20:00 | Lalmonirhat | 41 | 19:00 | Shyampur | 184 | 11:00
Brahmanbaria | 120 | 19:00 | Madanganj | 170 | 19:30 | Siddhirganj | 128 | 16:00
BSRM | 164 | 23:00 | Madaripur | 108 | 22:00 | Sirajganj | 103 | 22:00
Cantonment | 135 | 15:00 | Madartek | 76 | 19:30 | Sonargaon | 87 | 15:00
Chandpur | 78 | 21:00 | Madunaghat | 61 | 18:30 | Sreemongol | 41 | 18:30
Chandraghona | 30 | 19:00 | Magura | 58 | 22:00 | Srinagar | 43.71 | 21:00
Chapai | 80 | 22:00 | Mahasthangarh | 80 | 19:00 | SSM | 4 | 00:00
Charsaidpur | 46 | 22:00 | Manikganj | 98 | 19:00 | Sunamganj | 36 | 19:30
Chauddagram | 47 | 22:00 | Maniknagar | 70 | 13:00 | Sylhet | 111 | 20:00
Chhatak | 22 | 19:00 | Matarbari | 43 | 19:30 | Tangail | 237 | 19:00
Chowmuhani | 210 | 21:00 | Matuail | 60 | 12:00 | Thakurgaon | 74 | 19:00
Chuadanga | 103 | 19:30 | Millgate | 56 | 12:00 | TK | N/A | N/A
Coxsbazar | 117 | 19:00 | Mirpur | 127 | 18:30 | Tongi | 138 | 13:00
Cumilla(N) | 126 | 19:30 | Mirsorai | N/A | N/A | Ullon | 43 | 20:00
Cumilla(S) | 172 | 19:00 | Mithapukur | 28 | 19:00 | Uttara | 64 | 15:00
Daudkandi | 130 | 18:30 | Modern | 0 | 00:00 | UttaraNew | 32 | 15:00
Dhaka | 38 | 13:00 | Mogbazar | 119 | 16:00 | Zigatola | 42 | 18:00
Dhamrai | 128 | 19:00 | Mongla | 36 | 00:00
Dhanmondi | 205 | 13:00 | Motijheel | 30 | 13:00
Dohazari | 88 | 19:00 | Munshiganj | 102 | 20:00
Faridpur | 143 | 21:00 | Mymensingh | 244 | 17:00
Fatullah | 70 | 15:00 | Naogaon | 122 | 19:30
Fenchuganj | 25 | 19:00 | Narail | 54 | 19:00
Feni | 127 | 20:00 | Narinda | 61 | 13:00
Ghorashal | 79 | 19:00 | Narshingdi | 164 | 20:00
Goalpara | 27 | 20:00 | Natore | 146 | 21:00
Gollamari | 53 | 19:00 | Nawabganj | 53.6 | 20:00
Gopalganj | 98.8 | 20:00 | Netrakona | 105 | 21:00
GPH | 91 | 14:00 | New | 77 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 2:00 | 398 | 14:00 | Kaliakoir | 397 | 0.375 | 376 | 0.58333
| Bheramara | 396 | 6:00 | 386 | 16:00 | Bhulta | 406 | 0.083333 | 379 | 0.5
| Ashuganj(N) | 412 | 2:00 | 390 | 13:00 | Gopalganj | 415 | 0.625 | 395 | 0.91667
| Payra | 423 | 1:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 23:00 | 236 | 15:00 | Hathazari | 237 | 9:00 | 230 | 13:00
| Ishurdi | 234 | 18:00 | 228 | 19:00 | Megnaghat | 233 | 4:00 | 224 | 18:30
| Ashuganj | 242 | 4:00 | 232 | 13:00 | Fenchuganj | 244 | 4:00 | 237 | 15:00
| Serajganj | 235 | 3:00 | 232 | 7:00 | Siddhirganj | 230 | 1:00 | 216 | 13:00
| Baghabari | 233 | 18:00 | 229 | 19:30 | Maniknagar | 229 | 1:00 | 215 | 14:00
| Barapukuria | 230 | 11:00 | 218 | 7:00 | Agargaon | 228 | 7:00 | 211 | 13:00
| Bogra | 230 | 18:00 | 224 | 7:00 | Barisal | 243 | 9:00 | 233 | 19:30
| Rajshahi | 229 | 18:00 | 217 | 2:00 | Bhola 225 MW | 245 | 6:00 | 237 | 19:30
| Khulna South | 237 | 9:00 | 228 | 2:00 | AKSML | 237 | 9:00 | 228 | 13:00
| Rampura | 230 | 1:00 | 217 | 12:00 | BSRM | 234 | 6:00 | 226 | 13:00
| Haripur | 228 | 1:00 | 216 | 12:00 | Bibiyana | 241 | 9:00 | 233 | 15:00
| Hasnabad | 227 | 2:00 | 213 | 13:00 | Bhulta | 231 | 2:00 | 215 | 12:00
| Shyampur | 227 | 1:00 | 212 | 13:00 | Ashuganj (S) | 240 | 2:00 | 228 | 13:00
| Aminbazar | 229 | 1:00 | 212 | 2:00 | Kaliakoir | 231 | 2:00 | 216 | 14:00
| Tongi | 233 | 2:00 | 216 | 13:00 | GPH | 236 | 7:00 | 228 | 4:00
| Comilla (N) | 233 | 4:00 | 224 | 12:00 | Jhenaidah | 231 | 18:00 | 222 | 19:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 02:00 | 126 | 14:00 | Manikganj | 133 | 06:00 | 124 | 16:00
| Agargaon | 139 | 04:00 | 126 | 13:00 | Maniknagar | 133 | 01:00 | 124 | 12:00
| Agrabad | 134 | 06:00 | 129 | 18:30 | Matarbari | 126 | 09:00 | 113 | 00:00
| AKS | 134 | 08:00 | 130 | 11:00 | Matuail | 136 | 03:00 | 127 | 13:00
| Aminbazar | 135 | 03:00 | 132 | 18:00 | Millgate | 137 | 01:00 | 128 | 15:00
| Amnura | 134 | 18:00 | 125 | 07:00 | Mirpur | 134 | 01:00 | 124 | 12:00
| Ashuganj | 140 | 03:00 | 134 | 13:00 | Mithapukur | 134 | 15:00 | 120 | 08:00
| Bagerhat | 135 | 08:00 | 128 | 18:30 | Modern | 135 | 08:00 | 130 | 12:00
| Bakulia | 134 | 18:00 | 128 | 13:00 | Mogbazar | 136 | 22:00 | 127 | 12:00
| Banani | 136 | 00:00 | 128 | 15:00 | Mongla | 135 | 09:00 | 128 | 20:00
| Bangabhaban | 134 | 04:00 | 123 | 13:00 | Motijheel | 134 | 04:00 | 123 | 13:00
| Barapukuria | 133 | 11:00 | 124 | 07:00 | Munshiganj | 140 | 19:30 | 130 | 12:00
| Barguna | 136 | 08:00 | 129 | 01:00 | Mymensingh | 127 | 06:00 | 114 | 12:00
| Barishal | 141 | 09:00 | 127 | 21:00 | Naogaon | 130 | 18:00 | 119 | 07:00
| Barishal | 141 | 08:00 | 134 | 00:00 | Narail | 129 | 18:00 | 120 | 19:00
| Baroaulia | 137 | 18:00 | 132 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 135 | 00:00 | 130 | 18:30 | Narshingdi | 133 | 04:00 | 125 | 13:00
| Bashundhara | 137 | 00:00 | 128 | 15:00 | Natore | 135 | 11:00 | 130 | 07:00
| BashundharaCement | 140 | 20:00 | 130 | 12:00 | Nawabganj | 140 | 20:00 | 127 | 12:00
| Beanibazar | 136 | 04:00 | 132 | 11:00 | Netrakona | 127 | 05:00 | 114 | 12:00
| Benapole | 129 | 10:00 | 123 | 19:00 | New | 138 | 04:00 | 128 | 13:00
| Bhaluka | 129 | 04:00 | 112 | 12:00 | Niamatpur | 127 | 17:00 | 115 | 07:00
| Bhandaria | 141 | 09:00 | 129 | 21:00 | Noapara | 134 | 10:00 | 130 | 01:00
| Bhangura | 135 | 18:00 | 129 | 19:00 | Pabna | 134 | 18:00 | 129 | 19:30
| Bheramara | 135 | 18:00 | 132 | 03:00 | Palashbari | 130 | 22:00 | 119 | 07:00
| Bheramara(GK) | 136 | 03:00 | 135 | 00:00 | Panchagarh | 135 | 11:00 | 119 | 07:00
| Bhulta | 131 | 02:00 | 123 | 13:00 | Patuakhali | 136 | 08:00 | 129 | 21:00
| Bog-Sherpur | 133 | 18:00 | 127 | 07:00 | PHP | 135 | 00:00 | 130 | 18:30
| Bogura | 135 | 18:00 | 129 | 07:00 | Purbachal | 138 | 05:00 | 128 | 14:00
| Bogura | 135 | 18:30 | 129 | 07:00 | Purbasadipur | 133 | 11:00 | 120 | 07:00
| Brahmanbaria | 136 | 04:00 | 130 | 13:00 | Rahim | 136 | 01:00 | 128 | 12:00
| Cantonment | 137 | 02:00 | 123 | 13:00 | Rajbari | 134 | 09:00 | 126 | 19:30
| Chandpur | 141 | 18:00 | 136 | 08:00 | Rajendrapur | 136 | 02:00 | 126 | 13:00
| Chandraghona | 135 | 18:00 | 132 | 15:00 | Rajshahi | 136 | 18:00 | 130 | 07:00
| Chapai | 135 | 18:00 | 127 | 07:00 | Rajshahi | 138 | 18:00 | 131 | 03:00
| Charsaidpur | 140 | 21:00 | 129 | 13:00 | Ramganj | 137 | 09:00 | 133 | 03:00
| Chauddagram | 136 | 00:00 | 132 | 13:00 | Rampur | 133 | 02:00 | 130 | 12:00
| Chhatak | 135 | 05:00 | 131 | 11:00 | Rampura | 136 | 23:00 | 127 | 12:00
| Chowmuhani | 134 | 18:00 | 128 | 23:00 | Rangamati | 135 | 06:00 | 131 | 13:00
| Chuadanga | 124 | 09:00 | 112 | 20:00 | Rangpur | 133 | 15:00 | 122 | 06:00
| Coxsbazar | 124 | 09:00 | 111 | 00:00 | Ruppur | 136 | 18:00 | 132 | 19:00
| Cumilla(N) | 137 | 00:00 | 132 | 13:00 | Saidpur | 132 | 15:00 | 124 | 08:00
| Cumilla(S) | 137 | 00:00 | 125 | 12:00 | Satkhira | 138 | 10:00 | 132 | 15:00
| Daudkandi | 137 | 20:00 | 126 | 14:00 | Satmasjid | 138 | 04:00 | 125 | 13:00
| Dhaka | 136 | 22:00 | 125 | 13:00 | Savar | 136 | 02:00 | 123 | 13:00
| Dhamrai | 137 | 04:00 | 126 | 13:00 | Shahjadpur | 137 | 03:00 | 133 | 19:00
| Dhanmondi | 136 | 00:00 | 127 | 12:00 | Shahjibazar | 138 | 10:00 | 134 | 12:00
| Dohazari | 132 | 09:00 | 123 | 13:00 | Shahmirpur | 135 | 09:00 | 130 | 12:00
| Faridpur | 135 | 09:00 | 130 | 01:00 | Shariatpur | 138 | 12:00 | 127 | 19:30
| Fatullah | 136 | 03:00 | 126 | 13:00 | Sherpur | 131 | 03:00 | 116 | 12:00
| Fenchuganj | 142 | 09:00 | 135 | 18:30 | Shikalbaha | 135 | 07:00 | 130 | 12:00
| Feni | 136 | 00:00 | 131 | 18:30 | Shikalbaha | 134 | 07:00 | 130 | 13:00
| Ghorashal | 140 | 23:00 | 136 | 15:00 | Shitalakhya | 140 | 22:00 | 128 | 13:00
| Goalpara | 138 | 18:00 | 133 | 02:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 136 | 09:00 | 123 | 19:30 | Shyampur | 136 | 22:00 | 126 | 13:00
| Gopalganj | 138 | 09:00 | 127 | 19:00 | Shyampur | 136 | 21:00 | 126 | 12:00
| Gopalganj_I | 140 | 09:00 | 132 | 19:00 | Siddhirganj | 136 | 00:00 | 129 | 12:00
| Gulshan | 136 | 23:00 | 126 | 13:00 | Sirajganj | 134 | 18:30 | 128 | 08:00
| Halishahar | 134 | 05:00 | 129 | 12:00 | Sonargaon | 137 | 19:30 | 129 | 14:00
| Haripur | 136 | 01:00 | 128 | 12:00 | Sreemongol | 141 | 09:00 | 136 | 14:00
| HaripurSBU | 136 | 00:00 | 127 | 13:00 | Srinagar | 138 | 19:30 | 122 | 12:00
| Hasnabad | 137 | 19:30 | 129 | 12:00 | SSM | 139 | 18:00 | 132 | 12:00
| Hathazari | 138 | 09:00 | 132 | 13:00 | Sunamganj | 134 | 05:00 | 129 | 11:00
| Ishurdi | 136 | 18:00 | 132 | 19:30 | Sylhet | 135 | 01:00 | 132 | 11:00
| Jaldhaka | 131 | 15:00 | 119 | 07:00 | Tangail | 134 | 23:00 | 122 | 13:00
| Jamalpur | 134 | 02:00 | 118 | 12:00 | Thakurgaon | 135 | 11:00 | 117 | 07:00
| Jashore | 130 | 09:00 | 123 | 19:00 | TK | N/A | N/A | N/A | N/A
| Jhenaidah | 131 | 09:00 | 123 | 19:00 | Tongi | 138 | 01:00 | 135 | 07:00
| Jhenaidah | 132 | 18:00 | 125 | 19:00 | Ullon | 136 | 22:00 | 126 | 13:00
| Joydebpur | 140 | 18:00 | 133 | 10:00 | Uttara | 134 | 00:00 | 125 | 16:00
| Joypurhat | 129 | 18:00 | 116 | 07:00 | UttaraNew | 137 | 01:00 | 127 | 18:30
| Juldah | 135 | 08:00 | 130 | 12:00 | Zigatola | 139 | 21:00 | 125 | 13:00
| Kabirpur | 140 | 00:00 | 127 | 13:00
| Kachua | 138 | 00:00 | 133 | 13:00
| Kaliakoir | 138 | 06:00 | 129 | 12:00
| Kallyanpur | 134 | 23:00 | 124 | 13:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 139 | 19:30 | 127 | 12:00
| Kaptai | 135 | 18:00 | 132 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 192 | 7977 | 4224 | 12201 |  |  |  | QF-LDC-11
0:30 | 163 | 7852 | 3971.5 | 11823.5 | Date: | 2022-03-30
1:00 | 134 | 7727 | 3719 | 11446
1:30 | 134 | 7598 | 3671 | 11269
2:00 | 134 | 7469 | 3623 | 11092
2:30 | 107 | 7301.5 | 3535 | 10836.5 | [5 empty] | Gen. at Eve. Peak | 13283 | 13283 MW (19:30 )
3:00 | 80 | 7134 | 3447 | 10581 | [6 empty] | 19:30
3:30 | 56 | 7055.5 | 3438.5 | 10494 | [5 empty] | Gen. at Day Peak | 11517 | 11517 MW (12:00 )
4:00 | 32 | 6977 | 3430 | 10407 | [6 empty] | 12:00
4:30 | 22 | 6874.5 | 3398 | 10272.5 | [5 empty] | Highest Generation | 13283
5:00 | 12 | 6772 | 3366 | 10138 | [6 empty] | 19:30
5:30 | 32 | 6752.5 | 3350.5 | 10103
6:00 | 52 | 6733 | 3335 | 10068
6:30 | 77 | 6799.5 | 3315.5 | 10115
7:00 | 102 | 6866 | 3296 | 10162
7:30 | 80 | 6887 | 3368.5 | 10255.5
8:00 | 58 | 6908 | 3441 | 10349
8:30 | 156 | 6978.5 | 3480.5 | 10459
9:00 | 254 | 7049 | 3520 | 10569
9:30 | 321 | 7190 | 3495 | 10685
10:00 | 388 | 7331 | 3470 | 10801
10:30 | 440 | 7395.5 | 3562 | 10957.5
11:00 | 492 | 7460 | 3654 | 11114
11:30 | 631 | 7444.5 | 3871 | 11315.5
12:00 | 770 | 7429 | 4088 | 11517
12:30 | 738 | 7493 | 4114 | 11607
13:00 | 706 | 7557 | 4140 | 11697
13:30 | 720 | 7519 | 4160.5 | 11679.5
14:00 | 734 | 7481 | 4181 | 11662
14:30 | 719 | 7648 | 4189 | 11837
15:00 | 704 | 7815 | 4197 | 12012
15:30 | 581 | 7854 | 4035.5 | 11889.5
16:00 | 458 | 7893 | 3874 | 11767
16:30 | 448 | 7877 | 3785 | 11662
17:00 | 438 | 7861 | 3696 | 11557
17:30 | 417 | 7846 | 3677.5 | 11523.5
18:00 | 396 | 7831 | 3659 | 11490
18:30 | 216 | 8293.5 | 3961 | 12254.5
19:00 | 36 | 8756 | 4263 | 13019
19:30 | 58 | 8802 | 4481 | 13283
20:00 | 52 | 8665 | 4496 | 13161 |  |  |  | Executive Engineer
20:30 | 86 | 8578.5 | 4516 | 13094.5 |  |  |  | Network Operation Division
21:00 | 120 | 8492 | 4536 | 13028
21:30 | 166 | 8406.5 | 4538 | 12944.5
22:00 | 212 | 8321 | 4540 | 12861 |  |  |  |  | Page 6 of 7
22:30 | 181 | 8280 | 4463 | 12743
23:00 | 150 | 8239 | 4386 | 12625
23:30 | 171 | 8108 | 4305 | 12413
24:00 | 192 | 7977 | 4224 | 12201
13283 MW (19:30 )
11517 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-30 |  | Energy |  | 280110214
[13 empty] | 2022-03-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3668 | 898 | 1851 | 0 | 3881 | 901 | 71 | 250 | 657 | 154 | 0 | 0
0:30 | 3851.5 | 899 | 1693.5 | 0 | 3719 | 865 | 69.5 | 250 | 461 | 145 | 0 | 0 | Date: | 2022-03-30
1:00 | 4035 | 900 | 1536 | 0 | 3557 | 829 | 68 | 250 | 265 | 136 | 0 | 0
1:30 | 4003.5 | 900 | 1523 | 0 | 3462.5 | 829.5 | 68 | 250 | 229.5 | 133 | 0 | 0 | [8 empty] | Total Energy | 280.1102 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3972 | 900 | 1510 | 0 | 3368 | 830 | 68 | 250 | 194 | 130 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3972 | 900.5 | 1489 | 0 | 3140.5 | 829.5 | 68 | 250 | 186 | 131 | 0 | 0 | [8 empty] | Energy Requirement | 280.1102
3:00 | 3972 | 901 | 1468 | 0 | 2913 | 829 | 68 | 250 | 178 | 132 | 0 | 0
3:30 | 3962.5 | 902.5 | 1472 | 0 | 2864.5 | 814.5 | 68 | 250 | 162 | 128 | 0 | 0 | [6 empty] | Shortage
4:00 | 3953 | 904 | 1476 | 0 | 2816 | 800 | 68 | 250 | 146 | 124 | 0 | 0
4:30 | 3949.5 | 904 | 1471.5 | 0 | 2711.5 | 780 | 68 | 250 | 146 | 122 | 0 | 0
5:00 | 3946 | 904 | 1467 | 0 | 2607 | 760 | 68 | 250 | 146 | 120 | 0 | 0
5:30 | 3918.5 | 904 | 1453.5 | 0 | 2619.5 | 755 | 68.5 | 250 | 146 | 118 | 0 | 0
6:00 | 3891 | 904 | 1440 | 0 | 2632 | 750 | 69 | 250 | 146 | 116 | 0 | 0
6:30 | 3891 | 907 | 1444 | 0 | 2691 | 724.5 | 69.5 | 250 | 146 | 112 | 10 | 0 |  |  |  |  | Coal
7:00 | 3891 | 910 | 1448 | 0 | 2750 | 699 | 70 | 250 | 146 | 108 | 20 | 0
7:30 | 3859 | 911.5 | 1428.5 | 0 | 2868.5 | 688.5 | 70 | 250 | 154 | 116 | 39.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3827 | 913 | 1409 | 0 | 2987 | 678 | 70 | 250 | 162 | 124 | 59 | 0
8:30 | 3835 | 913 | 1384 | 0 | 3078.5 | 658.5 | 70 | 250 | 187 | 130 | 83 | 0
9:00 | 3843 | 913 | 1359 | 0 | 3170 | 639 | 70 | 250 | 212 | 136 | 107 | 0
9:30 | 3804 | 913.5 | 1398 | 0 | 3287 | 621.5 | 70 | 250 | 215 | 142 | 114 | 0
10:00 | 3765 | 914 | 1437 | 0 | 3404 | 604 | 70 | 250 | 218 | 148 | 121 | 0
10:30 | 3758 | 913.5 | 1463.5 | 0 | 3452 | 621.5 | 70 | 250 | 287.5 | 146 | 125.5 | 0
11:00 | 3751 | 913 | 1490 | 0 | 3500 | 639 | 70 | 250 | 357 | 144 | 130 | 0
11:30 | 3814.5 | 915 | 1573 | 0 | 3520 | 644 | 70 | 250 | 368 | 150 | 141 | 0
12:00 | 3878 | 917 | 1656 | 0 | 3540 | 649 | 70 | 250 | 379 | 156 | 152 | 0
12:30 | 3891 | 917 | 1695 | 0 | 3593.5 | 649 | 69 | 250 | 379.5 | 153 | 140 | 0
13:00 | 3904 | 917 | 1734 | 0 | 3647 | 649 | 68 | 250 | 380 | 150 | 128 | 0
13:30 | 3904 | 917 | 1734 | 0 | 3647 | 649 | 68 | 250 | 380 | 150 | 128 | 0
14:00 | 3904 | 917 | 1734 | 0 | 3647 | 649 | 68 | 250 | 380 | 150 | 128 | 0
14:30 | 3855.5 | 917 | 1750 | 90 | 3680.5 | 680.5 | 68 | 250 | 409 | 155 | 129 | 0
15:00 | 3807 | 917 | 1766 | 180 | 3714 | 712 | 68 | 250 | 438 | 160 | 130 | 0
15:30 | 3846 | 916.5 | 1807 | 90 | 3609.5 | 712 | 68 | 250 | 458 | 158 | 104.5 | 0
16:00 | 3885 | 916 | 1848 | 0 | 3505 | 712 | 68 | 250 | 478 | 156 | 79 | 0
16:30 | 3748 | 916.5 | 1799 | 0 | 3505 | 712 | 68 | 250 | 505 | 154 | 66 | 0
17:00 | 3748 | 917 | 1750 | 0 | 3505 | 712 | 68 | 250 | 532 | 152 | 53 | 0
17:30 | 3700 | 916.5 | 1679 | 0 | 3590 | 706.5 | 68 | 250 | 564 | 152 | 27.5 | 0
18:00 | 3652 | 916 | 1608 | 0 | 3675 | 701 | 68 | 250 | 596 | 152 | 2 | 0
18:30 | 3685 | 915.5 | 1723.5 | 236 | 3905 | 742.5 | 68.5 | 300.5 | 660.5 | 162 | 1 | 0
19:00 | 3718 | 915 | 1839 | 472 | 4135 | 784 | 69 | 351 | 725 | 172 | 0 | 0
19:30 | 3748 | 915 | 1830 | 492 | 4199 | 870 | 69 | 429 | 777 | 170 | 0 | 0
20:00 | 3593 | 915 | 1865 | 457 | 4215 | 892 | 69 | 429 | 778 | 164 | 0 | 0
20:30 | 3641 | 915.5 | 1871 | 343.5 | 4202.5 | 897.5 | 69 | 431 | 778.5 | 162 | 0 | 0
21:00 | 3689 | 916 | 1877 | 230 | 4190 | 903 | 69 | 433 | 779 | 160 | 0 | 0
21:30 | 3672 | 916 | 1880 | 155 | 4195 | 902 | 69 | 433 | 779.5 | 161 | 0 | 0
22:00 | 3655 | 916 | 1883 | 80 | 4200 | 901 | 69 | 433 | 780 | 162 | 0 | 0
22:30 | 3660.5 | 916 | 1869 | 40 | 4205 | 901.5 | 70 | 359.5 | 752.5 | 161 | 0 | 0
23:00 | 3666 | 916 | 1855 | 0 | 4210 | 902 | 71 | 286 | 725 | 160 | 0 | 0
23:30 | 3667 | 907 | 1853 | 0 | 4045.5 | 901.5 | 71 | 268 | 691 | 157 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.1° C
24:00 | 3668 | 898 | 1851 | 0 | 3881 | 901 | 71 | 250 | 657 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 68 | 68 | 68 | 68 | 68 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 68 |  | 69 | 69 | 69 | 69 | 69 | 71 | 71 | 1662349
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | 8 | [12 empty] | 3 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 273749
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 7 | 13 | 14 | 12 | 20 | 11 | 15 | 13 | 7 | 2 | 0 | [8 empty] | 120150
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 209 | 204 | 204 | 203 | 204 | 205 | 205 | 204 | 204 | 204 | 203 | 203 | 203 | 203 |  | 206 | 203 | 203 | 208 | 203 | 203 | 203 | 4866079
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 292672
12 | Hathazari 100 MW peaking PP | [15 empty] | 16 | 31 | 34 |  | 34 | 34 | 34 | 34 | 34 | 31 |  | 244848
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 91 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 |  | 95 | 105 | 105 | 105 | 105 | 105 | 105 | 2286618
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 100 | 100 | 100 | 30 |  |  |  | 210048
14 | Titas 50 MW Peaking PP | [16 empty] | 30 | 40 |  | 40 | 40 | 42 | 41 | 42 | 42 | 42 | 294656
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 57 | 40 | 40 | 37 | 38 | 0 | 0 | 60 | 60 | 35 |  | 57 | 55 | 57 | 57 | 57 | 56 | 59 | 1134000
17 | Siddhirganj 335 MW CCPP | 219 | 220 | 220 | 220 | 220 | 220 | 226 | 224 | 227 | 180 | 180 | 213 | 208 | 206 | 206 | 211 | 212 | 170 |  | 222 | 224 | 223 | 221 | 219 | 219 | 218 | 5161620
18 | Kodda 300 MW PP Unit-2 (Summit) | 281 | 281 | 210 | 210 | 145 | 145 | 145 | 145 | 145 | 202 | 240 | 245 | 195 | 210 | 230 | 230 | 230 | 238 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 5600289
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 208 | 214 | 141 | 200 | 171 | 210 | 210 | 210 | 210 |  | 205 | 210 | 210 | 210 | 210 | 210 | 210 | 4882000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 200 | 180 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4795500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 27 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 939792
33 | Ashuganj 225 MW CCPP | 207 | 212 | 211 | 213 | 210 | 196 | 188 | 180 | 190 | 210 | 200 | 199 | 185 | 180 | 190 | 202 | 203 | 204 |  | 180 | 194 | 197 | 205 | 210 | 212 | 217 | 4829000
34 | Ashuganj 450 MW CCPP(South) | 285 | 270 | 285 | 270 | 275 | 270 | 270 | 270 | 270 | 285 | 270 | 270 | 275 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 290 | 270 | 270 | 270 | 6743000
| Ashuganj 450 MW CCPP(North) | 280 | 270 | 285 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 270 | 270 | 280 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 290 | 270 | 270 | 270 | 6932000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144000
36 | Chandpur 150 MW CCPP | 138 | 139 | 138 | 137 | 137 | 137 | 138 | 137 | 134 | 137 | 137 | 137 | 137 | 137 | 137 | 138 | 138 | 136 |  | 137 | 137 | 0 |  |  |  |  | 2684610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6389600
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 108 | 108 | 108 | 108 | 108 | 109 | 108 | 108 | 108 | 106 | 106 | 96 | 95 | 92 | 92 | 98 | 98 | 106 |  | 105 | 108 | 107 | 107 | 107 | 109 | 109 | 2460480
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 11 | 16 | 22 | 26 | 31 | 27 | 27 | 26 | 12 | 10 | 1 | [8 empty] | 197200
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714000
45 | Fenchugonj CCPP Phase-2 | [10 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 315000
46 | Shajibazar 330 MW CCPP | 271 | 270 | 270 | 270 | 271 | 270 | 271 | 268 | 269 | 268 | 269 | 270 | 268 | 271 | 267 | 269 | 268 | 270 |  | 269 | 269 | 269 | 269 | 271 | 270 | 271 | 6185000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1246464
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 86 | 86 | 86 | 2130240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 130 | 20 | 25 | 30 | 77 | 84 | 108 | 120 | 136 | 136 | 143 |  | 150 | 150 | 155 | 163 | 163 | 163 | 162 | 2919080
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 22 | 23 | 21 | 22 | 22 | 24 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 24 | 25 | 24 | 555940
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250740
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218256
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 48 | 50 | 53 | 50 | 47 | 50 | 50 | 17 |  | 50 | 50 | 54 | 53 | 53 | 53 | 53 | 1193400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 17 | 19 | 20 | 21 | 437928
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 280 | 285 | 280 | 285 | 285 | 290 | 270 | 275 | 290 | 280 | 280 | 290 | 180 | 240 | 290 | 270 |  | 290 | 280 | 290 | 285 | 300 | 270 | 270 | 6833500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 17 | 17 | 30 | 35 | 1208713
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 586800
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 416556
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1327140
63 | Impoprt (Tripura) | 136 | 130 | 132 | 124 | 120 | 116 | 108 | 124 | 136 | 148 | 144 | 156 | 150 | 150 | 160 | 156 | 152 | 152 |  | 172 | 170 | 164 | 160 | 162 | 160 | 154 | 3518400
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 37 | 33 | 34 | 2 | 2 | 2 | 2 | 2 | 6 | 3 | 2 | 2 | 2 | 5 |  | 20 | 17 | 20 | 24 | 33 | 36 | 37 | 462240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 460116
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235980
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 17 | 17 | 17 | 17 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 584500
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 316440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 0 | 0 |  |  |  | 9 | 9 | 350820
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 737640
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 25 | 25 | 25 |  | 0 | 25 | 0 | 25 | 25 | 25 | 25 | 524100
73 | Ghorashal 108MW PP (Regent) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 99 | 99 | 96 | 93 | 99 | 102 | 102 | 102 | 98 | 98 | 60 |  | 100 | 99 | 99 | 100 | 100 | 101 | 100 | 2236227
| Feni Lanka Power | 98 | 98 | 70 | 34 | 17 | 17 | 17 | 34 | 54 | 84 | 98 | 98 | 98 | 80 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1836540
| Chowmuhani 113 MW | 108 | 106 | 107 | 106 | 107 | 106 | 105 | 106 | 105 | 103 | 103 | 102 | 103 | 102 | 100 | 89 | 84 | 95 |  | 102 | 103 | 104 | 103 | 103 | 104 | 103 | 2469600
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 72 | 72 | 72 | 79 | 105 | 117 | 126 | 98 | 82 | 91 | 90 | 90 | 96 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2122560
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | [6 empty] | 6 | 15 | 40 | 50 | 65 | 100 | 98 | 95 | 98 | 95 | 91 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1541760
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 25 |  | 5 | 24 | 32 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 44 | 44 | 44 |  | 48 | 44 | 44 | 44 | 51 | 51 | 51 | 987840
79 | Kodda 150MW PP | 135 | 64 | 48 | 16 | 16 | 16 | 16 | 32 | 82 | 82 | 115 | 133 | 133 | 133 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2532000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 34 | 36 | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 29 | 29 |  | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 903691
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2288400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 1 | 4 | 4 | 4 | 4 | 3 | 3 | 1 | [9 empty] | 26881
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1344968
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 103 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2665479
82 | Madanganj 102 PP(Summit) | [6 empty] | 0 | 10 | 25 | 55 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 77 | 77 | 77 | 78 | 79 | 79 | 0 | 1084536
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 150 | 135 | 145 | 145 | 140 | 135 | 150 | 140 | 110 | 140 | 135 | 0 |  | 70 | 115 | 135 | 135 | 120 |  | 135 | 125 | 130 | 140 | 125 | 130 | 132 | 2937309
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 7 | 16 | 16 | 16 | 38 | 92 | 91 | 85 | 90 | 94 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 72 | 1261440
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 87 | 90 | 90 | 86 | 76 | 86 | 90 |  | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 2147520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 29 | 31 | 31 | 31 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 752400
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1090459
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 58 | 58 | 58 | 32 | 32 | 40 | 58 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1874016
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | 103 | 103 | 103 | 103 | 96 | 96 | 96 | 96 | 92 | 85 | 88 | 82 | 88 | 91 | 91 | 91 | 98 | 98 |  | 102 | 102 | 102 | 102 | 102 | 103 | 103 | 2333760
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 30 | 30 | 15 | 15 | 28 | 40 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1127285
100 | Manikganj 55 MW PP (Northern) | 55 | 54 | [5 empty] | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 914186
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3502063
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 8100
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 978120
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 80 |  |  |  |  | 220 | 212 | 207 | 80 |  |  |  | 578541
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 50 |  |  |  |  | 50 | 50 | 50 | 50 | 50 |  |  | 239150
106 | Mymensingh 200 MW PP (United) | 200 | 193 | 193 | 200 | 200 | 195 | 194 | 194 | 194 | 194 | 135 | 135 | 126 | 120 | 125 | 115 | 115 | 155 |  | 182 | 193 | 193 | 194 | 194 | 194 | 194 | 4101600
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 50 |  |  |  |  | 100 | 100 | 100 | 70 | 30 |  |  | 364232
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 132 | 143 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3588910
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 90 | 90 | 90 | 76 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2060160
116 | Chandpur 200MW (Desh energy) | 155 | 100 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 50 | 51 | 60 | 100 | 69 | 117 | 180 | 180 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2712000
117 | Ashuganj 150MW PP (Midland) | 127 | 137 | 148 | 148 | 148 | 148 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 145 | 142 | 138 |  | 142 | 142 | 145 | 145 | 147 | 142 | 147 | 3470909
118 | Bibiyana-III 400 MW CCPP | 401 | 398 | 401 | 399 | 374 | 352 | 351 | 352 | 400 | 376 | 376 | 400 | 399 | 400 | 401 | 401 | 354 | 329 |  | 401 | 401 | 400 | 401 | 400 | 400 | 400 | 9305000
| Jamalpur 115 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 102 |  | 105 | 105 | 105 | 107 | 107 | 107 | 77 | 1480800
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7083164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2403840
| Anlima Energy Ltd. |  | 20 |  | 0 | 0 | 2 | 80 | 94 | 94 | 94 | 94 | 96 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 112 | 0 | 2066236
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 15 | 26 | 35 | 35 | 35 | 24 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 815760
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 7 | 12 | 25 | 21 | 24 | 28 | 27 | 27 | 28 | 22 | 0 | [8 empty] | 186220
| Chandpur 115(Doreen) | 99 | 99 | 34 | 34 | 17 | 17 | 17 | 17 | 22 | 51 | 86 | 98 | 78 | 63 | 63 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1776000
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  |  | 0 | 0 |  |  |  |  | 1022400
120 | Eastern Zone Total | 7727 | 7469 | 7134 | 6977 | 6772 | 6733 | 6866 | 6908 | 7049 | 7331 | 7460 | 7429 | 7557 | 7481 | 7815 | 7893 | 7861 | 7831 |  | 8756 | 8802 | 8665 | 8492 | 8321 | 8239 | 7977 | 185612769
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 95 | 49 | [5 empty] | 16 | 16 | 16 | 16 | 35 | 49 | 49 | 44 | 15 | 16 | 16 |  | 70 | 101 | 109 | 111 | 111 | 112 | 83 | 1010880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 2 | 29 |  | 40 | 38 | 38 | 38 | 38 | 38 | 38 | 226080
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 190 | 213 | 213 | 215 | 215 | 120 | 120 | 3353280
129 | Rupsha 105 MW PP (Orion rupsha) | 95 | 94 | 95 | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2248800
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 11 | 33 | 60 | 55 | 63 | 67 | 52 | 64 | 56 | 24 | 16 | 1 | [8 empty] | 514800
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 218 | 220 | 220 | 220 | 220 | 190 | 191 | 177 | 163 | 163 | 160 | 194 | 216 | 218 | 219 | 184 | 142 |  | 221 | 220 | 223 | 222 | 222 | 215 | 220 | 4877045
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 484416
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 66 | 67 | 66 | 68 | 67 | 67 | 66 | 67 | 67 | 64 | 64 | 65 | 64 | 66 | 64 | 63 | 63 | 66 |  | 65 | 66 | 66 | 66 | 66 | 67 | 66 | 1571000
140 | Bhola 33 MW PP (Venture) | 35 | 37 | 26 | 29 | 30 | 29 | 28 | 22 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 26 | 32 |  | 35 | 35 | 37 | 38 | 39 | 38 | 38 | 712749
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 2 | 30 | [5 empty] | 20160
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 8 | 8 | 8 | 8 | 32 | 32 | 32 | 32 | 8 | 8 | 8 |  | 32 | 29 | 32 | 32 | 32 | 32 | 16 | 34725
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 10 |  | 5 | [6 empty] | 9088
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 900 | 900 | 901 | 904 | 904 | 904 | 910 | 913 | 913 | 914 | 913 | 917 | 917 | 918 | 917 | 916 | 917 | 916 |  | 915 | 915 | 915 | 916 | 916 | 916 | 898 | 22049454
147 | Bheramara 410 MW CCPP | 330 | 335 | 345 | 355 | 365 | 370 | 375 | 380 | 350 | 330 | 330 | 350 | 320 | 295 | 260 | 240 | 220 | 215 |  | 210 | 215 | 215 | 215 | 215 | 215 | 210 | 7263360
148 | Payra 1320 MW | 550 | 550 | 550 | 520 | 480 | 470 | 420 | 400 | 370 | 360 | 370 | 370 | 370 | 390 | 430 | 430 | 430 | 420 |  | 500 | 590 | 610 | 620 | 622 | 622 | 622 | 12525000
149
150 | Barapukuria TPP Unit-1 | 79 | 80 | 79 | 80 | 80 | 80 | 79 | 78 | 80 | 79 | 79 | 80 | 80 | 80 | 83 | 83 | 82 | 81 |  | 84 | 80 | 82 | 83 | 79 | 80 | 79 | 1926981
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 189 | 165 | 190 | 199 | 199 | 200 | 199 | 199 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4791700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [10 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 568544
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 1 | 1 | 3 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 20100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 180 | 180 | 180 | 180 | 180 | 180 | 185 | 214 | 170 | 170 | 198 | 214 | 212 | 209 | 202 | 175 | 162 |  | 145 | 132 | 132 | 142 | 147 | 147 | 147 | 4655690
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 161 | 216 | 216 | 218 | 218 | 166 | 130 | 3672218
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 213 | 200 | 160 | 160 | 160 | 154 | 153 | 162 | 182 | 170 | 164 | 178 | 210 | 206 | 198 | 177 | 153 | 140 |  | 127 | 120 | 120 | 120 | 120 | 118 | 118 | 4129836
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [6 empty] | 10 |  |  | 60 | 107 | 417 | 414 | 414 | 414 | 414 | 354 | 351 |  | 335 | 335 | 341 | 340 | 340 | 340 | 330 | 4758909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 4 | 5 | 16 | 26 | 35 | 42 | 42 |  | 42 | 45 | 45 | 45 | 45 | 45 | 44 | 409449
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 0 | 13 | 22 | 22 | 22 | 18 | 18 | 18 | 17 | 17 | 17 | 20 | 20 |  | 0 | 16 | 18 | 22 | 22 | 22 | 22 | 449280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240462
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 8 | [16 empty] | 8 |  | 50 | 50 | 50 | 50 | 50 | 50 |  | 267768
167 | Katakhali 50 MW Peaking PP | [9 empty] | 6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 337480
168 | Santahar 50 MW Peaking PP | [14 empty] | 20 | 35 | 35 | 35 |  | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 345390
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 8 | 8 | 5 | 8 | 8 | 8 | 25 | 39 | 43 | 33 | 43 | 43 | 43 | 16 | 16 | 16 |  | 43 | 43 | 43 | 52 | 52 | 52 | 52 | 736296
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 59 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 893880
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 110 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2732640
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 50 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2574240
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 110 | 110 | 75 | 70 | 38 | 38 | 38 | 70 | 110 | 110 | 104 | 110 | 103 | 106 | 110 | 70 | 54 | 54 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2175590
177 | Sympa Solar Power 8MW | [8 empty] | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 2 | 0 | [8 empty] | 26056
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 88 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 34 | 34 | 34 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1884099
178