## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-06-17 | Monday
|  | Date (day): | 2019-06-17 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13669 | MW |  |  | (b) At Evening Peak Hour : |  | 15124 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-16 | 2019-06-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | ST-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shoetage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 300 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 66 | 66 | 66
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 108 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | Gas Shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 327 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 65 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 313 | 300 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 350 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 78 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 290 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 40 | 100 | 100 | 110 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 85 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 200 | 200
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 101 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 36 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 145 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 73 | 70 | 70 |  | 38 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 20 | 44 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 49 | 50 | 50
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 200 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 47 | 149 | 149 | 149
37 | Gazipur 100 MW |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 89 | 100 | 100
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 2606 | 3587 | 4590 | 4990 | 540 | 280
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 90 | 90 | 90 |  | Gas Shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.4 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 46 | 46 | 46
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 38 | 40 | 40 |  | 190 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 205 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 100 | 135 | 135
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 24 | 24 | 24 |  | 27 | Engine problem
47 | Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 105 | 105 | 71 | 0 | 105 | 105
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 85 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
51 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
52 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 25 | 6 | 25
53 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 51 | 96 | 100 | 100 |  | 8
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 5.3 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 162 | 296 | 300 | 300
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 987.7 | 1347 | 1612 | 1608 | 150 | 265
54 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 217 | 215 | 221 | 221
56 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 300 | 360 | 360
57 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 300 | 360 | 360
58 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 55 | 55 | 55
60 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
61 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
63 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 70 | 100 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 50
66 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 100 | 100 | 100
67 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 105 | 200 | 200 | 200
68 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
69 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 140 | 178 | 137 | 184
70 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
71 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
72 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
73 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1616 | 1757 | 1869 | 2166 | 533 | 61
74 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 144 | 144 | 144 | 58 |  | Gas shortage
75 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
76 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 84 | 87 | 87
77 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 2 | 0
78 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 200 | 100 | 200
79 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 81 | 85 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 302.3 | 533 | 453 | 551 | 58 | 0
80 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 56 | 60 | 60
81 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
82 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
83 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
84 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 52 | 50 | 50
85 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 46 | 44 | 44
86 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 69 | 71 | 86 | 86
89 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 42 | 45 | 45 | 45
90 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 110 | 112 | 130 | 130
91 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
92 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 47 | 45 | 45
93 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
94 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 250 | 250 | 341 | 341
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 296 | 292 | 285 | 285 |  |  | On test
95 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1246 | 1235 | 1438 | 1438 | 0 | 330
96 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 28 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 940 | 939 | 953 | 953
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
97 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
98 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 38
99 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 40 | 0 | 40 | 225
100 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 4 | 52 | 0 | 80
101 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 20/06/2019
102 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
104 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
105 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 71 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1114 | 1522 | 1358 | 1793 | 0 | 410
106 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
107 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
108 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 36 | 33 | 33
109 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 144 | 148 | 147 | 147
110 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 270 | 392 | 385 | 411 | 0 | 0
111 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
112 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
113 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 33 | 0 | 35
114 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 6 | 50
115 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 32 | 32 | 43
116 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 44 | 44
117 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 188 | 182 | 214 | 214 |  |  | FGMO
118 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 179 | 220 | 220 |  |  | FGMO
119 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 104 | 194 | 220 | 220
120 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 300 | 414 | 414
121 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 28
122 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
123 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 12 | 12 | 12
124 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
125 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 8 | 50 | 52 | 52
126 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 46 | 90 | 95 | 95
127 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
128 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 108 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1078 | 1423 | 1702 | 1870 | 0 | 100
129 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 65 | 62 | 62
130 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74
131 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
132 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 4 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 267 | 298 | 262 | 297 | 74 | 85
| Total |  |  |  |  | 18539 | 17996 | 9487 | 12094 | 13669 | 15124 | 1355 | 1531
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9108.9006 | 11612 | 13124.2292 | 14521.2409
A. |  | 2019-06-16 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12096 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7804 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12094 | MW
3 | Day peak Generation : |  |  | 9487 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11612 | MW
4 | Evening peak Generation : |  |  | 12094 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 243.5169 | MKWHr | By Solar | 0.16107 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 153.2456 | MKWHr |  | By Oil: | 56.9317 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.3891 | MKWHr |  | By Hydro: | 0.84462 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1355 | MW | Dhaka | 4092 | 4092 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1531 | MW | Chittagong | 1172 | 1172 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2886 | MW | Khulna | 1465 | 1465 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1348.08 | MMCFD |  |  | Rajshahi | 1276 | 1276 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 105810742.782 | ii) Oil : | Taka | 384566910.45 | Comilla | 1088 | 1088 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28033444.89 | Total | Taka | 518411098.122 | Mymensingh | 933 | 933 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.8355 | MKWHr. | Sylhet | 510 | 510 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -400 | MW (E to W) at | 21:00 | hrs | Barisal | 344 | 344 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -490 | MW at | 5:00 | hrs | Rangpur | 732 | 732 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 11612 | 11612 |  | 0
B. |  | 2019-06-17 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 38.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15124 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 2524 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 253.6634 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8670 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.5935 | MKWHr. | ii) HVDC Flow at Peak Time |  | 939 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3514 | MKWHr. | iii) Maximum HVDC Flow : |  | 948 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.74 |  | (b) Today: | 74.54 |  | (c) Rule Curve: |  | 80.22
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-06-16
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 200 | 0 | 300 | 107 | 50 | 328 | 357 | 0 | 20 | 380 | 285 | 0 | 0 | 0 | 170 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 25 | 19 | 42 | 100 | 0 | 0 | 300 | 300 | 220 | 8 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 120 | 148 | 86 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 0 | 63 | 70 | 46 | 110 | 19 | 47 | 10 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 200 | 87 | 89 | 18 | 0 | 140 |  | 948 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 16 | 0 | 32 | 144 | 29 | 80 | 0 | 0 | 60 | 43 | 0 | 90 | 12 | 34 | 42 | 25 | 28 | 22 | 14 | 8 | 0 | 65 | 199 | 0 | 0 | 158 | 0 | 156 | 0 | 97 | 0 | 175 | 0 | 350 | 105 | 0 | 108 | 104 | 0 |  | 6280 | 3313 | 9593 | 4224 | 948 | 2219 | 1441 | 264 | 38 | 339 | 120 | 0 | 0 | 73.34
2:00 | 35 | 0 | 200 | 0 | 300 | 107 | 50 | 326 | 357 | 0 | 20 | 380 | 280 | 0 | 0 | 0 | 170 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 24 | 33 | 33 | 4 | 0 | 38 | 0 | 0 | 120 | 0 | 203 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 15 | 19 | 42 | 100 | 0 | 0 | 300 | 300 | 221 | 8 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 116 | 149 | 26 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 0 | 63 | 70 | 46 | 109 | 19 | 47 | 10 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 200 | 87 | 70 | 0 | 0 | 139 |  | 947 | 0 | 0 | 0 | 49 | 40 | 0 | 0 | 0 | 0 | 32 | 144 | 28 | 64 | 0 | 0 | 60 | 43 | 0 | 90 | 12 | 34 | 0 | 25 | 0 | 22 | 14 | 8 | 0 | 65 | 199 | 0 | 0 | 157 | 0 | 156 | 0 | 97 | 0 | 174 | 0 | 350 | 90 | 0 | 53 | 105 | 0 |  | 6113 | 3058 | 9171 | 4220 | 947 | 2208 | 1205 | 264 | 38 | 173 | 116 | 0 | 0 | 73.42
3:00 | 35 | 0 | 200 | 0 | 300 | 104 | 50 | 336 | 357 | 0 | 20 | 380 | 275 | 0 | 0 | 0 | 170 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 18 | 42 | 100 | 0 | 0 | 300 | 300 | 220 | 8 | 100 | 0 | 53 | 5 | 40 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 114 | 150 | 8 | 20 | 0 | 57 | 58 | 50 | 50 | 100 | 0 | 63 | 70 | 46 | 109 | 19 | 47 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 200 | 87 | 35 | 0 | 0 | 115 |  | 947 | 0 | 0 | 0 | 49 | 40 | 0 | 0 | 0 | 0 | 32 | 144 | 26 | 64 | 0 | 0 | 60 | 43 | 0 | 90 | 12 | 14 | 0 | 25 | 0 | 22 | 14 | 8 | 0 | 65 | 199 | 0 | 0 | 165 | 0 | 164 | 0 | 95 | 0 | 176 | 0 | 350 | 90 | 0 | 53 | 104 | 0 |  | 5960 | 3051 | 9011 | 4247 | 947 | 2189 | 1039 | 264 | 38 | 173 | 114 | 0 | 0 | 73.5
4:00 | 35 | 0 | 199 | 0 | 300 | 104 | 50 | 328 | 357 | 0 | 20 | 380 | 285 | 0 | 0 | 0 | 170 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 19 | 42 | 100 | 0 | 0 | 300 | 300 | 219 | 8 | 100 | 0 | 52 | 5 | 40 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 112 | 148 | 8 | 20 | 0 | 57 | 58 | 50 | 50 | 100 | 0 | 63 | 40 | 45 | 108 | 19 | 47 | 0 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 200 | 87 | 35 | 0 | 0 | 115 |  | 947 | 0 | 0 | 0 | 49 | 40 | 0 | 0 | 0 | 0 | 32 | 144 | 27 | 64 | 0 | 0 | 60 | 0 | 0 | 90 | 12 | 0 | 0 | 25 | 0 | 22 | 14 | 8 | 0 | 66 | 199 | 0 | 0 | 159 | 0 | 158 | 0 | 96 | 0 | 0 | 0 | 350 | 90 | 0 | 34 | 104 | 0 |  | 5908 | 2790 | 8698 | 4047 | 947 | 2144 | 1016 | 265 | 37 | 130 | 112 | 0 | 0 | 73.58
5:00 | 35 | 0 | 200 | 0 | 300 | 104 | 50 | 341 | 357 | 0 | 20 | 380 | 285 | 0 | 0 | 0 | 170 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 21 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 202 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 19 | 42 | 100 | 0 | 0 | 300 | 300 | 220 | 8 | 95 | 0 | 52 | 5 | 40 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 112 | 148 | 0 | 20 | 0 | 57 | 58 | 50 | 50 | 100 | 0 | 63 | 40 | 45 | 109 | 19 | 47 | 0 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 200 | 87 | 35 | 0 | 0 | 115 |  | 946 | 0 | 0 | 0 | 49 | 40 | 0 | 0 | 0 | 0 | 16 | 144 | 25 | 32 | 0 | 0 | 60 | 0 | 0 | 90 | 12 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 66 | 199 | 0 | 0 | 167 | 0 | 171 | 0 | 95 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 104 | 0 |  | 5911 | 2708 | 8619 | 4074 | 946 | 2146 | 909 | 265 | 37 | 130 | 112 | 0 | 0 | 73.66
6:00 | 35 | 0 | 200 | 0 | 300 | 104 | 50 | 328 | 357 | 0 | 20 | 340 | 285 | 0 | 0 | 0 | 120 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 21 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 203 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 18 | 42 | 100 | 0 | 0 | 300 | 300 | 220 | 8 | 100 | 0 | 52 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 100 | 146 | 0 | 20 | 0.1 | 57 | 58 | 11 | 10 | 100 | 0 | 63 | 10 | 46 | 109 | 0 | 12 | 0 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 10 | 0 | 0 | 200 | 27 | 35 | 0 | 0.2 | 115 |  | 941 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 144 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 90 | 12 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 66 | 199 | 0 | 0 | 156 | 0 | 160 | 0 | 95 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 35 | 0 |  | 5489 | 2401 | 7890 | 3956 | 941 | 1851 | 609 | 265 | 37 | 130 | 100 | 1 | 0 | 73.74
7:00 | 35 | 0 | 200 | 0 | 300 | 104 | 50 | 333 | 320 | 0 | 20 | 340 | 290 | 0 | 0 | 0 | 120 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 21 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 16 | 37 | 100 | 0 | 0 | 300 | 280 | 200 | 8 | 100 | 0 | 52 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 10 | 90 | 144 | 0 | 20 | 0.1 | 58 | 58 | 11 | 10 | 100 | 0 | 63 | 10 | 46 | 122 | 0 | 10 | 0 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 10 | 0 | 0 | 200 | 24 | 35 | 0 | 0.2 | 115 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 144 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 8 | 0 | 66 | 199 | 0 | 0 | 163 | 0 | 158 | 0 | 95 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 35 | 0 |  | 5436 | 2368 | 7804 | 3934 | 940 | 1830 | 611 | 265 | 40 | 90 | 90 | 4 | 0 | 73.74
8:00 | 35 | 0 | 200 | 0 | 300 | 104 | 50 | 349 | 320 | 0 | 20 | 370 | 300 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 20 | 33 | 33 | 5 | 0 | 40 | 0 | 0 | 120 | 0 | 217 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 18 | 14 | 100 | 0 | 0 | 300 | 300 | 202 | 8 | 100 | 0 | 52 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 10 | 102 | 146 | 0 | 20 | 0.2 | 58 | 58 | 11 | 17 | 130 | 0 | 61 | 10 | 44 | 123 | 0 | 43 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 10 | 0 | 0 | 239 | 24 | 71 | 0 | 1 | 115 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 144 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 8 | 0 | 65 | 199 | 0 | 0 | 178 | 0 | 170 | 0 | 95 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 34 | 0 |  | 5586.5 | 2390 | 7976.5 | 3958 | 940 | 1912 | 661 | 264 | 40 | 90 | 102 | 9.5 | 0 | 0
9:00 | 35 | 0 | 200 | 0 | 300 | 101 | 68 | 363 | 347 | 0 | 20 | 400 | 280 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 40 | 36 | 6 | 0 | 0 | 20 | 33 | 33 | 26 | 0 | 40 | 0 | 0 | 120 | 0 | 209 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 1 | 15 | 19 | 2 | 100 | 0 | 0 | 330 | 300 | 198 | 26 | 100 | 0 | 51 | 5 | 15 | 0 | 0 | 5 | 19 | 11 | 25 | 10 | 116 | 145 | 5 | 20 | 0.6 | 60 | 58 | 47 | 50 | 163 | 0 | 61 | 50 | 44 | 120 | 0 | 47 | 8 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 60 | 14 | 6 | 240 | 38 | 71 | 14 | 0.3 | 124 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 144 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 5 | 0 | 65 | 199 | 0 | 0 | 201 | 0 | 199 | 0 | 93 | 0 | 0 | 0 | 400 | 17 | 0 | 23 | 35 | 0 |  | 6064.5 | 2561 | 8625.5 | 4009 | 940 | 2261 | 892 | 264 | 40 | 90 | 116 | 13.5 | 0 | 0
10:00 | 35 | 0 | 200 | 0 | 300 | 101 | 68 | 338 | 341 | 0 | 20 | 400 | 300 | 0 | 0 | 0 | 30 | 0 | 92 | 0 | 0 | 2 | 16 | 0 | 8 | 0 | 6 | 54 | 55 | 17 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 40 | 0 | 0 | 120 | 7 | 222 | 0 | 142 | 0 | 0 | 16 | 0 | 0 | 10 | 9 | 38 | 18 | 2 | 100 | 0 | 0 | 330 | 300 | 209 | 26 | 96 | 0 | 51 | 5 | 35 | 0 | 0 | 8 | 19 | 11 | 25 | 10 | 124 | 144 | 16 | 20 | 2 | 58 | 58 | 47 | 47 | 163 | 0 | 59 | 50 | 44 | 125 | 0 | 44 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 10 | 7.4 | 100 | 17 | 6 | 240 | 82 | 90 | 18 | 3.2 | 125 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 144 | 18 | 0 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 5 | 0 | 65 | 199 | 0 | 0 | 192 | 0 | 196 | 0 | 93 | 0 | 0 | 0 | 400 | 17 | 0 | 53 | 35 | 0 |  | 6417.6 | 2569 | 8986.6 | 4051 | 940 | 2270 | 1183 | 264 | 40 | 102 | 124 | 12.6 | 0 | 0
11:00 | 35 | 0 | 200 | 0 | 340 | 101 | 67 | 344 | 334 | 13 | 20 | 370 | 250 | 3 | 0 | 0 | 0 | 0 | 62 | 0 | 3 | 24 | 16 | 5 | 8 | 0 | 6 | 54 | 55 | 35 | 22 | 0 | 20 | 33 | 33 | 41 | 0 | 35 | 0 | 0 | 120 | 8 | 205 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 39 | 40 | 19 | 2 | 100 | 0 | 0 | 330 | 360 | 183 | 25 | 100 | 0 | 51 | 5 | 35 | 0 | 0 | 16 | 19 | 11 | 16 | 10 | 132 | 144 | 36 | 20 | 1.7 | 56 | 58 | 47 | 47 | 163 | 0 | 61 | 69 | 42 | 109 | 0 | 44 | 10 | 255 | 16 | 11 | 0 | 6 | 0 | 0 | 7 | 0 | 16 | 19.5 | 100 | 76 | 10 | 240 | 81 | 89 | 54 | 3.7 | 162 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 8 | 144 | 20 | 16 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 5 | 0 | 64 | 199 | 0 | 0 | 189 | 0 | 188 | 0 | 93 | 0 | 20 | 0 | 370 | 35 | 0 | 78 | 71 | 0 |  | 6574.9 | 2652 | 9226.9 | 4038 | 940 | 2185 | 1507 | 263 | 35 | 102 | 132 | 24.9 | 0 | 0
12:00 | 35 | 0 | 200 | 0 | 340 | 101 | 66 | 327 | 313 | 13 | 20 | 370 | 230 | 7 | 0 | 15 | 0 | 0 | 62 | 0 | 7 | 24 | 16 | 10 | 8 | 0 | 6 | 54 | 55 | 35 | 22 | 0 | 20 | 25 | 33 | 41 | 0 | 35 | 0 | 0 | 120 | 8 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 51 | 37 | 18 | 3 | 100 | 0 | 0 | 330 | 360 | 217 | 26 | 95 | 0 | 50 | 5 | 35 | 0 | 0 | 25 | 19 | 11 | 16 | 12 | 140 | 144 | 48 | 20 | 2.3 | 56 | 58 | 47 | 46 | 130 | 0 | 61 | 69 | 42 | 110 | 0 | 44 | 10 | 250 | 16 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 47 | 17.4 | 100 | 105 | 70 | 296 | 81 | 90 | 71 | 5.3 | 162 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 4 | 8 | 144 | 18 | 16 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 0 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 64 | 199 | 0 | 0 | 188 | 0 | 179 | 0 | 92 | 0 | 104 | 0 | 340 | 35 | 0 | 108 | 71 | 4 |  | 6758 | 2729 | 9487 | 4163 | 940 | 2090 | 1725 | 263 | 35 | 106 | 140 | 25 | 0 | 0
13:00 | 35 | 0 | 200 | 0 | 350 | 100 | 65 | 327 | 314 | 13 | 20 | 370 | 270 | 7 | 0 | 15 | 0 | 0 | 62 | 0 | 7 | 24 | 16 | 10 | 13 | 0 | 6 | 54 | 55 | 35 | 0 | 0 | 19 | 25 | 33 | 41 | 0 | 35 | 0 | 0 | 120 | 8 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 85 | 37 | 16 | 9 | 100 | 0 | 0 | 330 | 360 | 184 | 26 | 96 | 0 | 51 | 5 | 35 | 0 | 0 | 25 | 19 | 11 | 25 | 13 | 150 | 143 | 48 | 20 | 1.4 | 56 | 58 | 47 | 46 | 130 | 0 | 50 | 69 | 42 | 110 | 0 | 44 | 10 | 255 | 16 | 11 | 0 | 56 | 0 | 0 | 7 | 0 | 105 | 13.4 | 100 | 105 | 100 | 293 | 81 | 90 | 71 | 2.6 | 176 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 5 | 8 | 144 | 20 | 16 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 0 | 0 | 24 | 0 | 22 | 11 | 5 | 0 | 66 | 199 | 0 | 0 | 193 | 0 | 179 | 0 | 93 | 0 | 210 | 0 | 340 | 70 | 0 | 108 | 69 | 6 |  | 6942.4 | 2897 | 9839.4 | 4222 | 940 | 2104 | 1999 | 265 | 35 | 107 | 150 | 17.4 | 0 | 0
14:00 | 35 | 0 | 200 | 0 | 350 | 101 | 64 | 335 | 314 | 13 | 20 | 370 | 300 | 7 | 0 | 15 | 0 | 0 | 65 | 0 | 7 | 24 | 16 | 10 | 8 | 0 | 6 | 54 | 55 | 35 | 1 | 25 | 19 | 25 | 33 | 41 | 0 | 35 | 0 | 0 | 120 | 8 | 211 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 96 | 38 | 18 | 2 | 100 | 0 | 0 | 330 | 360 | 197 | 26 | 95 | 0 | 52 | 5 | 40 | 0 | 0 | 25 | 19 | 11 | 33 | 18 | 154 | 140 | 57 | 20 | 1 | 56 | 50 | 47 | 46 | 130 | 0 | 59 | 69 | 42 | 125 | 0 | 45 | 10 | 260 | 16 | 8 | 0 | 80 | 0 | 0 | 7 | 0 | 149 | 9.9 | 100 | 105 | 100 | 287 | 82 | 90 | 71 | 4.2 | 200 |  | 940 | 0 | 0 | 0 | 16 | 10 | 0 | 0 | 0 | 5 | 30 | 146 | 22 | 32 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 32 | 0 | 24 | 0 | 21 | 11 | 5 | 0 | 63 | 199 | 0 | 0 | 189 | 0 | 188 | 0 | 95 | 0 | 210 | 0 | 340 | 70 | 0 | 108 | 70 | 7 |  | 7173.1 | 2946 | 10119.1 | 4314 | 940 | 2112 | 2210 | 262 | 35 | 77 | 154 | 15.1 | 0 | 72.89
15:00 | 35 | 0 | 200 | 0 | 350 | 100 | 64 | 370 | 342 | 13 | 20 | 430 | 285 | 8 | 0 | 15 | 0 | 0 | 90 | 0 | 7 | 24 | 25 | 15 | 8 | 0 | 6 | 54 | 56 | 50 | 0 | 25 | 19 | 25 | 33 | 40 | 0 | 34 | 0 | 0 | 120 | 10 | 213 | 0 | 134 | 0 | 0 | 16 | 0 | 0 | 10 | 96 | 38 | 18 | 3 | 100 | 0 | 0 | 360 | 360 | 199 | 26 | 95 | 0 | 52 | 5 | 35 | 0 | 0 | 25 | 18 | 11 | 25 | 18 | 160 | 139 | 85 | 20 | 1.3 | 51 | 58 | 50 | 43 | 163 | 0 | 59 | 69 | 42 | 110 | 0 | 45 | 10 | 300 | 16 | 11 | 0 | 80 | 0 | 0 | 14 | 0 | 149 | 6.2 | 90 | 106 | 100 | 293 | 84 | 90 | 54 | 4 | 220 |  | 940 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 11 | 40 | 146 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 32 | 0 | 35 | 0 | 21 | 10 | 8 | 0 | 63 | 199 | 0 | 0 | 197 | 0 | 199 | 0 | 93 | 0 | 210 | 0 | 414 | 90 | 0 | 108 | 95 | 11 |  | 7452.5 | 3159 | 10611.5 | 4410 | 940 | 2344 | 2368 | 262 | 34 | 82 | 160 | 11.5 | 0 | 72.89
16:00 | 35 | 0 | 200 | 0 | 350 | 101 | 64 | 329 | 339 | 13 | 20 | 380 | 265 | 25 | 0 | 15 | 0 | 0 | 65 | 0 | 7 | 40 | 45 | 50 | 16 | 0 | 6 | 54 | 56 | 55 | 0 | 25 | 19 | 33 | 33 | 40 | 0 | 35 | 0 | 0 | 120 | 25 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 96 | 38 | 18 | 3 | 100 | 0 | 0 | 360 | 360 | 184 | 26 | 100 | 0 | 52 | 5 | 35 | 0 | 0 | 38 | 18 | 8 | 30 | 18 | 162 | 144 | 82 | 20 | 1 | 56 | 58 | 50 | 45 | 163 | 0 | 57 | 69 | 42 | 108 | 0 | 45 | 10 | 260 | 8 | 11 | 0 | 80 | 0 | 0 | 120 | 0 | 149 | 8.3 | 100 | 135 | 113 | 291 | 84 | 90 | 54 | 3.2 | 224 |  | 940 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 12 | 40 | 145 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 90 | 12 | 32 | 0 | 40 | 0 | 21 | 10 | 8 | 0 | 63 | 199 | 0 | 0 | 184 | 0 | 178 | 0 | 92 | 0 | 197 | 0 | 370 | 105 | 0 | 108 | 103 | 18 |  | 7551.5 | 3146 | 10697.5 | 4279 | 940 | 2209 | 2651 | 262 | 35 | 147 | 162 | 12.5 | 0 | 72.94
17:00 | 35 | 0 | 200 | 0 | 320 | 106 | 64 | 328 | 339 | 13 | 20 | 380 | 260 | 7 | 0 | 15 | 38 | 0 | 62 | 0 | 7 | 50 | 45 | 10 | 8 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 40 | 0 | 35 | 0 | 0 | 120 | 25 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 96 | 38 | 18 | 8 | 100 | 0 | 0 | 300 | 300 | 184 | 26 | 96 | 0 | 52 | 5 | 35 | 0 | 0 | 44 | 18 | 8 | 33 | 18 | 154 | 143 | 82 | 20 | 0.4 | 56 | 58 | 53 | 39 | 130 | 0 | 57 | 69 | 42 | 108 | 0 | 45 | 10 | 260 | 16 | 11 | 0 | 80 | 0 | 0 | 80 | 0 | 149 | 3.5 | 100 | 100 | 50 | 291 | 84 | 89 | 17 | 1.1 | 279 |  | 941 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 20 | 40 | 143 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 91 | 12 | 32 | 0 | 8 | 0 | 21 | 11 | 8 | 0 | 63 | 199 | 0 | 0 | 182 | 0 | 179 | 0 | 92 | 0 | 189 | 0 | 340 | 105 | 0 | 35 | 104 | 16 |  | 7245 | 3010 | 10255 | 4180 | 941 | 2154 | 2368 | 262 | 35 | 156 | 154 | 5 | 0 | 72.98
18:00 | 35 | 0 | 200 | 0 | 250 | 106 | 64 | 289 | 258 | 13 | 20 | 300 | 255 | 7 | 0 | 15 | 13 | 0 | 62 | 0 | 7 | 50 | 45 | 10 | 8 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 43 | 0 | 36 | 0 | 0 | 120 | 25 | 204 | 0 | 130 | 0 | 0 | 24 | 0 | 0 | 10 | 96 | 12 | 18 | 8 | 100 | 0 | 0 | 250 | 270 | 184 | 26 | 97 | 0 | 55 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 18 | 150 | 144 | 81 | 20 | 0.2 | 56 | 58 | 53 | 45 | 130 | 0 | 45 | 77 | 42 | 110 | 0 | 44 | 10 | 250 | 16 | 11 | 0 | 80 | 0 | 0 | 80 | 0 | 149 | 0.5 | 100 | 100 | 50 | 200 | 85 | 89 | 17 | 0.2 | 296 |  | 941 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 28 | 21 | 40 | 142 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 90 | 40 | 32 | 0 | 8 | 0 | 22 | 12 | 8 | 0 | 63 | 199 | 0 | 0 | 182 | 0 | 179 | 0 | 94 | 0 | 189 | 0 | 270 | 105 | 0 | 35 | 35 | 16 |  | 6778.9 | 2930 | 9708.9 | 3870 | 941 | 1933 | 2332 | 262 | 36 | 184 | 150 | 0.9 | 0 | 73.02
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 200 | 0 | 280 | 108 | 65 | 285 | 286 | 45 | 20 | 380 | 300 | 9 | 2 | 37 | 38 | 0 | 40 | 0 | 7 | 64 | 105 | 17 | 8 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 17 | 33 | 33 | 49 | 0 | 37 | 0 | 0 | 120 | 25 | 220 | 0 | 140 | 0 | 0 | 24 | 15 | 56 | 34 | 96 | 45 | 18 | 6 | 100 | 0 | 0 | 300 | 300 | 208 | 26 | 97 | 0 | 53 | 5 | 35 | 0 | 13 | 52 | 19 | 11 | 33 | 18 | 184 | 140 | 82 | 20 | 0 | 58 | 58 | 53 | 46 | 100 | 0 | 59 | 78 | 44 | 128 | 0 | 44 | 10 | 250 | 16 | 11 | 0 | 80 | 0 | 0 | 88 | 0 | 149 | 0 | 100 | 105 | 56 | 237 | 85 | 89 | 0 | 0 | 296 |  | 940 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 28 | 40 | 146 | 33 | 110 | 0 | 0 | 55 | 28 | 10 | 90 | 40 | 32 | 17 | 9 | 21 | 22 | 12 | 8 | 0 | 63 | 199 | 16 | 0 | 185 | 0 | 183 | 0 | 96 | 5 | 190 | 0 | 350 | 105 | 0 | 90 | 104 | 4 |  | 7452 | 3397 | 10849 | 4106 | 940 | 2102 | 2768 | 262 | 37 | 450 | 184 | 0 | 0 | 73.06
19:30 | 35 | 0 | 200 | 0 | 300 | 108 | 65 | 345 | 326 | 65 | 20 | 380 | 260 | 35 | 15 | 55 | 38 | 0 | 40 | 0 | 30 | 101 | 145 | 70 | 50 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 49 | 0 | 37 | 0 | 0 | 120 | 25 | 205 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 80 | 96 | 46 | 19 | 6 | 100 | 0 | 0 | 300 | 300 | 217 | 26 | 96 | 0 | 53 | 5 | 35 | 0 | 50 | 52 | 19 | 11 | 33 | 18 | 182 | 145 | 82 | 20 | 0 | 55 | 58 | 53 | 46 | 163 | 0 | 61 | 78 | 44 | 110 | 0 | 45 | 10 | 260 | 16 | 11 | 0 | 100 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 140 | 100 | 293 | 84 | 89 | 0 | 0 | 296 |  | 939 | 14 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 43 | 40 | 147 | 35 | 110 | 0 | 0 | 55 | 43 | 17 | 95 | 40 | 32 | 40 | 24 | 28 | 22 | 12 | 11 | 0 | 63 | 199 | 16 | 17 | 195 | 0 | 192 | 0 | 97 | 43 | 211 | 0 | 350 | 105 | 0 | 108 | 105 | 9 |  | 8240 | 3610 | 11850 | 4228 | 939 | 2219 | 3284 | 262 | 37 | 699 | 182 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 300 | 108 | 65 | 341 | 305 | 95 | 20 | 380 | 260 | 70 | 35 | 55 | 23 | 0 | 37 | 0 | 45 | 85 | 145 | 74 | 73 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 49 | 0 | 37 | 0 | 0 | 120 | 25 | 204 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 100 | 96 | 46 | 19 | 15 | 100 | 0 | 0 | 300 | 300 | 218 | 26 | 96 | 0 | 55 | 5 | 35 | 0 | 50 | 52 | 19 | 11 | 33 | 18 | 176 | 144 | 82 | 20 | 0 | 56 | 58 | 53 | 46 | 100 | 0 | 49 | 78 | 44 | 109 | 0 | 47 | 10 | 260 | 24 | 11 | 0 | 172 | 0 | 0 | 187 | 0 | 149 | 0 | 100 | 163 | 97 | 295 | 85 | 89 | 0 | 0 | 296 |  | 940 | 22 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 55 | 40 | 143 | 37 | 110 | 0 | 0 | 55 | 43 | 33 | 90 | 40 | 32 | 47 | 50 | 28 | 22 | 11 | 11 | 0 | 63 | 199 | 17 | 17 | 188 | 0 | 185 | 0 | 98 | 92 | 206 | 0 | 300 | 105 | 0 | 108 | 105 | 5 |  | 8359 | 3650 | 12009 | 4180 | 940 | 2100 | 3576 | 262 | 37 | 738 | 176 | 0 | 0 | 73.1
21:00 | 35 | 0 | 200 | 0 | 300 | 108 | 66 | 327 | 300 | 65 | 20 | 350 | 290 | 78 | 80 | 55 | 0 | 0 | 40 | 0 | 85 | 101 | 145 | 50 | 73 | 0 | 36 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 49 | 0 | 38 | 0 | 0 | 120 | 25 | 205 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 100 | 96 | 46 | 19 | 25 | 100 | 0 | 0 | 300 | 300 | 215 | 26 | 100 | 0 | 55 | 5 | 35 | 0 | 8 | 52 | 19 | 11 | 33 | 20 | 178 | 144 | 84 | 20 | 0 | 56 | 58 | 52 | 46 | 100 | 0 | 61 | 71 | 45 | 112 | 0 | 47 | 10 | 250 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 100 | 292 | 85 | 89 | 0 | 0 | 296 |  | 939 | 28 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 52 | 40 | 148 | 36 | 110 | 0 | 0 | 55 | 43 | 33 | 90 | 40 | 32 | 44 | 50 | 28 | 22 | 12 | 11 | 0 | 65 | 199 | 17 | 17 | 182 | 0 | 179 | 0 | 98 | 100 | 194 | 0 | 300 | 105 | 0 | 108 | 105 | 0 |  | 8459 | 3635 | 12094 | 4143 | 939 | 2059 | 3777 | 264 | 38 | 696 | 178 | 0 | 0 | 73.14
22:00 | 35 | 0 | 200 | 0 | 350 | 108 | 66 | 348 | 330 | 0 | 20 | 400 | 270 | 0 | 30 | 30 | 150 | 0 | 93 | 0 | 0 | 101 | 145 | 0 | 73 | 0 | 36 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 50 | 0 | 38 | 0 | 0 | 120 | 25 | 206 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 50 | 96 | 46 | 19 | 37 | 100 | 0 | 0 | 330 | 330 | 217 | 26 | 100 | 0 | 53 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 180 | 141 | 86 | 20 | 0 | 55 | 58 | 53 | 46 | 100 | 0 | 60 | 71 | 45 | 109 | 0 | 47 | 10 | 285 | 24 | 11 | 0 | 60 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 100 | 292 | 85 | 89 | 0 | 0 | 296 |  | 940 | 28 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 42 | 40 | 148 | 38 | 110 | 0 | 0 | 55 | 38 | 33 | 90 | 40 | 32 | 43 | 49 | 28 | 22 | 12 | 11 | 0 | 63 | 199 | 17 | 18 | 198 | 0 | 194 | 0 | 97 | 100 | 192 | 0 | 400 | 105 | 0 | 108 | 105 | 0 |  | 8348 | 3748 | 12096 | 4501 | 940 | 2286 | 3216 | 262 | 38 | 673 | 180 | 0 | 0 | 73.18
23:00 | 35 | 0 | 200 | 0 | 350 | 107 | 66 | 327 | 300 | 0 | 20 | 380 | 290 | 0 | 30 | 30 | 220 | 0 | 95 | 0 | 0 | 101 | 145 | 0 | 72 | 0 | 11 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 50 | 0 | 39 | 0 | 15 | 120 | 25 | 210 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 10 | 96 | 46 | 19 | 39 | 100 | 0 | 0 | 300 | 300 | 215 | 26 | 100 | 0 | 55 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 178 | 142 | 83 | 20 | 0 | 56 | 58 | 53 | 46 | 100 | 0 | 61 | 71 | 45 | 120 | 0 | 47 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 100 | 291 | 85 | 89 | 0 | 0 | 296 |  | 940 | 28 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 42 | 40 | 148 | 37 | 110 | 0 | 0 | 55 | 43 | 32 | 90 | 40 | 32 | 43 | 52 | 28 | 22 | 12 | 11 | 0 | 62 | 199 | 17 | 17 | 182 | 0 | 179 | 0 | 97 | 100 | 191 | 0 | 405 | 105 | 0 | 108 | 105 | 0 |  | 8177 | 3725 | 11902 | 4490 | 940 | 2218 | 3100 | 261 | 39 | 676 | 178 | 0 | 0 | 73.22
24:00 | 35 | 0 | 200 | 0 | 350 | 107 | 66 | 343 | 349 | 0 | 20 | 400 | 280 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 0 | 101 | 146 | 0 | 72 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 50 | 0 | 40 | 0 | 40 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 24 | 85 | 68 | 10 | 96 | 47 | 20 | 40 | 100 | 0 | 0 | 300 | 330 | 215 | 26 | 100 | 0 | 55 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 176 | 142 | 83 | 20 | 0 | 58 | 58 | 50 | 46 | 163 | 0 | 61 | 71 | 46 | 116 | 0 | 47 | 10 | 54 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 100 | 293 | 85 | 89 | 0 | 0 | 296 |  | 940 | 28 | 0 | 0 | 115 | 20 | 0 | 0 | 38 | 42 | 40 | 148 | 37 | 110 | 0 | 0 | 60 | 43 | 32 | 90 | 40 | 32 | 43 | 50 | 28 | 22 | 12 | 11 | 0 | 63 | 199 | 17 | 17 | 194 | 0 | 197 | 0 | 96 | 100 | 201 | 0 | 410 | 105 | 0 | 108 | 105 | 0 |  | 8058 | 3793 | 11851 | 4565 | 940 | 2147 | 3024 | 262 | 40 | 697 | 176 | 0 | 0 | 73.26
KWH | 814000 | 0 | 4811000 | 0 | 7490182 | 2440090 | 1436288 | 8182560 | 7868000 | 273600 | 484500 | 8938375 | 6663476 | 299520 | 222360 | 339249 | 1851292 | 0 | 1775000 | 0 | 229440 | 848016 | 1007520 | 341793 | 405120 | 0 | 236640 | 1024200 | 825883 | 708860 | 355356 | 525000 | 472860 | 728900 | 817500 | 713484 | 0 | 844620 | 0 | 100000 | 3000000 | 281262 | 4920636 | 0 | 3023110 | 0 | 0 | 453120 | 416752 | 355861 | 501600 | 1255680 | 644160 | 428016 | 483840 | 2263894 | 0 | 0 | 7795000 | 7906500 | 4957000 | 501818 | 2333060 | 0 | 1272000 | 120000 | 739068 | 0 | 76072 | 583627 | 440784 | 257040 | 605600 | 383420 | 3351360 | 3392320 | 1215360 | 437544 | 9750 | 1337000 | 1383000 | 1096200 | 1048968 | 3282455 | 0 | 1397481 | 1447680 | 1022400 | 2806900 | 96000 | 1019760 | 195120 | 6513750 | 410360 | 258960 | 0 | 1033750 | 0 | 0 | 1459200 | 0 | 1838880 | 122040 | 1696320 | 2108640 | 1242840 | 5995000 | 1842000 | 1832400 | 496797 | 29280 | 4686981 |  | 22593455 | 136800 | 0 | 0 | 1255680 | 698880 | 0 | 0 | 265920 | 301824 | 593250 | 3493396 | 622530 | 1229760 | 0 | 0 | 1365000 | 374952 | 174571 | 1604844 | 4297530 | 456706 | 274124 | 549120 | 196191 | 509040 | 279072 | 196596 | 0 | 1525527 | 4863600 | 89000 | 84000 | 4609427 | 0 | 4480473 | 0 | 2281099 | 550880 | 3345100 | 0 | 8401272 | 1851360 | 0 | 1729824 | 1968624 | 87360 |  | 166180100 | 77336787 | 243516887 | 101726767 | 22593455 | 51518825 | 50874352 | 6389127 | 844620 | 6057311 | 3351360 | 161070 | 0
Fuel Cost | 700040 | 0 | 4137460 | 0 | 4793716.48 | 1976472.9 | 1350110.72 | 4991361.6 | 4799480 | 2629296 | 663765 | 5988711.25 | 101218200.44 | 1880985.6 | 1485364.8 | 2072811.39 | 1203339.8 | 0 | 1970250 | 0 | 1434000 | 5588425.44 | 9742718.4 | 2177221.41 | 2426668.8 | 0 | 1578388.8 | 7302546 | 5161768.75 | 4444552.2 | 266517 | 393750 | 0 | 0 | 0 | 6749558.64 | 0 | 0 | 0 | 110000 | 3300000 | 2663551.14 | 3247619.76 | 0 | 3476576.5 | 0 | 0 | 3982924.8 | 4488419.04 | 3462527.53 | 3104904 | 8111692.8 | 4212806.4 | 363813.6 | 0 | 2060143.54 | 0 | 0 | 4832900 | 5455485 | 3469900 | 346254.42 | 2239737.6 | 0 | 1093920 | 110400 | 606035.76 | 0 | 824620.48 | 4330512.34 | 339403.68 | 192780 | 466312 | 287565 | 22923302.4 | 2544240 | 11169158.4 | 336908.88 | 0 | 1390480 | 1438320 | 1052352 | 944071.2 | 2560314.9 | 0 | 1593128.34 | 1549017.6 | 1124640 | 3199866 | 122880 | 948376.8 | 181461.6 | 4168800 | 307770 | 196809.6 | 0 | 7505025 | 0 | 0 | 10433280 | 0 | 0 | 0 | 0 | 19694697.6 | 11608125.6 | 5215650 | 0 | 0 | 0 | 0 | 0 |  | 115226620.5 | 3987720 | 0 | 0 | 10409587.2 | 11237990.4 | 0 | 0 | 2994259.2 | 3555486.72 | 4674810 | 2410443.24 | 616304.7 | 9100224 | 0 | 0 | 1433250 | 4293200.4 | 1871401.12 | 14379402.24 | 37173634.5 | 4064683.4 | 2919420.6 | 5447270.4 | 2309168.07 | 559944 | 262327.68 | 148823.172 | 0 | 9259948.89 | 18773496 | 2868470 | 2248680 | 3134410.36 | 0 | 3136331.1 | 0 | 0 | 9546750.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 368516962.73 | 288044058.292 | 656561021.022 | 75571747.252 | 115226620.5 | 30238995.53 | 313383426.25 | 28033444.89 | 0 | 71183484.2 | 22923302.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 200 | 0 | 340 | 101 | 66 | 327 | 313 | 13 | 20 | 370 | 230 | 7 | 0 | 15 | 0 | 0 | 62 | 0 | 7 | 24 | 16 | 10 | 8 | 0 | 6 | 54 | 55 | 35 | 22 | 0 | 20 | 25 | 33 | 41 | 0 | 35 | 0 | 0 | 120 | 8 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 51 | 37 | 18 | 3 | 100 | 0 | 0 | 330 | 360 | 217 | 26 | 95 | 0 | 50 | 5 | 35 | 0 | 0 | 25 | 19 | 11 | 16 | 12 | 140 | 144 | 48 | 20 | 2.3 | 56 | 58 | 47 | 46 | 130 | 0 | 61 | 69 | 42 | 110 | 0 | 44 | 10 | 250 | 16 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 47 | 17.4 | 100 | 105 | 70 | 296 | 81 | 90 | 71 | 5.3 | 162 |  | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 4 | 8 | 144 | 18 | 16 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 0 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 64 | 199 | 0 | 0 | 188 | 0 | 179 | 0 | 92 | 0 | 104 | 0 | 340 | 35 | 0 | 108 | 71 | 4 |  | 9487 | DayPeak
Yesterday Evening Peak | 35 | 0 | 200 | 0 | 300 | 108 | 66 | 327 | 300 | 65 | 20 | 350 | 290 | 78 | 80 | 55 | 0 | 0 | 40 | 0 | 85 | 101 | 145 | 50 | 73 | 0 | 36 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 49 | 0 | 38 | 0 | 0 | 120 | 25 | 205 | 0 | 100 | 0 | 0 | 24 | 85 | 68 | 100 | 96 | 46 | 19 | 25 | 100 | 0 | 0 | 300 | 300 | 215 | 26 | 100 | 0 | 55 | 5 | 35 | 0 | 8 | 52 | 19 | 11 | 33 | 20 | 178 | 144 | 84 | 20 | 0 | 56 | 58 | 52 | 46 | 100 | 0 | 61 | 71 | 45 | 112 | 0 | 47 | 10 | 250 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 100 | 292 | 85 | 89 | 0 | 0 | 296 |  | 939 | 28 | 0 | 0 | 115 | 0 | 0 | 0 | 38 | 52 | 40 | 148 | 36 | 110 | 0 | 0 | 55 | 43 | 33 | 90 | 40 | 32 | 44 | 50 | 28 | 22 | 12 | 11 | 0 | 65 | 199 | 17 | 17 | 182 | 0 | 179 | 0 | 98 | 100 | 194 | 0 | 300 | 105 | 0 | 108 | 105 | 0 |  | 12094 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 360 | 108 | 66 | 412 | 360 | 110 | 20 | 450 | 335 | 100 | 100 | 55 | 200 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 90 | 120 | 25 | 0 | 225 | 135 | 0 | 0 | 24 | 85 | 68 | 100 | 100 | 46 | 20 | 25 | 100 | 0 | 0 | 360 | 360 | 221 | 8 | 100 | 0 | 55 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 184 | 144 | 87 | 20 | 0 | 60 | 58 | 50 | 44 | 163 | 0 | 66 | 86 | 45 | 130 | 19 | 45 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 100 | 105 |  | 300 |  | 953 | 32 | 0 | 0 | 115 | 225 | 0 | 0 | 38 | 80 | 40 | 147 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 95 | 50 | 43 | 44 | 52 | 28 | 22 | 12 | 11 | 0 | 62 | 200 | 17 | 18 | 214 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 360 | 108 | 66 | 412 | 360 | 110 | 20 | 450 | 335 | 100 | 100 | 55 | 200 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 90 | 120 | 25 | 0 | 225 | 135 | 0 | 0 | 24 | 85 | 68 | 100 | 100 | 46 | 20 | 6 | 100 | 0 | 0 | 360 | 360 | 221 | 8 | 100 | 0 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 137 | 144 | 87 | 20 | 2 | 60 | 58 | 50 | 44 | 163 | 0 | 66 | 86 | 45 | 130 | 19 | 45 | 10 | 341 | 25 | 11 | 0 | 100 | 100 | 100 | 100 | 100 | 149 | 20 | 100 | 200 | 150 | 285 | 100 | 100 | 105 | 3 | 300 |  | 953 | 0 | 0 | 0 | 115 | 40 | 0 | 0 | 0 | 0 | 40 | 147 | 33 | 110 | 0 | 0 | 60 | 0 | 0 | 95 | 6 | 32 | 44 | 52 | 0 | 22 | 12 | 11 | 0 | 62 | 200 | 0 | 0 | 214 | 0 | 220 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 0
Generation at 08:00(Today) | 35 | 0 | 201 | 0 | 270 | 72 | 50 | 327 | 270 | 0 | 20 | 320 | 270 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 35 | 18 | 17 | 22 | 25 | 22 | 25 | 33 | 50 | 0 | 38 | 0 | 90 | 120 | 0 | 0 | 219 | 20 | 0 | 0 | 16 | 0 | 0 | 10 | 10 | 46 | 21 | 6 | 100 | 0 | 0 | 270 | 270 | 185 | 8 | 30 | 0 | 5 | 5 | 35 | 0 | 0 | 8 | 16 | 11 | 33 | 18 | 126 | 144 | 84 | 20 | 0.5 | 60 | 58 | 50 | 46 | 100 | 0 | 61 | 72 | 45 | 84 | 0 | 45 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10.7 | 90 | 106 | 10 | 250 | 87 | 90 | 7 | 2.8 | 300 | 0 | 940 | 0 | 0 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 147 | 27 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 62 | 199 | 0 | 0 | 156 | 0 | 143 | 0 | 95 | 0 | 159 | 0 | 270 | 17 | 0 | 34 | 70 | 0 | 0
199
| Minimum Generation |  | 7804 | 7:00
| Highest Generation |  | 12096 | 22:00
| Day Peak Generation |  | 9487 | 12:00
| Evening Peak Generation |  | 12094 | 21:00
| HVDC Max Flow |  | 948 | 1:00
| HVDC EvPeak Flow |  | 939 | 21:00
| Load factor L.F |  | 83.88%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-06-17
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9487 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8670 | MW
Evening Peak Generation : |  | 12094 | MW Hour : | 21:00 | Available Max Generation : |  | 15124 | MW
E.P. Demand (at gen end) : |  | 12094 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12600 | MW
Maximum Generation : |  | 12096 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2524 | MW
Total Gen. (MKWH) : |  | 243.5169 | System Load Factor : | 83.88% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -490 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-06-17
Actual : | 74.54 | Ft.(MSL) , | Rule curve : | 80.22 | Ft.( MSL )
Gas Consumed : | Total = | 1348.08 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 105810742.782
|  | Coal : | 28033444.89 | Oil : | 384566910.45 | Total : | 518411098.122
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4496.5547 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1533.0549 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1374.2751 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1242.0251 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1122.2614 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 905.6353 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 501.2683 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 233.0413 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 698.4954 |  |  | 0 | 0%
Total | 0 |  | 12106.6115 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-1 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal # 3,5
|  |  |  | 4) Bheramara 410 MW. | 10) Shahjibazar 330 MW
5) Siddhirganj ST
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sirajganj #3 CCPP GT & ST were synchronized at 10:02 & 11:16 respectively.
b) Rangpur 33 kV Bus section-2 was shut down at 08:40 due to red hot maintenance at bus Y-phase isolator of |  |  |  |  | About 40 MW power interruption occurred under Rangpur S/S
33 kV Maliganj feeder and was switched on at 09:40. |  |  |  |  | area from 08:40 to 09:40.
c) Sylhet-Chatak 132 kV Ckt-1 was under shut down from 11:05 to 13:59 for C/M.
d) Dhamrai 132/33 kV T-1 & T-2 transformers tripped at 11:43 due to 33 kV feeder fault ( Sky wire break) and was |  |  |  |  | About 40 MW power interruption occurred under Dhamrai S/S
switched on at 12:03. |  |  |  |  | area from 11:43 to 12:03.
e) Kabirpur 132/33 kV T-2 transformer was shut down at 09:05 due to red hot maintenance at 33 kV Bus isolator
of 33 kV EPZ feeder and was switched on at 10:30.
f) Kaliakoir-Kabirpur 132 kV Ckt-1 tripped at 10:43 showing Gen.trip, CB protection at Kabirpur end & dist.Z1, E/F |  |  |  |  | About 40 MW power interruption occurred under Kabirpur S/S
relay at Kaliakoir end and was switched on at 12:40. |  |  |  |  | area from 10:43 to 12:40.
g) After maintenance Ghorasal-Ashuganj 230 kV Ckt-2 was switched on at 10:11.
h) Sikalbaha 132/33 kV T-3 transformer tripped at 14:37 showing O/C, E/F relay from both end and was switched |  |  |  |  | About 15 MW power interruption occurred under Sikalbaha S/S
on at 15:14. |  |  |  |  | area from 14:37 to 15:14.
i) Faridpur 132/33 kV T-1 transformer was shut down at 15:04 due to red hot maintenance at 33 kV Y-phase |  |  |  |  | About 30 MW power interruption occurred under Faridpur S/S
incomer bus isolator and was switched on at 15:50. |  |  |  |  | area from 15:05 to 15:50.
j) After maintenance Madertek 132/33 kV T-2 transformer was switched on at 18:34.
k) After maintenance Dhanmondi 132/33 kV T-4 transformer was switched on at 20:38.
l) Bibiyana-2 CCPP ST tripped at 23:18 showing bearing vibration high and was synchronized at 03:05(17/6/19).
m) After maintenance Raozan #1 was synchronized at 22:54.
n) Fenchuganj 132/33 kV T-1 transformer tripped at 02:53(17/6/19) showing no relay and was switched
on at 03:16(17/06/2019).
o) After maintenance Khulna-225 MW CCPP GT was synchronized at 23:19.
p) Bagerhat 132/33 kV T-2 transformer was shut down at 06:19(17/6/19) due to red hot maintenance at CB |  |  |  |  | About 21 MW power interruption occurred under Bagerhat S/S
DS loop and was switched on at 08:25(17/6/19). |  |  |  |  | area from 06:19 to 08:25(17/6/19).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 814000 | Gas shortage
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 200 | 4811000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7490182
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 66 | 1436288 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 108 | 2440090
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 484500 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 327 | 8182560 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 65 | 273600 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 300 | 7868000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 350 | 8938375 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 78 | 299520 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 290 | 6663476 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 222360 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 339249
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 341793 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 355356
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 40 | 1775000 | Frequency control
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 85 | 229440 | Low demand
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 1851292 | under maint.
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 101 | 848016
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 36 | 236640 | Low demand
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1024200
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 145 | 1007520
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 825883
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 708860
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 73 | 405120 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 997860 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 728900
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 817500
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 49 | 713484
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 200 | 1033750 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 1838880
37 | Gazipur 100 MW |  | RPCL | 100 MW | 105 | 89 | 1832400 | Engine problem
| Dhaka area Total |  |  |  | 5803 | 3587 | 67835094
38 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 100000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
39 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 281262
40 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122040
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 644160
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 844620 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4920636 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 3023110 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 24 | 453120 | Engine problem
47 | Baraka Sikalbaha PL |  | IPP | 105 MW | 105 | 0 | 496797 | Reserve
48 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 85 | 416752
49 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 355861
50 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 501600
51 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1696320
52 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 428016
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 483840
53 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 96 | 1255680
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 29280
| Anwara United |  | United Group | 300 MW | 0 | 296 | 4686981 | on test
| Chattogram area Total |  |  |  | 1786 | 1347 | 23740075
54 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2263894
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 215 | 4957000 | FGMO
56 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7795000 | Frequency control
57 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7906500 | Frequency control
58 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 55 | 1272000
60 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Engine problem
61 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 26 | 501818 | Gas shortage
62 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 739068 | Engine problem
63 | Midland 150MW |  | IPP | 23*7.015 | 150 | 100 | 1242840 | Low demand
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 8 | 76072 | Low demand
66 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2333060
67 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 2108640
68 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440784
69 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257040
** | Tripura |  | Imported power | 0 | 160 | 178 | 3351360
70 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 605600
71 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 583627
72 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 383420 | Engine problem
73 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1757 | 36937723
74 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 144 | 3392320 | GT-1 Under maint
75 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 437544
76 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 84 | 1215360
77 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 9750
78 | United Mymensingh PPL |  | IPP | 200 | 200 | 200 | 1459200
79 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 85 | 1842000 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 533 | 8356174
80 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1337000
81 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1383000
82 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3282455 | Frequency control
83 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 52 | 1096200
85 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 46 | 1048968
86 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 258960
87 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1397481 | FGMO
88 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 71 | 1447680 | Engine problem
89 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 1022400
90 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 112 | 2806900 | FGMO
91 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 96000
92 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 1019760
93 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 410360
94 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 250 | 6513750 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 292 | 5995000 | On test
95 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 195120
| Sylhet Area Total |  |  |  | 1549 | 1235 | 29311034
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 28 | 136800 | Low demand
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 939 | 22593455
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1255680
98 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 38 | 265920
99 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 698880 | Reserve
100 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 52 | 301824 | Low demand
101 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 593250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 550880
104 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1851360
105 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 105 | 1968624
| Khulna Area Total |  |  |  | 2314 | 1522 | 30216673
106 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1229760
107 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
108 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 622530
109 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 148 | 3493396 | FGMO
110 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 2281099
| Barisal Area Total |  |  |  | 462 | 392 | 7626785
111 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1365000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 374952
113 | Bera Peaking |  | PDB | 9*8.29 | 71 | 33 | 174571
114 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 4297530 | Engine problem
115 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 32 | 456706 | Engine problem
116 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 274124
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4609427 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4480473 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 3345100 | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 8401272 | Frequency control
121 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 28 | 196191 | Engine problem
122 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 509040
123 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 12 | 279072
124 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 196596
125 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 549120
126 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 1604844
127 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
128 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 108 | 1729824
| Rajshahi Area Total |  |  |  | 2070 | 1423 | 32843842
129 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 65 | 1525527
130 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 199 | 4863600
131 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 89000
132 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 84000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 0 | 87360
| Rangpur Area Total |  |  |  | 484 | 298 | 6649487
| Total |  |  |  | 17996 | 12094 | 243516887
| Eastern Grid Total |  |  |  | 12666 | 8459 | 166180100
| Western Grid Total |  |  |  | 5330 | 3635 | 77336787
| National Grid Total |  |  |  | 17996 | 12094 | 243516887
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-16
| (a) ENTIRE EASTERN GRID : |  | 7795 | MW | (b) ENTIRE WESTERN GRID : |  | 3817 | MW
| i) Dhaka area |  | 4092 | MW | i) Khulna area |  | 1465 | MW
| ii) Chittagong area |  | 1172 | MW | ii) Rajshahi area |  | 1276 | MW
| iii) Comilla area |  | 1088 | MW | iii) Barisal area |  | 344 | MW
| iv) Mymensingh area |  | 933 | MW | iv) Rangpur area |  | 732 | MW
| v) Sylhet area |  | 510 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11612 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 116 | 1700 | Jamalpur | 126 | 2100 | Jessore | 116 | 2000
2 | Munsiganj | 124 | 2100 | Sherpur | 102 | 2200 | Jhenida | 113 | 2000
3 | Sonargaon | 48 | 100 | Srimongal | 40 | 2000 | Bottail | 134 | 1930
4 | Shyampur | 152 | 1600 | Shahjibazar | 124 | 2100 | G.K Project | 56 | 2000
5 | Bhulta | 167 | 1000 | Fenchuganj | 52 | 1930 | Faridpur | 174 | 2000
6 | Madanganj | 45 | 1200 | Kulawara | 47 | 1930 | Madaripur | 124 | 2200
7 | Shitalakhya | 102 | 1600 | Sylhet | 138 | 1900 | Gopalganj | 98 | 2100
8 | Rahim steel | 12 | 1400 | Chatak | 33 | 2100 | Bagerhat | 81 | 2200
9 | Matuail | 83 | 1200 | Sunamganj | 34 | 2000 | Mongla | 36 | 100
10 | Ghorasal | 85 | 2100 | Biani Bazar | 47 | 2100 | Satkhira | 102 | 2000
11 | Narsingdi | 136 | 2100 | Comilla (S) | 184 | 1900 | Gallamari | 53 | 1300
12 | Haripur (SBU) | 86 | 900 | Comilla(N) | 125 | 1930 | Magura | 51 | 2000
13 | Ullon | 86 | 1500 | Chandpur | 110 | 2400 | Chuadanga | 80 | 100
14 | Hasnabad | 210 | 2100 | Feni | 122 | 1900 | Barisal | 114 | 1930
15 | Magbazar | 133 | 1700 | Chowmuhani | 178 | 2100 | Patuakhali | 104 | 2100
16 | Maniknagar | 116 | 1600 | Ashuganj | 53 | 2200 | Bhandaria | 58 | 2200
17 | Bangabhaban | 38 | 1300 | Daudkandi | 128 | 1930 | Barisal (N) | 44 | 2100
18 | Narinda | 90 | 1700 | B.Baria | 146 | 2200 | Sariatpur | 31 | 2300
19 | Dhanmondi | 181 | 1300 | Ramganj | 94 | 2100 | Benapol | 43 | 2000
20 | Lalbag | 171 | 1700 | Madunaghat | 61 | 1830 | Borhan Uddin | 38 | 2200
21 | Madartek | 60 | 2100 | Hathazari | 104 | 1930 | Ishurdi | 65 | 2100
22 | Mirpur | 112 | `1930 | Khulshi | 207 | 1600 | Ruppur Paromanobik | 2 | 700
23 | Kalyanpur | 123 | 1930 | Halishahar | 153 | 1500 | Natore | 135 | 2100
24 | Gulshan | 166 | 1600 | Baraulia | 136 | 2100 | Bogra | 254 | 2100
25 | Uttara | 84 | 1900 | Sikalbaha | 33 | 2100 | Noagaon | 116 | 2100
26 | Uttara New | 19 | 1600 | Dohazari | 80 | 2000 | Rajshahi | 164 | 2100
27 | Kamrangirchar | 69 | 1930 | Cox'sbazar | 96 | 2000 | C.Nawabganj | 175 | 100
28 | Savar | 143 | 1600 | Chandraghona | 28 | 1930 | Amnura | 37 | 2000
29 | Bhasantec | 169 | 1500 | Kaptai | 4.5 | 1930 | Pabna | 119 | 2000
30 | Agargaon | 66 | 1600 | A. Khaer Stl. | 0 | 1200 | Shahjadpur | 92 | 2000
31 | Satmosjid | 108 | 2000 | Bakulia | 106 | 1930 | Serajganj | 100 | 2000
32 | Tongi | 167 | 1500 | Julda | 20 | 900 | Niyamatpur | 63 | 2000
33 | Kabirpur | 219 | 1600 | TK chemical | 2.4 | 1000 | Joypurhat | 48 | 2100
34 | Basundhara | 134 | 1500 | Modern Steel | 11 | 200 | Mohastangor | 16 | 2000
35 | Manikganj | 90 | 2100 | Shahmirpur | 31 | 2100 | Rangpur | 142 | 2000
36 | Joydevpur | 227 | 1930 | Khagrachhari | 20 | 2000 | Lalmonirhat | 86 | 2000
37 | New Tongi | 101 | 1500 | Matarbari | 29 | 2100 | Saidpur | 104 | 2000
38 | Korda | 262 | 2100 | Baroiar Hat | 30 | 1930 | Purbasadipur | 104 | 2100
39 | Dhamrai | 58 | 2000 | Rangamati | 12 | 1900 | Thakurgaon | 77 | 2100
40 | Valuka | 102 | 2000 | Abul Khair 230 | 146 | 1300 | Palashbari | 115 | 2100
41 | Tangail | 190 | 2000 | BSRM | 110 | 1800 | Barapukuria | 51 | 2000
42 | Mymensing | 230 | 2100 | Goalpara | 28 | 2100 | Panchagar | 40 | 1930
43 | Kishorganj | 120 | 2200 | Central (S) | 96 | 1930 | Joldhaka | 20 | 2100
44 | Netrokona | 100 | 2100 | Noapara | 101 | 2100
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-16
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 395 | 18:00 | 386 | 16:00 | Kaliakoir | 377 | 6:00 | 364
2 | Bheramara | 392 | 8:00 | 383 | 1:00 | Bhulta | 394 | 5:00 | 379
3 | Ashuganj(N) | 398 | 5:00 | 386 | 14:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 16:00
1 | Ghorasal | 232 | 1:00 | 230 | 9:00 | Hathazari | 223 | 4:00 | 219
2 | Ishurdi | 235 | 9:00 | 222 | 22:00 | Megnaghat | 230 | 1:00 | 222
3 | Ashuganj | 240 | 2:00 | 234 | 10:00 | Fenchuganj | 238 | 5:00 | 234
4 | Serajganj | 233 | 7:00 | 225 | 21:00 | Siddhirganj | 230 | 5:00 | 219
5 | Baghabari | 230 | 7:00 | 222 | 22:00 | Maniknagar | 228 | 5:00 | 216
6 | Barapukuria | 234 | 7:00 | 222 | 20:00 | Old Airport | 225 | 5:00 | 215
7 | Bogra | 225 | 9:00 | 211 | 21:00 | Barisal | 234 | 17:00 | 226
8 | Khulna South | 233 | 18:30 | 216 | 20:00 | AKSML | 221 | 20:00 | 214
9 | Rampura | 229 | 4:00 | 218 | 15:00 | BSRM | 223 | 6:00 | 216
10 | Haripur | 228 | 5:00 | 219 | 13:00 | Bibiyana | 236 | 2:00 | 230
11 | Hasnabad | 227 | 8:00 | 218 | 15:00 | Bhulta | 231 | 6:00 | 219
12 | Aminbazar | 227 | 3:00 | 217 | 14:00 | Ashuganj (S) | 238 | 5:00 | 232
13 | Tongi | 225 | 4:00 | 217 | 15:00 | Kaliakoir | 229 | 6:00 | 220
14 | Comilla (N) | 235 | 3:00 | 228 | 10:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 132 | 100 | 126 | 1500 | Hathazari | 132 | 400 | 128
2 | Munsiganj | 135 | 2000 | 126 | 1500 | Khulshi | 130 | 2000 | 126
3 | Megnaghat | 130 | 100 | 126 | 1000 | Halishahar | 134 | 2000 | 128
4 | Shyampur | 132 | 200 | 125 | 1500 | Baraulia | 130 | 600 | 126
5 | Bhulta | 129 | 500 | 120 | 1000 | Sikalbaha | 134 | 1930 | 129
6 | Madanganj | 136 | 2000 | 126 | 1000 | Dohazari | 132 | 1830 | 127
7 | Shitalakhya | 139 | 2000 | 127 | 1000 | Cox'sbazar | 126 | 1100 | 120
8 | Rahim steal | 133 | 100 | 127 | 1600 | Chandraghona | 132 | 1930 | 129
9 | Matuail | 132 | 600 | 126 | 1200 | Kaptai | 132 | 1930 | 130
10 | Ghorasal | 138 | 700 | 136 | 100 | A. Khaer Stl. | 130 | 1800 | 127
11 | Narsinghdi | 128 | 300 | 123 | 1500 | Bakulia | 132 | 1930 | 128
12 | Haripur (SBU) | 133 | 100 | 128 | 1600 | Julda | 134 | 2100 | 128
13 | Ullon | 135 | 600 | 126 | 1700 | TK Chemical | 134 | 1400 | 131
14 | Hasnabad | 135 | 2100 | 127 | 1000 | Modern Steel | 134 | 1930 | 128
15 | Magbazar | 136 | 600 | 125 | 1700 | Shahmirpur | 133 | 2000 | 129
16 | Maniknagar | 132 | 600 | 123 | 1600 | Khagrachhari | 131 | 1830 | 128
17 | Bangabhaban | 132 | 600 | 123 | 1600 | Matarbari | 128 | 1100 | 120
18 | Narinda | 132 | 600 | 123 | 1600 | Baroiar Hat | 130 | 400 | 125
19 | Dhanmondi | 135 | 600 | 126 | 1700 | Rangamati | 131 | 300 | 128
20 | Lalbag | 134 | 600 | 126 | 1500 | Goalpara | 138 | 1830 | 124
21 | Madartek | 136 | 700 | 126 | 1700 | Central s/s | 137 | 1830 | 124
22 | Mirpur | 135 | 600 | 126 | 1500 | Noapara | 133 | 1830 | 120
23 | Kalyanpur | 136 | 200 | 128 | 1600 | Jessore | 128 | 1830 | 112
24 | Gulshan | 134 | 300 | 126 | 1200 | Jhenida | 128 | 1830 | 108
25 | Uttara | 133 | 600 | 124 | 1200 | Bottail | 132 | 900 | 118
26 | Uttara New | 131 | 300 | 124 | 1500 | G.K.Project | 138 | 900 | 127
27 | Kamrangirchar | 133 | 300 | 128 | 1000 | Faridpur | 132 | 1830 | 119
28 | Savar | 131 | 100 | 125 | 1000 | Madaripur | 135 | 1700 | 123
29 | Bhasantec | 132 | 600 | 122 | 1600 | Gopalganj | 142 | 1700 | 131
30 | Agargaon | 132 | 200 | 123 | 1600 | Bagerhat | 131 | 1830 | 118
31 | Satmosjid | 132 | 200 | 123 | 1500 | Mongla | 133 | 1800 | 119
32 | Tongi | 134 | 2100 | 127 | 1500 | Satkhira | 136 | 1830 | 119
33 | Kabirpur | 136 | 400 | 126 | 2100 | Gallamari | 137 | 1830 | 124
34 | Basundhara | 130 | 100 | 123 | 1600 | Magura | 125 | 900 | 105
35 | Manikganj | 134 | 1830 | 128 | 1600 | Chuadanga | 121 | 1830 | 100
36 | Joydevpur | 138 | 1930 | 132 | 1400 | Barisal | 137 | 1830 | 130
37 | New Tongi | 132 | 100 | 125 | 1500 | Patuakhali | 136 | 1830 | 125
38 | Kodda | 133 | 2100 | 123 | 1600 | Bhandaria | 136 | 1830 | 124
39 | Dhamrai | 136 | 600 | 130 | 1930 | Barisal (N) | 138 | 1700 | 130
40 | Valuka | 128 | 100 | 115 | 2200 | Sariatpur | 134 | 1700 | 119
41 | Tangail | 136 | 400 | 123 | 2200 | Benapol | 128 | 1800 | 110
42 | Mymensing | 130 | 1830 | 118 | 2100 | Ishurdi | 137 | 1700 | 127
43 | Kishorganj | 130 | 100 | 121 | 2200 | Ruppur Paromanobik | 138 | 1700 | 131
44 | Netrokona | 130 | 600 | 117 | 2100 | Natore | 134 | 1830 | 122
45 | Jamalpur | 137 | 1700 | 125 | 300 | Bogra | 134 | 1300 | 121
46 | Sherpur | 134 | 1500 | 123 | 800 | Noagaon | 129 | 1900 | 115
47 | Srimongal | 137 | 500 | 134 | 1930 | Rajshahi | 132 | 1800 | 120
48 | Shahjibazar | 136 | 800 | 131 | 2200 | C.Nawabganj | 130 | 1800 | 118
49 | Fenchuganj | 136 | 100 | 133 | 1930 | Amnura | 134 | 1930 | 119
50 | Khulawara | 135 | 100 | 131 | 2200 | Pabna | 134 | 1700 | 126
51 | Sylhet | 135 | 100 | 132 | 2100 | Shahjadpur | 139 | 1700 | 133
52 | Chatak | 135 | 800 | 131 | 1900 | Serajganj | 133 | 1800 | 125
53 | Sunamganj | 134 | 500 | 129 | 2100 | Niyamatpur | 126 | 1100 | 109
54 | Biani Bazar | 136 | 900 | 129 | 2100 | Joypurhat | 128 | 900 | 113
55 | Comilla(s) | 126 | 600 | 121 | 1200 | Mohastangor | 132 | 900 | 119
56 | Comilla(n) | 136 | 2100 | 134 | 900 | Rangpur | 129 | 600 | 112
57 | Chandpur | 134 | 1100 | 130 | 700 | Lalmonirhat | 129 | 600 | 108
58 | Feni | 129 | 700 | 125 | 2200 | Saidpur | 128 | 700 | 112
59 | Chowmuhani | 127 | 700 | 120 | 2200 | Purbasadipur | 130 | 400 | 110
60 | Ashuganj | 137 | 600 | 133 | 2100 | Thakurgaon | 127 | 600 | 104
61 | Daudkandi | 132 | 700 | 126 | 1500 | Palashbari | 129 | 1830 | 115
62 | B.Baria | 135 | 600 | 126 | 2200 | Barapukuria | 134 | 1830 | 122

## L-Curve
Date | 2019-06-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 240 | 8058 | 3793 | 11851 |  |  |  | QF-LDC-12
0:30 | 260 | 7169 | 3553 | 10722 | Date: | 2019-06-16
1:00 | 280 | 6280 | 3313 | 9593
1:30 | 320 | 6196.5 | 3185.5 | 9382
2:00 | 360 | 6113 | 3058 | 9171
2:30 | 365 | 6036.5 | 3054.5 | 9091 | [5 empty] | Gen. at Eve. Peak | 12094 | 12094 MW (21:00 )
3:00 | 370 | 5960 | 3051 | 9011 | [6 empty] | 21:00
3:30 | 425 | 5934 | 2920.5 | 8854.5 | [5 empty] | Gen. at Day Peak | 9487 | 9487 MW (12:00 )
4:00 | 480 | 5908 | 2790 | 8698 | [6 empty] | 12:00
4:30 | 485 | 5909.5 | 2749 | 8658.5 | [5 empty] | Highest Generation | 12096
5:00 | 490 | 5911 | 2708 | 8619 | [6 empty] | 22:00
5:30 | 455 | 5700 | 2554.5 | 8254.5
6:00 | 420 | 5489 | 2401 | 7890
6:30 | 420 | 5462.5 | 2384.5 | 7847
7:00 | 420 | 5436 | 2368 | 7804
7:30 | 380 | 5511.25 | 2379 | 7890.25
8:00 | 340 | 5586.5 | 2390 | 7976.5
8:30 | 205 | 5825.5 | 2475.5 | 8301
9:00 | 70 | 6064.5 | 2561 | 8625.5
9:30 | 90 | 6241.05 | 2565 | 8806.05
10:00 | 110 | 6417.6 | 2569 | 8986.6
10:30 | 135 | 6496.25 | 2610.5 | 9106.75
11:00 | 160 | 6574.9 | 2652 | 9226.9
11:30 | 155 | 6666.45 | 2690.5 | 9356.95
12:00 | 150 | 6758 | 2729 | 9487
12:30 | 165 | 6850.2 | 2813 | 9663.2
13:00 | 180 | 6942.4 | 2897 | 9839.4
13:30 | 190 | 7057.75 | 2921.5 | 9979.25
14:00 | 200 | 7173.1 | 2946 | 10119.1
14:30 | 170 | 7312.8 | 3052.5 | 10365.3
15:00 | 140 | 7452.5 | 3159 | 10611.5
15:30 | 140 | 7502 | 3152.5 | 10654.5
16:00 | 140 | 7551.5 | 3146 | 10697.5
16:30 | 130 | 7398.25 | 3078 | 10476.25
17:00 | 120 | 7245 | 3010 | 10255
17:30 | 90 | 7011.95 | 2970 | 9981.95
18:00 | 60 | 6778.9 | 2930 | 9708.9
18:30 | 75 | 7115.45 | 3163.5 | 10278.95
19:00 | 90 | 7452 | 3397 | 10849
19:30 | 390 | 8240 | 3610 | 11850
20:00 | 410 | 8359 | 3650 | 12009 |  |  |  | Executive Engineer
20:30 | 405 | 8409 | 3642.5 | 12051.5 |  |  |  | Network Operation Division
21:00 | 400 | 8459 | 3635 | 12094
21:30 | 370 | 8403.5 | 3691.5 | 12095
22:00 | 340 | 8348 | 3748 | 12096 |  |  |  |  | Page 6 of 7
22:30 | 320 | 8262.5 | 3736.5 | 11999
23:00 | 300 | 8177 | 3725 | 11902
23:30 | 270 | 8117.5 | 3759 | 11876.5
24:00 | 240 | 8058 | 3793 | 11851
12094 MW (21:00 )
9487 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-16 |  | Energy | 243516887
[10 empty] | 2019-06-16 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4565 | 940 | 2147 | 3024 | 262 | 40 | 697 | 0 | 176
0:30 | 4394.5 | 944 | 2183 | 2232.5 | 263 | 39 | 518 | 0 | 148 | Date: | 2019-06-16
1:00 | 4224 | 948 | 2219 | 1441 | 264 | 38 | 339 | 0 | 120
1:30 | 4222 | 947.5 | 2213.5 | 1323 | 264 | 38 | 256 | 0 | 118 | [7 empty] | Total Energy | 243.5169 | Total Energy Gen 243.517 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.517 MKWHr
2:00 | 4220 | 947 | 2208 | 1205 | 264 | 38 | 173 | 0 | 116 | [7 empty] | Energy not Served | 0
2:30 | 4233.5 | 947 | 2198.5 | 1122 | 264 | 38 | 173 | 0 | 115 | [7 empty] | Energy Requirement | 243.5169
3:00 | 4247 | 947 | 2189 | 1039 | 264 | 38 | 173 | 0 | 114
3:30 | 4147 | 947 | 2166.5 | 1027.5 | 264.5 | 37.5 | 151.5 | 0 | 113 | [6 empty] | Shortage
4:00 | 4047 | 947 | 2144 | 1016 | 265 | 37 | 130 | 0 | 112
4:30 | 4060.5 | 946.5 | 2145 | 962.5 | 265 | 37 | 130 | 0 | 112
5:00 | 4074 | 946 | 2146 | 909 | 265 | 37 | 130 | 0 | 112
5:30 | 4015 | 943.5 | 1998.5 | 759 | 265 | 37 | 130 | 0 | 106
6:00 | 3956 | 941 | 1851 | 609 | 265 | 37 | 130 | 0 | 100
6:30 | 3945 | 940.5 | 1840.5 | 610 | 265 | 38.5 | 110 | 0 | 95 |  |  |  |  | Coal
7:00 | 3934 | 940 | 1830 | 611 | 265 | 40 | 90 | 0 | 90
7:30 | 3946 | 940 | 1871 | 636 | 264.5 | 40 | 90 | 0 | 96 |  |  |  | Oil |  |  |  | ,
8:00 | 3958 | 940 | 1912 | 661 | 264 | 40 | 90 | 0 | 102
8:30 | 3983.5 | 940 | 2086.5 | 776.5 | 264 | 40 | 90 | 0 | 109
9:00 | 4009 | 940 | 2261 | 892 | 264 | 40 | 90 | 0 | 116
9:30 | 4030 | 940 | 2265.5 | 1037.5 | 264 | 40 | 96 | 0 | 120
10:00 | 4051 | 940 | 2270 | 1183 | 264 | 40 | 102 | 0 | 124
10:30 | 4044.5 | 940 | 2227.5 | 1345 | 263.5 | 37.5 | 102 | 0 | 128
11:00 | 4038 | 940 | 2185 | 1507 | 263 | 35 | 102 | 0 | 132
11:30 | 4100.5 | 940 | 2137.5 | 1616 | 263 | 35 | 104 | 0 | 136
12:00 | 4163 | 940 | 2090 | 1725 | 263 | 35 | 106 | 0 | 140
12:30 | 4192.5 | 940 | 2097 | 1862 | 264 | 35 | 106.5 | 0 | 145
13:00 | 4222 | 940 | 2104 | 1999 | 265 | 35 | 107 | 0 | 150
13:30 | 4222 | 940 | 2104 | 1999 | 265 | 35 | 107 | 0 | 150
14:00 | 4222 | 940 | 2104 | 1999 | 265 | 35 | 107 | 0 | 150
14:30 | 4316 | 940 | 2224 | 2183.5 | 263.5 | 34.5 | 94.5 | 0 | 155
15:00 | 4410 | 940 | 2344 | 2368 | 262 | 34 | 82 | 0 | 160
15:30 | 4344.5 | 940 | 2276.5 | 2509.5 | 262 | 34.5 | 114.5 | 0 | 161
16:00 | 4279 | 940 | 2209 | 2651 | 262 | 35 | 147 | 0 | 162
16:30 | 4229.5 | 940.5 | 2181.5 | 2509.5 | 262 | 35 | 151.5 | 0 | 158
17:00 | 4180 | 941 | 2154 | 2368 | 262 | 35 | 156 | 0 | 154
17:30 | 4025 | 941 | 2043.5 | 2350 | 262 | 35.5 | 170 | 0 | 152
18:00 | 3870 | 941 | 1933 | 2332 | 262 | 36 | 184 | 0 | 150
18:30 | 3988 | 940.5 | 2017.5 | 2550 | 262 | 36.5 | 317 | 0 | 167
19:00 | 4106 | 940 | 2102 | 2768 | 262 | 37 | 450 | 0 | 184
19:30 | 4228 | 939 | 2219 | 3284 | 262 | 37 | 699 | 0 | 182
20:00 | 4180 | 940 | 2100 | 3576 | 262 | 37 | 738 | 0 | 176
20:30 | 4161.5 | 939.5 | 2079.5 | 3676.5 | 263 | 37.5 | 717 | 0 | 177
21:00 | 4143 | 939 | 2059 | 3777 | 264 | 38 | 696 | 0 | 178
21:30 | 4322 | 939.5 | 2172.5 | 3496.5 | 263 | 38 | 684.5 | 0 | 179
22:00 | 4501 | 940 | 2286 | 3216 | 262 | 38 | 673 | 0 | 180
22:30 | 4495.5 | 940 | 2252 | 3158 | 261.5 | 38.5 | 674.5 | 0 | 179
23:00 | 4490 | 940 | 2218 | 3100 | 261 | 39 | 676 | 0 | 178
23:30 | 4527.5 | 940 | 2182.5 | 3062 | 261.5 | 39.5 | 686.5 | 0 | 177 | Max Temp. in Dhaka |  | 35.1° C
24:00 | 4565 | 940 | 2147 | 3024 | 262 | 40 | 697 | 0 | 176
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 243.517 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.517 MKWHr
Note on W13: Author:

## Generation
2019-06-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 38 | 38 | 38 | 37 | 37 | 37 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 36 |  | 37 | 37 | 37 | 38 | 38 | 39 | 40 | 844620
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | [24 empty] | 15 | 40 | 100000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW (RPCL) | 0 | [7 empty] | 0 | 7 | 8 | 8 | 8 | 8 | 10 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 281262
| Teknaf Solartech 20MW | [5 empty] | 0.7 | 3.7 | 8.3 | 12.6 | 7.4 | 19.5 | 17.4 | 13.4 | 9.9 | 6.2 | 8.3 | 3.5 | 0.5 |  | 0 | [6 empty] | 122040
6 | Sikalbaha 225MW (Gas) | 204 | 203 | 204 | 204 | 202 | 203 | 206 | 217 | 209 | 222 | 205 | 204 | 204 | 211 | 213 | 204 | 204 | 204 |  | 220 | 205 | 204 | 205 | 206 | 210 | 205 | 4920636
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 142 | 140 | 130 | 130 | 140 | 134 | 130 | 130 | 130 |  | 140 | 100 | 100 | 100 | 100 | 100 | 130 | 3023110
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 0 |  | 56 | 68 | 68 | 68 | 68 | 68 | 68 | 355861
12 | Hathazari peaking | [19 empty] | 15 | 85 | 85 | 85 | 85 | 85 | 85 | 416752
| Baraka Sikalbaha PL | 18 | 0 | [5 empty] | 0 | 14 | 18 | 54 | 71 | 71 | 71 | 54 | 54 | 17 | 17 |  | 0 | [6 empty] | 496797
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 13 | 50 | 50 | 8 | 0 | 0 |  | 76072
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 94 | 94 | 92 | 62 | 62 | 62 | 65 | 90 | 65 | 62 | 62 |  | 40 | 40 | 37 | 40 | 93 | 95 | 65 | 1775000
17 | Siddhirganj CCPP-335 MW | 170 | 170 | 170 | 170 | 170 | 120 | 120 | 0 | 0 | 30 | 0 | 0 |  |  |  |  | 38 | 13 |  | 38 | 38 | 23 | 0 | 150 | 220 | 180 | 1851292
18 | Summit Gazipur -2 | [9 empty] | 0 | 6 | 14 | 56 | 80 | 80 | 80 | 80 | 80 |  | 80 | 100 | 172 | 200 | 60 | 0 | 0 | 1033750
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 501818
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 814000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4811000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 340 | 340 | 350 | 350 | 350 | 350 | 320 | 250 |  | 280 | 300 | 300 | 300 | 350 | 350 | 350 | 7490182
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2263894
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 220 | 221 | 220 | 219 | 220 | 220 | 200 | 202 | 198 | 209 | 183 | 217 | 184 | 197 | 199 | 184 | 184 | 184 |  | 208 | 217 | 218 | 215 | 217 | 215 | 215 | 4957000
34 | Ashuganj CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 300 | 300 | 300 | 360 | 360 | 360 | 360 | 360 | 360 | 300 | 270 |  | 300 | 300 | 300 | 300 | 330 | 300 | 330 | 7906500
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 330 | 360 | 360 | 300 | 250 |  | 300 | 300 | 300 | 300 | 330 | 300 | 300 | 7795000
35 | Ashuganj (Precision) 55MW | 55 | 55 | 53 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 50 | 51 | 52 | 52 | 52 | 52 | 55 |  | 53 | 53 | 55 | 55 | 53 | 55 | 55 | 1272000
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 95 | 100 | 100 | 100 | 100 | 96 | 100 | 95 | 96 | 95 | 95 | 100 | 96 | 97 |  | 97 | 96 | 96 | 100 | 100 | 100 | 100 | 2333060
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 484500
39 | Haripur 412 MW CCPP | 328 | 326 | 336 | 328 | 341 | 328 | 333 | 349 | 363 | 338 | 344 | 327 | 327 | 335 | 370 | 329 | 328 | 289 |  | 285 | 345 | 341 | 327 | 348 | 327 | 343 | 8182560
40 | Meghnaghat CCPP 450MW | 380 | 380 | 380 | 380 | 380 | 340 | 340 | 370 | 400 | 400 | 370 | 370 | 370 | 370 | 430 | 380 | 380 | 300 |  | 380 | 380 | 380 | 350 | 400 | 380 | 400 | 8938375
41 | Haripur Power CCPP 360MW | 357 | 357 | 357 | 357 | 357 | 357 | 320 | 320 | 347 | 341 | 334 | 313 | 314 | 314 | 342 | 339 | 339 | 258 |  | 286 | 326 | 305 | 300 | 330 | 300 | 349 | 7868000
42 | Mymensingh RPCL 210MW | 148 | 149 | 150 | 148 | 148 | 146 | 144 | 146 | 145 | 144 | 144 | 144 | 143 | 140 | 139 | 144 | 143 | 144 |  | 140 | 145 | 144 | 144 | 141 | 142 | 142 | 3392320
43 | Haripur NEPC 110MW | [9 empty] | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 45 | 65 | 95 | 65 | 0 | 0 |  | 273600
44 | Fenchugonj CCPP-1 | 58 | 58 | 57 | 57 | 57 | 57 | 58 | 58 | 60 | 58 | 56 | 56 | 56 | 56 | 51 | 56 | 56 | 56 |  | 58 | 55 | 56 | 56 | 55 | 56 | 58 | 1337000
45 | Fenchugonj CCPP-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1383000
46 | Shajibazar 330 MW
47 | Shahjibazar GT: Unit- 8, 9 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 61 | 61 | 59 | 61 | 61 | 50 | 59 | 59 | 57 | 57 | 45 |  | 59 | 61 | 49 | 61 | 60 | 61 | 61 | 1397481
48 | Shahjibazar 86MW | 70 | 70 | 70 | 40 | 40 | 10 | 10 | 10 | 50 | 50 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 77 |  | 78 | 78 | 78 | 71 | 71 | 71 | 71 | 1447680
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 45 | 45 | 46 | 46 | 44 | 44 | 44 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 44 | 44 | 44 | 45 | 45 | 45 | 46 | 1022400
50 | Sylhet GT 150 MW | 110 | 109 | 109 | 108 | 109 | 109 | 122 | 123 | 120 | 125 | 109 | 110 | 110 | 125 | 110 | 108 | 108 | 110 |  | 128 | 110 | 109 | 112 | 109 | 120 | 116 | 2806900
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 0 | 0 | [19 empty] | 96000
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 12 | 10 | 43 | 47 | 44 | 44 | 44 | 44 | 45 | 45 | 45 | 45 | 44 |  | 44 | 45 | 47 | 47 | 47 | 47 | 47 | 1019760
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 0 |  |  |  |  | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 195120
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 258960
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 53 | 53 |  | 53 | 53 | 53 | 52 | 53 | 53 | 50 | 1096200
56 | Shahjahanulla 25 MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 |  | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 410360
57 | Summit Bibiana- 2 | 260 | 250 | 270 | 265 | 270 | 250 | 270 | 280 | 290 | 290 | 255 | 250 | 255 | 260 | 300 | 260 | 260 | 250 |  | 250 | 260 | 260 | 250 | 285 | 260 | 54 | 6513750
58 | Southern 55MW | 0 | [7 empty] | 6 | 17 | 35 | 35 | 35 | 35 | 50 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 708860
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 453120
60 | Barabkunda (Regent) | 19 | 19 | 18 | 19 | 19 | 18 | 16 | 18 | 19 | 18 | 19 | 18 | 16 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 20 | 428016
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 1 | 0 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 355356
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 437544
63 | Tripura | 120 | 116 | 114 | 112 | 112 | 100 | 90 | 102 | 116 | 124 | 132 | 140 | 150 | 154 | 160 | 162 | 154 | 150 |  | 184 | 182 | 176 | 178 | 180 | 178 | 176 | 3351360
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 37 | 14 | 2 | 2 | 2 | 3 | 9 | 2 | 3 | 3 | 8 | 8 |  | 6 | 6 | 15 | 25 | 37 | 39 | 40 | 483840
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440784
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257040
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 25 | 25 | 16 | 16 | 25 | 33 | 25 | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 605600
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 10 | 12 | 13 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 383420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 0 | 0 | 0 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 525000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 |  | 17 | 19 | 19 | 19 | 19 | 19 | 22 | 472860
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 728900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817500
73 | Ghorashal (Regent) | 107 | 107 | 104 | 104 | 104 | 104 | 104 | 104 | 101 | 101 | 101 | 101 | 100 | 101 | 100 | 101 | 106 | 106 |  | 108 | 108 | 108 | 108 | 108 | 107 | 107 | 2440090
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [9 empty] | 0 | 3 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 30 | 45 | 85 | 0 | 0 |  | 229440
78 | Gazipur (RPCL) | 0 | 4 | 0 |  |  |  |  | 5 | 26 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 43 |  | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 713484
79 | Kodda 149MW | [8 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 25 | 45 | 45 | 45 |  | 105 | 145 | 145 | 145 | 145 | 145 | 146 | 1007520
80 | Jamalpur 95MW | 86 | 26 | 8 | 8 | 0 |  |  |  | 5 | 16 | 36 | 48 | 48 | 57 | 85 | 82 | 82 | 81 |  | 82 | 82 | 82 | 84 | 86 | 83 | 83 | 1215360
81 | Lakdhanvi 52 MW | [7 empty] | 0 | 5 | 8 | 16 | 25 | 25 | 25 | 25 | 38 | 44 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 583627
| Gazipur 100 MW | 89 | 70 | 35 | 35 | 35 | 35 | 35 | 71 | 71 | 90 | 89 | 90 | 90 | 90 | 90 | 90 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1832400
| Kaptai Solar | [5 empty] | 0.2 | 0.2 | 1 | 0.3 | 3.2 | 3.7 | 5.3 | 2.6 | 4.2 | 4 | 3.2 | 1.1 | 0.2 |  | 0 | 0 | 0 |  |  |  |  | 29280
82 | Madanganj 102MW | [19 empty] | 2 | 15 | 35 | 80 | 30 | 30 | 0 | 222360
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [9 empty] | 0 | 5 | 10 | 10 | 10 | 15 | 50 | 10 | 10 |  | 17 | 70 | 74 | 50 | 0 | 0 |  | 341793
86 | Meghnaghat CCPP(Summit) | 285 | 280 | 275 | 285 | 285 | 285 | 290 | 300 | 280 | 300 | 250 | 230 | 270 | 300 | 285 | 265 | 260 | 255 |  | 300 | 260 | 260 | 290 | 270 | 290 | 280 | 6663476
87 | Meghnaghat (IEL) | [9 empty] | 0 | 3 | 7 | 7 | 7 | 8 | 25 | 7 | 7 |  | 9 | 35 | 70 | 78 | 0 | 0 |  | 299520
88 | Ghorashal 78MW (MAX) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 68 | 68 | 67 | 66 | 65 | 64 | 64 | 64 | 64 | 64 |  | 65 | 65 | 65 | 66 | 66 | 66 | 66 | 1436288
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 34 | 80 | 100 | 100 | 50 | 10 | 10 | 501600
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 17 | 50 | 47 | 47 | 46 | 46 | 46 | 43 | 45 | 39 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1048968
93 | Ashuganj (Midland) 51MW | 40 | 40 | 40 | 40 | 40 | 5 | 5 | 5 | 15 | 35 | 35 | 35 | 35 | 40 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 739068
94 | Gagnagar (Orion) | [9 empty] | 2 | 24 | 24 | 24 | 24 | 24 | 40 | 50 | 50 |  | 64 | 101 | 85 | 101 | 101 | 101 | 101 | 848016
95 | Patenga 50MW | 25 | 15 | 0 |  |  |  |  | 0 | 15 | 38 | 40 | 37 | 37 | 38 | 38 | 38 | 38 | 12 |  | 45 | 46 | 46 | 46 | 46 | 46 | 47 | 644160
96 | Chattogram ECPV 108 MW | 0 | [7 empty] | 1 | 9 | 39 | 51 | 85 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1255680
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 36 | 36 | 11 | 6 | 236640
98 | Bosila 108MW | 8 | 4 | 0 |  |  |  |  | 0 | 8 | 8 | 8 | 8 | 13 | 8 | 8 | 16 | 8 | 8 |  | 8 | 50 | 73 | 73 | 73 | 72 | 72 | 405120
99 | Madanganj-55 MW | [10 empty] | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 37 | 55 | 55 | 55 | 30 | 30 | 0 | 339249
100 | Northern 55 MW | 0 | [6 empty] | 0 | 36 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 825883
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 130 | 130 | 130 | 163 | 163 | 130 | 130 |  | 100 | 163 | 100 | 100 | 100 | 100 | 163 | 3282455
102 | Sarishabari (Solar) | [5 empty] | 0.1 | 0.1 | 0.2 | 0.6 | 2 | 1.7 | 2.3 | 1.4 | 1 | 1.3 | 1 | 0.4 | 0.2 |  | 0 | 0 | 0 |  |  |  |  | 9750
103 | Banco Energy 54MW | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1024200
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 0 | [7 empty] | 0 | 7 | 7 | 7 | 7 | 7 | 14 | 120 | 80 | 80 |  | 88 | 190 | 187 | 200 | 200 | 200 | 200 | 1459200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [8 empty] | 0 | 10 | 16 | 47 | 105 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 1838880
115 | Juldah 100 MW Unit-3 | 70 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 60 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 1696320
116 | Chandpur Desh 200MW | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 14 | 17 | 76 | 105 | 105 | 105 | 106 | 135 | 100 | 100 |  | 105 | 140 | 163 | 200 | 200 | 200 | 200 | 2108640
117 | Midland 150MW | [7 empty] | 0 | 6 | 6 | 10 | 70 | 100 | 100 | 100 | 113 | 50 | 50 |  | 56 | 100 | 97 | 100 | 100 | 100 | 100 | 1242840
118 | Bibiyana-3 285 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 239 | 240 | 240 | 240 | 296 | 293 | 287 | 293 | 291 | 291 | 200 |  | 237 | 293 | 295 | 292 | 292 | 291 | 293 | 5995000
| United Jamalpur PPL | 87 | 87 | 87 | 87 | 87 | 27 | 24 | 24 | 38 | 82 | 81 | 81 | 81 | 82 | 84 | 84 | 84 | 85 |  | 85 | 84 | 85 | 85 | 85 | 85 | 85 | 1842000
| Anwara United | 140 | 139 | 115 | 115 | 115 | 115 | 115 | 115 | 124 | 125 | 162 | 162 | 176 | 200 | 220 | 224 | 279 | 296 |  | 296 | 296 | 296 | 296 | 296 | 296 | 296 | 4686981
120 | Eastern Zone Total | 6280 | 6113 | 5960 | 5908 | 5911 | 5489 | 5436 | 5586.5 | 6020.5 | 6399.6 | 6520.9 | 6687 | 6942.4 | 7173.1 | 7452.5 | 7551.5 | 7245 | 6778.9 | 0 | 7452 | 8240 | 8359 | 8459 | 8348 | 8177 | 8058 | 166180100
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 49 | 49 | 49 | 49 | 49 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 49 | 49 | 49 | 49 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1255680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 16 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 |  | 35 | 38 | 38 | 38 | 38 | 38 | 38 | 265920
| Khulna CCPP 225MW | 120 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 0 | 0 | 0 | [8 empty] | 20 | 698880
129 | Labon Chora 105 MW | 105 | 90 | 90 | 90 | 90 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 70 | 70 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1851360
130
131
132
133
| Summit Barisal 110 MW | 80 | 64 | 64 | 64 | 32 | 0 |  |  |  | 0 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1229760
136 | Barisal GT: Unit-1, 2 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Bhola Aggreko 95MW | 97 | 97 | 95 | 96 | 95 | 95 | 95 | 95 | 93 | 93 | 93 | 92 | 93 | 95 | 93 | 92 | 92 | 94 |  | 96 | 97 | 98 | 98 | 97 | 97 | 96 | 2281099
| Bhola CCPP 194MW | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 146 | 146 | 145 | 143 | 142 |  | 146 | 147 | 143 | 148 | 148 | 148 | 148 | 3493396
140 | Bhola (Venture) 33MW | 29 | 28 | 26 | 27 | 25 | 18 | 22 | 19 | 19 | 18 | 20 | 18 | 20 | 22 | 27 | 27 | 27 | 27 |  | 33 | 35 | 37 | 36 | 38 | 37 | 37 | 622530
141 | Bangla Trak Noapara | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5 | 43 | 92 | 100 | 100 | 100 | 100 | 550880
142 | Noapara (KZA) 40MW | 32 | 32 | 32 | 32 | 16 | 0 |  |  |  | 0 | 8 | 8 | 8 | 30 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 593250
143 | Gopalganj Peaking | [9 empty] | 0 | 0 | 4 | 5 | 5 | 11 | 12 | 20 | 21 |  | 28 | 43 | 55 | 52 | 42 | 42 | 42 | 301824
144 | Bheramara GT-1,2,3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 16 | 14 | 22 | 28 | 28 | 28 | 28 | 136800
145 | Madhumati Power Plant | 104 | 105 | 104 | 104 | 104 | 35 | 35 | 34 | 35 | 35 | 71 | 71 | 69 | 70 | 95 | 103 | 104 | 35 |  | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 1968624
146 | Bheramara HVDC | 948 | 947 | 947 | 947 | 946 | 941 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 940 | 941 | 941 |  | 940 | 939 | 940 | 939 | 940 | 940 | 940 | 22593455
147 | Bheramara 360 MW | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 65 | 65 | 65 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 64 | 64 | 66 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 65 | 63 | 62 | 63 | 1525527
152 | Barapukuria Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4863600
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 1365000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 43 | 43 | 43 | 0 | [15 empty] | 28 | 43 | 43 | 43 | 38 | 43 | 43 | 374952
157 | Sirajgonj Unit-1 225MW (Gas) | 158 | 157 | 165 | 159 | 167 | 156 | 163 | 178 | 201 | 192 | 189 | 188 | 193 | 189 | 197 | 184 | 182 | 182 |  | 185 | 195 | 188 | 182 | 198 | 182 | 194 | 4609427
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 156 | 156 | 164 | 158 | 171 | 160 | 158 | 170 | 199 | 196 | 188 | 179 | 179 | 188 | 199 | 178 | 179 | 179 |  | 183 | 192 | 185 | 179 | 194 | 179 | 197 | 4480473
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 175 | 174 | 176 | 0 | [5 empty] | 0 | 20 | 104 | 210 | 210 | 210 | 197 | 189 | 189 |  | 190 | 211 | 206 | 194 | 192 | 191 | 201 | 3345100
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 400 | 400 | 370 | 340 | 340 | 340 | 414 | 370 | 340 | 270 |  | 350 | 350 | 300 | 300 | 400 | 405 | 410 | 8401272
161 | Bera Peaking | 0 | [18 empty] | 10 | 17 | 33 | 33 | 33 | 32 | 32 | 174571
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509040
163 | Bogra (EPL) | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 10 | 10 | 11 | 12 |  | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 279072
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 196596
165 | Amnura 50MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 4297530
166 | Katakhali (Northern) | 34 | 34 | 14 | 0 | [9 empty] | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 456706
167 | Katakhali Peaking | 42 | 0 | [17 empty] | 17 | 40 | 47 | 44 | 43 | 43 | 43 | 274124
168 | Santahar Peaking | 28 | 0 | [17 empty] | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 196191
169 | Rajlanka 52 MW | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 35 | 40 | 8 | 8 |  | 9 | 24 | 50 | 50 | 49 | 52 | 50 | 549120
170 | Chapainawabganj-100 MW | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 46 | 46 | 46 | 46 | 46 | 46 | 90 | 91 | 90 |  | 90 | 95 | 90 | 90 | 90 | 90 | 90 | 1604844
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 53 | 53 | 34 | 0 |  |  | 0 | 23 | 53 | 78 | 108 | 108 | 108 | 108 | 108 | 35 | 35 |  | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 1729824
173 | Rangpur GT | [19 empty] | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 89000
175 | Saidpur GT | [19 empty] | 0 | 17 | 17 | 17 | 18 | 17 | 17 | 84000
176 | Confidence Rangpur | [11 empty] | 4 | 6 | 7 | 11 | 18 | 16 | 16 |  | 4 | 9 | 5 | 0 | 0 |  |  | 87360
177
178
178 | Western Zone Total | 3313 | 3058 | 3051 | 2790 | 2708 | 2401 | 2368 | 2390 | 2561 | 2569 | 2652 | 2729 | 2897 | 2946 | 3159 | 3146 | 3010 | 2930 | 0 | 3397 | 3610 | 3650 | 3635 | 3748 | 3725 | 3793 | 77336787