## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-06 | Wednesday
|  |  | Date (day): | 2022-04-06 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13331.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14251 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-05 | 2022-04-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 220 | 220 | 200 | 220 | 145 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 68 | 88 | 90 | 90 | 18 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 128 | 142 | 150 | 150 | 270 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | under maint
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 83 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 65 | 65 | 78 | 78 |  | 24 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 88 | 99 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 21 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 21 | 21 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 40 | 49 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 298 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 301 | 304 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 60 | 95 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 96 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 147 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 90 | 90 | 90 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Engine problem
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 2547 | 2738 | 2699 | 2794 | 2046 | 1063
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | 33 kV BPDB feeder problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 72 | 75 | 75 |  | 155 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 213 | 229 | 230 | 230
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 51 | 0 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 51 | 85 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 35 | 5 | 35
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 95 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 280 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1416 | 1656 | 1575 | 1664 | 81 | 573
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 139 | 146 | 210 | 200 | 21 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 250 | 300 | 300 | 60 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 0 | 26 | 26 | 19 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 5 | 25 | 25 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 147 | 145 | 145
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 32 | 42 |  | 10 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 79 | 40 | 80 |  | 83 | Mach. Prob, Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 8 | 31 | 31
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 150 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 80 | 80 | 80 |  | 34 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 95 | 113 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 54 | 35 | 54 |  |  | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 59 | 101 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1781 | 2020 | 2037 | 2219 | 660 | 151
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 8 | 20 | 10 | 10 | 192 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 106 | 190 | 106 | 190 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 90 | 115 | 106 | 107 |  | 8 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 39 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 285 | 367 | 315.6 | 349 | 192 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 20 | 20 |  | 50 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 31 | 20 | 30 |  | 60 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 140 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 239 | 239 | 240 | 240 | 90 |  | GT-2 S/D for Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 38 | 40 | 41 | 41
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 55 | 55 | 55
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 88 | 86 | 88
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 25 | 28 | 27 | 28
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 23 | 24 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 305 | 305 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 392 | 403 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1989 | 2071 | 2072 | 2086 | 110 | 210
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 917 | 940 | 940
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 16 | 115 | 16 | 115
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 13 | 15 | 0 | 42 |  | 12 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 200 | 200 | 225 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 140 | 140 | 170 | 170 | 240 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 16 | 40 | 32 | 40
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 54 | 99 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 76 | 94 | 94 | 94
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1506 | 1635 | 1727 | 1856 | 240 | 91
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 32 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 37 | 25 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 89 | 90 | 90 | 104 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 600 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 221 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 100
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 772 | 1012 | 1027 | 1215 | 104 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 6 | 22 | 40 | 45 |  | 26 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 40 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 211 | 213 | 220 | 220 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 114 | 114 | 120 | 120 | 100 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 263 | 255 | 325 | 325 | 89 |  | Gas shortage
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 36 | 36 |  | 14 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 52 | 43 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 90 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 169 | 171 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1068 | 1330 | 1313 | 1483 | 570 | 70
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17 |  | 3
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 102 | 109 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 550 | 577 | 566 | 585 | 24 | 98
|  | Total |  |  |  |  | 22291 | 21215 | 11914 | 13406 | 13331.6 | 14251 | 4027 | 2264
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11942.4208 | 13437.98 | 13363.4025 | 14284.9957
| A. |  | 2022-04-05 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13431 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 10597 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13986 | MW
| 3 | Day peak Generation : |  |  | 11914 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13437.98 | MW
| 4 | Evening peak Generation : |  |  | 13406 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 580 | MW
| 5 | Total Energy Generation : |  | 296.4805 | MKWHr | By Solar | 1.3333 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 116.5042 | MKWHr |  | By Oil: | 129.59 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 21.5265 | MKWHr |  | By Hydro: | 1.7183 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4027 | MW | Dhaka | 4946.98 | 4901.98 |  | 45
|  |  |  | For Plants S/D or M/C prob = |  |  | 2264 | MW | Chittagong | 1326 | 1281 |  | 45 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6291 | MW | Khulna | 1654.4 | 1554.4 |  | 100 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 917.74 | MMCFD |  |  | Rajshahi | 1406.6 | 1296.6 |  | 110 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 117217674.44 | ii) Oil : | Taka | 1182903612 | Comilla | 1287 | 1267 |  | 20 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 103798283.89 | Total | Taka | 1403919570.33 | Mymensingh | 1096 | 926 |  | 170 |  | 20:00 |  | 580
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 513 | 493 |  | 20 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 346 | MW (E to W) at | 20:00 | hrs | Barisal | 381 | 381 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 198 | MW at | 18:30 | hrs | Rangpur | 827 | 757 |  | 70 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 13437.98 | 12857.98 |  | 580
| B. |  | 2022-04-06 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 371.7958 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14251 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 322.2854 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10715 | MW at | 7:00 | 25.1351 | 20.5559 | 76.4249 | 89.6258 | 0.33498 | 153.9622 | -0.41439 | 0.073545 | 6.0977
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2131 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5952 | MKWHr. | iii) Maximum HVDC Flow : |  | 922 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.88 |  | (b) Today: | 83.64 |  | (c) Rule Curve: |  | 87
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 0 | 22 | 64 | 0 | 0 | 110 |  | 0 | 0 | 0 | 92 | 65 | 30 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 21 | 16 | 21 | 49 | 0 | 75 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 22 | 20 | 0 | 0 | 87 | 42 | 0 | 33 | 0 | 0 | 0 | 270 | 260 | 220 | 8 | 40 | 23 | 5 | 0 | 51 | 0 | 33 | 43 | 22 | 11 | 31 | 21 | 148 | 8 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 163 | 240 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 280 | 24 | 11 | 200 | 300 | 300 | 100 | 106 | 100 | 144 | 0 | 76 | 200 | 128 | 402 | 106 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 105 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 35 | 0 | 101 | 0 |  | 921 | 0 | 150 | 0 | 32 | 200 | 0 | 0 | 34 | 0 | 16 | 68 | 34 | 16 | 0 | 0 | 0 | 43 | 15 | 92 | 0 | 0 | 40 | 8 | 32 | 22 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 99 | 117 | 0 | 218 | 94 | 172 | 113 | 15 | 110 | 0 | 0 | 113 | 580 | 224 | 0 | 0 | 0 | 0 | 115 |  | 8231 | 4248 | 12479 | 3257 | 921 | 1404 | 971 | 3920 | 907 | 75 | 417 | 676 | 148 | 0 | 0 | 83.93
2:00 | 0 | 0 | 100 | 0 | 36 | 65 | 0 | 0 | 110 |  | 0 | 0 | 0 | 92 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 21 | 16 | 21 | 49 | 0 | 75 | 0 | 0 | 150 | 25 | 205 | 0 | 0 | 0 |  | 22 | 20 | 0 | 0 | 95 | 42 | 0 | 36 | 0 | 0 | 0 | 270 | 260 | 221 | 8 | 39 | 23 | 5 | 0 | 51 | 0 | 33 | 43 | 22 | 11 | 31 | 21 | 146 | 8 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 163 | 245 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 270 | 16 | 11 | 150 | 300 | 255 | 60 | 106 | 100 | 149 | 0 | 90 | 200 | 132 | 401 | 106 | 105 | 105 | 0 | 300 | 40 | 110 | 80 | 105 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 35 | 0 | 101 | 0 |  | 921 | 0 | 150 | 0 | 16 | 200 | 0 | 0 | 29 | 0 | 16 | 68 | 32 | 16 | 0 | 0 | 0 | 43 | 15 | 92 | 0 | 0 | 40 | 8 | 32 | 22 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 50 | 117 | 0 | 218 | 94 | 171 | 113 | 15 | 110 | 0 | 0 | 113 | 560 | 216 | 0 | 0 | 0 | 0 | 115 |  | 8141 | 4149 | 12290 | 3269 | 921 | 1388 | 786 | 3945 | 887 | 75 | 419 | 673 | 146 | 0 | 0 | 83.92
3:00 | 0 | 0 | 100 | 0 | 86 | 63 | 0 | 0 | 110 |  | 0 | 0 | 0 | 92 | 65 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 21 | 16 | 21 | 49 | 0 | 75 | 0 | 0 | 150 | 25 | 215 | 0 | 0 | 0 |  | 24 | 30 | 0 | 0 | 96 | 42 | 0 | 36 | 0 | 0 | 0 | 270 | 260 | 220 | 8 | 40 | 23 | 5 | 0 | 51 | 0 | 33 | 43 | 22 | 11 | 31 | 21 | 148 | 7 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 163 | 240 | 50 | 86 | 0 | 219 | 0 | 24 | 9 | 285 | 24 | 11 | 120 | 298 | 261 | 60 | 107 | 100 | 149 | 0 | 90 | 200 | 135 | 401 | 97 | 105 | 105 | 0 | 300 | 54 | 102 | 80 | 104 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 35 | 0 | 80 | 0 |  | 921 | 0 | 155 | 0 | 16 | 200 | 0 | 0 | 29 | 0 | 16 | 68 | 31 | 16 | 0 | 0 | 0 | 43 | 15 | 92 | 0 | 0 | 40 | 8 | 31 | 22 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 50 | 117 | 0 | 224 | 94 | 170 | 113 | 15 | 110 | 0 | 0 | 113 | 560 | 224 | 0 | 0 | 0 | 0 | 115 |  | 8162 | 4165 | 12327 | 3314 | 921 | 1413 | 761 | 3926 | 887 | 75 | 419 | 682 | 148 | 0 | 0 | 83.91
4:00 | 0 | 0 | 100 | 0 | 197 | 58 | 0 | 0 | 110 |  | 0 | 0 | 0 | 86 | 65 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 12 | 16 | 21 | 50 | 0 | 75 | 0 | 0 | 150 | 25 | 202 | 0 | 0 | 0 |  | 24 | 30 | 0 | 0 | 96 | 42 | 0 | 36 | 0 | 0 | 0 | 270 | 260 | 222 | 8 | 40 | 23 | 5 | 0 | 51 | 0 | 33 | 43 | 22 | 11 | 31 | 21 | 152 | 7 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 163 | 243 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 280 | 24 | 11 | 10 | 300 | 203 | 25 | 107 | 52 | 149 | 0 | 90 | 200 | 137 | 400 | 97 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 93 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 35 | 0 | 59 | 0 |  | 922 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 29 | 0 | 16 | 69 | 31 | 16 | 0 | 0 | 0 | 43 | 15 | 92 | 0 | 0 | 40 | 8 | 31 | 22 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 50 | 117 | 0 | 232 | 93 | 170 | 113 | 15 | 110 | 0 | 0 | 113 | 560 | 218 | 0 | 0 | 0 | 0 | 115 |  | 7974 | 4174 | 12148 | 3413 | 922 | 1406 | 510 | 3900 | 887 | 75 | 420 | 683 | 152 | 0 | 0 | 83.9
5:00 | 0 | 0 | 100 | 0 | 219 | 57 | 0 | 0 | 110 |  | 0 | 0 | 0 | 92 | 65 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 12 | 17 | 21 | 50 | 0 | 75 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 42 | 0 | 38 | 0 | 0 | 0 | 270 | 260 | 224 | 8 | 39 | 23 | 5 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 32 | 21 | 140 | 7 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 163 | 241 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 275 | 24 | 11 | 0 | 298 | 12 | 0 | 107 | 0 | 149 | 0 | 90 | 200 | 142 | 401 | 97 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 99 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 35 | 0 | 59 | 0 |  | 921 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 5 | 0 | 16 | 68 | 27 | 0 | 0 | 0 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 118 | 0 | 243 | 93 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 510 | 221 | 0 | 0 | 0 | 0 | 115 |  | 7657 | 3735 | 11392 | 3438 | 921 | 1412 | 12 | 3884 | 838 | 75 | 420 | 472 | 140 | 0 | 0 | 83.89
6:00 | 0 | 0 | 100 | 0 | 219 | 56 | 0 | 0 | 110 |  | 0 | 0 | 0 | 82 | 45 | 55 | 0 | 0 | 0 | 99 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 17 | 17 | 21 | 50 | 0 | 74 | 0 | 0 | 150 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 42 | 0 | 28 | 0 | 0 | 0 | 270 | 260 | 224 | 8 | 40 | 23 | 15 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 126 | 7 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 110 | 242 | 50 | 86 | 0 | 219 | 0 | 23 | 10 | 285 | 24 | 5 | 0 | 245 | 0 | 0 | 107 | 0 | 149 | 0 | 90 | 120 | 137 | 401 | 106 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 100 | 70 | 400 | 104 | 0 | 78 | 113 | 0 | 35 | 0 | 59 | 0 |  | 921 | 0 | 160 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 68 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 119 | 0 | 272 | 53 | 0 | 113 | 0 | 85 | 0 | 0 | 70 | 470 | 220 | 0 | 0 | 0 | 0 | 75 |  | 7272 | 3439 | 10711 | 3441 | 921 | 1392 | 0 | 3406 | 798 | 74 | 420 | 353 | 126 | 0 | 0 | 83.88
7:00 | 0 | 0 | 100 | 0 | 220 | 58 | 0 | 0 | 110 |  | 0 | 0 | 0 | 74 | 59 | 55 | 0 | 0 | 0 | 99 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 20 | 17 | 21 | 50 | 0 | 75 | 0 | 0 | 150 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 42 | 0 | 8 | 0 | 0 | 0 | 270 | 260 | 207 | 8 | 30 | 23 | 40 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 32 | 21 | 122 | 10 | 0 | 20 | 0 | 30 | 29 | 31 | 41 | 110 | 238 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 295 | 24 | 5 | 0 | 245 | 0 | 0 | 107 | 0 | 149 | 4 | 90 | 85 | 132 | 402 | 106 | 105 | 105 | 0 | 281 | 54 | 110 | 80 | 95 | 50 | 400 | 104 | 5 | 72 | 113 | 0 | 35 | 4 | 59 | 0 |  | 922 | 0 | 160 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 120 | 0 | 276 | 53 | 0 | 113 | 0 | 76 | 0 | 0 | 70 | 470 | 220 | 0 | 0 | 0 | 13 | 74 |  | 7205 | 3392 | 10597 | 3378 | 922 | 1411 | 0 | 3312 | 798 | 75 | 420 | 353 | 122 | 26 | 0 | 83.87
8:00 | 0 | 0 | 100 | 0 | 220 | 59 | 0 | 0 | 116 |  | 0 | 0 | 0 | 74 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 20 | 35 | 0 | 25 | 23 | 17 | 21 | 43 | 0 | 75 | 0 | 0 | 150 | 2 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 96 | 42 | 0 | 3 | 0 | 0 | 0 | 270 | 260 | 208 | 8 | 30 | 23 | 25 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 30 | 21 | 134 | 10 | 0 | 20 | 0 | 30 | 29 | 42 | 41 | 140 | 240 | 50 | 86 | 0 | 219 | 0 | 24 | 10 | 300 | 24 | 11 | 0 | 258 | 12 | 25 | 106 | 25 | 149 | 9 | 90 | 90 | 140 | 400 | 97 | 90 | 105 | 2 | 300 | 54 | 110 | 80 | 96 | 61 | 400 | 104 | 14 | 72 | 113 | 0 | 22 | 7 | 60 | 0 |  | 922 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 0 | 0 | 16 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 120 | 0 | 280 | 70 | 0 | 113 | 0 | 104 | 0 | 0 | 100 | 490 | 210 | 0 | 0 | 0 | 37 | 96 |  | 7350 | 3561 | 10911 | 3373 | 922 | 1438 | 62 | 3467 | 819 | 75 | 419 | 352 | 134 | 69 | 0 | 83.86
9:00 | 0 | 0 | 100 | 0 | 220 | 62 | 0 | 0 | 128 |  | 0 | 0 | 0 | 74 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 23 | 21 | 21 | 43 | 0 | 75 | 0 | 0 | 150 | 8 | 220 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 88 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 211 | 8 | 30 | 23 | 10 | 0 | 51 | 0 | 0 | 43 | 0 | 8 | 25 | 20 | 140 | 10 | 0 | 20 | 0 | 30 | 29 | 42 | 38 | 110 | 240 | 50 | 86 | 0 | 220 | 0 | 24 | 10 | 290 | 24 | 11 | 0 | 280 | 122 | 25 | 107 | 50 | 149 | 14 | 90 | 100 | 138 | 402 | 97 | 90 | 105 | 3 | 300 | 54 | 110 | 80 | 96 | 100 | 397 | 104 | 9 | 72 | 113 | 0 | 35 | 13 | 60 | 0 |  | 921 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 0 | 0 | 16 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 120 | 0 | 280 | 93 | 0 | 113 | 0 | 110 | 0 | 1 | 113 | 460 | 220 | 0 | 0 | 2 | 50 | 115 |  | 7580 | 3633 | 11213 | 3366 | 921 | 1397 | 197 | 3668 | 789 | 75 | 418 | 368 | 140 | 92 | 0 | 83.85
10:00 | 0 | 0 | 101 | 0 | 220 | 63 | 0 | 0 | 128 |  | 0 | 0 | 0 | 74 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 21 | 21 | 43 | 0 | 75 | 0 | 0 | 150 | 14 | 207 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 69 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 212 | 8 | 30 | 23 | 10 | 0 | 51 | 0 | 0 | 43 | 0 | 8 | 20 | 20 | 144 | 10 | 0 | 17 | 1 | 30 | 29 | 45 | 38 | 110 | 241 | 50 | 86 | 0 | 220 | 0 | 24 | 10 | 300 | 24 | 2 | 50 | 280 | 154 | 50 | 106 | 96 | 149 | 18 | 90 | 128 | 138 | 402 | 96 | 90 | 105 | 4 | 300 | 54 | 110 | 80 | 96 | 100 | 400 | 104 | 9 | 72 | 113 | 0 | 35 | 14 | 60 | 0 |  | 916 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 0 | 0 | 16 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 118 | 0 | 275 | 93 | 50 | 113 | 0 | 109 | 0 | 2 | 113 | 490 | 220 | 0 | 0 | 1 | 80 | 115 |  | 7766 | 3725 | 11491 | 3359 | 916 | 1401 | 400 | 3680 | 820 | 75 | 417 | 367 | 144 | 129 | 0 | 83.84
11:00 | 0 | 0 | 100 | 0 | 220 | 65 | 0 | 0 | 127 |  | 0 | 0 | 0 | 75 | 65 | 50 | 0 | 0 | 0 | 80 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 21 | 21 | 40 | 0 | 75 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 24 | 17 | 0 | 0 | 74 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 185 | 8 | 31 | 20 | 10 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 18 | 20 | 146 | 8 | 0 | 17 | 1 | 30 | 29 | 47 | 38 | 110 | 244 | 50 | 85 | 0 | 220 | 0 | 25 | 10 | 300 | 16 | 5 | 120 | 280 | 220 | 60 | 106 | 97 | 149 | 19 | 90 | 194 | 142 | 401 | 96 | 90 | 93 | 5 | 300 | 54 | 96 | 80 | 96 | 100 | 391 | 104 | 48 | 72 | 113 | 0 | 35 | 21 | 59 | 0 |  | 916 | 0 | 160 | 0 | 16 | 200 | 0 | 0 | 11 | 0 | 16 | 88 | 12 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 13 | 116 | 0 | 263 | 75 | 170 | 113 | 0 | 102 | 0 | 3 | 113 | 470 | 220 | 0 | 0 | 3 | 90 | 115 |  | 7961 | 3895 | 11856 | 3384 | 916 | 1390 | 680 | 3679 | 798 | 75 | 415 | 398 | 146 | 190 | 0 | 83.83
12:00 | 0 | 0 | 100 | 0 | 220 | 68 | 0 | 0 | 128 |  | 0 | 0 | 0 | 83 | 65 | 55 | 0 | 0 | 0 | 88 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 21 | 21 | 40 | 0 | 35 | 0 | 0 | 150 | 25 | 213 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 77 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 139 | 8 | 30 | 23 | 10 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 14 | 20 | 148 | 8 | 0 | 17 | 1 | 30 | 20 | 50 | 38 | 110 | 239 | 55 | 84 | 0 | 220 | 0 | 25 | 10 | 300 | 16 | 8 | 150 | 298 | 301 | 60 | 106 | 96 | 147 | 19 | 90 | 200 | 135 | 392 | 90 | 90 | 87 | 2 | 280 | 54 | 93 | 80 | 95 | 100 | 392 | 104 | 39 | 72 | 113 | 0 | 35 | 35 | 59 | 0 |  | 914 | 0 | 140 | 0 | 16 | 200 | 0 | 0 | 13 | 0 | 16 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 14 | 34 | 0 | 17 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 54 | 114 | 0 | 263 | 76 | 169 | 113 | 0 | 102 | 0 | 3 | 113 | 450 | 220 | 0 | 0 | 3 | 77 | 115 |  | 8018 | 3896 | 11914 | 3309 | 914 | 1399 | 830 | 3692 | 780 | 35 | 411 | 428 | 148 | 179 | 0 | 83.82
13:00 | 0 | 0 | 86 | 0 | 220 | 76 | 0 | 0 | 133 |  | 0 | 0 | 0 | 84 | 65 | 55 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 21 | 21 | 46 | 0 | 72 | 0 | 0 | 150 | 25 | 223 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 81 | 42 | 0 | 9 | 0 | 0 | 0 | 270 | 260 | 142 | 8 | 85 | 10 | 5 | 0 | 51 | 0 | 11 | 43 | 0 | 11 | 14 | 20 | 158 | 8 | 0 | 20 | 2 | 30 | 21 | 50 | 38 | 110 | 231 | 50 | 84 | 0 | 220 | 0 | 26 | 10 | 305 | 16 | 8 | 200 | 298 | 307 | 80 | 106 | 99 | 145 | 19 | 90 | 200 | 132 | 363 | 92 | 70 | 92 | 4 | 300 | 54 | 92 | 62 | 95 | 100 | 393 | 104 | 44 | 72 | 113 | 0 | 47 | 32 | 59 | 0 |  | 914 | 0 | 110 | 0 | 16 | 200 | 0 | 0 | 17 | 0 | 16 | 87 | 17 | 0 | 0 | 0 | 0 | 43 | 6 | 28 | 0 | 0 | 36 | 43 | 0 | 17 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 98 | 114 | 0 | 263 | 80 | 169 | 113 | 0 | 102 | 0 | 5 | 113 | 450 | 217 | 0 | 0 | 5 | 91 | 115 |  | 8194 | 4033 | 12227 | 3283 | 914 | 1419 | 953 | 3714 | 778 | 72 | 409 | 534 | 158 | 202 | 0 | 83.81
14:00 | 0 | 0 | 100 | 0 | 220 | 76 | 0 | 0 | 131 |  | 0 | 0 | 0 | 95 | 45 | 55 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 25 | 21 | 48 | 0 | 71 | 0 | 0 | 150 | 25 | 206 | 0 | 0 | 0 |  | 22 | 34 | 0 | 0 | 86 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 135 | 8 | 85 | 8 | 5 | 0 | 51 | 0 | 31 | 43 | 0 | 11 | 12 | 20 | 168 | 12 | 0 | 20 | 1 | 30 | 21 | 50 | 38 | 110 | 235 | 50 | 84 | 0 | 220 | 0 | 25 | 10 | 305 | 16 | 8 | 200 | 300 | 300 | 80 | 106 | 97 | 149 | 17 | 90 | 200 | 137 | 380 | 96 | 70 | 100 | 4 | 300 | 54 | 94 | 80 | 94 | 100 | 390 | 104 | 43 | 72 | 113 | 0 | 34 | 28 | 59 | 0 |  | 915 | 0 | 142 | 0 | 16 | 200 | 0 | 0 | 17 | 0 | 16 | 86 | 18 | 0 | 0 | 0 | 0 | 43 | 6 | 43 | 0 | 0 | 40 | 43 | 0 | 17 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 98 | 113 | 0 | 254 | 70 | 169 | 113 | 0 | 108 | 0 | 4 | 113 | 470 | 217 | 0 | 0 | 2 | 82 | 115 |  | 8235 | 4075 | 12310 | 3327 | 915 | 1401 | 944 | 3735 | 799 | 71 | 405 | 569 | 168 | 181 | 0 | 83.8
15:00 | 0 | 0 | 100 | 0 | 220 | 73 | 0 | 0 | 130 |  | 0 | 0 | 0 | 100 | 55 | 45 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 9 | 32 | 21 | 48 | 0 | 72 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 22 | 35 | 0 | 0 | 88 | 38 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 128 | 8 | 85 | 8 | 5 | 0 | 51 | 0 | 32 | 43 | 0 | 11 | 8 | 20 | 168 | 12 | 0 | 20 | 1 | 30 | 31 | 50 | 39 | 163 | 238 | 50 | 85 | 0 | 220 | 0 | 26 | 10 | 295 | 22 | 8 | 200 | 291 | 300 | 98 | 104 | 97 | 149 | 13 | 90 | 200 | 137 | 402 | 103 | 85 | 91 | 3 | 300 | 54 | 110 | 80 | 99 | 100 | 388 | 104 | 14 | 112 | 113 | 0 | 54 | 22 | 56 | 0 |  | 916 | 0 | 140 | 0 | 16 | 200 | 0 | 0 | 17 | 0 | 16 | 88 | 16 | 0 | 0 | 0 | 0 | 43 | 6 | 51 | 0 | 0 | 40 | 43 | 0 | 17 | 0 | 11 | 80 | 0 | 250 | 0 | 8 | 0 | 0 | 0 | 208 | 0 | 97 | 112 | 0 | 255 | 90 | 169 | 113 | 0 | 109 | 0 | 3 | 113 | 550 | 216 | 0 | 0 | 2 | 64 | 112 |  | 8356 | 4171 | 12527 | 3341 | 916 | 1441 | 961 | 3836 | 880 | 72 | 416 | 582 | 168 | 122 | 0 | 83.79
16:00 | 0 | 0 | 100 | 0 | 220 | 77 | 0 | 0 | 130 |  | 0 | 0 | 0 | 93 | 48 | 55 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 9 | 32 | 21 | 48 | 0 | 72 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 22 | 42 | 0 | 0 | 88 | 36 | 0 | 4 | 0 | 0 | 0 | 260 | 260 | 127 | 8 | 85 | 8 | 5 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 8 | 19 | 162 | 12 | 0 | 20 | 1 | 30 | 31 | 50 | 37 | 140 | 238 | 50 | 86 | 0 | 220 | 0 | 25 | 10 | 290 | 22 | 8 | 200 | 291 | 301 | 100 | 104 | 94 | 149 | 8 | 90 | 200 | 135 | 404 | 97 | 85 | 90 | 2 | 300 | 54 | 110 | 80 | 99 | 100 | 398 | 104 | 19 | 162 | 113 | 0 | 54 | 14 | 59 | 0 |  | 917 | 0 | 135 | 0 | 16 | 200 | 0 | 0 | 17 | 0 | 16 | 88 | 26 | 32 | 0 | 0 | 0 | 43 | 23 | 51 | 0 | 0 | 40 | 43 | 24 | 17 | 0 | 11 | 81 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 210 | 0 | 97 | 112 | 0 | 239 | 90 | 169 | 113 | 0 | 109 | 0 | 2 | 113 | 500 | 214 | 0 | 0 | 1 | 41 | 114 |  | 8333 | 4177 | 12510 | 3339 | 917 | 1409 | 961 | 3908 | 831 | 72 | 433 | 600 | 162 | 88 | 0 | 83.78
17:00 | 0 | 0 | 100 | 0 | 220 | 77 | 0 | 0 | 130 |  | 0 | 0 | 0 | 97 | 48 | 55 | 0 | 0 | 0 | 92 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 17 | 33 | 21 | 48 | 0 | 72 | 0 | 0 | 150 | 25 | 219 | 0 | 0 | 0 |  | 22 | 51 | 0 | 0 | 83 | 42 | 0 | 10 | 0 | 0 | 0 | 270 | 255 | 132 | 8 | 85 | 8 | 5 | 0 | 51 | 0 | 3 | 40 | 0 | 11 | 8 | 19 | 150 | 12 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 110 | 241 | 50 | 87 | 0 | 193 | 0 | 27 | 10 | 290 | 22 | 11 | 200 | 298 | 254 | 98 | 104 | 100 | 149 | 2 | 90 | 200 | 133 | 401 | 114 | 70 | 105 | 1 | 300 | 54 | 110 | 80 | 108 | 100 | 382 | 104 | 8 | 162 | 113 | 0 | 54 | 6 | 61 | 0 |  | 916 | 0 | 135 | 0 | 32 | 200 | 0 | 0 | 17 | 6 | 16 | 86 | 28 | 32 | 0 | 0 | 0 | 43 | 23 | 51 | 0 | 0 | 40 | 43 | 30 | 17 | 0 | 11 | 78 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 180 | 0 | 50 | 112 | 0 | 236 | 94 | 100 | 113 | 0 | 109 | 0 | 2 | 113 | 450 | 215 | 0 | 0 | 0 | 17 | 115 |  | 8279 | 3983 | 12262 | 3332 | 916 | 1394 | 802 | 3965 | 778 | 72 | 403 | 594 | 150 | 36 | 0 | 83.77
18:00 | 0 | 0 | 100 | 0 | 220 | 77 | 0 | 0 | 130 |  | 0 | 0 | 0 | 100 | 48 | 55 | 0 | 0 | 0 | 92 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 21 | 48 | 0 | 71 | 0 | 0 | 150 | 25 | 203 | 0 | 0 | 0 |  | 22 | 51 | 51 | 0 | 88 | 42 | 0 | 27 | 0 | 0 | 0 | 280 | 250 | 139 | 8 | 84 | 0 | 5 | 0 | 51 | 0 | 33 | 43 | 0 | 11 | 8 | 19 | 158 | 12 | 0 | 20 | 0 | 30 | 31 | 52 | 40 | 110 | 241 | 40 | 87 | 0 | 193 | 0 | 27 | 10 | 260 | 23 | 11 | 200 | 298 | 157 | 96 | 188 | 100 | 149 | 0 | 90 | 200 | 137 | 365 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 350 | 104 | 0 | 162 | 113 | 0 | 54 | 1 | 94 | 0 |  | 917 | 0 | 135 | 0 | 83 | 200 | 0 | 0 | 27 | 0 | 40 | 89 | 30 | 32 | 0 | 0 | 0 | 43 | 23 | 57 | 0 | 43 | 32 | 52 | 30 | 18 | 0 | 11 | 80 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 180 | 0 | 40 | 112 | 0 | 236 | 94 | 80 | 113 | 0 | 109 | 0 | 0 | 113 | 430 | 184 | 0 | 0 | 0 | 1 | 115 |  | 8310 | 4022 | 12332 | 3248 | 917 | 1352 | 673 | 4251 | 760 | 71 | 403 | 677 | 158 | 2 | 0 | 83.76
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 0 | 220 | 80 | 0 | 0 | 137 |  | 0 | 0 | 0 | 100 | 60 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 21 | 48 | 0 | 72 | 0 | 0 | 150 | 25 | 221 | 0 | 0 | 0 |  | 22 | 51 | 59 | 0 | 88 | 42 | 0 | 31 | 0 | 0 | 0 | 280 | 250 | 147 | 8 | 78 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 10 | 11 | 8 | 19 | 168 | 18 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 140 | 240 | 50 | 88 | 0 | 220 | 0 | 28 | 10 | 275 | 23 | 11 | 200 | 298 | 303 | 94 | 187 | 98 | 149 | 0 | 90 | 200 | 137 | 404 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 382 | 104 | 0 | 162 | 113 | 0 | 54 | 0 | 101 | 0 |  | 917 | 0 | 135 | 0 | 99 | 200 | 0 | 0 | 34 | 0 | 40 | 87 | 35 | 64 | 0 | 0 | 0 | 43 | 20 | 93 | 0 | 43 | 32 | 52 | 24 | 22 | 0 | 11 | 80 | 0 | 250 | 17 | 8 | 0 | 0 | 0 | 190 | 0 | 65 | 113 | 0 | 243 | 94 | 172 | 113 | 15 | 108 | 0 | 0 | 113 | 480 | 219 | 0 | 4 | 0 | 0 | 115 |  | 8716 | 4350 | 13066 | 3398 | 917 | 1465 | 932 | 4342 | 810 | 72 | 415 | 737 | 168 | 0 | 0 | 83.73
19:30 | 0 | 0 | 100 | 0 | 220 | 88 | 0 | 0 | 143 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 21 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 90 | 42 | 0 | 33 | 0 | 0 | 0 | 280 | 250 | 147 | 8 | 79 | 0 | 5 | 0 | 51 | 0 | 41 | 42 | 22 | 11 | 8 | 19 | 160 | 18 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 140 | 240 | 55 | 88 | 0 | 220 | 0 | 28 | 10 | 300 | 23 | 11 | 200 | 298 | 302 | 92 | 190 | 100 | 149 | 0 | 90 | 200 | 146 | 403 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 395 | 104 | 0 | 162 | 113 | 0 | 54 | 0 | 101 | 0 |  | 916 | 0 | 140 | 0 | 115 | 200 | 0 | 0 | 18 | 0 | 40 | 89 | 35 | 64 | 0 | 0 | 0 | 43 | 25 | 93 | 0 | 43 | 32 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 212 | 0 | 100 | 113 | 0 | 249 | 94 | 171 | 113 | 15 | 108 | 0 | 0 | 113 | 580 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8830 | 4536 | 13366 | 3443 | 916 | 1513 | 965 | 4390 | 910 | 72 | 435 | 774 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 0 | 220 | 88 | 0 | 0 | 142 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 21 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 |  | 22 | 51 | 85 | 0 | 95 | 42 | 0 | 35 | 0 | 0 | 0 | 280 | 250 | 146 | 8 | 79 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 8 | 19 | 162 | 20 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 140 | 239 | 55 | 88 | 0 | 220 | 0 | 28 | 10 | 305 | 23 | 11 | 200 | 300 | 304 | 95 | 190 | 100 | 149 | 0 | 90 | 200 | 147 | 403 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 395 | 104 | 0 | 162 | 113 | 0 | 54 | 0 | 101 | 0 |  | 917 | 0 | 140 | 0 | 115 | 200 | 0 | 0 | 15 | 0 | 40 | 89 | 37 | 48 | 0 | 0 | 0 | 43 | 22 | 93 | 0 | 43 | 40 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 213 | 0 | 99 | 114 | 0 | 255 | 94 | 171 | 113 | 15 | 109 | 0 | 0 | 113 | 600 | 221 | 0 | 17 | 0 | 0 | 115 |  | 8852 | 4554 | 13406 | 3444 | 917 | 1528 | 969 | 4383 | 930 | 72 | 436 | 778 | 162 | 0 | 580 | 83.74
21:00 | 0 | 0 | 100 | 0 | 220 | 86 | 0 | 0 | 138 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 22 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 |  | 22 | 51 | 68 | 0 | 96 | 42 | 0 | 35 | 0 | 0 | 0 | 280 | 250 | 152 | 8 | 78 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 8 | 19 | 164 | 22 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 163 | 242 | 50 | 88 | 0 | 213 | 0 | 28 | 10 | 290 | 23 | 11 | 200 | 300 | 302 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 142 | 403 | 115 | 72 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 390 | 104 | 0 | 162 | 113 | 0 | 44 | 0 | 101 | 0 |  | 916 | 0 | 150 | 0 | 115 | 200 | 0 | 0 | 23 | 0 | 40 | 89 | 39 | 32 | 0 | 0 | 0 | 43 | 22 | 90 | 0 | 43 | 40 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 250 | 14 | 8 | 0 | 0 | 0 | 212 | 0 | 97 | 116 | 0 | 278 | 94 | 171 | 113 | 15 | 109 | 0 | 0 | 113 | 622 | 221 | 0 | 17 | 0 | 0 | 115 |  | 8805 | 4597 | 13402 | 3450 | 916 | 1555 | 970 | 4336 | 952 | 72 | 434 | 765 | 164 | 0 | 0 | 83.73
22:00 | 0 | 0 | 100 | 0 | 220 | 86 | 0 | 0 | 136 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 22 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 |  | 22 | 50 | 68 | 0 | 95 | 42 | 0 | 37 | 0 | 0 | 0 | 280 | 250 | 152 | 8 | 78 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 16 | 21 | 162 | 22 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 163 | 240 | 50 | 89 | 0 | 219 | 0 | 28 | 10 | 300 | 23 | 11 | 200 | 300 | 304 | 100 | 189 | 100 | 149 | 0 | 90 | 200 | 142 | 402 | 115 | 72 | 105 | 0 | 300 | 54 | 110 | 80 | 117 | 100 | 400 | 104 | 0 | 146 | 113 | 0 | 37 | 0 | 101 | 0 |  | 916 | 0 | 155 | 0 | 115 | 200 | 0 | 0 | 26 | 0 | 40 | 89 | 39 | 32 | 0 | 0 | 0 | 43 | 22 | 89 | 0 | 43 | 40 | 52 | 29 | 22 | 0 | 11 | 79 | 0 | 250 | 14 | 8 | 0 | 0 | 0 | 215 | 0 | 96 | 120 | 0 | 282 | 94 | 171 | 113 | 15 | 110 | 0 | 0 | 113 | 622 | 217 | 0 | 17 | 0 | 0 | 115 |  | 8817 | 4614 | 13431 | 3482 | 916 | 1566 | 971 | 4316 | 951 | 72 | 437 | 773 | 162 | 0 | 0 | 83.72
23:00 | 0 | 0 | 100 | 0 | 220 | 86 | 0 | 0 | 132 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 22 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 |  | 22 | 41 | 68 | 0 | 96 | 42 | 0 | 36 | 0 | 0 | 0 | 280 | 250 | 153 | 8 | 78 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 17 | 21 | 152 | 22 | 0 | 20 | 0 | 30 | 31 | 53 | 41 | 163 | 239 | 50 | 89 | 0 | 220 | 0 | 27 | 10 | 290 | 23 | 11 | 200 | 298 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 147 | 403 | 106 | 70 | 105 | 0 | 281 | 54 | 110 | 80 | 112 | 100 | 400 | 104 | 0 | 146 | 113 | 0 | 52 | 0 | 101 | 0 |  | 920 | 0 | 160 | 0 | 83 | 200 | 0 | 0 | 26 | 0 | 16 | 88 | 34 | 32 | 0 | 0 | 0 | 43 | 22 | 90 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 11 | 78 | 0 | 250 | 12 | 8 | 0 | 0 | 0 | 216 | 0 | 98 | 120 | 0 | 289 | 95 | 170 | 113 | 15 | 110 | 0 | 0 | 113 | 622 | 221 | 0 | 17 | 0 | 0 | 115 |  | 8767 | 4574 | 13341 | 3489 | 920 | 1557 | 968 | 4246 | 950 | 72 | 436 | 767 | 152 | 0 | 0 | 83.71
24:00 | 0 | 0 | 100 | 0 | 220 | 86 | 0 | 0 | 132 |  | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 98 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 18 | 29 | 33 | 24 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 231 | 0 | 0 | 0 |  | 22 | 41 | 47 | 0 | 95 | 42 | 0 | 37 | 0 | 0 | 0 | 280 | 250 | 167 | 8 | 78 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 25 | 21 | 154 | 22 | 0 | 20 | 0 | 30 | 31 | 53 | 41 | 163 | 240 | 50 | 89 | 0 | 219 | 0 | 27 | 10 | 290 | 23 | 11 | 200 | 300 | 305 | 100 | 107 | 100 | 149 | 0 | 90 | 200 | 148 | 402 | 106 | 70 | 105 | 0 | 281 | 54 | 102 | 80 | 106 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 52 | 0 | 101 | 0 |  | 921 | 0 | 160 | 0 | 49 | 200 | 0 | 0 | 26 | 0 | 16 | 88 | 40 | 16 | 0 | 0 | 0 | 43 | 22 | 90 | 0 | 43 | 40 | 52 | 30 | 21 | 0 | 11 | 78 | 0 | 250 | 12 | 8 | 0 | 0 | 0 | 217 | 0 | 99 | 120 | 0 | 287 | 95 | 170 | 113 | 0 | 110 | 0 | 0 | 113 | 600 | 203 | 0 | 17 | 0 | 0 | 115 |  | 8665 | 4475 | 13140 | 3508 | 921 | 1543 | 974 | 4073 | 928 | 72 | 437 | 747 | 154 | 0 | 0 | 83.7
KWH | 0 | 0 | 2399000 | 0 | 4649736 | 1674818 | 0 | 0 | 3006000 |  | 0 | 0 | 0 | 2180160 | 1468920 | 1322555 | 0 | 0 | 0 | 2320320 | 2216736 | 3539520 | 0 | 0 | 0 | 0 | 1309680 | 1113133 | 886846 | 358884 | 600000 | 473400 | 609100 | 501500 | 1132320 | 0 | 1718313 | 0 | 0 | 3700000 | 511336 | 5015234 | 0 | 0 | 0 |  | 559680 | 671904 | 438752 | 0 | 2160000 | 1003680 | 0 | 505920 | 0 | 0 | 0 | 6999500 | 6274000 | 4277000 | 200727 | 1361100 | 317808 | 255360 | 0 | 1226387 | 0 | 492992 | 1017475 | 279216 | 239040 | 482500 | 498200 | 3595200 | 265920 | 0 | 435924 | 9350 | 716000 | 672264 | 1054800 | 951768 | 3407972 | 5476000 | 1201632 | 2078400 | 0 | 5237900 | 0 | 592740 | 248400 | 7146500 | 542658 | 223632 | 3258816 | 7032979 | 5282358 | 1633301 | 3036000 | 1879365 | 3627792 | 139860 | 2084160 | 4300320 | 3315345 | 9576000 | 2462400 | 2122800 | 2454727 | 27600 | 6997855 | 1327317 | 2592720 | 1904940 | 2478000 | 2369280 | 9406300 | 2606400 | 238390 | 2934720 | 2713582 | 0 | 1030320 | 192714 | 1827840 | 0 |  | 22213090 | 0 | 3725280 | 0 | 861120 | 4896000 | 0 | 0 | 385920 | 3328 | 449250 | 1955633 | 608593 | 385536 | 0 | 0 | 0 | 677536 | 297185 | 1233408 | 0 | 283664 | 534800 | 771840 | 386450 | 456240 | 0 | 268300 | 1866763 | 0 | 6054000 | 128000 | 76000 | 0 | 0 | 0 | 5266173 | 0 | 1440960 | 3031118 | 0 | 6127200 | 2109120 | 2906907 | 2732544 | 155664 | 2548464 | 0 | 36313 | 2671488 | 13605700 | 5192564 | 0 | 94800 | 25200 | 663840 | 2674457 |  | 196680013 | 99800448 | 296480461 | 81769779 | 22213090 | 34734389 | 16401707 | 94160285 | 21526463 | 1718313 | 10366173 | 8661795 | 3595200 | 1333267 | 0
Fuel Cost | 0 | 0 | 3502540 | 0 | 5161206.96 | 2210759.76 | 0 | 0 | 3096180 |  | 0 | 0 | 0 | 16547414.4 | 10120858.8 | 11188815.3 | 0 | 0 | 0 | 17472009.6 | 20216632.32 | 34828876.8 | 0 | 0 | 0 | 0 | 9560664 | 8604518.09 | 8744301.56 | 269163 | 450000 | 0 | 0 | 0 | 10949534.4 | 0 | 463944.51 | 0 | 0 | 6697000 | 4750311.44 | 5466605.06 | 0 | 0 | 0 |  | 0 | 6497311.68 | 4255894.4 | 0 | 18792000 | 7949145.6 | 0 | 1502582.4 | 0 | 0 | 0 | 5179630 | 6274000 | 3934840 | 258937.83 | 1565265 | 359123.04 | 357504 | 0 | 2097121.77 | 0 | 4979219.2 | 9716886.25 | 354604.32 | 179280 | 844375 | 373650 | 26964000 | 281875.2 | 0 | 553623.48 | 149039 | 1174240 | 1075622.4 | 1877544 | 1484758.08 | 3885088.08 | 5695040 | 2367215.04 | 3969744 | 0 | 9061567 | 0 | 693505.8 | 506736 | 7217965 | 406993.5 | 169960.32 | 55432460.16 | 53169321.24 | 89694438.84 | 27308792.72 | 15787200 | 31422982.8 | 35697473.28 | 1634963.4 | 16985904 | 46658472 | 23373182.25 | 8905680 | 22457088 | 20060460 | 21380672.17 | 0 | 52903783.8 | 11560931.07 | 22790008.8 | 19011301.2 | 21236460 | 15779404.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127947398.4 | 0 | 3911544 | 0 | 6768403.2 | 67858560 | 0 | 0 | 4048300.8 | 34877.44 | 4681185 | 2209865.29 | 943319.15 | 3762831.36 | 0 | 0 | 0 | 6666954.24 | 3019399.6 | 10915660.8 | 0 | 3835137.28 | 5182212 | 7479129.6 | 3748565 | 875980.8 | 0 | 203103.1 | 11256580.89 | 0 | 32812680 | 4435200 | 2168280 | 0 | 0 | 0 | 77518066.56 | 0 | 24510729.6 | 3546408.06 | 0 | 6065928 | 22019212.8 | 49446488.07 | 25931842.56 | 1469468.16 | 19776080.64 | 0 | 401258.65 | 19742296.32 | 59729023 | 0 | 0 | 0 | 0 | 0 | 0 |  | 936558203.92 | 624921970.37 | 1561480174.29 | 80174019.77 | 127947398.4 | 37043654.67 | 277815892.19 | 668930341.29 | 103798283.89 | 463944.51 | 151980106.56 | 84177271.96 | 26964000 | 2185261.05 | 0
Yesterday Day Peak | 0 | 0 | 100 | 0 | 220 | 68 | 0 | 0 | 128 |  | 0 | 0 | 0 | 83 | 65 | 55 | 0 | 0 | 0 | 88 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 21 | 21 | 40 | 0 | 35 | 0 | 0 | 150 | 25 | 213 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 77 | 42 | 0 | 2 | 0 | 0 | 0 | 270 | 260 | 139 | 8 | 30 | 23 | 10 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 14 | 20 | 148 | 8 | 0 | 17 | 1 | 30 | 20 | 50 | 38 | 110 | 239 | 55 | 84 | 0 | 220 | 0 | 25 | 10 | 300 | 16 | 8 | 150 | 298 | 301 | 60 | 106 | 96 | 147 | 19 | 90 | 200 | 135 | 392 | 90 | 90 | 87 | 2 | 280 | 54 | 93 | 80 | 95 | 100 | 392 | 104 | 39 | 72 | 113 | 0 | 35 | 35 | 59 | 0 |  | 914 | 0 | 140 | 0 | 16 | 200 | 0 | 0 | 13 | 0 | 16 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 14 | 34 | 0 | 17 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 54 | 114 | 0 | 263 | 76 | 169 | 113 | 0 | 102 | 0 | 3 | 113 | 450 | 220 | 0 | 0 | 3 | 77 | 115 |  | 11914 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 0 | 220 | 88 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 100 | 65 | 55 | 0 | 0 | 0 | 99 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 21 | 49 | 0 | 72 | 0 | 0 | 150 | 25 | 229 | 0 | 0 | 0 | 0 | 22 | 51 | 85 | 0 | 95 | 42 | 0 | 35 | 0 | 0 | 0 | 280 | 250 | 146 | 8 | 79 | 0 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 8 | 19 | 162 | 20 | 0 | 20 | 0 | 30 | 31 | 53 | 40 | 140 | 239 | 55 | 88 | 0 | 220 | 0 | 28 | 10 | 305 | 23 | 11 | 200 | 300 | 304 | 95 | 190 | 100 | 149 | 0 | 90 | 200 | 147 | 403 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 395 | 104 | 0 | 162 | 113 | 0 | 54 | 0 | 101 | 0 |  | 917 | 0 | 140 | 0 | 115 | 200 | 0 | 0 | 15 | 0 | 40 | 89 | 37 | 48 | 0 | 0 | 0 | 43 | 22 | 93 | 0 | 43 | 40 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 250 | 15 | 8 | 0 | 0 | 0 | 213 | 0 | 99 | 114 | 0 | 255 | 94 | 171 | 113 | 15 | 109 | 0 | 0 | 113 | 600 | 221 | 0 | 17 | 0 | 0 | 115 |  | 13406 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 220 | 90 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 78 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 75 | 0 | 0 | 150 | 25 | 230 | 0 | 0 | 0 | 0 | 22 | 50 | 85 | 0 | 100 | 42 | 0 | 35 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 80 | 26 | 25 | 0 | 51 | 0 | 42 | 43 | 22 | 11 | 31 | 22 | 166 | 10 | 0 | 20 | 0 | 20 | 30 | 51 | 41 | 163 | 240 | 55 | 88 | 0 | 220 | 0 | 28 | 10 | 305 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 145 | 400 | 107 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 54 |  | 100 | 0 |  | 940 | 0 | 170 | 0 | 115 | 225 | 0 | 0 | 42 | 30 | 40 | 90 | 35 | 110 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 50 | 40 | 52 | 36 | 22 | 0 | 11 | 80 | 0 | 250 | 17 | 10 | 0 | 0 | 0 | 220 | 0 | 100 | 120 | 0 | 325 | 94 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 220 |  | 100 |  |  | 115
Forecast for Day | 0 | 0 | 100 | 0 | 200 | 90 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 78 | 55 | 0 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 75 | 0 | 0 | 150 | 25 | 230 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 100 | 42 | 0 | 5 | 0 | 0 | 0 | 300 | 300 | 210 | 8 | 40 | 26 | 25 | 0 | 51 | 0 | 32 | 43 | 22 | 11 | 31 | 22 | 143 | 10 | 0 | 20 | 1.6 | 20 | 20 | 50 | 41 | 163 | 240 | 55 | 86 | 0 | 220 | 0 | 27 | 10 | 305 | 24 | 11 | 100 | 300 | 300 | 100 | 106 | 100 | 149 | 20 | 90 | 200 | 145 | 400 | 106 | 90 | 105 | 5 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 50 | 72 | 113 | 0 | 35 | 30 | 100 | 0 |  | 940 | 0 | 170 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 32 | 90 | 25 | 32 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 40 | 0 | 43 | 36 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 120 | 0 | 325 | 94 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 660 | 220 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 220 | 92 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 100 | 78 | 55 | 0 | 0 | 0 | 100 | 84 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 29 | 33 | 25 | 41 | 0 | 72 | 0 | 0 | 150 | 8 | 230 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 92 | 42 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 130 | 8 | 84 | 0 | 5 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 28 | 21 | 130 | 54 | 0 | 20 | 0 | 30 | 31 | 10 | 0 | 163 | 241 | 50 | 85 | 0 | 219 | 0 | 27 | 10 | 290 | 23 | 11 | 0 | 253 | 0 | 50 | 106 | 25 | 149 | 9 | 90 | 116 | 125 | 401 | 106 | 70 | 105 | 2 | 300 | 54 | 110 | 62 | 105 | 50 | 400 | 104 | 13 | 72 | 113 | 0 | 36 | 7 | 59 | 0 | 0 | 922 | 0 | 170 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 16 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 120 | 0 | 325 | 95 | 0 | 113 | 0 | 109 | 0 | 1 | 113 | 450 | 219 | 0 | 0 | 0 | 38 | 115 | 0 |  |  |  |  | 129589960 |  | 0
129589960
| Minimum Generation |  | 10597 | 7:00
| Highest Generation |  | 13431 | 22:00
| Day Peak Generation |  | 11914 | 12:00
| Evening Peak Generation |  | 13406 | 20:00
| HVDC Max Flow |  | 922 | 4:00
| HVDC EvPeak Flow |  | 917 | 20:00
| Load factor L.F |  | 91.98%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-06
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-04-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11914 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10715 | MW
Evening Peak Generation : |  | 13406 | MW Hour : | 20:00 | Available Max Generation : |  | 14251 | MW
E.P. Demand (at gen end) : |  | 13986 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14600 | MW
Maximum Generation : |  | 13431 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 296.4805 | System Load Factor : | 91.98% | Load Shed : |  | 371.7958 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 198 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-06
Actual : | 83.64 | Ft.(MSL) , | Rule curve : | 87 | Ft.( MSL )
Gas Consumed : | Total = | 917.74 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 117217674.44
: |  | Coal : | 103798283.89 | Oil : | 1182903612 | Total : | 1403919570.33
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 45 | 1080:00 | 5475.1351 |  |  | 25.1351 | 0.4612%
Chittagong Area | 45 | 1080:00 | 1870.5559 |  |  | 20.5559 | 1.111%
Khulna Area | 100 | 2400:00 | 1657.4249 |  |  | 76.4249 | 4.834%
Rajshahi Area | 110 | 2640:00 | 1489.6258 |  |  | 89.6258 | 6.402%
Cumilla Area | 20 | 480:00 | 1350.335 |  |  | 0.33498 | 0.02481%
Mymensingh Area | 170 | 4080:00 | 1053.9622 |  |  | 153.9622 | 17.11%
Sylhet Area | 20 | 480:00 | 599.5856 |  |  | -0.41439 | -0.06906%
Barisal Area | 0 | 0:00 | 280.0735 |  |  | 0.073545 | 0.02627%
Rangpur Area | 70 | 1680:00 | 856.0977 |  |  | 6.0977 | 0.7174%
Total | 580 |  | 14632.7958 |  |  | 371.7958
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1
6) Siddhirganj 210 MW .
7) Siddhirganj 335 MW CCPP
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Payra-Gopalganj(P) 132 kV Ckt-1 was switched on at 09:01.
b) Mirsharai 230/132 kV T02 transformer was under shut down from 10:01 to 13:48 for D/W.
c) Keraniganj 230/132 kV ATR-3 transformer was under shut down from 10:00 to 15:39 for D/W.
d) Baghabari-Bhangura 132 kV Ckt-2 was switched on at 09:59.
e) Sreenagar 132/33 kV T-2 transformer was under shut down from 10:27 to 12:05 for C/M.
f) Aminbazar 132 kV Main Bus was under shut down from 09:16 to 13:08 for C/M.
g) Chandpur CCPP ST was synchronized at 12:30.
h) Bhola CCPP ST was synchronized at 10:08.
i) Hasnabad-Brammangaon 132 kV Ckt was shut down at 14:12.
j) Haripur-Madanganj 132 kV Ckt was switched on at 16:45.
k) Gopalganj-Rampal 400 kV Ckt-1 charge at 16:34 from Gopalganj end.
l) Fenchuganj EPL was shut down at 00:14(06/04/2022).
m) Dohazari-Cox'sbazar 132 kV Ckt2 tripped at 04:32(06-04-2022) from both end showing Dist. Z1,
3-phase relays.
n) Ashuganj 132 kV Bus-2 is shut down since 07:05(06-04-2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2399000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 4649736 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 88 | 1674818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 142 | 3006000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 100 | 2180160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 65 | 1468920 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1322555
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 358884
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 99 | 2320320
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2216736 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1309680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3539520
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1113133
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 886846 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1073400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 609100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 501500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1132320 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 7032979
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 5282358
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 95 | 1633301
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1879365
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3627792
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2122800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2606400
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2934720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 192714
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Engine problem
| Dhaka area Total |  |  |  | 5696 | 2738 | 59075057
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 511336
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 139860
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 1003680 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 72 | 1718313 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 229 | 5015234
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2454727
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 671904 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 438752 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2084160 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 505920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 2160000 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27600
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6997855
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1327317
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2592720
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2369280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2713582
| Chattogram area Total |  |  |  | 2382 | 1656 | 36432240
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 146 | 4277000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6999500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6274000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 317808 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 255360 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1226387
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 3315345
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 492992 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 79 | 1361100 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4300320
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 279216
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3595200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 8 | 482500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1017475 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 498200 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 3258816
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1904940 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2478000
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 54 | 1030320 | DCT
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1827840 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2020 | 45632086
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 20 | 265920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 435924
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 190 | 3036000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 2462400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 238390
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 559680
| Mymensingh Area Total |  |  |  | 622 | 367 | 7007664
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 672264 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3407972
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 239 | 5476000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1054800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 40 | 951768
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 223632
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1201632 | Machine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 2078400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5237900
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 28 | 592740
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 542658
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7146500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9576000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248400
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9406300
| Sylhet Area Total |  |  |  | 2377 | 2071 | 48532966
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22213090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 115 | 861120
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 385920 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 4896000 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 3328 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 140 | 3725280 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 40 | 449250
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 99 | 1440960
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 2109120 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 155664 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 663840
| Khulna Area Total |  |  |  | 2229 | 1635 | 36903572
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 385536 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 37 | 608593
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 1955633 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 13605700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 5192564
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 94800 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 1012 | 21842826
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 677536 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 22 | 297185 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 283664 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 534800 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 5266173 | Running on HSD
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 114 | 3031118 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 255 | 6127200 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 386450 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 456240
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 268300
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 771840
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 1233408 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 171 | 2906907
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2732544
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2671488
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25200
| Rajshahi Area Total |  |  |  | 2129 | 1330 | 27670053
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1866763
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6054000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 128000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 76000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 109 | 2548464 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36313
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2674457
| Rangpur Area Total |  |  |  | 720 | 577 | 13383997
| Total |  |  |  | 21215 | 13406 | 296480461
| Eastern Grid Total |  |  |  | 14091 | 8852 | 196680013
| Western Grid Total |  |  |  | 7124 | 4554 | 99800448
| National Grid Total |  |  |  | 21215 | 13406 | 296480461
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-05
(a) ENTIRE EASTERN GRID : |  | 8868.98 | MW | (b) ENTIRE WESTERN GRID : |  | 3989 | MW
i) Dhaka area |  | 4901.98 | MW | i) Khulna area |  | 1554.4 | MW
ii) Chittagong area |  | 1281 | MW | ii) Rajshahi area |  | 1296.6 | MW
iii) Comilla area |  | 1267 | MW | iii) Barisal area |  | 381 | MW
iv) Mymensingh area |  | 926 | MW | iv) Rangpur area |  | 757 | MW
v) Sylhet area |  | 493 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12857.98 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 19:00 | Hasnabad | 71 | 22:00 | Palashbari | 122 | 23:00
Agargaon | 88 | 13:00 | Hathazari | 98 | 19:00 | Panchagarh | 53 | 19:30
Agrabad | 84 | 14:00 | Ishurdi | 70 | 03:00 | Patuakhali | 121 | 21:00
AKS | 10 | 12:00 | Jaldhaka | 48 | 18:00 | PHP | 10 | 01:00
AKSML | 136 | 10:00 | Jamalpur | 117 | 18:30 | Purbachal | 19 | 20:00
Amnura | 58 | 00:00 | Jashore | 125 | 21:00 | Purbasadipur | 102 | 18:00
Ashuganj | 36 | 22:00 | Jhenaidah | 118 | 22:00 | Rahim | 25 | 09:00
Bagerhat | 104 | 23:00 | Joydebpur | 194 | 10:00 | Rajbari | 62 | 03:00
Bakulia | 123 | 22:00 | Joypurhat | 59 | 03:00 | Rajendrapur | 124 | 19:30
Banani | 236 | 15:00 | Juldah | 23 | 23:00 | Rajshahi | 155 | 23:00
Bangabhaban | 20 | 11:00 | Kabirpur | 287 | 09:00 | Rajshahi | 35 | 22:00
Barapukuria | 57 | 14:00 | Kachua | 72 | 21:00 | Ramganj | 90 | 19:00
Barguna | 18 | 19:30 | Kallyanpur | 102 | 20:00 | Rampur | 16.7 | 18:30
Barishal | 103 | 19:30 | Kalurghat | N/A | N/A | Rangamati | 12 | 18:00
Barishal | 60 | 22:00 | Kamrangirchar | 72 | 16:00 | Rangpur | 134 | 23:00
Baroaulia | 75 | 11:00 | Kaptai | 4 | 03:00 | Ruppur | 4.8 | 15:00
Baroirhat | 53 | 21:00 | Kazla | 84 | 16:00 | Saidpur | 99 | 19:00
Bashundhara | 170 | 14:00 | Keranigonj | 76 | 01:00 | Satkhira | 114 | 23:00
BashundharaCement | 12 | 00:00 | Khagrachori | 26 | 18:00 | Satmasjid | 98 | 19:00
Beanibazar | 57 | 19:00 | Khulna | 90 | 21:00 | Savar | 189 | 12:00
Benapole | 52 | 19:00 | Khulshi | 180 | 16:00 | Shahjadpur | 103 | 19:30
Bhaluka | 88 | 10:00 | Kishoreganj | 104 | 20:00 | Shahjibazar | 112 | 22:00
Bhandaria | 58 | 21:00 | Kodda | 320 | 14:00 | Shahmirpur | 45.5 | 04:00
Bhangura | 32 | 05:00 | KSRM | 22 | 13:00 | Shariatpur | 72 | 21:00
Bheramara(GK) | 59 | 23:00 | Kulaura | 46 | 18:30 | Sherpur | 114 | 21:00
Bhulta | 251 | 22:00 | Kurigram | 56 | 20:00 | Shikalbaha | 32 | 15:00
Bog-Sherpur | 66 | 03:00 | Kushtia | 132 | 20:00 | Shitalakhya | 128 | 16:00
Bogura | 169 | 23:00 | Lalbag | 95 | 16:00 | Sholosohor | N/A | N/A
Borhanuddin | 244 | 09:00 | Lalmonirhat | 44 | 20:00 | Shyampur | 168 | 09:00
Brahmanbaria | 146 | 00:00 | Madanganj | 162 | 00:00 | Siddhirganj | 112 | 15:00
BSRM | 163 | 19:30 | Madaripur | 107 | 21:00 | Sirajganj | 108 | 11:00
Cantonment | 136 | 14:00 | Madartek | 83 | 22:00 | Sonargaon | 116 | 23:00
Chandpur | 76 | 21:00 | Madunaghat | 58.5 | 19:30 | Sreemongol | 56 | 19:30
Chandraghona | 34 | 08:00 | Magura | 56 | 03:00 | Srinagar | 44.8 | 21:00
Chapai | 70 | 23:00 | Mahasthangarh | 74 | 03:00 | SSM | 15 | 06:00
Charsaidpur | 44 | 12:00 | Manikganj | 90 | 21:00 | Sunamganj | 51 | 21:00
Chauddagram | 60 | 20:00 | Maniknagar | 73 | 14:00 | Sylhet | 135 | 19:00
Chhatak | 26 | 18:30 | Matarbari | 40 | 22:00 | Tangail | 232 | 20:00
Chowmuhani | 219 | 20:00 | Matuail | 64 | 10:00 | Thakurgaon | 74 | 19:00
Chuadanga | 98 | 04:00 | Millgate | 62 | 11:00 | TK | 27.6 | 00:00
Coxsbazar | 119 | 23:00 | Mirpur | 127 | 21:00 | Tongi | 134 | 20:00
Cumilla(N) | 149 | 20:00 | Mirsorai | N/A | N/A | Ullon | 51 | 19:30
Cumilla(S) | 168 | 14:00 | Mithapukur | 30 | 03:00 | Uttara | 69 | 19:00
Daudkandi | 148 | 20:00 | Modern | 0 | 00:00 | UttaraNew | 33 | 12:00
Dhaka | 37 | 11:00 | Mogbazar | 127 | 15:00 | Zigatola | 42 | 20:00
Dhamrai | 120 | 19:30 | Mongla | 36 | 12:00
Dhanmondi | 198 | 13:00 | Motijheel | 35 | 15:00
Dohazari | 90 | 00:00 | Munshiganj | 108 | 00:00
Faridpur | 146 | 21:00 | Mymensingh | 224 | 18:00
Fatullah | 73 | 15:00 | Naogaon | 122 | 23:00
Fenchuganj | 46 | 19:00 | Narail | 48 | 18:30
Feni | 132 | 20:00 | Narinda | 61 | 12:00
Ghorashal | 80 | 15:00 | Narshingdi | 175 | 23:00
Goalpara | 29 | 21:00 | Natore | 136 | 19:30
Gollamari | 51 | 23:00 | Nawabganj | 56 | 21:00
Gopalganj | 101.8 | 21:00 | Netrakona | 97 | 08:00
GPH | 93 | 14:00 | New | 84.6 | 14:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 4:00 | 395 | 9:00 | Kaliakoir | 385 | 0.75 | 370 | 0.41667
| Bheramara | 395 | 2:00 | 388 | 16:00 | Bhulta | 398 | 0.16667 | 378 | 0.45833
| Ashuganj(N) | 408 | 18:30 | 387 | 10:00 | Gopalganj | 412 | 0.625 | 395 | 0.95833
| Payra | 420 | 4:00 | 407 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 23:00 | 225 | 14:00 | Hathazari | 236 | 17:00 | 231 | 10:00
| Ishurdi | 237 | 18:30 | 230 | 3:00 | Megnaghat | 228 | 17:00 | 222 | 9:00
| Ashuganj | 240 | 4:00 | 230 | 9:00 | Fenchuganj | 239 | 2:00 | 234 | 10:00
| Serajganj | 235 | 1:00 | 232 | 9:00 | Siddhirganj | 227 | 4:00 | 215 | 9:00
| Baghabari | 235 | 18:30 | 229 | 5:00 | Maniknagar | 226 | 4:00 | 212 | 10:00
| Barapukuria | 231 | 5:00 | 225 | 23:00 | Agargaon | 226 | 8:00 | 212 | 10:00
| Bogra | 231 | 4:00 | 226 | 23:00 | Barisal | 240 | 22:00 | 234 | 19:30
| Rajshahi | 227 | 18:00 | 220 | 6:00 | Bhola 225 MW | 244 | 9:00 | 237 | 22:00
| Khulna South | 240 | 18:30 | 232 | 3:00 | AKSML | 238 | 22:00 | 228 | 10:00
| Rampura | 226 | 4:00 | 213 | 11:00 | BSRM | 233 | 2:00 | 226 | 10:00
| Haripur | 225 | 1:00 | 213 | 10:00 | Bibiyana | 236 | 12:00 | 232 | 7:00
| Hasnabad | 224 | 24:00 | 214 | 9:00 | Bhulta | 228 | 4:00 | 215 | 10:00
| Shyampur | 228 | 4:00 | 213 | 9:00 | Ashuganj (S) | 237 | 4:00 | 227 | 9:00
| Aminbazar | 225 | 1:00 | 213 | 2:00 | Kaliakoir | 226 | 4:00 | 214 | 11:00
| Tongi | 230 | 19:30 | 212 | 10:00 | GPH | 236 | 8:00 | 228 | 10:00
| Comilla (N) | 230 | 2:00 | 222 | 9:00 | Jhenaidah | 232 | 18:30 | 224 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 18:00 | 125 | 10:00 | Manikganj | 130 | 03:00 | 122 | 19:00
| Agargaon | 137 | 04:00 | 127 | 10:00 | Maniknagar | 131 | 03:00 | 122 | 10:00
| Agrabad | 138 | 18:30 | 129 | 13:00 | Matarbari | 121 | 06:00 | 111 | 15:00
| AKS | 136 | 06:00 | 129 | 10:00 | Matuail | 138 | 17:00 | 125 | 09:00
| Aminbazar | 130 | 18:00 | 125 | 14:00 | Millgate | 134 | 03:00 | 124 | 13:00
| Amnura | 136 | 18:00 | 130 | 05:00 | Mirpur | 130 | 01:00 | 123 | 11:00
| Ashuganj | 135 | 05:00 | 131 | 16:00 | Mithapukur | 133 | 05:00 | 126 | 23:00
| Bagerhat | 135 | 18:00 | 130 | 03:00 | Modern | 135 | 21:00 | 131 | 09:00
| Bakulia | 135 | 08:00 | 129 | 15:00 | Mogbazar | 136 | 02:00 | 125 | 11:00
| Banani | 133 | 03:00 | 123 | 12:00 | Mongla | 135 | 18:00 | 131 | 15:00
| Bangabhaban | 132 | 04:00 | 122 | 11:00 | Motijheel | 132 | 04:00 | 122 | 11:00
| Barapukuria | 133 | 05:00 | 129 | 23:00 | Munshiganj | 141 | 03:00 | 130 | 10:00
| Barguna | 138 | 18:30 | 128 | 00:00 | Mymensingh | 116 | 13:00 | 112 | 03:00
| Barishal | 139 | 06:00 | 126 | 00:00 | Naogaon | 130 | 18:30 | 125 | 14:00
| Barishal | 141 | 08:00 | 134 | 19:30 | Narail | 130 | 18:00 | 125 | 23:00
| Baroaulia | 136 | 18:00 | 131 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 03:00 | 130 | 19:00 | Narshingdi | 128 | 19:00 | 120 | 10:00
| Bashundhara | 133 | 01:00 | 123 | 10:00 | Natore | 138 | 18:30 | 133 | 01:00
| BashundharaCement | 140 | 04:00 | 130 | 10:00 | Nawabganj | 140 | 02:00 | 130 | 15:00
| Beanibazar | 133 | 05:00 | 128 | 19:00 | Netrakona | 116 | 05:00 | 111 | 23:00
| Benapole | 132 | 18:00 | 127 | 06:00 | New | 133 | 04:00 | 124 | 10:00
| Bhaluka | 119 | 11:00 | 109 | 23:00 | Niamatpur | 127 | 18:30 | 120 | 14:00
| Bhandaria | 139 | 08:00 | 127 | 21:00 | Noapara | 137 | 18:30 | 131 | 07:00
| Bhangura | 136 | 18:30 | 131 | 07:00 | Pabna | 135 | 18:30 | 130 | 03:00
| Bheramara | 136 | 18:30 | 132 | 03:00 | Palashbari | 130 | 02:00 | 126 | 16:00
| Bheramara(GK) | 137 | 13:00 | 133 | 23:00 | Panchagarh | 134 | 02:00 | 127 | 19:30
| Bhulta | 126 | 04:00 | 116 | 10:00 | Patuakhali | 137 | 18:30 | 128 | 00:00
| Bog-Sherpur | 135 | 18:30 | 131 | 03:00 | PHP | 135 | 04:00 | 129 | 13:00
| Bogura | 136 | 03:00 | 132 | 07:00 | Purbachal | 134 | 03:00 | 122 | 13:00
| Bogura | 136 | 18:30 | 132 | 23:00 | Purbasadipur | 133 | 05:00 | 126 | 23:00
| Brahmanbaria | 129 | 06:00 | 124 | 23:00 | Rahim | 134 | 03:00 | 126 | 09:00
| Cantonment | 135 | 01:00 | 125 | 10:00 | Rajbari | 135 | 18:30 | 126 | 23:00
| Chandpur | 140 | 11:00 | 136 | 07:00 | Rajendrapur | 131 | 04:00 | 120 | 11:00
| Chandraghona | 136 | 06:00 | 132 | 13:00 | Rajshahi | 139 | 18:00 | 132 | 06:00
| Chapai | 138 | 18:00 | 130 | 07:00 | Rajshahi | 138 | 00:00 | 133 | 08:00
| Charsaidpur | 139 | 18:00 | 130 | 10:00 | Ramganj | 135 | 04:00 | 130 | 19:00
| Chauddagram | 136 | 04:00 | 131 | 13:00 | Rampur | 135 | 22:00 | 130 | 15:00
| Chhatak | 132 | 03:00 | 128 | 21:00 | Rampura | 136 | 18:30 | 125 | 10:00
| Chowmuhani | 132 | 07:00 | 127 | 00:00 | Rangamati | 135 | 04:00 | 131 | 15:00
| Chuadanga | 127 | 18:00 | 121 | 03:00 | Rangpur | 132 | 05:00 | 125 | 23:00
| Coxsbazar | 122 | 08:00 | 110 | 15:00 | Ruppur | 135 | 01:00 | 133 | 08:00
| Cumilla(N) | 136 | 02:00 | 132 | 09:00 | Saidpur | 130 | 06:00 | 126 | 23:00
| Cumilla(S) | 137 | 01:00 | 123 | 14:00 | Satkhira | 134 | 14:00 | 130 | 17:00
| Daudkandi | 137 | 18:30 | 128 | 10:00 | Satmasjid | 136 | 02:00 | 127 | 09:00
| Dhaka | 135 | 03:00 | 124 | 10:00 | Savar | 135 | 04:00 | 124 | 09:00
| Dhamrai | 133 | 04:00 | 125 | 09:00 | Shahjadpur | 137 | 02:00 | 134 | 07:00
| Dhanmondi | 134 | 02:00 | 125 | 10:00 | Shahjibazar | 132 | 05:00 | 128 | 21:00
| Dohazari | 131 | 08:00 | 122 | 15:00 | Shahmirpur | 135 | 04:00 | 130 | 13:00
| Faridpur | 135 | 18:00 | 128 | 15:00 | Shariatpur | 138 | 06:00 | 130 | 19:30
| Fatullah | 137 | 04:00 | 126 | 09:00 | Sherpur | 124 | 18:00 | 116 | 23:00
| Fenchuganj | 135 | 00:00 | 133 | 10:00 | Shikalbaha | 136 | 21:00 | 131 | 14:00
| Feni | 135 | 08:00 | 130 | 15:00 | Shikalbaha | 135 | 18:00 | 130 | 16:00
| Ghorashal | 136 | 23:00 | 130 | 01:00 | Shitalakhya | 140 | 03:00 | 131 | 10:00
| Goalpara | 139 | 18:30 | 135 | 02:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 134 | 11:00 | 127 | 19:30 | Shyampur | 135 | 01:00 | 126 | 09:00
| Gopalganj | 136 | 09:00 | 129 | 20:00 | Shyampur | 136 | 04:00 | 126 | 09:00
| Gopalganj_I | 139 | 09:00 | 132 | 21:00 | Siddhirganj | 133 | 01:00 | 125 | 10:00
| Gulshan | 135 | 03:00 | 124 | 11:00 | Sirajganj | 133 | 18:30 | 129 | 10:00
| Halishahar | 135 | 18:30 | 130 | 13:00 | Sonargaon | 134 | 00:00 | 128 | 09:00
| Haripur | 134 | 03:00 | 126 | 09:00 | Sreemongol | 134 | 00:00 | 132 | 23:00
| HaripurSBU | 135 | 03:00 | 125 | 10:00 | Srinagar | 141 | 02:00 | 130 | 11:00
| Hasnabad | 137 | 18:30 | 128 | 09:00 | SSM | 136 | 03:00 | 130 | 17:00
| Hathazari | 138 | 18:00 | 132 | 15:00 | Sunamganj | 131 | 06:00 | 125 | 21:00
| Ishurdi | 137 | 18:30 | 133 | 03:00 | Sylhet | 133 | 04:00 | 130 | 21:00
| Jaldhaka | 130 | 02:00 | 123 | 06:00 | Tangail | 123 | 13:00 | 119 | 15:00
| Jamalpur | 127 | 18:00 | 120 | 01:00 | Thakurgaon | 134 | 05:00 | 128 | 20:00
| Jashore | 133 | 18:30 | 127 | 07:00 | TK | 136 | 07:00 | 133 | 00:00
| Jhenaidah | 134 | 18:30 | 129 | 07:00 | Tongi | 132 | 03:00 | 126 | 10:00
| Jhenaidah | 134 | 18:30 | 129 | 03:00 | Ullon | 134 | 02:00 | 125 | 10:00
| Joydebpur | 138 | 04:00 | 129 | 10:00 | Uttara | 134 | 04:00 | 122 | 11:00
| Joypurhat | 127 | 11:00 | 122 | 00:00 | UttaraNew | 133 | 00:00 | 123 | 09:00
| Juldah | 136 | 03:00 | 130 | 15:00 | Zigatola | 141 | 03:00 | 130 | 11:00
| Kabirpur | 133 | 03:00 | 122 | 10:00
| Kachua | 137 | 03:00 | 133 | 13:00
| Kaliakoir | 134 | 18:30 | 127 | 15:00
| Kallyanpur | 134 | 02:00 | 124 | 14:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 143 | 03:00 | 130 | 09:00
| Kaptai | 136 | 22:00 | 132 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 334 | 8665 | 4475 | 13140 |  |  |  | QF-LDC-11
0:30 | 358 | 8448 | 4361.5 | 12809.5 | Date: | 2022-04-05
1:00 | 382 | 8231 | 4248 | 12479
1:30 | 361 | 8186 | 4198.5 | 12384.5
2:00 | 340 | 8141 | 4149 | 12290
2:30 | 282 | 8151.5 | 4157 | 12308.5 | [5 empty] | Gen. at Eve. Peak | 13406 | 13406 MW (20:00 )
3:00 | 224 | 8162 | 4165 | 12327 | [6 empty] | 20:00
3:30 | 294 | 8068 | 4169.5 | 12237.5 | [5 empty] | Gen. at Day Peak | 11914 | 11914 MW (12:00 )
4:00 | 364 | 7974 | 4174 | 12148 | [6 empty] | 12:00
4:30 | 338 | 7815.5 | 3954.5 | 11770 | [5 empty] | Highest Generation | 13431
5:00 | 312 | 7657 | 3735 | 11392 | [6 empty] | 22:00
5:30 | 306 | 7464.5 | 3587 | 11051.5
6:00 | 300 | 7272 | 3439 | 10711
6:30 | 354 | 7238.5 | 3415.5 | 10654
7:00 | 408 | 7205 | 3392 | 10597
7:30 | 438 | 7277.5 | 3476.5 | 10754
8:00 | 468 | 7350 | 3561 | 10911
8:30 | 510 | 7465 | 3597 | 11062
9:00 | 552 | 7580 | 3633 | 11213
9:30 | 588 | 7673 | 3679 | 11352
10:00 | 624 | 7766 | 3725 | 11491
10:30 | 645 | 7863.5 | 3810 | 11673.5
11:00 | 666 | 7961 | 3895 | 11856
11:30 | 649 | 7989.5 | 3895.5 | 11885
12:00 | 632 | 8018 | 3896 | 11914
12:30 | 594 | 8106 | 3964.5 | 12070.5
13:00 | 556 | 8194 | 4033 | 12227
13:30 | 585 | 8214.5 | 4054 | 12268.5
14:00 | 614 | 8235 | 4075 | 12310
14:30 | 597 | 8295.5 | 4123 | 12418.5
15:00 | 580 | 8356 | 4171 | 12527
15:30 | 570 | 8344.5 | 4174 | 12518.5
16:00 | 560 | 8333 | 4177 | 12510
16:30 | 447 | 8306 | 4080 | 12386
17:00 | 334 | 8279 | 3983 | 12262
17:30 | 303 | 8294.5 | 4002.5 | 12297
18:00 | 272 | 8310 | 4022 | 12332
18:30 | 299 | 8513 | 4186 | 12699
19:00 | 326 | 8716 | 4350 | 13066
19:30 | 328 | 8830 | 4536 | 13366
20:00 | 346 | 8852 | 4554 | 13406 |  |  |  | Executive Engineer
20:30 | 330 | 8828.5 | 4575.5 | 13404 |  |  |  | Network Operation Division
21:00 | 314 | 8805 | 4597 | 13402
21:30 | 317 | 8811 | 4605.5 | 13416.5
22:00 | 320 | 8817 | 4614 | 13431 |  |  |  |  | Page 6 of 7
22:30 | 305 | 8792 | 4594 | 13386
23:00 | 290 | 8767 | 4574 | 13341
23:30 | 312 | 8716 | 4524.5 | 13240.5
24:00 | 334 | 8665 | 4475 | 13140
13406 MW (20:00 )
11914 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-05 |  | Energy |  | 296480461
[13 empty] | 2022-04-05 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3508 | 921 | 1543 | 974 | 4073 | 928 | 72 | 437 | 747 | 154 | 0 | 0
0:30 | 3382.5 | 921 | 1473.5 | 972.5 | 3996.5 | 917.5 | 73.5 | 427 | 711.5 | 151 | 0 | 0 | Date: | 2022-04-05
1:00 | 3257 | 921 | 1404 | 971 | 3920 | 907 | 75 | 417 | 676 | 148 | 0 | 0
1:30 | 3263 | 921 | 1396 | 878.5 | 3932.5 | 897 | 75 | 418 | 674.5 | 147 | 0 | 0 | [7 empty] | Total Energy | 296.4805 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3269 | 921 | 1388 | 786 | 3945 | 887 | 75 | 419 | 673 | 146 | 0 | 0 | [7 empty] | Energy not Served | 0.4176
2:30 | 3291.5 | 921 | 1400.5 | 773.5 | 3935.5 | 887 | 75 | 419 | 677.5 | 147 | 0 | 0 | [7 empty] | Energy Requirement | 296.8981
3:00 | 3314 | 921 | 1413 | 761 | 3926 | 887 | 75 | 419 | 682 | 148 | 0 | 0
3:30 | 3363.5 | 921.5 | 1409.5 | 635.5 | 3913 | 887 | 75 | 419.5 | 682.5 | 150 | 0 | 0 | [5 empty] | Shortage
4:00 | 3413 | 922 | 1406 | 510 | 3900 | 887 | 75 | 420 | 683 | 152 | 0 | 0
4:30 | 3425.5 | 921.5 | 1409 | 261 | 3892 | 862.5 | 75 | 420 | 577.5 | 146 | 0 | 0
5:00 | 3438 | 921 | 1412 | 12 | 3884 | 838 | 75 | 420 | 472 | 140 | 0 | 0
5:30 | 3439.5 | 921 | 1402 | 6 | 3645 | 818 | 74.5 | 420 | 412.5 | 133 | 0 | 0
6:00 | 3441 | 921 | 1392 | 0 | 3406 | 798 | 74 | 420 | 353 | 126 | 0 | 0
6:30 | 3409.5 | 921.5 | 1401.5 | 0 | 3359 | 798 | 74.5 | 420 | 353 | 124 | 13 | 0 |  |  |  | Coal
7:00 | 3378 | 922 | 1411 | 0 | 3312 | 798 | 75 | 420 | 353 | 122 | 26 | 0
7:30 | 3375.5 | 922 | 1424.5 | 31 | 3389.5 | 808.5 | 75 | 419.5 | 352.5 | 128 | 47.5 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3373 | 922 | 1438 | 62 | 3467 | 819 | 75 | 419 | 352 | 134 | 69 | 0
8:30 | 3369.5 | 921.5 | 1417.5 | 129.5 | 3567.5 | 804 | 75 | 418.5 | 360 | 137 | 80.5 | 0
9:00 | 3366 | 921 | 1397 | 197 | 3668 | 789 | 75 | 418 | 368 | 140 | 92 | 0
9:30 | 3362.5 | 918.5 | 1399 | 298.5 | 3674 | 804.5 | 75 | 417.5 | 367.5 | 142 | 110.5 | 0
10:00 | 3359 | 916 | 1401 | 400 | 3680 | 820 | 75 | 417 | 367 | 144 | 129 | 0
10:30 | 3371.5 | 916 | 1395.5 | 540 | 3679.5 | 809 | 75 | 416 | 382.5 | 145 | 159.5 | 0
11:00 | 3384 | 916 | 1390 | 680 | 3679 | 798 | 75 | 415 | 398 | 146 | 190 | 0
11:30 | 3346.5 | 915 | 1394.5 | 755 | 3685.5 | 789 | 55 | 413 | 413 | 147 | 184.5 | 0
12:00 | 3309 | 914 | 1399 | 830 | 3692 | 780 | 35 | 411 | 428 | 148 | 179 | 0
12:30 | 3296 | 914 | 1409 | 891.5 | 3703 | 779 | 53.5 | 410 | 481 | 153 | 190.5 | 0
13:00 | 3283 | 914 | 1419 | 953 | 3714 | 778 | 72 | 409 | 534 | 158 | 202 | 0
13:30 | 3283 | 914 | 1419 | 953 | 3714 | 778 | 72 | 409 | 534 | 158 | 202 | 0
14:00 | 3283 | 914 | 1419 | 953 | 3714 | 778 | 72 | 409 | 534 | 158 | 202 | 0
14:30 | 3312 | 915 | 1430 | 957 | 3775 | 829 | 72 | 412.5 | 558 | 163 | 162 | 0
15:00 | 3341 | 916 | 1441 | 961 | 3836 | 880 | 72 | 416 | 582 | 168 | 122 | 0
15:30 | 3340 | 916.5 | 1425 | 961 | 3872 | 855.5 | 72 | 424.5 | 591 | 165 | 105 | 0
16:00 | 3339 | 917 | 1409 | 961 | 3908 | 831 | 72 | 433 | 600 | 162 | 88 | 0
16:30 | 3332 | 916.5 | 1401.5 | 881.5 | 3936.5 | 804.5 | 72 | 418 | 597 | 156 | 62 | 0
17:00 | 3332 | 916 | 1394 | 802 | 3965 | 778 | 72 | 403 | 594 | 150 | 36 | 0
17:30 | 3290 | 916.5 | 1373 | 737.5 | 4108 | 769 | 71.5 | 403 | 635.5 | 154 | 19 | 0
18:00 | 3248 | 917 | 1352 | 673 | 4251 | 760 | 71 | 403 | 677 | 158 | 2 | 0
18:30 | 3323 | 917 | 1408.5 | 802.5 | 4296.5 | 785 | 71.5 | 409 | 707 | 163 | 1 | 0
19:00 | 3398 | 917 | 1465 | 932 | 4342 | 810 | 72 | 415 | 737 | 168 | 0 | 0
19:30 | 3443 | 916 | 1513 | 965 | 4390 | 910 | 72 | 435 | 774 | 160 | 0 | 0
20:00 | 3444 | 917 | 1528 | 969 | 4383 | 930 | 72 | 436 | 778 | 162 | 0 | 580
20:30 | 3447 | 916.5 | 1541.5 | 969.5 | 4359.5 | 941 | 72 | 435 | 771.5 | 163 | 0 | 290
21:00 | 3450 | 916 | 1555 | 970 | 4336 | 952 | 72 | 434 | 765 | 164 | 0 | 0
21:30 | 3466 | 916 | 1560.5 | 970.5 | 4326 | 951.5 | 72 | 435.5 | 769 | 163 | 0 | 0
22:00 | 3482 | 916 | 1566 | 971 | 4316 | 951 | 72 | 437 | 773 | 162 | 0 | 0
22:30 | 3485.5 | 918 | 1561.5 | 969.5 | 4281 | 950.5 | 72 | 436.5 | 770 | 157 | 0 | 0
23:00 | 3489 | 920 | 1557 | 968 | 4246 | 950 | 72 | 436 | 767 | 152 | 0 | 0
23:30 | 3498.5 | 920.5 | 1550 | 971 | 4159.5 | 939 | 72 | 436.5 | 757 | 153 | 0 | 0 | Max Temp. in Dhaka |  | 34.2° C
24:00 | 3508 | 921 | 1543 | 974 | 4073 | 928 | 72 | 437 | 747 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-04-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 74 | 75 | 75 | 75 | 75 | 75 | 35 | 72 | 71 | 72 | 72 | 72 | 71 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1718313
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 |  |  | 2 | 8 | 14 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 511336
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 9 | 14 | 18 | 19 | 19 | 19 | 17 | 13 | 8 | 2 | [9 empty] | 139860
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 205 | 215 | 202 | 203 | 203 | 216 | 203 | 220 | 207 | 203 | 213 | 223 | 206 | 203 | 203 | 219 | 203 |  | 221 | 229 | 229 | 229 | 229 | 229 | 231 | 5015234
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 59 | 85 | 85 | 68 | 68 | 68 | 47 | 438752
12 | Hathazari 100 MW peaking PP | 20 | 20 | 30 | 30 | [6 empty] | 17 | 34 | 34 | 34 | 35 | 42 | 51 | 51 |  | 51 | 50 | 51 | 51 | 50 | 41 | 41 | 671904
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 93 | 87 | 92 | 100 | 91 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2454727
| Daudkandi 200 MW PP (B.Trac) | 200 | 150 | 120 | 10 |  |  |  |  | 0 | 50 | 120 | 150 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3258816
14 | Titas 50 MW Peaking PP | 33 | 33 | 33 | 33 | [8 empty] | 11 | 31 | 32 |  | 3 | 33 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 492992
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 298 | 300 | 298 | 245 | 245 | 258 | 280 | 280 | 280 | 298 | 298 | 300 | 291 | 291 | 298 | 298 |  | 298 | 298 | 300 | 300 | 300 | 298 | 300 | 7032979
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 86 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2399000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 22 | 36 | 86 | 197 | 219 | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4649736
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 10 | 8 | 8 | 8 | 8 | [8 empty] | 0 | 317808
33 | Ashuganj 225 MW CCPP | 220 | 221 | 220 | 222 | 224 | 224 | 207 | 208 | 211 | 212 | 185 | 139 | 142 | 135 | 128 | 127 | 132 | 139 |  | 147 | 147 | 146 | 152 | 152 | 153 | 167 | 4277000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 255 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6274000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 260 | 270 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6999500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 15 | 40 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 255360
36 | Chandpur 150 MW CCPP | 40 | 39 | 40 | 40 | 39 | 40 | 30 | 30 | 30 | 30 | 31 | 30 | 85 | 85 | 85 | 85 | 85 | 84 |  | 78 | 79 | 79 | 78 | 78 | 78 | 78 | 1361100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP | [16 empty] | 0
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 116 | 128 | 128 | 127 | 128 | 133 | 131 | 130 | 130 | 130 | 130 |  | 137 | 143 | 142 | 138 | 136 | 132 | 132 | 3006000
42 | RPCL 210MW CCPP | 8 | 8 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 12 | 12 | 12 | 12 | 12 |  | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 265920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 14 | 9 | 9 | 48 | 39 | 44 | 43 | 14 | 19 | 8 | [9 empty] | 238390
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 20 | 21 | 21 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 672264
46 | Shajibazar 330 MW CCPP | 240 | 245 | 240 | 243 | 241 | 242 | 238 | 240 | 240 | 241 | 244 | 239 | 231 | 235 | 238 | 238 | 241 | 241 |  | 240 | 240 | 239 | 242 | 240 | 239 | 240 | 5476000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 50 | 50 | 50 | 50 | 50 | 40 |  | 50 | 55 | 55 | 50 | 50 | 50 | 50 | 1201632
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 84 | 84 | 84 | 85 | 86 | 87 | 87 |  | 88 | 88 | 88 | 88 | 89 | 89 | 89 | 2078400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 193 | 193 |  | 220 | 220 | 220 | 213 | 219 | 220 | 219 | 5237900
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 24 | 25 | 25 | 26 | 25 | 26 | 25 | 27 | 27 |  | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 592740
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248400
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 11 | 11 | 2 | 5 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223632
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 42 | 42 | 45 | 47 | 50 | 50 | 50 | 50 | 50 | 53 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1054800
56 | Shahjahanulla 25 MW PP | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 22 | 22 | 22 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 542658
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 285 | 280 | 275 | 285 | 295 | 300 | 290 | 300 | 300 | 300 | 305 | 305 | 295 | 290 | 290 | 260 |  | 275 | 300 | 305 | 290 | 300 | 290 | 290 | 7146500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 397 | 400 | 391 | 392 | 393 | 390 | 388 | 398 | 382 | 350 |  | 382 | 395 | 395 | 390 | 400 | 400 | 400 | 9406300
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 886846
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 559680
60 | Barabkunda 22 MW PP (Regent) | [19 empty] | 0 |  | 0 |  |  |  | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | [6 empty] | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 358884
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 435924
63 | Impoprt (Tripura) | 148 | 146 | 148 | 152 | 140 | 126 | 122 | 134 | 140 | 144 | 146 | 148 | 158 | 168 | 168 | 162 | 150 | 158 |  | 168 | 160 | 162 | 164 | 162 | 152 | 154 | 3595200
64 | Malancha, Ctg. EPZ (United) | 33 | 36 | 36 | 36 | 38 | 28 | 8 | 3 | 2 | 2 | 2 | 2 | 9 | 2 | 2 | 4 | 10 | 27 |  | 31 | 33 | 35 | 35 | 37 | 36 | 37 | 505920
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [10 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 279216
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239040
67 | Jangalia 33MW PP (Summit) | 31 | 31 | 31 | 31 | 32 | 33 | 32 | 30 | 25 | 20 | 18 | 14 | 14 | 12 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 16 | 17 | 25 | 482500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 498200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 18 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 12 | 12 | 17 | 20 | 23 | 23 | 23 | 24 | 24 | 24 | 26 | 9 | 9 | 17 | 20 |  | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 473400
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 21 | 21 | 21 | 21 | 21 | 25 | 32 | 32 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 609100
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 24 | 501500
73 | Ghorashal 108MW PP (Regent) | 64 | 65 | 63 | 58 | 57 | 56 | 58 | 59 | 62 | 63 | 65 | 68 | 76 | 76 | 73 | 77 | 77 | 77 |  | 80 | 88 | 88 | 86 | 86 | 86 | 86 | 1674818
| Feni Lanka Power | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 62 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1904940
| Chowmuhani 113 MW | 105 | 105 | 104 | 93 | 99 | 100 | 95 | 96 | 96 | 96 | 96 | 95 | 95 | 94 | 99 | 99 | 108 | 114 |  | 114 | 114 | 113 | 114 | 117 | 112 | 106 | 2478000
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 78 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 112 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 146 | 146 | 144 | 2934720
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 99 | 100 | 100 | 100 | 99 | 99 | 99 | 99 | 99 | 80 | 88 | 91 | 91 | 91 | 91 | 92 | 92 |  | 99 | 99 | 99 | 99 | 100 | 100 | 98 | 2320320
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 43 | 43 | 43 | 40 | 40 | 46 | 48 | 48 | 48 | 48 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 1132320
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 133 | 133 | 133 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3539520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 43 |  | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 1017475
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 85 | 85 | 70 | 90 |  | 90 | 90 | 90 | 72 | 72 | 70 | 70 | 2122800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 5 | 2 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 27600
| Jodiac Power | 54 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1327317
| Karnaphuli Power Ltd. | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 96 | 93 | 92 | 94 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 2592720
82 | Madanganj 102 PP(Summit) | 65 | 65 | 65 | 65 | 65 | 45 | 59 | 65 | 65 | 65 | 65 | 65 | 65 | 45 | 55 | 48 | 48 | 48 |  | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 1468920
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 92 | 92 | 92 | 86 | 92 | 82 | 74 | 74 | 74 | 74 | 75 | 83 | 84 | 95 | 100 | 93 | 97 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2180160
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2606400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 37 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 951768
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1226387
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 84 | 2216736
95 | Patenga 50MW PP (Baraka) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 36 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1003680
96 | Chattogram 108 MW PP (ECPV) | 87 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 88 | 69 | 74 | 77 | 81 | 86 | 88 | 88 | 83 | 88 |  | 88 | 90 | 95 | 96 | 95 | 96 | 95 | 2160000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 55 | 55 | 45 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1322555
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1113133
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 140 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 140 | 110 | 110 |  | 140 | 140 | 140 | 163 | 163 | 163 | 163 | 3407972
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 9350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1309680
104 | Keranigonj 300 MW PP (APR) | 300 | 255 | 261 | 203 | 12 |  |  | 12 | 122 | 154 | 220 | 301 | 307 | 300 | 300 | 301 | 254 | 157 |  | 303 | 302 | 304 | 302 | 304 | 300 | 305 | 5282358
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | 60 | 60 | 25 |  |  |  | 25 | 25 | 50 | 60 | 60 | 80 | 80 | 98 | 100 | 98 | 96 |  | 94 | 92 | 95 | 100 | 100 | 100 | 100 | 1633301
106 | Mymensingh 200 MW PP (United) | 106 | 106 | 107 | 107 | 107 | 107 | 107 | 106 | 107 | 106 | 106 | 106 | 106 | 106 | 104 | 104 | 104 | 188 |  | 187 | 190 | 190 | 190 | 189 | 190 | 107 | 3036000
112 | Aurahati 100MW PP (Aggreko) | 100 | 100 | 100 | 52 |  |  |  | 25 | 50 | 96 | 97 | 96 | 99 | 97 | 97 | 94 | 100 | 100 |  | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 1879365
114 | Kodda 149 MW PP Unit-1 (Summit) | 144 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 147 | 145 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3627792
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2084160
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 120 | 85 | 90 | 100 | 128 | 194 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4300320
117 | Ashuganj 150MW PP (Midland) | 128 | 132 | 135 | 137 | 142 | 137 | 132 | 140 | 138 | 138 | 142 | 135 | 132 | 137 | 137 | 135 | 133 | 137 |  | 137 | 146 | 147 | 142 | 142 | 147 | 148 | 3315345
118 | Bibiyana-III 400 MW CCPP | 402 | 401 | 401 | 400 | 401 | 401 | 402 | 400 | 402 | 402 | 401 | 392 | 363 | 380 | 402 | 404 | 401 | 365 |  | 404 | 403 | 403 | 403 | 402 | 403 | 402 | 9576000
| Jamalpur 115 MW PP (United) | 106 | 106 | 97 | 97 | 97 | 106 | 106 | 97 | 97 | 96 | 96 | 90 | 92 | 96 | 103 | 97 | 114 | 115 |  | 115 | 115 | 115 | 115 | 115 | 106 | 106 | 2462400
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 281 | 300 | 300 | 300 | 300 | 280 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 281 | 281 | 6997855
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 70 | 50 | 61 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2369280
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2713582
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 22 | 35 | 35 | 35 | 35 | 47 | 34 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 44 | 37 | 52 | 52 | 1030320
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 7 | 13 | 14 | 21 | 35 | 32 | 28 | 22 | 14 | 6 | 1 | [8 empty] | 192714
| Chandpur 115(Doreen) | 101 | 101 | 80 | 59 | 59 | 59 | 59 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 56 | 59 | 61 | 94 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 1827840
Kanchan Purbachal Power Generation Ltd.
120 | Eastern Zone Total | 8231 | 8141 | 8162 | 7974 | 7657 | 7272 | 7205 | 7350 | 7580 | 7766 | 7961 | 8018 | 8194 | 8235 | 8356 | 8333 | 8279 | 8310 |  | 8716 | 8830 | 8852 | 8805 | 8817 | 8767 | 8665 | 196680013
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 83 |  | 99 | 115 | 115 | 115 | 115 | 83 | 49 | 861120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 34 | 29 | 29 | 29 | 5 | [5 empty] | 11 | 13 | 17 | 17 | 17 | 17 | 17 | 27 |  | 34 | 18 | 15 | 23 | 26 | 26 | 26 | 385920
| Khulna 225 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4896000
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 93 | 93 | 53 | 53 | 70 | 93 | 93 | 75 | 76 | 80 | 70 | 90 | 90 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 95 | 95 | 2109120
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 13 | 37 | 50 | 80 | 90 | 77 | 91 | 82 | 64 | 41 | 17 | 1 | [8 empty] | 663840
131
132 | United Payra Power Ltd. | [19 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 94800
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 216 | 224 | 218 | 221 | 220 | 220 | 210 | 220 | 220 | 220 | 220 | 217 | 217 | 216 | 214 | 215 | 184 |  | 219 | 220 | 221 | 221 | 217 | 221 | 203 | 5192564
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | [11 empty] | 32 | 32 | 32 |  | 64 | 64 | 48 | 32 | 32 | 32 | 16 | 385536
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 68 | 68 | 68 | 69 | 68 | 68 | 15 | 15 | 15 | 15 | 88 | 87 | 87 | 86 | 88 | 88 | 86 | 89 |  | 87 | 89 | 89 | 89 | 89 | 88 | 88 | 1955633
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 31 | 31 | 27 | 24 | 21 | 21 | 14 | 13 | 12 | 15 | 17 | 18 | 16 | 26 | 28 | 30 |  | 35 | 35 | 37 | 39 | 39 | 34 | 40 | 608593
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 50 | 50 | 50 | [6 empty] | 13 | 54 | 98 | 98 | 97 | 97 | 50 | 40 |  | 65 | 100 | 99 | 97 | 96 | 98 | 99 | 1440960
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 |  | 40 | 40 | 40 | 40 | 40 | 16 | 16 | 449250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 6 | [9 empty] | 3328
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | [15 empty] | 15 | 15 | 15 | 15 | 15 | 15 |  | 155664
146 | Bheramara HVDC | 921 | 921 | 921 | 922 | 921 | 921 | 922 | 922 | 921 | 916 | 916 | 914 | 914 | 915 | 916 | 917 | 916 | 917 |  | 917 | 916 | 917 | 916 | 916 | 920 | 921 | 22213090
147 | Bheramara 410 MW CCPP | 150 | 150 | 155 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 140 | 110 | 142 | 140 | 135 | 135 | 135 |  | 135 | 140 | 140 | 150 | 155 | 160 | 160 | 3725280
148 | Payra 1320 MW | 580 | 560 | 560 | 560 | 510 | 470 | 470 | 490 | 460 | 490 | 470 | 450 | 450 | 470 | 550 | 500 | 450 | 430 |  | 480 | 580 | 600 | 622 | 622 | 622 | 600 | 13605700
149
150 | Barapukuria TPP Unit-1 | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 79 | 79 | 80 | 78 | 80 | 78 | 79 | 80 | 81 | 78 | 80 |  | 80 | 80 | 80 | 80 | 79 | 78 | 78 | 1866763
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6054000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 43 | 43 | 0 | [7 empty] | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 677536
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 1 | 3 | 3 | 5 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 25200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 217 | 219 | 219 | 220 | 220 | 220 | 220 | 219 | 218 | 217 | 215 | 211 | 209 | 205 | 208 | 210 | 180 | 180 |  | 190 | 212 | 213 | 212 | 215 | 216 | 217 | 5266173
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 117 | 117 | 117 | 117 | 118 | 119 | 120 | 120 | 120 | 118 | 116 | 114 | 114 | 113 | 112 | 112 | 112 | 112 |  | 113 | 113 | 114 | 116 | 120 | 120 | 120 | 3031118
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 218 | 218 | 224 | 232 | 243 | 272 | 276 | 280 | 280 | 275 | 263 | 263 | 263 | 254 | 255 | 239 | 236 | 236 |  | 243 | 249 | 255 | 278 | 282 | 289 | 287 | 6127200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 15 | 15 | 15 | 15 | 5 | 0 |  |  |  |  | 5 | 6 | 6 | 6 | 6 | 23 | 23 | 23 |  | 20 | 25 | 22 | 22 | 22 | 22 | 22 | 297185
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 456240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 268300
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 0 | [16 empty] | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 283664
167 | Katakhali 50 MW Peaking PP | 40 | 40 | 40 | 40 |  | 0 | [5 empty] | 14 | 36 | 40 | 40 | 40 | 40 | 32 |  | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 534800
168 | Santahar 50 MW Peaking PP | 32 | 32 | 31 | 31 |  | 0 | [9 empty] | 24 | 30 | 30 |  | 24 | 25 | 25 | 25 | 29 | 30 | 30 | 386450
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 34 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 771840
170 | Chapainawabganj 100 MW Peaking PP | 92 | 92 | 92 | 92 | 92 | 0 | [6 empty] | 28 | 43 | 51 | 51 | 51 | 57 |  | 93 | 93 | 93 | 90 | 89 | 90 | 90 | 1233408
171 | Baghabari 200 MW PP (Paramount) | 172 | 171 | 170 | 170 | 0 | 0 |  |  | 0 | 50 | 170 | 169 | 169 | 169 | 169 | 169 | 100 | 80 |  | 172 | 171 | 171 | 171 | 171 | 170 | 170 | 2906907
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2732544
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2671488
173 | Rangpur 20 MW GTPP | 0 | [14 empty] | 15 | 15 | 15 |  | 17 | 15 | 15 | 14 | 14 | 12 | 12 | 128000
175 | Saidpur 20 MW GTPP | 0 | [13 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 76000
176 | Rangpur 113 MW PP (Confidence) | 110 | 110 | 110 | 110 | 110 | 85 | 76 | 104 | 110 | 109 | 102 | 102 | 102 | 108 | 109 | 109 | 109 | 109 |  | 108 | 108 | 109 | 109 | 110 | 110 | 110 | 2548464
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 5 | 4 | 3 | 2 | 2 | 0 | [8 empty] | 36313
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 75 | 74 | 96 | 115 | 115 | 115 | 115 | 115 | 115 | 112 | 114 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2674457
178