## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-12 | Tuesday
|  |  | Date (day): | 2022-04-12 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14689.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15460 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-11 | 2022-04-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 233 | 233 | 240 | 240
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 170 | 220 | 220 | 220 | 145 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 20 | 0 | 0
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 221 | 250 | 300 | 112 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 317 | 329 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 110 | 350 | 350 | 350 | 100 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 92 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 265 | 275 | 275 | 275 | 60 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 64 | 78 | 78 | 80 |  | 22 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 45 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 19 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 97 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 323 | 331 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 40 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 50 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 24 | 49 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 215 | 281 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 134 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 70 | 70 | 70 | 70 |  | 35 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 74 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 17 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5898 | 2705 | 3776 | 4233 | 4288 | 898 | 629
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 2 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 15 | 35 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 67 | 68 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 200 | 210
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 50 | 0 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 51 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 25 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 80 | 80 | 80 |  | 28 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 280 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 100 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2282 | 1190 | 1423 | 1368 | 1457 | 180 | 625
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 213 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 225 | 355 | 300 | 360
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 300 | 300 | 300 | 60 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 50 | 51 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 73 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 35 | 133 | 130 | 135 |  | 15 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 24 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Mach. Prob, Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 12 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 0 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 80 | 80 | 80 |  | 34 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 114 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 34 | 36 | 36 | 36 |  |  | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 101 | 90 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1349 | 1978 | 2022 | 2221 | 561 | 255
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 157 | 140 | 130 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 140 | 190 | 150 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 97 | 106 | 96 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 464 | 475 | 469.6 | 487 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 41 | 41 |  | 29 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 0 | 0 |  | 90 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 10 | 10 | 10 | 41 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 3 | 3 | 3 | 3 | 47 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 200 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 25 | 27 | 26 | 27
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 24 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 275 | 305 | 320 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 370 | 370 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 401 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1744 | 1697 | 1739 | 1775 | 438 | 219
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 923 | 943 | 943
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 113 | 115 | 115
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 140 | 200 | 200
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 400 | 410 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 74 | 105 | 94 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 100 | 100
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1607 | 1771 | 2102 | 2083 | 0 | 93
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 48 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 18 | 39 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 88 | 90 | 90 | 104 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 622 | 550 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 140 | 219 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 17 | 100
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 876 | 1051 | 958 | 1213 | 104 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 40 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 195 | 220 | 220 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 164 | 191 | 170 | 190 | 30 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 418 | 400 | 414
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 30 | 36 |  | 14 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 43 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 90 | 92 |  | 12 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 150 | 170 |  | 30 | Engine problem
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 995 | 1360 | 1482 | 1599 | 411 | 113
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 82 | 80 | 82
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 97 | 104 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 17 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 199 | 301 | 316 | 337 | 0 | 369
|  | Total |  |  |  |  | 22343 | 21484 | 11129 | 13832 | 14689.6 | 15460 | 2654 | 2311
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10840.1465 | 13472.99 | 14308.331 | 15058.7352
| A. |  | 2022-04-11 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13832 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9421 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13832 | MW
| 3 | Day peak Generation : |  |  | 11129 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13472.99 | MW
| 4 | Evening peak Generation : |  |  | 13832 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 279.2026 | MKWHr | By Solar | 1.1818 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 143.8064 | MKWHr |  | By Oil: | 90.3849 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.4188 | MKWHr |  | By Hydro: | 1.6056 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2654 | MW | Dhaka | 4921.89 | 4921.89 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2311 | MW | Chittagong | 1370.6 | 1370.6 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4965 | MW | Khulna | 1777.2 | 1777.2 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1126.66 | MMCFD |  |  | Rajshahi | 1532.3 | 1532.3 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146082319.302 | ii) Oil : | Taka | 692172843.74 | Comilla | 1330 | 1330 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 75008223.16 | Total | Taka | 913263386.202 | Mymensingh | 1062 | 1062 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.212 | MKWHr. | Sylhet | 417 | 417 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -126 | MW (E to W) at | 21:00 | hrs | Barisal | 411 | 411 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -214 | MW at | 23:00 | hrs | Rangpur | 651 | 651 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 13472.99 | 13472.99 |  | 0
| B. |  | 2022-04-12 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15460 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1260 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 286.6308 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10211 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3549 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4502 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82 |  | (b) Today: | 81.76 |  | (c) Rule Curve: |  | 85.8
.

## YesterdayGen
2022-04-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 234 | 0 | 50 | 102 | 0 | 0 | 327 |  | 0 | 0 | 275 | 100 | 79 | 0 | 336 | 0 | 96 | 80 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 0 | 33 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 38 | 0 | 22 | 0 | 0 | 0 | 150 | 280 | 184 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 42 | 19 | 11 | 33 | 0 | 142 | 163 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 86 | 0 | 218 | 0 | 26 | 10 | 280 | 24 | 8 | 0 | 268 | 0 | 0 | 45 | 0 | 149 | 0 | 90 | 120 | 130 | 371 | 45 | 52 | 105 | 0 | 280 | 54 | 105 | 98 | 115 | 100 | 401 | 94 | 0 | 35 | 113 | 0 | 36 | 0 | 35 | 55 |  | 924 | 0 | 275 | 0 | 84 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 161 | 0 | 417 | 95 | 0 | 113 | 51 | 104 | 0 | 0 | 113 | 560 | 221 | 0 | 17 | 0 | 0 | 115 |  | 7415 | 3861 | 11276 | 3558 | 924 | 2066 | 0 | 3605 | 586 | 69 | 310 | 206 | 142 | 0 | 0 | 82.06
2:00 | 0 | 0 | 238 | 0 | 70 | 102 | 0 | 0 | 327 |  | 0 | 0 | 300 | 100 | 78 | 12 | 335 | 0 | 37 | 50 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 13 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 38 | 0 | 22 | 0 | 0 | 0 | 150 | 280 | 183 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 42 | 19 | 11 | 33 | 0 | 138 | 164 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 40 | 86 | 0 | 218 | 0 | 26 | 10 | 285 | 24 | 8 | 0 | 270 | 0 | 0 | 16 | 0 | 136 | 0 | 90 | 51 | 130 | 371 | 45 | 52 | 105 | 0 | 265 | 54 | 110 | 98 | 116 | 100 | 400 | 94 | 0 | 35 | 113 | 0 | 36 | 0 | 35 | 55 |  | 925 | 0 | 275 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 38 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 350 | 95 | 0 | 113 | 32 | 98 | 0 | 0 | 113 | 560 | 221 | 0 | 17 | 0 | 0 | 34 |  | 7278 | 3611 | 10889 | 3540 | 925 | 2029 | 0 | 3270 | 622 | 69 | 280 | 176 | 138 | 0 | 0 | 82.04
3:00 | 0 | 0 | 238 | 0 | 80 | 102 | 0 | 0 | 327 |  | 0 | 0 | 300 | 100 | 78 | 55 | 335 | 0 | 97 | 7 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 14 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 38 | 0 | 24 | 0 | 0 | 0 | 150 | 285 | 182 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 42 | 19 | 11 | 33 | 21 | 142 | 163 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 86 | 0 | 218 | 0 | 26 | 10 | 300 | 24 | 11 | 0 | 278 | 0 | 0 | 33 | 0 | 147 | 0 | 90 | 61 | 135 | 371 | 20 | 52 | 105 | 0 | 265 | 54 | 110 | 98 | 115 | 100 | 400 | 94 | 0 | 35 | 113 | 0 | 36 | 0 | 36 | 55 |  | 924 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 89 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 161 | 0 | 419 | 95 | 0 | 113 | 32 | 99 | 0 | 0 | 113 | 560 | 220 | 0 | 17 | 0 | 0 | 34 |  | 7465 | 3682 | 11147 | 3663 | 924 | 2109 | 0 | 3297 | 635 | 69 | 260 | 188 | 142 | 0 | 0 | 82.03
4:00 | 0 | 0 | 238 | 0 | 150 | 102 | 0 | 0 | 327 |  | 0 | 25 | 250 | 100 | 78 | 15 | 335 | 0 | 97 | 0 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 14 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 38 | 0 | 22 | 0 | 0 | 0 | 150 | 280 | 190 | 8 | 0 | 29 | 4 | 0 | 51 | 0 | 0 | 42 | 19 | 11 | 33 | 21 | 142 | 164 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 45 | 0 | 0 | 218 | 0 | 26 | 10 | 280 | 24 | 0 | 0 | 195 | 0 | 0 | 18 | 0 | 145 | 0 | 90 | 100 | 135 | 370 | 45 | 50 | 105 | 0 | 265 | 54 | 110 | 98 | 155 | 100 | 400 | 94 | 0 | 35 | 113 | 0 | 2 | 0 | 36 | 55 |  | 924 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 161 | 0 | 418 | 90 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 560 | 202 | 0 | 17 | 0 | 0 | 0 |  | 7266 | 3594 | 10860 | 3713 | 924 | 1957 | 0 | 3142 | 637 | 69 | 260 | 156 | 142 | 0 | 0 | 82.02
5:00 | 0 | 0 | 238 | 0 | 150 | 98 | 0 | 0 | 327 |  | 0 | 25 | 250 | 100 | 78 | 15 | 335 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 14 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 15 | 0 | 21 | 0 | 0 | 0 | 150 | 280 | 186 | 8 | 0 | 28 | 5 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 134 | 166 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 50 | 86 | 0 | 191 | 0 | 26 | 10 | 280 | 22 | 0 | 0 | 145 | 0 | 0 | 18 | 0 | 100 | 0 | 90 | 51 | 40 | 370 | 16 | 50 | 91 | 0 | 265 | 54 | 110 | 70 | 116 | 100 | 350 | 72 | 0 | 35 | 113 | 0 | 6 | 0 | 36 | 55 |  | 924 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 89 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 166 | 0 | 380 | 53 | 0 | 113 | 0 | 96 | 0 | 0 | 50 | 560 | 200 | 0 | 17 | 0 | 0 | 0 |  | 6723 | 3417 | 10140 | 3560 | 924 | 1999 | 0 | 2558 | 636 | 69 | 260 | 140 | 134 | 0 | 0 | 82.01
6:00 | 0 | 0 | 238 | 0 | 170 | 98 | 0 | 0 | 308 |  | 0 | 150 | 250 | 100 | 70 | 15 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 14 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 12 | 0 | 20 | 0 | 0 | 0 | 150 | 280 | 184 | 8 | 0 | 28 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 130 | 166 | 0 | 20 | 0 | 0 | 41 | 53 | 3 | 120 | 0 | 50 | 86 | 0 | 178 | 0 | 26 | 10 | 280 | 22 | 0 | 0 | 45 | 0 | 0 | 8 | 0 | 102 | 1 | 90 | 17 | 10 | 370 | 16 | 50 | 51 | 0 | 265 | 54 | 110 | 70 | 115 | 50 | 350 | 35 | 1 | 35 | 69 | 0 | 17 | 0 | 36 | 17 |  | 924 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 166 | 0 | 380 | 17 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 530 | 222 | 0 | 17 | 0 | 1 | 0 |  | 6311 | 3224 | 9535 | 3529 | 924 | 2121 | 0 | 1902 | 607 | 69 | 250 | 130 | 130 | 3 | 0 | 82
7:00 | 0 | 0 | 238 | 0 | 170 | 98 | 0 | 0 | 307 |  | 0 | 110 | 290 | 100 | 52 | 15 | 280 | 0 | 60 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 15 | 25 | 14 | 33 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 12 | 0 | 9 | 0 | 0 | 0 | 150 | 280 | 184 | 8 | 0 | 25 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 126 | 162 | 0 | 20 | 1 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 30 | 0 | 178 | 0 | 26 | 10 | 290 | 22 | 2 | 0 | 45 | 0 | 0 | 8 | 0 | 100 | 3 | 90 | 16 | 10 | 370 | 16 | 50 | 51 | 1 | 265 | 54 | 110 | 70 | 115 | 20 | 350 | 24 | 1 | 35 | 69 | 0 | 17 | 3 | 36 | 17 |  | 925 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 166 | 0 | 380 | 17 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 480 | 221 | 0 | 17 | 0 | 15 | 0 |  | 6241 | 3180 | 9421 | 3604 | 925 | 2060 | 0 | 1806 | 557 | 69 | 250 | 130 | 126 | 24 | 0 | 81.99
8:00 | 0 | 0 | 238 | 0 | 170 | 98 | 0 | 0 | 307 |  | 0 | 110 | 285 | 100 | 78 | 15 | 282 | 0 | 60 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 15 | 25 | 12 | 33 | 33 | 24 | 0 | 69 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 12 | 0 | 3 | 0 | 0 | 0 | 150 | 275 | 184 | 8 | 0 | 25 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 124 | 162 | 0 | 20 | 1 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 30 | 0 | 178 | 0 | 26 | 10 | 300 | 22 | 2 | 0 | 60 | 0 | 0 | 8 | 0 | 115 | 9 | 90 | 17 | 10 | 370 | 16 | 50 | 51 | 2 | 280 | 54 | 110 | 70 | 111 | 20 | 350 | 17 | 10 | 35 | 69 | 0 | 17 | 6 | 35 | 35 |  | 924 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 173 | 0 | 383 | 35 | 0 | 50 | 0 | 35 | 0 | 1 | 35 | 480 | 221 | 0 | 17 | 0 | 38 | 0 |  | 6383 | 3228 | 9611 | 3612 | 924 | 2056 | 0 | 1922 | 555 | 69 | 250 | 162 | 124 | 67 | 0 | 81.98
9:00 | 0 | 0 | 236 | 0 | 170 | 98 | 0 | 0 | 313 |  | 0 | 110 | 310 | 92 | 78 | 15 | 328 | 0 | 97 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 15 | 25 | 18 | 33 | 33 | 24 | 0 | 69 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 87 | 12 | 0 | 2 | 0 | 0 | 0 | 200 | 315 | 202 | 8 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 130 | 158 | 0 | 20 | 1 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 86 | 0 | 205 | 0 | 26 | 10 | 305 | 22 | 2 | 0 | 115 | 0 | 0 | 8 | 0 | 134 | 12 | 90 | 17 | 10 | 370 | 19 | 50 | 51 | 3 | 282 | 54 | 110 | 70 | 105 | 20 | 400 | 17 | 34 | 35 | 73 | 0 | 17 | 11 | 36 | 35 |  | 924 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 85 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 187 | 0 | 415 | 35 | 0 | 50 | 0 | 35 | 0 | 2 | 35 | 490 | 220 | 0 | 17 | 3 | 52 | 0 |  | 6862 | 3297 | 10159 | 3904 | 924 | 2169 | 0 | 1995 | 568 | 69 | 250 | 162 | 130 | 118 | 0 | 81.97
10:00 | 0 | 0 | 236 | 0 | 170 | 97 | 0 | 0 | 316 |  | 0 | 110 | 300 | 92 | 78 | 15 | 330 | 0 | 95 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 15 | 25 | 20 | 0 | 16 | 24 | 0 | 68 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 12 | 0 | 2 | 0 | 0 | 0 | 235 | 290 | 191 | 26 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 18 | 134 | 158 | 0 | 20 | 2 | 0 | 41 | 53 | 3 | 120 | 0 | 60 | 86 | 0 | 218 | 0 | 26 | 10 | 310 | 22 | 2 | 0 | 115 | 0 | 0 | 50 | 0 | 133 | 14 | 74 | 17 | 10 | 370 | 100 | 50 | 72 | 2 | 280 | 54 | 110 | 70 | 104 | 46 | 400 | 17 | 43 | 35 | 113 | 0 | 17 | 14 | 36 | 45 |  | 924 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 415 | 35 | 0 | 79 | 15 | 35 | 0 | 5 | 95 | 530 | 220 | 0 | 17 | 4 | 75 | 17 |  | 7041 | 3518 | 10559 | 3885 | 924 | 2180 | 0 | 2318 | 609 | 68 | 250 | 162 | 134 | 159 | 0 | 81.96
11:00 | 0 | 0 | 232 | 0 | 170 | 97 | 0 | 0 | 318 |  | 0 | 110 | 300 | 92 | 78 | 15 | 320 | 0 | 95 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 20 | 0 | 8 | 24 | 0 | 68 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 81 | 12 | 0 | 2 | 0 | 0 | 0 | 225 | 310 | 211 | 26 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 18 | 140 | 157 | 0 | 20 | 2 | 0 | 41 | 50 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 26 | 10 | 305 | 22 | 5 | 0 | 148 | 0 | 0 | 98 | 0 | 133 | 17 | 76 | 17 | 10 | 371 | 97 | 50 | 86 | 5 | 280 | 54 | 110 | 70 | 105 | 67 | 395 | 17 | 29 | 35 | 113 | 0 | 17 | 29 | 36 | 55 |  | 924 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 199 | 0 | 414 | 35 | 0 | 110 | 15 | 44 | 0 | 5 | 113 | 540 | 140 | 0 | 17 | 5 | 85 | 17 |  | 7249 | 3504 | 10753 | 3895 | 924 | 2136 | 0 | 2512 | 619 | 68 | 250 | 162 | 140 | 177 | 0 | 0
12:00 | 0 | 0 | 233 | 0 | 170 | 97 | 0 | 0 | 317 |  | 0 | 110 | 265 | 92 | 64 | 30 | 323 | 0 | 97 | 0 | 64 | 40 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 0 | 0 | 8 | 24 | 0 | 67 | 0 | 0 | 0 | 2 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 12 | 0 | 2 | 0 | 0 | 0 | 225 | 295 | 212 | 45 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 32 | 18 | 140 | 157 | 0 | 20 | 2 | 0 | 41 | 50 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 25 | 10 | 290 | 22 | 5 | 0 | 215 | 0 | 0 | 140 | 0 | 134 | 10 | 76 | 12 | 35 | 370 | 97 | 70 | 90 | 3 | 280 | 54 | 100 | 52 | 105 | 100 | 400 | 74 | 26 | 35 | 113 | 0 | 34 | 17 | 36 | 55 |  | 925 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 85 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 414 | 74 | 0 | 113 | 15 | 97 | 0 | 5 | 113 | 600 | 140 | 0 | 17 | 5 | 100 | 17 |  | 7452 | 3677 | 11129 | 3835 | 925 | 2103 | 0 | 2921 | 680 | 67 | 250 | 170 | 140 | 168 | 0 | 81.94
13:00 | 0 | 0 | 232 | 0 | 170 | 97 | 0 | 0 | 317 |  | 0 | 150 | 255 | 92 | 70 | 55 | 321 | 0 | 91 | 40 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 18 | 33 | 17 | 41 | 0 | 67 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 81 | 12 | 0 | 6 | 0 | 0 | 0 | 40 | 310 | 212 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 31 | 18 | 142 | 157 | 0 | 20 | 1 | 0 | 41 | 50 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 26 | 10 | 280 | 22 | 5 | 0 | 263 | 0 | 0 | 146 | 0 | 133 | 16 | 76 | 52 | 70 | 370 | 97 | 70 | 105 | 4 | 300 | 54 | 110 | 72 | 106 | 100 | 400 | 92 | 40 | 58 | 113 | 0 | 36 | 16 | 36 | 55 |  | 924 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 119 | 0 | 417 | 95 | 0 | 113 | 15 | 97 | 0 | 6 | 113 | 622 | 140 | 0 | 35 | 3 | 72 | 70 |  | 7835 | 3740 | 11575 | 3677 | 924 | 2135 | 0 | 3420 | 702 | 67 | 250 | 230 | 142 | 158 | 0 | 81.93
14:00 | 0 | 0 | 231 | 0 | 170 | 12 | 0 | 0 | 317 |  | 0 | 225 | 305 | 98 | 77 | 55 | 319 | 0 | 95 | 75 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 18 | 33 | 33 | 41 | 0 | 67 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 86 | 6 | 0 | 2 | 0 | 0 | 0 | 20 | 330 | 210 | 45 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 34 | 0 | 8 | 25 | 15 | 156 | 151 | 0 | 20 | 1 | 0 | 41 | 0 | 3 | 163 | 0 | 60 | 84 | 0 | 219 | 0 | 27 | 10 | 300 | 22 | 5 | 0 | 263 | 50 | 50 | 150 | 50 | 131 | 15 | 90 | 74 | 75 | 372 | 96 | 70 | 105 | 2 | 300 | 54 | 110 | 80 | 105 | 100 | 390 | 92 | 45 | 108 | 113 | 0 | 36 | 21 | 36 | 55 |  | 923 | 0 | 370 | 0 | 6 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 415 | 94 | 0 | 113 | 15 | 100 | 0 | 6 | 113 | 622 | 117 | 0 | 35 | 3 | 41 | 110 |  | 8176 | 3747 | 11923 | 3679 | 923 | 2115 | 150 | 3632 | 702 | 67 | 250 | 245 | 156 | 134 | 0 | 81.92
15:00 | 0 | 0 | 140 | 0 | 150 | 12 | 0 | 0 | 317 |  | 0 | 225 | 250 | 98 | 77 | 55 | 320 | 0 | 92 | 97 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 41 | 0 | 67 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 81 | 24 | 0 | 2 | 0 | 0 | 0 | 30 | 260 | 212 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 33 | 0 | 8 | 28 | 15 | 144 | 143 | 0 | 20 | 1 | 0 | 41 | 0 | 3 | 163 | 0 | 60 | 84 | 0 | 219 | 0 | 27 | 10 | 285 | 22 | 8 | 80 | 265 | 230 | 50 | 150 | 50 | 135 | 11 | 90 | 168 | 88 | 370 | 96 | 70 | 105 | 3 | 300 | 54 | 110 | 80 | 105 | 100 | 399 | 93 | 32 | 124 | 112 | 0 | 35 | 12 | 36 | 55 |  | 924 | 0 | 400 | 0 | 24 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 16 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 146 | 0 | 414 | 94 | 0 | 113 | 50 | 104 | 0 | 5 | 113 | 622 | 122 | 0 | 35 | 3 | 56 | 115 |  | 8368 | 3908 | 12276 | 3549 | 924 | 2078 | 410 | 3885 | 703 | 67 | 263 | 273 | 144 | 123 | 0 | 81.91
16:00 | 0 | 0 | 200 | 0 | 190 | 55 | 0 | 0 | 317 |  | 0 | 240 | 240 | 98 | 76 | 55 | 324 | 0 | 92 | 98 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 42 | 0 | 67 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 44 | 0 | 0 | 81 | 35 | 0 | 2 | 0 | 0 | 0 | 45 | 270 | 214 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 12 | 34 | 0 | 8 | 33 | 15 | 148 | 127 | 0 | 20 | 1 | 0 | 41 | 0 | 3 | 163 | 0 | 60 | 84 | 0 | 219 | 0 | 27 | 10 | 280 | 22 | 2 | 0 | 280 | 0 | 0 | 177 | 0 | 144 | 7 | 90 | 155 | 115 | 371 | 105 | 70 | 105 | 2 | 300 | 54 | 110 | 80 | 109 | 100 | 400 | 104 | 18 | 126 | 111 | 0 | 36 | 12 | 38 | 55 |  | 924 | 0 | 395 | 0 | 93 | 120 | 0 | 0 | 10 | 0 | 8 | 87 | 24 | 16 | 0 | 0 | 0 | 43 | 5 | 39 | 0 | 0 | 14 | 52 | 19 | 0 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 165 | 0 | 418 | 70 | 0 | 113 | 50 | 100 | 0 | 2 | 113 | 622 | 122 | 0 | 35 | 2 | 34 | 110 |  | 8290 | 4026 | 12316 | 3679 | 924 | 2114 | 0 | 4018 | 702 | 67 | 250 | 466 | 148 | 78 | 0 | 81.9
17:00 | 0 | 0 | 200 | 0 | 200 | 96 | 0 | 0 | 320 |  | 0 | 240 | 275 | 98 | 76 | 55 | 324 | 0 | 0 | 50 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 68 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 51 | 0 | 0 | 81 | 12 | 0 | 17 | 0 | 0 | 0 | 95 | 270 | 210 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 47 | 40 | 0 | 8 | 30 | 18 | 150 | 123 | 0 | 20 | 0 | 0 | 41 | 0 | 3 | 110 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 280 | 22 | 0 | 0 | 281 | 0 | 0 | 186 | 0 | 132 | 2 | 90 | 136 | 132 | 371 | 105 | 70 | 68 | 1 | 300 | 54 | 110 | 52 | 85 | 50 | 360 | 72 | 6 | 130 | 111 | 0 | 36 | 5 | 62 | 55 |  | 923 | 0 | 395 | 0 | 93 | 120 | 0 | 0 | 29 | 0 | 8 | 86 | 26 | 16 | 0 | 0 | 0 | 43 | 6 | 54 | 0 | 0 | 40 | 24 | 32 | 0 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 198 | 0 | 305 | 70 | 0 | 70 | 50 | 75 | 0 | 1 | 70 | 570 | 144 | 0 | 35 | 0 | 10 | 72 |  | 8031 | 3784 | 11815 | 3630 | 923 | 2068 | 0 | 3636 | 648 | 68 | 250 | 547 | 150 | 25 | 0 | 81.89
18:00 | 0 | 0 | 200 | 0 | 200 | 98 | 0 | 0 | 300 |  | 0 | 260 | 305 | 98 | 76 | 55 | 321 | 0 | 0 | 50 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 68 | 0 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 22 | 48 | 38 | 0 | 81 | 12 | 0 | 22 | 0 | 0 | 0 | 120 | 330 | 210 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 40 | 41 | 0 | 8 | 31 | 18 | 158 | 114 | 0 | 17 | 0 | 0 | 41 | 0 | 3 | 110 | 0 | 40 | 86 | 0 | 219 | 0 | 27 | 10 | 290 | 23 | 0 | 0 | 278 | 0 | 0 | 189 | 0 | 149 | 1 | 90 | 137 | 140 | 371 | 106 | 70 | 68 | 0 | 300 | 54 | 110 | 52 | 85 | 50 | 360 | 72 | 1 | 144 | 68 | 0 | 36 | 1 | 76 | 55 |  | 923 | 0 | 360 | 0 | 93 | 120 | 0 | 0 | 31 | 0 | 8 | 86 | 28 | 16 | 0 | 0 | 0 | 43 | 28 | 54 | 0 | 0 | 40 | 24 | 36 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 205 | 0 | 303 | 70 | 0 | 70 | 50 | 75 | 0 | 0 | 70 | 550 | 158 | 0 | 35 | 0 | 1 | 72 |  | 8210 | 3793 | 12003 | 3672 | 923 | 2151 | 0 | 3638 | 631 | 68 | 250 | 638 | 158 | 4 | 0 | 81.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 233 | 0 | 200 | 99 | 0 | 0 | 320 |  | 0 | 320 | 250 | 100 | 76 | 55 | 330 | 0 | 0 | 75 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 50 | 35 | 13 | 25 | 17 | 33 | 33 | 49 | 0 | 69 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 80 | 12 | 0 | 15 | 0 | 0 | 0 | 255 | 296 | 200 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 41 | 43 | 0 | 8 | 33 | 18 | 154 | 122 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 130 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 285 | 24 | 5 | 10 | 281 | 60 | 50 | 190 | 50 | 149 | 0 | 90 | 167 | 140 | 370 | 106 | 70 | 74 | 0 | 300 | 54 | 110 | 80 | 100 | 64 | 401 | 79 | 0 | 144 | 88 | 0 | 36 | 0 | 91 | 55 |  | 923 | 0 | 405 | 0 | 114 | 220 | 0 | 0 | 44 | 21 | 40 | 87 | 35 | 32 | 0 | 0 | 0 | 43 | 30 | 93 | 0 | 34 | 40 | 34 | 36 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 2 | 208 | 0 | 416 | 90 | 10 | 80 | 50 | 97 | 0 | 0 | 100 | 550 | 200 | 0 | 35 | 0 | 0 | 85 |  | 8822 | 4421 | 13243 | 3893 | 923 | 2357 | 182 | 4028 | 630 | 69 | 374 | 787 | 154 | 0 | 0 | 81.85
19:30 | 0 | 0 | 233 | 0 | 200 | 99 | 0 | 0 | 326 |  | 0 | 320 | 265 | 100 | 77 | 55 | 332 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 13 | 25 | 25 | 33 | 33 | 49 | 0 | 69 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 75 | 12 | 0 | 18 | 0 | 0 | 0 | 355 | 300 | 182 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 41 | 43 | 0 | 11 | 33 | 18 | 152 | 140 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 130 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 288 | 24 | 5 | 0 | 281 | 11 | 25 | 190 | 25 | 149 | 0 | 90 | 200 | 140 | 370 | 106 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 400 | 0 | 113 | 220 | 0 | 0 | 37 | 24 | 40 | 88 | 35 | 32 | 0 | 0 | 0 | 43 | 30 | 93 | 0 | 34 | 40 | 52 | 36 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 211 | 0 | 417 | 105 | 7 | 113 | 50 | 104 | 0 | 0 | 113 | 600 | 217 | 0 | 35 | 0 | 0 | 115 |  | 9053 | 4632 | 13685 | 4008 | 924 | 2402 | 68 | 4342 | 681 | 69 | 410 | 819 | 152 | 0 | 0 | 0
20:00 | 0 | 0 | 233 | 0 | 220 | 22 | 0 | 39 | 326 |  | 0 | 330 | 260 | 100 | 77 | 55 | 333 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 13 | 25 | 25 | 33 | 33 | 49 | 0 | 69 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 75 | 12 | 0 | 21 | 0 | 0 | 0 | 360 | 300 | 209 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 41 | 43 | 0 | 11 | 33 | 18 | 158 | 139 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 275 | 24 | 8 | 0 | 281 | 12 | 25 | 190 | 25 | 149 | 0 | 90 | 200 | 145 | 371 | 106 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 115 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 53 |  | 923 | 0 | 400 | 0 | 113 | 223 | 0 | 0 | 37 | 23 | 40 | 88 | 37 | 32 | 0 | 0 | 0 | 43 | 30 | 93 | 0 | 34 | 40 | 52 | 36 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 207 | 0 | 418 | 105 | 0 | 113 | 50 | 104 | 0 | 0 | 113 | 600 | 220 | 0 | 35 | 0 | 0 | 115 |  | 9112 | 4627 | 13739 | 4100 | 923 | 2359 | 62 | 4347 | 680 | 69 | 413 | 818 | 158 | 0 | 0 | 81.86
21:00 | 0 | 0 | 233 | 0 | 220 | 20 | 0 | 221 | 329 |  | 0 | 350 | 275 | 100 | 78 | 45 | 331 | 0 | 97 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 49 | 0 | 68 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 80 | 15 | 0 | 25 | 0 | 0 | 0 | 355 | 300 | 213 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 24 | 43 | 0 | 11 | 33 | 18 | 162 | 140 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 275 | 24 | 8 | 0 | 281 | 0 | 0 | 190 | 0 | 149 | 0 | 90 | 200 | 133 | 370 | 106 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 400 | 0 | 113 | 140 | 0 | 0 | 0 | 0 | 40 | 88 | 39 | 48 | 0 | 0 | 0 | 43 | 0 | 92 | 0 | 34 | 40 | 52 | 36 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 191 | 0 | 418 | 105 | 0 | 113 | 50 | 104 | 0 | 0 | 113 | 622 | 219 | 0 | 35 | 0 | 0 | 115 |  | 9349 | 4483 | 13832 | 4369 | 923 | 2400 | 0 | 4351 | 704 | 68 | 335 | 715 | 162 | 0 | 0 | 81.85
22:00 | 0 | 0 | 233 | 0 | 220 | 20 | 0 | 283 | 328 |  | 0 | 350 | 260 | 100 | 78 | 45 | 334 | 0 | 95 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 49 | 0 | 67 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 85 | 0 | 88 | 37 | 0 | 25 | 0 | 0 | 0 | 355 | 300 | 212 | 73 | 0 | 26 | 35 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 33 | 18 | 160 | 141 | 0 | 22 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 218 | 0 | 27 | 10 | 285 | 24 | 8 | 0 | 281 | 0 | 0 | 191 | 0 | 149 | 0 | 90 | 200 | 143 | 371 | 97 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 115 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 405 | 0 | 113 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 39 | 48 | 0 | 0 | 0 | 43 | 0 | 92 | 0 | 0 | 40 | 52 | 36 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 194 | 0 | 416 | 105 | 0 | 113 | 50 | 104 | 0 | 0 | 113 | 622 | 218 | 0 | 35 | 0 | 0 | 115 |  | 9447 | 4369 | 13816 | 4446 | 924 | 2421 | 0 | 4350 | 702 | 67 | 250 | 626 | 160 | 0 | 0 | 81.84
23:00 | 0 | 0 | 233 | 0 | 220 | 20 | 0 | 286 | 328 |  | 0 | 350 | 300 | 100 | 78 | 45 | 343 | 0 | 57 | 24 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 67 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 22 | 0 | 85 | 0 | 88 | 38 | 0 | 26 | 0 | 0 | 0 | 325 | 325 | 212 | 73 | 0 | 26 | 40 | 0 | 51 | 0 | 0 | 43 | 0 | 8 | 33 | 18 | 158 | 137 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 218 | 0 | 27 | 10 | 260 | 24 | 8 | 0 | 230 | 0 | 0 | 191 | 0 | 149 | 0 | 90 | 200 | 100 | 370 | 97 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 116 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 400 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 88 | 39 | 48 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 36 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 192 | 0 | 416 | 105 | 0 | 113 | 15 | 104 | 0 | 0 | 113 | 610 | 221 | 0 | 35 | 0 | 0 | 72 |  | 9207 | 4192 | 13399 | 4396 | 923 | 2445 | 0 | 4107 | 690 | 67 | 250 | 493 | 158 | 0 | 0 | 81.83
24:00 | 0 | 0 | 234 | 0 | 220 | 20 | 0 | 263 | 328 |  | 0 | 350 | 265 | 100 | 79 | 45 | 335 | 0 | 0 | 24 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 23 | 33 | 33 | 50 | 0 | 67 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 89 | 38 | 0 | 26 | 0 | 0 | 0 | 305 | 305 | 186 | 73 | 0 | 26 | 51 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 25 | 18 | 154 | 138 | 0 | 20 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 218 | 0 | 26 | 10 | 300 | 24 | 0 | 0 | 230 | 0 | 0 | 191 | 0 | 149 | 0 | 90 | 200 | 100 | 370 | 97 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 117 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 410 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 89 | 39 | 48 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 199 | 0 | 419 | 105 | 0 | 113 | 15 | 104 | 0 | 0 | 113 | 530 | 220 | 0 | 35 | 0 | 0 | 72 |  | 8979 | 4124 | 13103 | 4248 | 923 | 2462 | 0 | 4085 | 610 | 67 | 250 | 434 | 154 | 0 | 0 | 81.82
KWH | 0 | 0 | 5424000 | 0 | 3888600 | 1757409 | 0 | 1075200 | 7648000 |  | 0 | 3791150 | 6638051 | 2368320 | 1844064 | 924686 | 7761458 | 0 | 1562000 | 1092480 | 1662336 | 1788000 | 0 | 0 | 0 | 0 | 1296360 | 950764 | 886604 | 409068 | 600000 | 418680 | 623200 | 710700 | 708480 | 0 | 1605600 | 0 | 0 | 0 | 327213 | 4799710 | 0 | 0 | 0 |  | 530880 | 340280 | 473290 | 0 | 2037120 | 526080 | 0 | 392640 | 0 | 0 | 0 | 4577000 | 7166000 | 4868000 | 986909 | 0 | 607608 | 267840 | 0 | 1206103 | 0 | 204352 | 741341 | 200700 | 228420 | 751800 | 399170 | 3450240 | 3517440 | 0 | 418572 | 12450 | 0 | 959512 | 726000 | 67392 | 3460663 | 0 | 1381536 | 1843200 | 0 | 5065610 | 0 | 624860 | 250200 | 7068500 | 589392 | 96432 | 70848 | 5407089 | 399869 | 195924 | 2659200 | 205561 | 3294720 | 98955 | 2056320 | 2583840 | 2219709 | 8909000 | 1774800 | 1527600 | 2176218 | 29281 | 6772036 | 1343400 | 2677188 | 1841100 | 2640960 | 1923840 | 9256700 | 1903680 | 281550 | 2014560 | 2520382 | 0 | 708480 | 164482 | 1323840 | 1263240 |  | 22354909 | 0 | 8715744 | 0 | 1072320 | 322720 | 0 | 0 | 135840 | 43648 | 209625 | 2109507 | 667548 | 777408 | 0 | 0 | 0 | 322574 | 122365 | 675232 | 0 | 132054 | 227983 | 789864 | 245515 | 452880 | 0 | 232886 | 1786472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702845 | 0 | 9600 | 4489855 | 0 | 9566327 | 1972800 | 8594 | 2394720 | 727200 | 1998470 | 0 | 45584 | 2264736 | 14632300 | 4577209 | 0 | 650400 | 26760 | 522720 | 1371341 |  | 188844037 | 90358555 | 279202592 | 91813500 | 22354909 | 51992881 | 890396 | 80889868 | 16418772 | 1605600 | 4025565 | 4579079 | 3450240 | 1181782 | 0
Fuel Cost | 0 | 0 | 7919040 | 0 | 4316346 | 2319779.88 | 0 | 1085952 | 7877440 |  | 0 | 4132353.5 | 7368236.61 | 17975548.8 | 12705600.96 | 7822843.56 | 8071916.32 | 0 | 2702260 | 8226374.4 | 15160504.32 | 17593920 | 0 | 0 | 0 | 0 | 9463428 | 7349405.72 | 8741915.44 | 306801 | 450000 | 0 | 0 | 0 | 6851001.6 | 0 | 433512 | 0 | 0 | 0 | 3039808.77 | 5231683.9 | 0 | 0 | 0 |  | 0 | 3290507.6 | 4590913 | 0 | 17722944 | 4166553.6 | 0 | 1166140.8 | 0 | 0 | 0 | 3386980 | 7166000 | 4478560 | 1273112.61 | 0 | 686597.04 | 374976 | 0 | 2062436.13 | 0 | 2063955.2 | 7079806.55 | 254889 | 171315 | 1315650 | 299377.5 | 25876800 | 3728486.4 | 0 | 531586.44 | 198453 | 0 | 1535219.2 | 1292280 | 105131.52 | 3945155.82 | 0 | 2721625.92 | 3520512 | 0 | 8763505.3 | 0 | 731086.2 | 510408 | 7139185 | 442044 | 73288.32 | 1205124.48 | 40877592.84 | 6789775.62 | 3275849.28 | 13827840 | 3436979.92 | 32420044.8 | 1156783.95 | 16759008 | 28034664 | 15648948.45 | 8285370 | 16186176 | 14435820 | 18954858.78 | 0 | 51196592.16 | 11701014 | 23532482.52 | 18374178 | 22633027.2 | 12812774.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128764275.84 | 0 | 9151531.2 | 0 | 8428435.2 | 4472899.2 | 0 | 0 | 1424961.6 | 457431.04 | 2184292.5 | 2383742.91 | 1034699.4 | 7587502.08 | 0 | 0 | 0 | 3174128.16 | 1243228.4 | 5975803.2 | 0 | 1785370.08 | 2209155.27 | 7653782.16 | 2381495.5 | 869529.6 | 0 | 176294.702 | 10772426.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54505878.4 | 0 | 163296 | 5253130.35 | 0 | 9470663.73 | 20596032 | 146183.94 | 22725892.8 | 6864768 | 15508127.2 | 0 | 503703.2 | 16736399.04 | 64235797 | 0 | 0 | 0 | 0 | 0 | 0 |  | 651356058.33 | 418840855.862 | 1070196914.192 | 90889192.502 | 128764275.84 | 55193126.8 | 15017209.24 | 573771357.93 | 75008223.16 | 433512 | 58978777.6 | 44405498.97 | 25876800 | 1858940.15 | 0
Yesterday Day Peak | 0 | 0 | 233 | 0 | 170 | 97 | 0 | 0 | 317 |  | 0 | 110 | 265 | 92 | 64 | 30 | 323 | 0 | 97 | 0 | 64 | 40 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 0 | 0 | 8 | 24 | 0 | 67 | 0 | 0 | 0 | 2 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 12 | 0 | 2 | 0 | 0 | 0 | 225 | 295 | 212 | 45 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 32 | 18 | 140 | 157 | 0 | 20 | 2 | 0 | 41 | 50 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 25 | 10 | 290 | 22 | 5 | 0 | 215 | 0 | 0 | 140 | 0 | 134 | 10 | 76 | 12 | 35 | 370 | 97 | 70 | 90 | 3 | 280 | 54 | 100 | 52 | 105 | 100 | 400 | 74 | 26 | 35 | 113 | 0 | 34 | 17 | 36 | 55 |  | 925 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 85 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 414 | 74 | 0 | 113 | 15 | 97 | 0 | 5 | 113 | 600 | 140 | 0 | 17 | 5 | 100 | 17 |  | 11129 | DayPeak
Yesterday Evening Peak | 0 | 0 | 233 | 0 | 220 | 20 | 0 | 221 | 329 | 0 | 0 | 350 | 275 | 100 | 78 | 45 | 331 | 0 | 97 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 49 | 0 | 68 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 22 | 50 | 85 | 0 | 80 | 15 | 0 | 25 | 0 | 0 | 0 | 355 | 300 | 213 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 24 | 43 | 0 | 11 | 33 | 18 | 162 | 140 | 0 | 17 | 0 | 0 | 41 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 219 | 0 | 27 | 10 | 275 | 24 | 8 | 0 | 281 | 0 | 0 | 190 | 0 | 149 | 0 | 90 | 200 | 133 | 370 | 106 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 114 | 100 | 401 | 104 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 400 | 0 | 113 | 140 | 0 | 0 | 0 | 0 | 40 | 88 | 39 | 48 | 0 | 0 | 0 | 43 | 0 | 92 | 0 | 34 | 40 | 52 | 36 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 191 | 0 | 418 | 105 | 0 | 113 | 50 | 104 | 0 | 0 | 113 | 622 | 219 | 0 | 35 | 0 | 0 | 115 |  | 13832 | EvPeak
Forecast for Evening | 0 | 0 | 240 | 0 | 220 | 0 | 0 | 300 | 330 | 0 | 0 | 350 | 275 | 100 | 80 | 55 | 335 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 0 | 25 | 210 | 0 | 0 | 0 | 0 | 22 | 50 | 85 | 0 | 80 | 40 |  | 25 | 0 | 0 | 0 | 360 | 300 | 210 | 26 | 0 | 26 | 51 | 0 | 51 | 0 | 40 | 43 | 22 | 11 | 33 | 18 | 166 | 140 | 0 | 20 | 0 | 41 | 0 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 220 | 0 | 27 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 135 | 400 | 115 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 |  | 100 | 55 |  | 943 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 30 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 43 | 40 | 92 | 0 | 43 | 40 | 52 | 36 | 22 | 0 | 11 | 82 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 220 | 0 | 100 | 190 | 0 | 414 | 105 | 170 | 113 | 100 | 113 | 0 | 0 | 113 | 660 | 220 |  | 100 |  |  | 115
Forecast for Day | 0 | 0 | 240 | 0 | 220 | 0 | 0 | 250 | 300 | 0 | 0 | 350 | 275 | 100 | 78 | 55 | 335 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 0 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 80 | 35 | 0 | 10 | 0 | 0 | 0 | 300 | 300 | 210 | 26 | 0 | 26 | 50 | 0 | 51 | 0 | 40 | 43 | 22 | 11 | 33 | 18 | 143 | 130 | 0 | 20 | 1.6 | 41 | 0 | 10 | 3 | 163 | 0 | 60 | 86 | 0 | 200 | 0 | 26 | 10 | 305 | 24 | 11 | 100 | 300 | 300 | 100 | 150 | 100 | 149 | 20 | 90 | 200 | 130 | 400 | 96 | 70 | 105 | 5 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 36 | 30 | 90 | 55 |  | 943 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 90 | 33 | 48 | 0 | 0 | 0 | 34 | 40 | 90 | 0 | 40 | 0 | 43 | 30 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 170 | 0 | 400 | 94 | 150 | 113 | 100 | 113 | 0 | 8 | 113 | 550 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 220 | 0 | 0 | 141 | 322 | 0 | 0 | 350 | 250 | 100 | 78 | 15 | 335 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 18 | 25 | 6 | 33 | 33 | 38 | 0 | 68 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 81 | 19 | 0 | 2 | 0 | 0 | 0 | 305 | 305 | 219 | 26 | 0 | 26 | 47 | 0 | 51 | 0 | 0 | 43 | 0 | 11 | 25 | 17 | 124 | 137 | 0 | 20 | 0 | 41 | 0 | 10 | 3 | 120 | 0 | 60 | 84 | 0 | 218 | 0 | 26 | 10 | 295 | 16 | 5 | 0 | 15 | 0 | 0 | 35 | 0 | 100 | 8 | 88 | 17 | 10 | 371 | 72 | 52 | 77 | 2 | 264 | 54 | 110 | 80 | 30 | 30 | 350 | 53 | 0 | 126 | 100 | 0 | 36 | 12 | 51 | 28 | 0 | 922 | 0 | 410 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 168 | 0 | 391 | 35 | 0 | 62 | 0 | 34 | 0 | 2 | 90 | 320 | 204 | 0 | 11 | 0 | 41 | 17 | 0 |  |  |  |  | 90384908 |  | 0
90384908
| Minimum Generation |  | 9421 | 7:00
| Highest Generation |  | 13832 | 21:00
| Day Peak Generation |  | 11129 | 12:00
| Evening Peak Generation |  | 13832 | 21:00
| HVDC Max Flow |  | 925 | 2:00
| HVDC EvPeak Flow |  | 923 | 21:00
| Load factor L.F |  | 84.11%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-12
Till now the maximum generation is : - |  |  | 14008 | 22:00 | Hrs on | 2022-04-07
The Summary of Yesterday's |  | 2022-04-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11129 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10211 | MW
Evening Peak Generation : |  | 13832 | MW Hour : | 21:00 | Available Max Generation : |  | 15460 | MW
E.P. Demand (at gen end) : |  | 13832 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 13832 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1260 | MW
Total Gen. (MKWH) : |  | 279.2026 | System Load Factor : | 84.11% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -214 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-12
Actual : | 81.76 | Ft.(MSL) , | Rule curve : | 85.8 | Ft.( MSL )
Gas Consumed : | Total = | 1126.66 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146082319.302
: |  | Coal : | 75008223.16 | Oil : | 692172843.74 | Total : | 913263386.202
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5092.2045 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1653.8195 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1609.8941 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1441.7856 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1314.5476 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1078.6061 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 528.5704 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 323.6058 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 793.535 |  |  | 0 | 0%
Total | 0 |  | 13836.5685 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1
6) Siddhirganj 210 MW .
7) Raozan unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Keraniganj 230 kV Ckt-2 was under shut down from 08:38 to 13:28 for D/W.
b) Barapukuria 230/132 kV T-2 transformer was under shut down from 08:25 to 10:47 for C/M.
c) Kallyanpur 132/33 kV GT-1 transformer was under shut down from 09:22 to 17:25 for C/M.
d) Kishorganj 132/33 kV T-2 transformer was under shut down from 09:54 to 11:17 due to red hot maintenance
at LT R-phase.
e) Bhola Natun Biddut-220 MW CCPP ST tripped at 10:56 showing E/F relay and was synchronized at 16:26.
f) Mymensing-Kishorganj 132 kV Ckt-2 tripped at 08:48 showing dist.Z2,BC phase and was switched on at 12:55.
g) Chowmuhani-Ramganj 132 kV Ckt-1 was under shut down from 11:34 to 14:09 for line DS high temperature.
h) Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-1 was under shut down at 12:31 for C/M.
i) GK project 132/33 kV T-2 transformer was under shut down from 11:57 to 12:48 for bird nest remove.
j) Kishorganj 132/33 kV T-3 transformer was under shut down from 12:11 to 13:11 for GTC maintenance.
k) Keraniganj-Srinagar 132 kV Ckt-2 was under shut down from 14:26 to 15:48 for D/W.
l) Ghorasal-Bhulta 230 kV Ckt-2 was under shut down from 14:32 to 15:16 for protection test.
m) Gopalganj-Gopalganj P/S 132 kV Ckt was under shut down from 14:52 to 15:58 for protection test.
n) Cox's Bazar 132/33 kV T-3 transformer tripped at 15:13 showing O/C relay and was switched on at 15:30. | [5 empty] | About 55 MW power interruption occurred under
Cox's Bazar S/S area from 15:13 to 15:30.
o) Keraniganj-Aurahati 132 kV Ckt was under shut down from 15:56 to 17:01 for protection test.
p) AES Megnaghat-450 MW GT-2 was synchronized at 15:57.
q) Siddirganj peaking GT-1 tripped at 16:12 due to GVC trip and was synchronized at 20:12.
r) Ashuganj-360 MW CCPP ST was synchronized at 15:55.
s) Bogura 33 kV bus section-3 was under shut down from 15:38 to 16:50 for D/W.
t) Shyampur-APR 230 kV Ckt tripped at 16:11 showing E/F relay and was switched on at 16:33.
u) Shyampur(N)-Shyampur(O) 132 kV Ckt-1 & 2 tripped at 16:13 showing E/F,dist.B at Shyampur(N) end & | [5 empty] | About 150 MW power interruption occurred under
main protection at Shyampur(O) end and was switched on at 17:08 & 16:50 respectively. | [5 empty] | Shyampur S/S area from 16:13 to 16:50.
v) After maintenance Haripur-412 MW CCPP GT was synchronized at 19:55.
w) Mymensing-Sutiakhali solar P/S 132 kV Ckt tripped at 02:35(12/4/22) showing differential relay.
y) Payra-Gopalganj 400 kV Ckt-2 tripped at 02:42(12/4/22) showing dist.AB at Gopalganj end & dist.Z1,Z2
Z4,3-phase at Payra end.
z) Cox's Bazar-Dohazari 132 kV Ckt is under shut down since 06:36(12/4/22) for D/W.
aa) Tangail 132/33 kv T-3 transformer is under shut down since 07:07(12/4/22) for D/W.
ab) Siddirganj peaking GT-1 was shut down at 23:08 due to gas shortage.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 233 | 5424000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 3888600 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 20 | 1757409 | red hot.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 221 | 1075200
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 329 | 7648000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 3791150 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2368320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 6638051 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 78 | 1844064 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 924686 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 409068
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1562000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1092480
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7761458
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1662336 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1296360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1788000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 950764
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 886604 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1018680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 623200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 710700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 708480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 5407089 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 399869 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 195924 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 205561 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3294720
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1527600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1903680
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2014560 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 164482
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1263240
| Dhaka area Total |  |  |  | 5898 | 3776 | 72206335
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 327213
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 98955
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 15 | 526080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1605600 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4799710
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2176218
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 340280 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 473290 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2056320 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 392640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 2037120 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29281
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6772036
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1343400
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2677188
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1923840
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2520382
| Chattogram area Total |  |  |  | 2282 | 1423 | 30099553
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4868000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 355 | 4577000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7166000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 607608 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 267840 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 986909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1206103
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 2219709 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 204352 | low demand.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2583840
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 200700 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228420
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3450240
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 751800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 741341 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 399170
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 70848 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1841100 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 2640960
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 708480 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1323840 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1978 | 37044260
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 3517440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 418572
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12450
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 190 | 2659200 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 1774800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 281550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 530880
| Mymensingh Area Total |  |  |  | 622 | 475 | 9194892
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 959512 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3460663
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 10 | 726000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 3 | 67392 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 96432
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1381536 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1843200
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5065610 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 27 | 624860
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 589392
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7068500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 370 | 8909000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250200
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 9256700
| Sylhet Area Total |  |  |  | 2477 | 1697 | 40298997
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22354909
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 113 | 1072320
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 135840 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 140 | 322720 | low demand.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 43648 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 8715744
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 209625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 9600 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1972800 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 727200 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 522720
| Khulna Area Total |  |  |  | 2384 | 1771 | 36087126
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 777408 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 39 | 667548
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2109507 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14632300 | Transformer O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4577209
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 650400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1051 | 23414372
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 322574 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 122365 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 132054 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 227983 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 195 | 3702845 | Running on HSD
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4489855 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 418 | 9566327
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 245515 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 452880
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232886
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 789864 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 675232 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 8594 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2394720
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2264736
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26760
| Rajshahi Area Total |  |  |  | 2129 | 1360 | 25655190
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1786472
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1998470
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45584
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1371341
| Rangpur Area Total |  |  |  | 720 | 301 | 5201867
| Total |  |  |  | 21484 | 13832 | 279202592
| Eastern Grid Total |  |  |  | 14293 | 9349 | 188844037
| Western Grid Total |  |  |  | 7191 | 4483 | 90358555
| National Grid Total |  |  |  | 21484 | 13832 | 279202592
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-11
(a) ENTIRE EASTERN GRID : |  | 9101.49 | MW | (b) ENTIRE WESTERN GRID : |  | 4371.5 | MW
i) Dhaka area |  | 4921.89 | MW | i) Khulna area |  | 1777.2 | MW
ii) Chittagong area |  | 1370.6 | MW | ii) Rajshahi area |  | 1532.3 | MW
iii) Comilla area |  | 1330 | MW | iii) Barisal area |  | 411 | MW
iv) Mymensingh area |  | 1062 | MW | iv) Rangpur area |  | 651 | MW
v) Sylhet area |  | 417 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13472.99 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 19:00 | Hasnabad | 77 | 23:00 | Palashbari | 92 | 21:00
Agargaon | 105 | 13:00 | Hathazari | 98 | 20:00 | Panchagarh | 50 | 19:30
Agrabad | 84 | 14:00 | Ishurdi | 78 | 21:00 | Patuakhali | 127 | 22:00
AKS | 19 | 05:00 | Jaldhaka | 46 | 18:30 | PHP | 9 | 04:00
AKSML | 0 | 00:00 | Jamalpur | 143 | 22:00 | Purbachal | 20 | 20:00
Amnura | 64 | 22:00 | Jashore | 139 | 20:00 | Purbasadipur | 97 | 19:30
Ashuganj | 38 | 00:00 | Jhenaidah | 136 | 20:00 | Rahim | 27 | 12:00
Bagerhat | 108 | 19:00 | Joydebpur | 179 | 22:00 | Rajbari | 72 | 19:30
Bakulia | 126 | 19:00 | Joypurhat | 54 | 21:00 | Rajendrapur | 118 | 16:00
Banani | 54 | 13:00 | Juldah | 29 | 15:00 | Rajshahi | 176 | 19:30
Bangabhaban | 20 | 10:00 | Kabirpur | 251 | 16:00 | Rajshahi | 35 | 23:00
Barapukuria | 47 | 20:00 | Kachua | 68 | 19:00 | Ramganj | 100 | 22:00
Barguna | 20 | 22:00 | Kallyanpur | 96 | 18:30 | Rampur | 17 | 20:00
Barishal | 106 | 20:00 | Kalurghat | N/A | N/A | Rangamati | 12 | 18:00
Barishal | 63 | 22:00 | Kamrangirchar | 72 | 17:00 | Rangpur | 116 | 18:00
Baroaulia | 78 | 00:00 | Kaptai | 5 | 19:00 | Ruppur | 3.8 | 10:00
Baroirhat | 54 | 21:00 | Kazla | 91 | 16:00 | Saidpur | 80 | 17:00
Bashundhara | 182 | 15:00 | Keranigonj | 76 | 20:00 | Satkhira | 126 | 21:00
BashundharaCement | 13 | 00:00 | Khagrachori | 26 | 21:00 | Satmasjid | 109 | 19:00
Beanibazar | 50 | 21:00 | Khulna | 91 | 20:00 | Savar | 199 | 15:00
Benapole | 64 | 21:00 | Khulshi | 188 | 16:00 | Shahjadpur | 125 | 20:00
Bhaluka | 116 | 23:00 | Kishoreganj | 140 | 21:00 | Shahjibazar | 91 | 00:00
Bhandaria | 58 | 21:00 | Kodda | 272 | 08:00 | Shahmirpur | 34 | 07:00
Bhangura | 38 | 19:00 | KSRM | 25 | 12:00 | Shariatpur | 74 | 21:00
Bheramara(GK) | 69 | 22:00 | Kulaura | 36 | 18:30 | Sherpur | 140 | 19:00
Bhulta | 225 | 19:30 | Kurigram | 44 | 18:30 | Shikalbaha | 38 | 23:00
Bog-Sherpur | 66 | 21:00 | Kushtia | 142 | 21:00 | Shitalakhya | 113 | 12:00
Bogura | 171 | 21:00 | Lalbag | 85 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 46 | 22:00 | Lalmonirhat | 32 | 19:00 | Shyampur | 168 | 10:00
Brahmanbaria | 160 | 20:00 | Madanganj | 169 | 19:30 | Siddhirganj | 130 | 15:00
BSRM | 158 | 09:00 | Madaripur | 113 | 21:00 | Sirajganj | 123 | 20:00
Cantonment | 146 | 15:00 | Madartek | 86 | 19:00 | Sonargaon | 82 | 00:00
Chandpur | 77 | 21:00 | Madunaghat | 64 | 21:00 | Sreemongol | 60 | 19:30
Chandraghona | 34 | 19:00 | Magura | 66 | 20:00 | Srinagar | 45.69 | 21:00
Chapai | 68 | 00:00 | Mahasthangarh | 64 | 20:00 | SSM | 4 | 14:00
Charsaidpur | 39 | 04:00 | Manikganj | 96 | 20:00 | Sunamganj | 38 | 18:30
Chauddagram | 64 | 21:00 | Maniknagar | 80 | 15:00 | Sylhet | 118 | 18:30
Chhatak | 24 | 00:00 | Matarbari | 45 | 18:30 | Tangail | 256 | 21:00
Chowmuhani | 232 | 22:00 | Matuail | 64 | 10:00 | Thakurgaon | 68 | 21:00
Chuadanga | 119 | 22:00 | Millgate | 58 | 12:00 | TK | 30.8 | 22:00
Coxsbazar | 125 | 20:00 | Mirpur | 137 | 20:00 | Tongi | 132 | 15:00
Cumilla(N) | 161 | 20:00 | Mirsorai | N/A | N/A | Ullon | 43 | 19:00
Cumilla(S) | 162 | 21:00 | Mithapukur | 21 | 03:00 | Uttara | 76 | 18:30
Daudkandi | 142 | 22:00 | Modern | 0 | 00:00 | UttaraNew | 36 | 14:00
Dhaka | 37 | 12:00 | Mogbazar | 127 | 15:00 | Zigatola | 45 | 19:00
Dhamrai | 120 | 15:00 | Mongla | 38 | 12:00
Dhanmondi | 218 | 13:00 | Motijheel | 36 | 14:00
Dohazari | 112 | 21:00 | Munshiganj | 106 | 21:00
Faridpur | 159 | 21:00 | Mymensingh | 199 | 18:30
Fatullah | 68 | 10:00 | Naogaon | 120 | 21:00
Fenchuganj | 41 | 19:00 | Narail | 58 | 21:00
Feni | 139 | 21:00 | Narinda | 77 | 15:00
Ghorashal | 82 | 19:30 | Narshingdi | 192 | 22:00
Goalpara | 30 | 21:00 | Natore | 152 | 21:00
Gollamari | 60 | 19:30 | Nawabganj | 58.2 | 21:00
Gopalganj | 106.6 | 22:00 | Netrakona | 100 | 21:00
GPH | 12 | 14:00 | New | 84 | 14:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 3:00 | 395 | 10:00 | Kaliakoir | 390 | 0.66667 | 375 | 0.45833
| Bheramara | 396 | 5:00 | 387 | 23:00 | Bhulta | 400 | 0.125 | 379 | 0.45833
| Ashuganj(N) | 407 | 18:30 | 387 | 11:00 | Gopalganj | 411 | 0.625 | 400 | 0.875
| Payra | 418 | 18:30 | 410 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 15:00 | Hathazari | 236 | 1:00 | 230 | 11:00
| Ishurdi | 233 | 18:30 | 226 | 11:00 | Megnaghat | 230 | 5:00 | 218 | 11:00
| Ashuganj | 242 | 3:00 | 230 | 10:00 | Fenchuganj | 241 | 3:00 | 236 | 9:00
| Serajganj | 234 | 1:00 | 230 | 9:00 | Siddhirganj | 229 | 1:00 | 216 | 10:00
| Baghabari | 233 | 5:00 | 220 | 3:00 | Maniknagar | 226 | 1:00 | 212 | 11:00
| Barapukuria | 231 | 1:00 | 216 | 9:00 | Agargaon | 224 | 11:00 | 210 | 11:00
| Bogra | 233 | 1:00 | 222 | 9:00 | Barisal | 239 | 1:00 | 232 | 21:00
| Rajshahi | 223 | 16:00 | 215 | 3:00 | Bhola 225 MW | 244 | 17:00 | 237 | 22:00
| Khulna South | 235 | 18:00 | 226 | 21:00 | AKSML | 0 | 1:00 | 0 | 1:00
| Rampura | 228 | 3:00 | 215 | 11:00 | BSRM | 236 | 2:00 | 228 | 9:00
| Haripur | 225 | 1:00 | 213 | 11:00 | Bibiyana | 237 | 5:00 | 231 | 9:00
| Hasnabad | 225 | 1:00 | 212 | 10:00 | Bhulta | 229 | 3:00 | 216 | 11:00
| Shyampur | 226 | 18:30 | 211 | 11:00 | Ashuganj (S) | 237 | 1:00 | 226 | 11:00
| Aminbazar | 223 | 1:00 | 212 | 2:00 | Kaliakoir | 227 | 7:00 | 215 | 13:00
| Tongi | 231 | 5:00 | 213 | 10:00 | GPH | 234 | 18:30 | 228 | 1:00
| Comilla (N) | 230 | 3:00 | 219 | 11:00 | Jhenaidah | 225 | 18:30 | 217 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 139 | 01:00 | 129 | 11:00 | Manikganj | 133 | 05:00 | 122 | 10:00
| Agargaon | 139 | 02:00 | 129 | 11:00 | Maniknagar | 130 | 01:00 | 122 | 11:00
| Agrabad | 135 | 22:00 | 129 | 10:00 | Matarbari | 122 | 08:00 | 98 | 14:00
| AKS | 135 | 01:00 | 130 | 10:00 | Matuail | 135 | 04:00 | 125 | 11:00
| Aminbazar | 139 | 03:00 | 129 | 11:00 | Millgate | 138 | 06:00 | 128 | 09:00
| Amnura | 134 | 17:00 | 126 | 03:00 | Mirpur | 138 | 03:00 | 128 | 11:00
| Ashuganj | 142 | 04:00 | 136 | 11:00 | Mithapukur | 137 | 01:00 | 123 | 09:00
| Bagerhat | 132 | 08:00 | 128 | 21:00 | Modern | 134 | 00:00 | 131 | 09:00
| Bakulia | 135 | 22:00 | 131 | 09:00 | Mogbazar | 139 | 00:00 | 130 | 09:00
| Banani | 138 | 03:00 | 126 | 11:00 | Mongla | 132 | 15:00 | 128 | 21:00
| Bangabhaban | 131 | 02:00 | 121 | 11:00 | Motijheel | 131 | 02:00 | 121 | 11:00
| Barapukuria | 134 | 00:00 | 121 | 09:00 | Munshiganj | 137 | 18:30 | 127 | 11:00
| Barguna | 134 | 07:00 | 130 | 14:00 | Mymensingh | 136 | 03:00 | 123 | 22:00
| Barishal | 138 | 11:00 | 127 | 14:00 | Naogaon | 131 | 00:00 | 121 | 09:00
| Barishal | 139 | 11:00 | 133 | 19:00 | Narail | 131 | 08:00 | 123 | 22:00
| Baroaulia | 137 | 13:00 | 133 | 06:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 03:00 | 130 | 11:00 | Narshingdi | 132 | 04:00 | 122 | 11:00
| Bashundhara | 139 | 03:00 | 126 | 10:00 | Natore | 134 | 00:00 | 130 | 09:00
| BashundharaCement | 137 | 19:00 | 125 | 11:00 | Nawabganj | 138 | 04:00 | 127 | 11:00
| Beanibazar | 135 | 05:00 | 131 | 13:00 | Netrakona | 135 | 03:00 | 122 | 21:00
| Benapole | 130 | 16:00 | 124 | 21:00 | New | 140 | 03:00 | 127 | 11:00
| Bhaluka | 132 | 04:00 | 119 | 14:00 | Niamatpur | 130 | 08:00 | 116 | 21:00
| Bhandaria | 136 | 10:00 | 126 | 21:00 | Noapara | 134 | 17:00 | 130 | 21:00
| Bhangura | 134 | 00:00 | 129 | 09:00 | Pabna | 133 | 05:00 | 128 | 11:00
| Bheramara | 134 | 04:00 | 123 | 21:00 | Palashbari | 135 | 00:00 | 123 | 09:00
| Bheramara(GK) | 137 | 18:30 | 133 | 01:00 | Panchagarh | 137 | 00:00 | 115 | 09:00
| Bhulta | 131 | 03:00 | 121 | 11:00 | Patuakhali | 135 | 03:00 | 132 | 14:00
| Bog-Sherpur | 135 | 00:00 | 126 | 09:00 | PHP | 133 | 13:00 | 129 | 02:00
| Bogura | 136 | 00:00 | 130 | 07:00 | Purbachal | 139 | 04:00 | 127 | 11:00
| Bogura | 136 | 00:00 | 129 | 09:00 | Purbasadipur | 136 | 15:00 | 117 | 09:00
| Brahmanbaria | 139 | 04:00 | 130 | 21:00 | Rahim | 135 | 01:00 | 126 | 10:00
| Cantonment | 137 | 02:00 | 127 | 11:00 | Rajbari | 134 | 08:00 | 128 | 21:00
| Chandpur | 139 | 18:30 | 126 | 06:00 | Rajendrapur | 136 | 01:00 | 122 | 11:00
| Chandraghona | 138 | 16:00 | 132 | 09:00 | Rajshahi | 134 | 00:00 | 129 | 23:00
| Chapai | 133 | 18:00 | 128 | 09:00 | Rajshahi | 137 | 18:30 | 130 | 22:00
| Charsaidpur | 138 | 04:00 | 126 | 11:00 | Ramganj | 135 | 16:00 | 125 | 05:00
| Chauddagram | 134 | 03:00 | 129 | 10:00 | Rampur | 134 | 01:00 | 131 | 10:00
| Chhatak | 135 | 07:00 | 131 | 00:00 | Rampura | 140 | 03:00 | 129 | 09:00
| Chowmuhani | 131 | 15:00 | 126 | 05:00 | Rangamati | 136 | 13:00 | 132 | 09:00
| Chuadanga | 130 | 06:00 | 117 | 21:00 | Rangpur | 132 | 00:00 | 123 | 09:00
| Coxsbazar | 118 | 10:00 | 102 | 14:00 | Ruppur | 134 | 00:00 | 132 | 10:00
| Cumilla(N) | 135 | 00:00 | 129 | 11:00 | Saidpur | 134 | 00:00 | 120 | 09:00
| Cumilla(S) | 137 | 03:00 | 122 | 14:00 | Satkhira | 131 | 06:00 | 126 | 21:00
| Daudkandi | 132 | 01:00 | 124 | 11:00 | Satmasjid | 138 | 02:00 | 129 | 11:00
| Dhaka | 139 | 01:00 | 128 | 11:00 | Savar | 138 | 02:00 | 128 | 11:00
| Dhamrai | 134 | 00:00 | 125 | 11:00 | Shahjadpur | 137 | 02:00 | 132 | 09:00
| Dhanmondi | 136 | 03:00 | 126 | 12:00 | Shahjibazar | 139 | 00:00 | 135 | 19:00
| Dohazari | 133 | 16:00 | 123 | 18:00 | Shahmirpur | 135 | 13:00 | 132 | 10:00
| Faridpur | 135 | 17:00 | 129 | 22:00 | Shariatpur | 135 | 07:00 | 128 | 22:00
| Fatullah | 135 | 18:30 | 124 | 11:00 | Sherpur | 137 | 02:00 | 123 | 09:00
| Fenchuganj | 138 | 06:00 | 134 | 16:00 | Shikalbaha | 135 | 00:00 | 130 | 06:00
| Feni | 135 | 16:00 | 129 | 06:00 | Shikalbaha | 135 | 00:00 | 132 | 07:00
| Ghorashal | 140 | 00:00 | 135 | 15:00 | Shitalakhya | 138.4 | 18:30 | 126 | 11:00
| Goalpara | 137 | 18:30 | 133 | 02:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 135 | 16:00 | 131 | 02:00 | Shyampur | 133 | 03:00 | 124 | 11:00
| Gopalganj | 137 | 16:00 | 131 | 23:00 | Shyampur | 135 | 18:30 | 124 | 11:00
| Gopalganj_I | 139 | 18:00 | 133 | 21:00 | Siddhirganj | 136 | 03:00 | 126 | 11:00
| Gulshan | 138 | 00:00 | 128 | 09:00 | Sirajganj | 133 | 00:00 | 125 | 22:00
| Halishahar | 136 | 16:00 | 130 | 11:00 | Sonargaon | 137 | 00:00 | 125 | 10:00
| Haripur | 135 | 01:00 | 126 | 10:00 | Sreemongol | 141 | 05:00 | 135 | 20:00
| HaripurSBU | 136 | 18:30 | 128 | 10:00 | Srinagar | 137 | 00:00 | 128 | 11:00
| Hasnabad | 135 | 00:00 | 128 | 11:00 | SSM | 140 | 16:00 | 134 | 04:00
| Hathazari | 137 | 00:00 | 132 | 07:00 | Sunamganj | 133 | 06:00 | 129 | 18:30
| Ishurdi | 135 | 05:00 | 132 | 02:00 | Sylhet | 135 | 05:00 | 132 | 16:00
| Jaldhaka | 134 | 00:00 | 117 | 09:00 | Tangail | 135 | 03:00 | 127 | 09:00
| Jamalpur | 138 | 10:00 | 124 | 09:00 | Thakurgaon | 139 | 01:00 | 114 | 09:00
| Jashore | 131 | 18:00 | 125 | 21:00 | TK | 135 | 07:00 | 131 | 10:00
| Jhenaidah | 134 | 05:00 | 128 | 21:00 | Tongi | 139 | 01:00 | 129 | 10:00
| Jhenaidah | 135 | 06:00 | 129 | 21:00 | Ullon | 140 | 03:00 | 128 | 10:00
| Joydebpur | 139 | 18:00 | 127 | 11:00 | Uttara | 138 | 04:00 | 128 | 09:00
| Joypurhat | 131 | 00:00 | 120 | 09:00 | UttaraNew | 137 | 03:00 | 123 | 17:00
| Juldah | 135 | 00:00 | 132 | 18:30 | Zigatola | 138 | 04:00 | 128 | 11:00
| Kabirpur | 138 | 02:00 | 125 | 11:00
| Kachua | 137 | 19:00 | 128 | 07:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 138 | 02:00 | 129 | 10:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 138 | 01:00 | 129 | 11:00
| Kaptai | 135 | 00:00 | 133 | 07:00
Page 7 of 7

## L-Curve
Date | 2022-04-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 18 | 8979 | 4124 | 13103 |  |  |  | QF-LDC-11
0:30 | 97 | 8197 | 3992.5 | 12189.5 | Date: | 2022-04-11
1:00 | 176 | 7415 | 3861 | 11276
1:30 | 111 | 7346.5 | 3736 | 11082.5
2:00 | 46 | 7278 | 3611 | 10889
2:30 | 85 | 7371.5 | 3646.5 | 11018 | [5 empty] | Gen. at Eve. Peak | 13832 | 13832 MW (21:00 )
3:00 | 124 | 7465 | 3682 | 11147 | [6 empty] | 21:00
3:30 | 75 | 7365.5 | 3638 | 11003.5 | [5 empty] | Gen. at Day Peak | 11129 | 11129 MW (12:00 )
4:00 | 26 | 7266 | 3594 | 10860 | [6 empty] | 12:00
4:30 | 94 | 6994.5 | 3505.5 | 10500 | [5 empty] | Highest Generation | 13832
5:00 | 162 | 6723 | 3417 | 10140 | [6 empty] | 21:00
5:30 | 203 | 6517 | 3320.5 | 9837.5
6:00 | 244 | 6311 | 3224 | 9535
6:30 | 254 | 6276 | 3202 | 9478
7:00 | 264 | 6241 | 3180 | 9421
7:30 | 260 | 6312 | 3204 | 9516
8:00 | 256 | 6383 | 3228 | 9611
8:30 | 302 | 6622.5 | 3262.5 | 9885
9:00 | 348 | 6862 | 3297 | 10159
9:30 | 412 | 6951.5 | 3407.5 | 10359
10:00 | 476 | 7041 | 3518 | 10559
10:30 | 447 | 7145 | 3511 | 10656
11:00 | 418 | 7249 | 3504 | 10753
11:30 | 383 | 7350.5 | 3590.5 | 10941
12:00 | 348 | 7452 | 3677 | 11129
12:30 | 317 | 7643.5 | 3708.5 | 11352
13:00 | 286 | 7835 | 3740 | 11575
13:30 | 270 | 8005.5 | 3743.5 | 11749
14:00 | 254 | 8176 | 3747 | 11923
14:30 | 296 | 8272 | 3827.5 | 12099.5
15:00 | 338 | 8368 | 3908 | 12276
15:30 | 367 | 8329 | 3967 | 12296
16:00 | 396 | 8290 | 4026 | 12316
16:30 | 335 | 8160.5 | 3905 | 12065.5
17:00 | 274 | 8031 | 3784 | 11815
17:30 | 207 | 8120.5 | 3788.5 | 11909
18:00 | 140 | 8210 | 3793 | 12003
18:30 | 152 | 8516 | 4107 | 12623
19:00 | 164 | 8822 | 4421 | 13243
19:30 | 174 | 9053 | 4632 | 13685
20:00 | 138 | 9112 | 4627 | 13739 |  |  |  | Executive Engineer
20:30 | 132 | 9230.5 | 4555 | 13785.5 |  |  |  | Network Operation Division
21:00 | 126 | 9349 | 4483 | 13832
21:30 | 149 | 9398 | 4426 | 13824
22:00 | 172 | 9447 | 4369 | 13816 |  |  |  |  | Page 6 of 7
22:30 | 193 | 9327 | 4280.5 | 13607.5
23:00 | 214 | 9207 | 4192 | 13399
23:30 | 116 | 9093 | 4158 | 13251
24:00 | 18 | 8979 | 4124 | 13103
13832 MW (21:00 )
11129 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-11 |  | Energy |  | 279202592
[13 empty] | 2022-04-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4248 | 923 | 2462 | 0 | 4085 | 610 | 67 | 250 | 434 | 154 | 0 | 0
0:30 | 3903 | 923.5 | 2264 | 0 | 3845 | 598 | 68 | 280 | 320 | 148 | 0 | 0 | Date: | 2022-04-11
1:00 | 3558 | 924 | 2066 | 0 | 3605 | 586 | 69 | 310 | 206 | 142 | 0 | 0
1:30 | 3549 | 924.5 | 2047.5 | 0 | 3437.5 | 604 | 69 | 295 | 191 | 140 | 0 | 0 | [8 empty] | Total Energy | 279.2026 | Total Energy Gen 279.203 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.203 MKWHr
2:00 | 3540 | 925 | 2029 | 0 | 3270 | 622 | 69 | 280 | 176 | 138 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3601.5 | 924.5 | 2069 | 0 | 3283.5 | 628.5 | 69 | 270 | 182 | 140 | 0 | 0 | [8 empty] | Energy Requirement | 279.2026
3:00 | 3663 | 924 | 2109 | 0 | 3297 | 635 | 69 | 260 | 188 | 142 | 0 | 0
3:30 | 3688 | 924 | 2033 | 0 | 3219.5 | 636 | 69 | 260 | 172 | 142 | 0 | 0 | [6 empty] | Shortage
4:00 | 3713 | 924 | 1957 | 0 | 3142 | 637 | 69 | 260 | 156 | 142 | 0 | 0
4:30 | 3636.5 | 924 | 1978 | 0 | 2850 | 636.5 | 69 | 260 | 148 | 138 | 0 | 0
5:00 | 3560 | 924 | 1999 | 0 | 2558 | 636 | 69 | 260 | 140 | 134 | 0 | 0
5:30 | 3544.5 | 924 | 2060 | 0 | 2230 | 621.5 | 69 | 255 | 135 | 132 | 1.5 | 0
6:00 | 3529 | 924 | 2121 | 0 | 1902 | 607 | 69 | 250 | 130 | 130 | 3 | 0
6:30 | 3566.5 | 924.5 | 2090.5 | 0 | 1854 | 582 | 69 | 250 | 130 | 128 | 13.5 | 0 |  |  |  |  | Coal
7:00 | 3604 | 925 | 2060 | 0 | 1806 | 557 | 69 | 250 | 130 | 126 | 24 | 0
7:30 | 3608 | 924.5 | 2058 | 0 | 1864 | 556 | 69 | 250 | 146 | 125 | 45.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3612 | 924 | 2056 | 0 | 1922 | 555 | 69 | 250 | 162 | 124 | 67 | 0
8:30 | 3758 | 924 | 2112.5 | 0 | 1958.5 | 561.5 | 69 | 250 | 162 | 127 | 92.5 | 0
9:00 | 3904 | 924 | 2169 | 0 | 1995 | 568 | 69 | 250 | 162 | 130 | 118 | 0
9:30 | 3894.5 | 924 | 2174.5 | 0 | 2156.5 | 588.5 | 68.5 | 250 | 162 | 132 | 138.5 | 0
10:00 | 3885 | 924 | 2180 | 0 | 2318 | 609 | 68 | 250 | 162 | 134 | 159 | 0
10:30 | 3890 | 924 | 2158 | 0 | 2415 | 614 | 68 | 250 | 162 | 137 | 168 | 0
11:00 | 3895 | 924 | 2136 | 0 | 2512 | 619 | 68 | 250 | 162 | 140 | 177 | 0
11:30 | 3865 | 924.5 | 2119.5 | 0 | 2716.5 | 649.5 | 67.5 | 250 | 166 | 140 | 172.5 | 0
12:00 | 3835 | 925 | 2103 | 0 | 2921 | 680 | 67 | 250 | 170 | 140 | 168 | 0
12:30 | 3756 | 924.5 | 2119 | 0 | 3170.5 | 691 | 67 | 250 | 200 | 141 | 163 | 0
13:00 | 3677 | 924 | 2135 | 0 | 3420 | 702 | 67 | 250 | 230 | 142 | 158 | 0
13:30 | 3677 | 924 | 2135 | 0 | 3420 | 702 | 67 | 250 | 230 | 142 | 158 | 0
14:00 | 3677 | 924 | 2135 | 0 | 3420 | 702 | 67 | 250 | 230 | 142 | 158 | 0
14:30 | 3613 | 924 | 2106.5 | 205 | 3652.5 | 702.5 | 67 | 256.5 | 251.5 | 143 | 140.5 | 0
15:00 | 3549 | 924 | 2078 | 410 | 3885 | 703 | 67 | 263 | 273 | 144 | 123 | 0
15:30 | 3614 | 924 | 2096 | 205 | 3951.5 | 702.5 | 67 | 256.5 | 369.5 | 146 | 100.5 | 0
16:00 | 3679 | 924 | 2114 | 0 | 4018 | 702 | 67 | 250 | 466 | 148 | 78 | 0
16:30 | 3630 | 923.5 | 2091 | 0 | 3827 | 675 | 67.5 | 250 | 506.5 | 149 | 51.5 | 0
17:00 | 3630 | 923 | 2068 | 0 | 3636 | 648 | 68 | 250 | 547 | 150 | 25 | 0
17:30 | 3651 | 923 | 2109.5 | 0 | 3637 | 639.5 | 68 | 250 | 592.5 | 154 | 14.5 | 0
18:00 | 3672 | 923 | 2151 | 0 | 3638 | 631 | 68 | 250 | 638 | 158 | 4 | 0
18:30 | 3782.5 | 923 | 2254 | 91 | 3833 | 630.5 | 68.5 | 312 | 712.5 | 156 | 2 | 0
19:00 | 3893 | 923 | 2357 | 182 | 4028 | 630 | 69 | 374 | 787 | 154 | 0 | 0
19:30 | 4008 | 924 | 2402 | 68 | 4342 | 681 | 69 | 410 | 819 | 152 | 0 | 0
20:00 | 4100 | 923 | 2359 | 62 | 4347 | 680 | 69 | 413 | 818 | 158 | 0 | 0
20:30 | 4234.5 | 923 | 2379.5 | 31 | 4349 | 692 | 68.5 | 374 | 766.5 | 160 | 0 | 0
21:00 | 4369 | 923 | 2400 | 0 | 4351 | 704 | 68 | 335 | 715 | 162 | 0 | 0
21:30 | 4407.5 | 923.5 | 2410.5 | 0 | 4350.5 | 703 | 67.5 | 292.5 | 670.5 | 161 | 0 | 0
22:00 | 4446 | 924 | 2421 | 0 | 4350 | 702 | 67 | 250 | 626 | 160 | 0 | 0
22:30 | 4421 | 923.5 | 2433 | 0 | 4228.5 | 696 | 67 | 250 | 559.5 | 159 | 0 | 0
23:00 | 4396 | 923 | 2445 | 0 | 4107 | 690 | 67 | 250 | 493 | 158 | 0 | 0
23:30 | 4322 | 923 | 2453.5 | 0 | 4096 | 650 | 67 | 250 | 463.5 | 156 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.8° C
24:00 | 4248 | 923 | 2462 | 0 | 4085 | 610 | 67 | 250 | 434 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 279.203 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.203 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 68 | 68 |  | 69 | 69 | 69 | 68 | 67 | 67 | 67 | 1605600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 0 | 2 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 327213
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 9 | 12 | 14 | 17 | 10 | 16 | 15 | 11 | 7 | 2 | 1 |  | 0 | [6 empty] | 98955
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 214 | 204 | 203 | 203 | 203 | 203 | 204 | 217 | 204 | 222 | 204 | 204 | 216 | 203 | 203 | 204 | 222 |  | 203 | 203 | 203 | 203 | 203 | 205 | 203 | 4799710
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 38 |  | 85 | 85 | 85 | 85 | 85 | 85 | 51 | 473290
12 | Hathazari 100 MW peaking PP | [14 empty] | 0 | 44 | 51 | 48 |  | 50 | 50 | 50 | 50 | 50 |  |  | 340280
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 91 | 51 | 51 | 51 | 51 | 72 | 86 | 90 | 105 | 105 | 105 | 105 | 68 | 68 |  | 74 | 105 | 105 | 105 | 105 | 105 | 105 | 2176218
| Daudkandi 200 MW PP (B.Trac) | [14 empty] | 80 | 0 |  | 0 |  | 10 | 0 | [5 empty] | 70848
14 | Titas 50 MW Peaking PP | [14 empty] | 0 | 12 | 47 | 40 |  | 41 | 41 | 41 | 24 |  |  |  | 204352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 96 | 37 | 97 | 97 |  | 0 | 60 | 60 | 97 | 95 | 95 | 97 | 91 | 95 | 92 | 92 | 0 |  |  |  |  | 0 | 97 | 95 | 57 | 0 | 1562000
17 | Siddhirganj 335 MW CCPP | 336 | 335 | 335 | 335 | 335 | 280 | 280 | 282 | 328 | 330 | 320 | 323 | 321 | 319 | 320 | 324 | 324 | 321 |  | 330 | 332 | 333 | 331 | 334 | 343 | 335 | 7761458
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 270 | 278 | 195 | 145 | 45 | 45 | 60 | 115 | 115 | 148 | 215 | 263 | 263 | 265 | 280 | 281 | 278 |  | 281 | 281 | 281 | 281 | 281 | 230 | 230 | 5407089
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 45 | 45 | 45 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 986909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 234 | 238 | 238 | 238 | 238 | 238 | 238 | 238 | 236 | 236 | 232 | 233 | 232 | 231 | 140 | 200 | 200 | 200 |  | 233 | 233 | 233 | 233 | 233 | 233 | 234 | 5424000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 50 | 70 | 80 | 150 | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 190 | 200 | 200 |  | 200 | 200 | 220 | 220 | 220 | 220 | 220 | 3888600
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 28 | 28 | 25 | 25 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 607608
33 | Ashuganj 225 MW CCPP | 184 | 183 | 182 | 190 | 186 | 184 | 184 | 184 | 202 | 191 | 211 | 212 | 212 | 210 | 212 | 214 | 210 | 210 |  | 200 | 182 | 209 | 213 | 212 | 212 | 186 | 4868000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 285 | 280 | 280 | 280 | 280 | 275 | 315 | 290 | 310 | 295 | 310 | 330 | 260 | 270 | 270 | 330 |  | 296 | 300 | 300 | 300 | 300 | 325 | 305 | 7166000
| Ashuganj 450 MW CCPP(North) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 235 | 225 | 225 | 40 | 20 | 30 | 45 | 95 | 120 |  | 255 | 355 | 360 | 355 | 355 | 325 | 305 | 4577000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 35 | 40 | 51 | 267840
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [20 empty] | 0 | 39 | 221 | 283 | 286 | 263 | 1075200
40 | Meghnaghat 450 MW CCPP(MPL) |  |  | 0 | 25 | 25 | 150 | 110 | 110 | 110 | 110 | 110 | 110 | 150 | 225 | 225 | 240 | 240 | 260 |  | 320 | 320 | 330 | 350 | 350 | 350 | 350 | 3791150
41 | Haripur 360MW CCPP(HPL) | 327 | 327 | 327 | 327 | 327 | 308 | 307 | 307 | 313 | 316 | 318 | 317 | 317 | 317 | 317 | 317 | 320 | 300 |  | 320 | 326 | 326 | 329 | 328 | 328 | 328 | 7648000
42 | RPCL 210MW CCPP | 163 | 164 | 163 | 164 | 166 | 166 | 162 | 162 | 158 | 158 | 157 | 157 | 157 | 151 | 143 | 127 | 123 | 114 |  | 122 | 140 | 139 | 140 | 141 | 137 | 138 | 3517440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 1 | 10 | 34 | 43 | 29 | 26 | 40 | 45 | 32 | 18 | 6 | 1 |  | 0 | [6 empty] | 281550
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 959512
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 40 | 60 | 45 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1381536
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 |  | 86 | 86 | 30 | 30 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1843200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 191 | 178 | 178 | 178 | 205 | 218 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 |  | 219 | 219 | 219 | 219 | 218 | 218 | 218 | 5065610
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 26 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 624860
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250200
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 11 |  |  |  | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 8 | 2 | 0 |  |  | 5 | 5 | 8 | 8 | 8 | 8 | 0 | 96432
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 0 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 726000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 589392
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 300 | 280 | 280 | 280 | 290 | 300 | 305 | 310 | 305 | 290 | 280 | 300 | 285 | 280 | 280 | 290 |  | 285 | 288 | 275 | 275 | 285 | 260 | 300 | 7068500
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 400 | 400 | 395 | 400 | 400 | 390 | 399 | 400 | 360 | 360 |  | 401 | 400 | 401 | 401 | 401 | 401 | 401 | 9256700
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 886604
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530880
60 | Barabkunda 22 MW PP (Regent) | [9 empty] | 0 | 0 | [14 empty] | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 13 | 13 | 13 | 22 | 22 | 22 | 22 | 409068
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 |  | 17 | 17 | 17 | 17 | 22 | 17 | 20 | 418572
63 | Impoprt (Tripura) | 142 | 138 | 142 | 142 | 134 | 130 | 126 | 124 | 130 | 134 | 140 | 140 | 142 | 156 | 144 | 148 | 150 | 158 |  | 154 | 152 | 158 | 162 | 160 | 158 | 154 | 3450240
64 | Malancha, Ctg. EPZ (United) | 22 | 22 | 24 | 22 | 21 | 20 | 9 | 3 | 2 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 17 | 22 |  | 15 | 18 | 21 | 25 | 25 | 26 | 26 | 392640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 0 | [12 empty] | 200700
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 8 | 11 | 228420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 25 | 28 | 33 | 30 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 751800
68 | Cumilla 25 MW PP (Summit) |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 399170
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi |  | 13 | 14 | 14 | 14 | 14 | 14 | 12 | 18 | 20 | 20 | 0 | 18 | 18 | 26 | 26 | 26 | 26 |  | 17 | 25 | 25 | 25 | 25 | 25 | 23 | 418680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 623200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 8 | 8 | 17 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 710700
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 98 | 98 | 98 | 98 | 98 | 97 | 97 | 97 | 97 | 12 | 12 | 55 | 96 | 98 |  | 99 | 99 | 22 | 20 | 20 | 20 | 20 | 1757409
| Feni Lanka Power | 98 | 98 | 98 | 98 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 52 | 72 | 80 | 80 | 80 | 52 | 52 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1841100
| Chowmuhani 113 MW | 115 | 116 | 115 | 155 | 116 | 115 | 115 | 111 | 105 | 104 | 105 | 105 | 106 | 105 | 105 | 109 | 85 | 85 |  | 100 | 113 | 115 | 114 | 115 | 116 | 117 | 2640960
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 58 | 108 | 124 | 126 | 130 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2014560
77 | Siddhirganj 100 PP(Dutch Bangla) | 80 | 50 | 7 | [9 empty] | 40 | 75 | 97 | 98 | 50 | 50 |  | 75 | 100 | 100 | 100 | 100 | 24 | 24 | 1092480
78 | Gazipur 52 MW PP | 8 | [5 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 41 | 41 | 41 | 42 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 708480
79 | Kodda 150MW PP | 16 | 16 | 48 | 16 |  |  |  | 32 | 32 | 32 | 32 | 40 | 100 | 115 | 115 | 150 | 115 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 133 | 1788000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 42 | 42 | 42 | 42 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 34 | 33 | 34 | 40 | 41 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 741341
| Gazipur 100 MW PP | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1527600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 5 | 3 | 4 | 2 | 3 | 2 | 1 | 0 | [8 empty] | 29281
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1343400
| Karnaphuli Power Ltd. | 105 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2677188
82 | Madanganj 102 PP(Summit) | 79 | 78 | 78 | 78 | 78 | 70 | 52 | 78 | 78 | 78 | 78 | 64 | 70 | 77 | 77 | 76 | 76 | 76 |  | 76 | 77 | 77 | 78 | 78 | 78 | 79 | 1844064
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 275 | 300 | 300 | 250 | 250 | 250 | 290 | 285 | 310 | 300 | 300 | 265 | 255 | 305 | 250 | 240 | 275 | 305 |  | 250 | 265 | 260 | 275 | 260 | 300 | 265 | 6638051
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 92 | 92 | 92 | 98 | 98 | 98 | 98 | 98 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2368320
| Meghnaghat 104 MW PP (OPCL) | 94 | 94 | 94 | 94 | 72 | 35 | 24 | 17 | 17 | 17 | 17 | 74 | 92 | 92 | 93 | 104 | 72 | 72 |  | 79 | 104 | 104 | 104 | 104 | 104 | 104 | 1903680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 67392
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1206103
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 64 | 7 | 7 | 7 | 7 | 7 | 7 | 64 | 93 | 93 | 93 | 84 | 84 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1662336
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 24 | 35 | 12 | 12 |  | 12 | 12 | 12 | 15 | 37 | 38 | 38 | 526080
96 | Chattogram 108 MW PP (ECPV) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 84 | 87 | 89 | 81 | 77 | 81 | 86 | 81 | 81 | 81 | 81 |  | 80 | 75 | 75 | 80 | 88 | 88 | 89 | 2037120
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 0 | 12 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 45 | 45 | 45 | 45 | 924686
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 35 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 950764
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3460663
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 12450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1296360
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 0 | 50 | 230 | 0 |  | 0 |  | 60 | 11 | 12 | 0 |  |  |  | 399869
105 | Bramhangoan 100 MW PP (Aggreko) | [13 empty] | 50 | 50 | 0 |  | 0 |  | 50 | 25 | 25 | 0 |  |  | 0 | 195924
106 | Mymensingh 200 MW PP (United) | 45 | 16 | 33 | 18 | 18 | 8 | 8 | 8 | 8 | 50 | 98 | 140 | 146 | 150 | 150 | 177 | 186 | 189 |  | 190 | 190 | 190 | 190 | 191 | 191 | 191 | 2659200
112 | Aurahati 100MW PP (Aggreko) | [13 empty] | 50 | 50 | 0 |  | 0 |  | 50 | 25 | 25 | 0 |  |  |  | 205561
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 136 | 147 | 145 | 100 | 102 | 100 | 115 | 134 | 133 | 133 | 134 | 133 | 131 | 135 | 144 | 132 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3294720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 74 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2056320
116 | Chandpur 200MW (Desh energy) | 120 | 51 | 61 | 100 | 51 | 17 | 16 | 17 | 17 | 17 | 17 | 12 | 52 | 74 | 168 | 155 | 136 | 137 |  | 167 | 200 | 200 | 200 | 200 | 200 | 200 | 2583840
117 | Ashuganj 150MW PP (Midland) | 130 | 130 | 135 | 135 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 70 | 75 | 88 | 115 | 132 | 140 |  | 140 | 140 | 145 | 133 | 143 | 100 | 100 | 2219709
118 | Bibiyana-III 400 MW CCPP | 371 | 371 | 371 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 371 | 370 | 370 | 372 | 370 | 371 | 371 | 371 |  | 370 | 370 | 371 | 370 | 371 | 370 | 370 | 8909000
| Jamalpur 115 MW PP (United) | 45 | 45 | 20 | 45 | 16 | 16 | 16 | 16 | 19 | 100 | 97 | 97 | 97 | 96 | 96 | 105 | 105 | 106 |  | 106 | 106 | 106 | 106 | 97 | 97 | 97 | 1774800
| Anwara 300 MW PP (United) | 280 | 265 | 265 | 265 | 265 | 265 | 265 | 280 | 282 | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6772036
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 20 | 20 | 20 | 46 | 67 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 64 | 100 | 100 | 100 | 100 | 100 | 100 | 1923840
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 69 | 69 | 69 | 73 | 113 | 113 | 113 | 113 | 113 | 112 | 111 | 111 | 68 |  | 88 | 113 | 113 | 113 | 113 | 113 | 113 | 2520382
| Bhairob 54.5 MW | 36 | 36 | 36 | 2 | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 36 | 36 | 35 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 708480
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 6 | 11 | 14 | 29 | 17 | 16 | 21 | 12 | 12 | 5 | 1 | [8 empty] | 164482
| Chandpur 115(Doreen) | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 38 | 62 | 76 |  | 91 | 101 | 101 | 101 | 101 | 101 | 101 | 1323840
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 35 | 35 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 53 | 55 | 55 | 55 | 55 | 1263240
120 | Eastern Zone Total | 7415 | 7278 | 7465 | 7266 | 6723 | 6311 | 6241 | 6383 | 6862 | 7041 | 7249 | 7452 | 7835 | 8176 | 8368 | 8290 | 8031 | 8210 |  | 8822 | 9053 | 9112 | 9349 | 9447 | 9207 | 8979 | 188844037
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 84 | [11 empty] | 0 | 6 | 24 | 93 | 93 | 93 |  | 114 | 113 | 113 | 113 | 113 | 115 | 115 | 1072320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 10 | 29 | 31 |  | 44 | 37 | 37 | 0 |  |  |  | 135840
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 220 | 220 | 223 | 140 | 120 | 120 | 120 | 322720
129 | Rupsha 105 MW PP (Orion rupsha) | 95 | 95 | 95 | 90 | 53 | 17 | 17 | 35 | 35 | 35 | 35 | 74 | 95 | 94 | 94 | 70 | 70 | 70 |  | 90 | 105 | 105 | 105 | 105 | 105 | 105 | 1972800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 15 | 38 | 52 | 75 | 85 | 100 | 72 | 41 | 56 | 34 | 10 | 1 | [8 empty] | 522720
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 650400
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 220 | 202 | 200 | 222 | 221 | 221 | 220 | 220 | 140 | 140 | 140 | 117 | 122 | 122 | 144 | 158 |  | 200 | 217 | 220 | 219 | 218 | 221 | 220 | 4577209
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 777408
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 89 | 89 | 89 | 88 | 89 | 88 | 88 | 88 | 85 | 85 | 84 | 85 | 87 | 87 | 87 | 87 | 86 | 86 |  | 87 | 88 | 88 | 88 | 89 | 88 | 89 | 2109507
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 33 | 34 | 34 | 29 | 27 | 21 | 12 | 16 | 17 | 18 | 17 | 17 | 17 | 24 | 26 | 28 |  | 35 | 35 | 37 | 39 | 39 | 39 | 39 | 667548
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 0 |  | 2 | 0 |  |  |  |  | 0 | 9600
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 209625
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 21 | 24 | 23 |  |  |  |  | 43648
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 51 | 32 | 32 | [6 empty] | 15 | 15 | 15 | 15 | 15 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 15 | 15 | 727200
146 | Bheramara HVDC | 924 | 925 | 924 | 924 | 924 | 924 | 925 | 924 | 924 | 924 | 924 | 925 | 924 | 923 | 924 | 924 | 923 | 923 |  | 923 | 924 | 923 | 923 | 924 | 923 | 923 | 22354909
147 | Bheramara 410 MW CCPP | 275 | 275 | 290 | 295 | 310 | 330 | 340 | 345 | 350 | 355 | 355 | 365 | 370 | 370 | 400 | 395 | 395 | 360 |  | 405 | 400 | 400 | 400 | 405 | 400 | 410 | 8715744
148 | Payra 1320 MW | 560 | 560 | 560 | 560 | 560 | 530 | 480 | 480 | 490 | 530 | 540 | 600 | 622 | 622 | 622 | 622 | 570 | 550 |  | 550 | 600 | 600 | 622 | 622 | 610 | 530 | 14632300
149
150 | Barapukuria TPP Unit-1 | 26 | 62 | 75 | 77 | 76 | 77 | 77 | 75 | 78 | 79 | 79 | 80 | 80 | 80 | 81 | 80 | 78 | 81 |  | 80 | 81 | 80 | 82 | 80 | 80 | 80 | 1786472
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 0 | [13 empty] | 15 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 |  |  | 322574
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 3 | 4 | 5 | 5 | 3 | 3 | 3 | 2 | 0 | 0 | [8 empty] | 26760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 190 | 160 | 140 | 140 | 140 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 143 | 130 | 130 | 130 |  | 154 | 190 | 190 | 195 | 130 | 130 | 130 | 3702845
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 161 | 161 | 161 | 161 | 166 | 166 | 166 | 173 | 187 | 210 | 199 | 164 | 119 | 135 | 146 | 165 | 198 | 205 |  | 208 | 211 | 207 | 191 | 194 | 192 | 199 | 4489855
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 350 | 419 | 418 | 380 | 380 | 380 | 383 | 415 | 415 | 414 | 414 | 417 | 415 | 414 | 418 | 305 | 303 |  | 416 | 417 | 418 | 418 | 416 | 416 | 419 | 9566327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 0 | [14 empty] | 5 | 6 | 28 |  | 30 | 30 | 30 | 0 |  |  |  | 122365
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 17 | 17 | 18 | 0 |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 452880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232886
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 0 | [18 empty] | 34 | 34 | 34 | 34 |  |  |  | 132054
167 | Katakhali 50 MW Peaking PP | 0 | [14 empty] | 14 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 |  |  | 227983
168 | Santahar 50 MW Peaking PP | 0 | [14 empty] | 19 | 32 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 28 | 245515
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 43 | 43 | 52 | 52 | 24 | 24 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 789864
170 | Chapainawabganj 100 MW Peaking PP | 0 | [14 empty] | 39 | 54 | 54 |  | 93 | 93 | 93 | 92 | 92 | 92 | 92 | 675232
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 10 | 7 | 0 |  |  |  | 0 | 8594
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 50 | 50 | 79 | 110 | 113 | 113 | 113 | 113 | 113 | 70 | 70 |  | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 2394720
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 50 | 35 | 35 | 35 | 35 | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2264736
173 | Rangpur 20 MW GTPP | [26 empty] | 0
175 | Saidpur 20 MW GTPP | [26 empty] | 0
176 | Rangpur 113 MW PP (Confidence) | 104 | 98 | 99 | 102 | 96 | 35 | 35 | 35 | 35 | 35 | 44 | 97 | 97 | 100 | 104 | 100 | 75 | 75 |  | 97 | 104 | 104 | 104 | 104 | 104 | 104 | 1998470
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 5 | 5 | 5 | 6 | 6 | 5 | 2 | 1 | 0 |  | 0 | [6 empty] | 45584
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 34 | 34 | 0 | [5 empty] | 17 | 17 | 17 | 70 | 110 | 115 | 110 | 72 | 72 |  | 85 | 115 | 115 | 115 | 115 | 72 | 72 | 1371341
178