## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-17 | Sunday
|  |  | Date (day): | 2022-04-17 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15049.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15740 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-16 | 2022-04-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 232 | 232 | 230 | 232
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 98 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 397 | 399 | 400 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 260 | 329 | 320 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 66 | 96 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 150 | 140 | 150 | 185 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 64 | 76 | 75 | 76 |  | 26 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 20 | 98 | 90 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 325 | 330 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 67 | 84 | 84 | 84 |  | 18 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 80 | 132 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 205 | 263 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 301 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 70 | 70 |  | 35 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 92 | 90 | 92 |  | 12 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 21 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3269 | 4212 | 4262 | 4281 | 986 | 633
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 37 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 68 | 101 | 65 | 66 |  | 164 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 221 | 203 | 215 | 215
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 43 | 40 | 43 |  | 55 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 84 |  | 18 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 20 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 86 | 95 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 280 | 283 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 112 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2282 | 1169 | 1431 | 1448 | 1470 | 180 | 622
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 214 | 210 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 200 | 300
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 175 | 360 | 360
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 25 | 26 | 26 | 19 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 56 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 63 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 135 | 135 | 135 |  | 15 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 91 | 90 | 91 |  | 72 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 36 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 170 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 62 | 62 | 60 | 62 |  | 52 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 115 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 36 | 36 |  |  | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 82 | 101 | 101 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1187 | 1872 | 2085 | 2322 | 451 | 162
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 166 | 144 | 140 | 150 | 52 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 151 | 180 | 180 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 72 | 115 | 106 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 11 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 444 | 481 | 519.6 | 487 | 52 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 40 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 116 | 250 | 280 | 50 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 11 | 10 | 11 | 40 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 3 | 3 | 3 | 3 | 47 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 55 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 220 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 27 | 27 | 26 | 27 | 23 |  | Gas shortage
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 19 | 24 | 20 | 24
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 310 | 320 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 402 | 370 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 400 | 383 | 383
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1879 | 1857 | 1962 | 2039 | 180 | 219
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 924 | 942 | 942
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 66 | 66 | 66 |  | 49 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 0 | 36 |  | 18 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 200 | 200
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 320 | 300 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 25 | 94 | 94 | 94 |  | 11 | Engine problem
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 89 | 70 | 89 |  | 16 | Engine problem
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1529 | 1861 | 1904 | 1909 | 90 | 181
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 50 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 22 | 40 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 67 | 66 | 67 | 127 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 622 | 622 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 219 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 134 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 906 | 1192 | 1041 | 1240 | 127 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 |  | 16 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 133 | 190 | 220 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 419 | 414 | 414 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 20 | 26 | 30 | 32 |  | 18 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 20 | 43 | 43 | 43 |  | 9 | Engine problem
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 88 | 88 |  | 16 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 168 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 108 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 845 | 1333 | 1268 | 1413 | 601 | 109
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 74 | 74 | 74
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 110 | 109 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 110 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 473 | 543 | 560 | 579 | 0 | 95
|  | Total |  |  |  |  | 22348 | 21484 | 11701 | 14782 | 15049.6 | 15740 | 2667 | 2029
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11223.2474 | 14178.45 | 14435.1239 | 15097.3348
| A. |  | 2022-04-16 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 14782 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10790 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14782 | MW
| 3 | Day peak Generation : |  |  | 11701 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14178.45 | MW
| 4 | Evening peak Generation : |  |  | 14782 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 303.6867 | MKWHr | By Solar | 1.1592 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 152.0442 | MKWHr |  | By Oil: | 99.9562 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 23.0078 | MKWHr |  | By Hydro: | 1.6623 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2667 | MW | Dhaka | 4920.95 | 4920.95 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2029 | MW | Chittagong | 1396.3 | 1396.3 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4696 | MW | Khulna | 1843 | 1843 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1133.56 | MMCFD |  |  | Rajshahi | 1635.2 | 1635.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 154925755.81 | ii) Oil : | Taka | 790163642.24 | Comilla | 1392 | 1392 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 110028470.92 | Total | Taka | 1055117868.97 | Mymensingh | 1150 | 1150 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.784 | MKWHr. | Sylhet | 514 | 514 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -118 | MW (E to W) at | 21:00 | hrs | Barisal | 419 | 419 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -304 | MW at | 3:00 | hrs | Rangpur | 908 | 908 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 14178.45 | 14178.45 |  | 0
| B. |  | 2022-04-17 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 36.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15740 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 740 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 308.1654 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10867 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3367 | MKWHr. | ii) HVDC Flow at Peak Time |  | 924 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5203 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.42 |  | (b) Today: | 79.96 |  | (c) Rule Curve: |  | 84.8
.

## YesterdayGen
2022-04-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 396 | 333 |  | 0 | 225 | 145 | 96 | 65 | 55 | 329 | 0 | 0 | 40 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 67 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 25 | 0 | 0 | 95 | 38 | 0 | 41 | 0 | 0 | 0 | 0 | 300 | 187 | 45 | 0 | 25 | 45 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 20 | 144 | 195 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 159 | 55 | 85 | 0 | 191 | 0 | 27 | 10 | 290 | 16 | 11 | 0 | 265 | 0 | 0 | 150 | 0 | 149 | 0 | 90 | 200 | 145 | 369 | 77 | 72 | 105 | 0 | 264 | 54 | 110 | 62 | 18 | 100 | 401 | 72 | 0 | 118 | 92 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 390 | 0 | 47 | 120 | 0 | 0 | 0 | 0 | 8 | 65 | 37 | 80 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 25 | 52 | 0 | 22 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 376 | 105 | 0 | 113 | 67 | 109 | 0 | 0 | 113 | 622 | 217 | 0 | 54 | 0 | 0 | 115 |  | 8642 | 4248 | 12890 | 4257 | 923 | 2188 | 0 | 3975 | 945 | 67 | 120 | 271 | 144 | 0 | 0 | 80.52
2:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 360 | 292 |  | 0 | 225 | 140 | 96 | 79 | 55 | 300 | 0 | 0 | 40 | 84 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 66 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 95 | 38 | 0 | 41 | 0 | 0 | 0 | 0 | 300 | 194 | 45 | 0 | 25 | 45 | 0 | 51 | 0 | 0 | 38 | 22 | 9 | 33 | 20 | 146 | 196 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 160 | 55 | 85 | 0 | 191 | 0 | 27 | 10 | 285 | 19 | 11 | 0 | 278 | 0 | 0 | 151 | 0 | 149 | 0 | 90 | 200 | 135 | 369 | 77 | 72 | 105 | 0 | 265 | 54 | 110 | 62 | 8 | 100 | 401 | 72 | 0 | 108 | 92 | 0 | 36 | 0 | 102 | 55 |  | 923 | 0 | 390 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 66 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 71 | 0 | 249 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 345 | 105 | 0 | 113 | 67 | 109 | 0 | 0 | 113 | 622 | 217 | 0 | 54 | 0 | 0 | 115 |  | 8468 | 4100 | 12568 | 4183 | 923 | 2105 | 0 | 3933 | 942 | 66 | 120 | 150 | 146 | 0 | 0 | 80.5
3:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 360 | 333 |  | 0 | 225 | 125 | 97 | 80 | 55 | 336 | 0 | 0 | 40 | 84 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 95 | 38 | 0 | 41 | 0 | 0 | 0 | 0 | 300 | 195 | 45 | 0 | 25 | 45 | 0 | 51 | 0 | 0 | 42 | 22 | 9 | 33 | 20 | 148 | 197 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 159 | 55 | 85 | 0 | 191 | 0 | 27 | 10 | 285 | 19 | 11 | 0 | 281 | 0 | 0 | 151 | 0 | 149 | 0 | 90 | 200 | 147 | 368 | 77 | 72 | 105 | 0 | 265 | 54 | 110 | 62 | 8 | 100 | 401 | 72 | 0 | 108 | 95 | 0 | 36 | 0 | 102 | 55 |  | 923 | 0 | 395 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 67 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 386 | 105 | 0 | 113 | 67 | 109 | 0 | 0 | 113 | 622 | 216 | 0 | 54 | 0 | 0 | 115 |  | 8561 | 4143 | 12704 | 4222 | 923 | 2171 | 0 | 3963 | 944 | 65 | 120 | 148 | 148 | 0 | 0 | 80.48
4:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 399 | 333 |  | 0 | 225 | 140 | 98 | 79 | 55 | 336 | 0 | 0 | 0 | 76 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 65 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 95 | 38 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 201 | 45 | 0 | 25 | 45 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 20 | 148 | 202 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 160 | 55 | 85 | 0 | 191 | 0 | 27 | 10 | 285 | 19 | 11 | 0 | 268 | 0 | 0 | 151 | 0 | 149 | 0 | 90 | 200 | 100 | 368 | 77 | 72 | 105 | 0 | 268 | 54 | 110 | 62 | 8 | 100 | 401 | 72 | 0 | 108 | 112 | 0 | 36 | 0 | 102 | 55 |  | 923 | 0 | 403 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 36 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 249 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 385 | 53 | 0 | 113 | 0 | 109 | 0 | 0 | 113 | 622 | 216 | 0 | 54 | 0 | 0 | 115 |  | 8516 | 3951 | 12467 | 4276 | 923 | 2186 | 0 | 3708 | 943 | 65 | 120 | 98 | 148 | 0 | 0 | 80.46
5:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 399 | 333 |  | 0 | 225 | 132 | 96 | 79 | 30 | 337 | 0 | 0 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 66 | 0 | 0 | 0 | 15 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 27 | 0 | 42 | 0 | 0 | 0 | 0 | 305 | 198 | 45 | 0 | 25 | 45 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 20 | 134 | 212 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 159 | 55 | 86 | 0 | 218 | 0 | 27 | 10 | 280 | 19 | 11 | 0 | 145 | 0 | 0 | 152 | 0 | 149 | 0 | 90 | 155 | 60 | 368 | 78 | 35 | 105 | 0 | 268 | 54 | 95 | 62 | 8 | 100 | 400 | 55 | 0 | 108 | 112 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 398 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 385 | 35 | 0 | 113 | 0 | 53 | 0 | 0 | 70 | 622 | 215 | 0 | 17 | 0 | 0 | 45 |  | 8147 | 3663 | 11810 | 4309 | 924 | 2171 | 0 | 3093 | 945 | 66 | 120 | 48 | 134 | 0 | 0 | 80.44
6:00 | 0 | 0 | 232 | 0 | 270 | 98 | 0 | 392 | 333 |  | 0 | 225 | 130 | 98 | 79 | 15 | 280 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 66 | 0 | 0 | 0 | 17 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 198 | 45 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 20 | 126 | 212 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 130 | 159 | 55 | 86 | 0 | 218 | 0 | 27 | 10 | 265 | 19 | 11 | 0 | 141 | 0 | 0 | 104 | 0 | 149 | 1 | 90 | 120 | 30 | 369 | 49 | 35 | 68 | 0 | 272 | 54 | 92 | 62 | 8 | 40 | 401 | 34 | 1 | 108 | 113 | 0 | 36 | 0 | 101 | 35 |  | 923 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 385 | 17 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 560 | 214 | 0 | 17 | 0 | 1 | 17 |  | 7607 | 3427 | 11034 | 4209 | 923 | 2122 | 0 | 2548 | 885 | 66 | 120 | 32 | 126 | 3 | 0 | 80.42
7:00 | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 376 | 282 |  | 0 | 225 | 150 | 65 | 79 | 15 | 280 | 0 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 67 | 0 | 0 | 0 | 16 | 210 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 188 | 45 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 20 | 130 | 210 | 0 | 20 | 1 | 0 | 41 | 11 | 3 | 130 | 159 | 55 | 84 | 0 | 218 | 0 | 27 | 10 | 295 | 19 | 11 | 0 | 45 | 0 | 0 | 104 | 0 | 149 | 4 | 90 | 85 | 10 | 369 | 49 | 45 | 34 | 1 | 267 | 54 | 92 | 62 | 8 | 40 | 401 | 17 | 4 | 108 | 113 | 0 | 36 | 1 | 101 | 35 |  | 924 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 387 | 17 | 0 | 113 | 0 | 34 | 0 | 1 | 35 | 560 | 219 | 0 | 17 | 0 | 11 | 17 |  | 7349 | 3441 | 10790 | 4212 | 924 | 2117 | 0 | 2279 | 886 | 67 | 120 | 32 | 130 | 23 | 0 | 80.4
8:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 377 | 281 |  | 0 | 225 | 120 | 55 | 80 | 15 | 280 | 0 | 0 | 0 | 32 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 67 | 0 | 0 | 0 | 16 | 202 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 174 | 45 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 19 | 9 | 33 | 20 | 130 | 211 | 0 | 20 | 1 | 0 | 41 | 11 | 3 | 130 | 157 | 50 | 84 | 0 | 218 | 0 | 27 | 10 | 290 | 19 | 11 | 0 | 48 | 0 | 0 | 104 | 0 | 149 | 7 | 90 | 85 | 10 | 368 | 49 | 70 | 34 | 2 | 280 | 54 | 92 | 62 | 8 | 40 | 401 | 17 | 11 | 108 | 113 | 0 | 36 | 8 | 101 | 44 |  | 923 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 8 | 39 | 0 | 3 | 70 | 560 | 180 | 0 | 17 | 0 | 20 | 17 |  | 7392 | 3483 | 10875 | 4154 | 923 | 2069 | 0 | 2395 | 885 | 67 | 120 | 80 | 130 | 52 | 0 | 80.38
9:00 | 0 | 0 | 232 | 0 | 270 | 92 | 0 | 351 | 282 |  | 0 | 225 | 150 | 55 | 78 | 15 | 280 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 67 | 0 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 183 | 8 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 19 | 9 | 33 | 20 | 132 | 200 | 0 | 20 | 1 | 0 | 40 | 11 | 3 | 110 | 159 | 50 | 84 | 0 | 218 | 0 | 27 | 10 | 275 | 19 | 8 | 0 | 107 | 0 | 0 | 104 | 0 | 149 | 12 | 90 | 34 | 10 | 369 | 49 | 70 | 34 | 3 | 280 | 54 | 92 | 52 | 8 | 40 | 340 | 51 | 19 | 75 | 113 | 0 | 36 | 9 | 101 | 55 |  | 924 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 32 | 70 | 0 | 3 | 70 | 520 | 130 | 0 | 17 | 3 | 53 | 17 |  | 7310 | 3510 | 10820 | 4093 | 924 | 1972 | 0 | 2484 | 845 | 67 | 120 | 80 | 132 | 103 | 0 | 80.36
10:00 | 0 | 0 | 232 | 0 | 270 | 92 | 0 | 381 | 312 |  | 0 | 225 | 150 | 50 | 70 | 15 | 325 | 0 | 0 | 0 | 32 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 44 | 0 | 68 | 0 | 0 | 0 | 16 | 215 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 330 | 198 | 8 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 19 | 9 | 32 | 20 | 138 | 199 | 0 | 20 | 1 | 0 | 41 | 11 | 3 | 130 | 157 | 60 | 84 | 0 | 218 | 0 | 27 | 10 | 300 | 19 | 8 | 0 | 117 | 0 | 0 | 150 | 0 | 149 | 15 | 90 | 34 | 10 | 400 | 72 | 70 | 34 | 2 | 280 | 54 | 92 | 52 | 8 | 40 | 397 | 53 | 24 | 72 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 416 | 17 | 0 | 113 | 32 | 70 | 0 | 3 | 70 | 520 | 220 | 0 | 17 | 2 | 37 | 17 |  | 7668 | 3566 | 11234 | 4314 | 923 | 2128 | 0 | 2537 | 842 | 68 | 120 | 80 | 138 | 84 | 0 | 80.34
11:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 401 | 313 |  | 0 | 225 | 120 | 53 | 64 | 15 | 326 | 0 | 0 | 3 | 43 | 80 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 69 | 0 | 0 | 0 | 16 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 75 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 203 | 8 | 0 | 25 | 57 | 0 | 51 | 0 | 0 | 43 | 0 | 9 | 33 | 20 | 146 | 180 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 158 | 60 | 83 | 0 | 218 | 0 | 27 | 10 | 290 | 19 | 8 | 0 | 122 | 0 | 0 | 151 | 0 | 149 | 18 | 76 | 34 | 10 | 400 | 72 | 70 | 41 | 5 | 280 | 54 | 92 | 62 | 8 | 90 | 396 | 54 | 34 | 72 | 113 | 0 | 36 | 31 | 96 | 55 |  | 923 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 94 | 15 | 79 | 0 | 4 | 100 | 540 | 120 | 0 | 17 | 4 | 87 | 17 |  | 7789 | 3522 | 11311 | 4239 | 923 | 2031 | 0 | 2656 | 862 | 69 | 120 | 80 | 146 | 185 | 0 | 80.32
12:00 | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 397 | 260 |  | 0 | 225 | 140 | 66 | 64 | 40 | 322 | 0 | 0 | 20 | 67 | 80 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 68 | 0 | 0 | 0 | 16 | 221 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 330 | 212 | 8 | 0 | 28 | 56 | 0 | 51 | 0 | 0 | 43 | 16 | 9 | 24 | 20 | 146 | 166 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 154 | 60 | 83 | 0 | 219 | 0 | 27 | 10 | 285 | 19 | 8 | 0 | 205 | 0 | 0 | 151 | 0 | 149 | 17 | 76 | 36 | 20 | 401 | 72 | 70 | 51 | 3 | 280 | 54 | 92 | 62 | 8 | 100 | 395 | 72 | 11 | 72 | 112 | 0 | 36 | 21 | 82 | 55 |  | 923 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 25 | 0 | 108 | 15 | 110 | 0 | 4 | 113 | 550 | 220 | 0 | 17 | 5 | 86 | 34 |  | 7948 | 3753 | 11701 | 4274 | 923 | 2096 | 0 | 2950 | 875 | 68 | 120 | 100 | 146 | 149 | 0 | 80.3
13:00 | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 397 | 272 |  | 0 | 225 | 120 | 81 | 70 | 50 | 321 | 0 | 0 | 60 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 66 | 0 | 0 | 0 | 20 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 75 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 305 | 214 | 8 | 0 | 28 | 57 | 0 | 51 | 0 | 0 | 43 | 16 | 9 | 25 | 20 | 148 | 161 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 157 | 60 | 85 | 0 | 192 | 0 | 26 | 10 | 280 | 21 | 8 | 0 | 243 | 0 | 0 | 151 | 0 | 149 | 18 | 90 | 118 | 71 | 402 | 72 | 70 | 51 | 5 | 280 | 54 | 92 | 62 | 8 | 100 | 400 | 73 | 32 | 72 | 113 | 0 | 36 | 29 | 86 | 55 |  | 923 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 15 | 8 | 65 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 33 | 20 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 415 | 61 | 0 | 113 | 15 | 109 | 0 | 6 | 113 | 550 | 213 | 0 | 17 | 4 | 76 | 110 |  | 8232 | 3940 | 12172 | 4215 | 923 | 2082 | 0 | 3410 | 873 | 66 | 120 | 163 | 148 | 172 | 0 | 80.28
14:00 | 0 | 0 | 231 | 0 | 270 | 94 | 0 | 393 | 323 |  | 0 | 225 | 140 | 93 | 75 | 55 | 325 | 0 | 0 | 86 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 34 | 0 | 0 | 75 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 211 | 8 | 0 | 28 | 55 | 0 | 51 | 0 | 0 | 43 | 18 | 9 | 32 | 20 | 152 | 150 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 153 | 60 | 84 | 0 | 192 | 0 | 27 | 10 | 300 | 21 | 8 | 0 | 265 | 56 | 25 | 151 | 25 | 149 | 15 | 90 | 169 | 122 | 403 | 72 | 70 | 51 | 3 | 280 | 54 | 92 | 62 | 8 | 90 | 394 | 72 | 26 | 72 | 112 | 0 | 36 | 28 | 83 | 55 |  | 923 | 0 | 355 | 0 | 15 | 140 | 0 | 0 | 0 | 25 | 8 | 64 | 26 | 32 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 8 | 52 | 33 | 20 | 0 | 11 | 73 | 0 | 214 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 4 | 0 | 0 | 408 | 72 | 1 | 113 | 37 | 109 | 0 | 6 | 113 | 550 | 220 | 0 | 17 | 5 | 66 | 110 |  | 8575 | 4050 | 12625 | 4257 | 923 | 2170 | 111 | 3584 | 837 | 65 | 140 | 235 | 152 | 151 | 0 | 80.26
15:00 | 0 | 0 | 231 | 0 | 270 | 94 | 0 | 402 | 312 |  | 0 | 225 | 135 | 94 | 76 | 55 | 325 | 0 | 0 | 98 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 45 | 0 | 64 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 34 | 0 | 0 | 75 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 310 | 211 | 8 | 0 | 25 | 56 | 0 | 51 | 0 | 13 | 43 | 19 | 9 | 32 | 20 | 158 | 150 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 153 | 60 | 84 | 0 | 192 | 0 | 27 | 10 | 300 | 21 | 8 | 0 | 263 | 180 | 25 | 150 | 25 | 149 | 11 | 90 | 200 | 128 | 404 | 76 | 70 | 55 | 3 | 280 | 54 | 92 | 62 | 8 | 90 | 391 | 72 | 25 | 72 | 98 | 0 | 36 | 18 | 83 | 55 |  | 923 | 0 | 350 | 0 | 15 | 190 | 0 | 0 | 0 | 27 | 8 | 64 | 23 | 32 | 0 | 0 | 0 | 3 | 5 | 38 | 0 | 34 | 21 | 52 | 32 | 20 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 20 | 0 | 0 | 414 | 72 | 18 | 113 | 50 | 109 | 0 | 4 | 113 | 622 | 217 | 0 | 17 | 3 | 44 | 109 |  | 8732 | 4300 | 13032 | 4263 | 923 | 2155 | 268 | 3668 | 945 | 64 | 190 | 288 | 158 | 110 | 0 | 80.24
16:00 | 0 | 0 | 231 | 0 | 250 | 94 | 0 | 401 | 312 |  | 0 | 225 | 130 | 96 | 44 | 55 | 325 | 0 | 0 | 98 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 41 | 0 | 64 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 20 | 25 | 0 | 0 | 75 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 213 | 50 | 0 | 28 | 53 | 0 | 5 | 0 | 48 | 43 | 21 | 9 | 32 | 20 | 154 | 142 | 0 | 20 | 1 | 0 | 41 | 11 | 3 | 163 | 110 | 60 | 84 | 0 | 192 | 0 | 27 | 10 | 290 | 21 | 8 | 0 | 263 | 205 | 100 | 151 | 100 | 149 | 7 | 90 | 200 | 50 | 402 | 77 | 70 | 86 | 3 | 280 | 54 | 92 | 62 | 31 | 100 | 401 | 72 | 11 | 84 | 97 | 0 | 36 | 13 | 99 | 55 |  | 923 | 0 | 350 | 0 | 16 | 200 | 0 | 0 | 4 | 26 | 8 | 66 | 25 | 32 | 0 | 0 | 0 | 43 | 29 | 40 | 0 | 34 | 12 | 52 | 32 | 19 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 20 | 0 | 0 | 414 | 78 | 46 | 113 | 50 | 108 | 0 | 3 | 113 | 622 | 210 | 0 | 17 | 2 | 35 | 110 |  | 8515 | 4335 | 12850 | 3896 | 923 | 2127 | 471 | 3674 | 892 | 64 | 200 | 374 | 154 | 75 | 0 | 80.22
17:00 | 0 | 0 | 232 | 0 | 250 | 97 | 0 | 400 | 319 |  | 0 | 225 | 145 | 95 | 44 | 55 | 325 | 0 | 0 | 93 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 3 | 42 | 0 | 0 | 77 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 212 | 185 | 0 | 25 | 54 | 0 | 40 | 0 | 49 | 43 | 21 | 5 | 32 | 20 | 146 | 135 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 0 | 60 | 84 | 0 | 192 | 0 | 27 | 10 | 280 | 21 | 8 | 0 | 247 | 0 | 25 | 151 | 25 | 149 | 2 | 90 | 200 | 90 | 403 | 76 | 70 | 105 | 1 | 280 | 54 | 79 | 62 | 111 | 100 | 397 | 78 | 7 | 148 | 113 | 0 | 36 | 5 | 101 | 55 |  | 923 | 0 | 340 | 0 | 16 | 200 | 0 | 0 | 8 | 21 | 8 | 65 | 24 | 32 | 0 | 0 | 0 | 43 | 29 | 87 | 0 | 34 | 24 | 52 | 32 | 20 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 113 | 50 | 108 | 0 | 2 | 113 | 622 | 214 | 0 | 17 | 0 | 16 | 110 |  | 8395 | 4349 | 12744 | 3760 | 923 | 2319 | 50 | 3874 | 924 | 65 | 200 | 450 | 146 | 33 | 0 | 80.2
18:00 | 0 | 0 | 231 | 0 | 260 | 97 | 0 | 357 | 251 |  | 0 | 225 | 140 | 95 | 50 | 55 | 300 | 0 | 0 | 97 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 213 | 0 | 0 | 0 |  | 21 | 43 | 0 | 0 | 75 | 3 | 0 | 20 | 0 | 0 | 0 | 0 | 90 | 208 | 185 | 0 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 21 | 5 | 25 | 20 | 162 | 114 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 108 | 62 | 84 | 0 | 192 | 0 | 27 | 10 | 280 | 23 | 11 | 0 | 263 | 0 | 0 | 179 | 0 | 149 | 0 | 90 | 200 | 127 | 405 | 115 | 70 | 105 | 0 | 280 | 54 | 110 | 62 | 113 | 100 | 350 | 92 | 1 | 162 | 113 | 0 | 36 | 1 | 101 | 55 |  | 924 | 0 | 300 | 0 | 16 | 200 | 0 | 0 | 34 | 20 | 8 | 65 | 27 | 40 | 0 | 0 | 0 | 43 | 28 | 88 | 0 | 34 | 24 | 52 | 33 | 20 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 305 | 76 | 0 | 113 | 50 | 93 | 0 | 1 | 113 | 622 | 162 | 0 | 20 | 0 | 2 | 110 |  | 8597 | 4161 | 12758 | 3802 | 924 | 2116 | 0 | 4062 | 944 | 65 | 200 | 478 | 162 | 5 | 0 | 80.18
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 231 | 0 | 260 | 98 | 0 | 375 | 322 |  | 0 | 225 | 150 | 96 | 73 | 55 | 325 | 0 | 0 | 98 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 42 | 51 | 0 | 82 | 34 | 0 | 22 | 0 | 0 | 0 | 0 | 95 | 173 | 185 | 0 | 28 | 54 | 0 | 51 | 0 | 50 | 43 | 21 | 10 | 25 | 20 | 170 | 115 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 108 | 60 | 85 | 0 | 219 | 0 | 27 | 10 | 290 | 24 | 11 | 75 | 263 | 295 | 100 | 179 | 98 | 149 | 0 | 90 | 200 | 142 | 402 | 115 | 70 | 105 | 0 | 280 | 54 | 110 | 62 | 114 | 100 | 388 | 93 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 340 | 0 | 66 | 200 | 0 | 0 | 44 | 20 | 32 | 66 | 36 | 110 | 0 | 0 | 0 | 43 | 28 | 93 | 0 | 34 | 24 | 52 | 34 | 22 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 3 | 0 | 0 | 414 | 91 | 15 | 113 | 89 | 108 | 0 | 0 | 113 | 622 | 211 | 0 | 54 | 0 | 0 | 111 |  | 9459 | 4649 | 14108 | 3906 | 923 | 2379 | 586 | 4391 | 944 | 65 | 200 | 544 | 170 | 0 | 0 | 80.12
19:30 | 0 | 0 | 230 | 0 | 270 | 98 | 0 | 400 | 330 |  | 0 | 225 | 140 | 96 | 73 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 42 | 51 | 0 | 82 | 37 | 0 | 20 | 0 | 0 | 0 | 0 | 95 | 193 | 102 | 0 | 28 | 54 | 0 | 51 | 0 | 50 | 43 | 21 | 10 | 30 | 20 | 164 | 124 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 111 | 60 | 85 | 0 | 219 | 0 | 27 | 10 | 285 | 24 | 11 | 200 | 265 | 303 | 100 | 179 | 100 | 149 | 0 | 90 | 200 | 144 | 402 | 115 | 70 | 105 | 0 | 280 | 54 | 110 | 62 | 114 | 100 | 400 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 922 | 0 | 335 | 0 | 66 | 200 | 0 | 0 | 35 | 5 | 32 | 67 | 37 | 110 | 0 | 0 | 0 | 43 | 28 | 92 | 0 | 34 | 40 | 52 | 30 | 22 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 100 | 0 | 0 | 416 | 94 | 48 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 217 | 0 | 90 | 0 | 0 | 110 |  | 9609 | 4810 | 14419 | 3993 | 922 | 2296 | 851 | 4436 | 944 | 65 | 200 | 548 | 164 | 0 | 0 | 0
20:00 | 0 | 0 | 231 | 0 | 270 | 98 | 0 | 399 | 329 |  | 0 | 225 | 150 | 97 | 76 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 49 | 0 | 66 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 43 | 51 | 0 | 82 | 37 | 0 | 30 | 0 | 0 | 0 | 0 | 125 | 192 | 63 | 0 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 21 | 10 | 30 | 21 | 168 | 144 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 110 | 60 | 85 | 0 | 219 | 0 | 27 | 10 | 290 | 24 | 11 | 200 | 263 | 223 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 145 | 402 | 115 | 70 | 105 | 0 | 280 | 54 | 110 | 62 | 115 | 100 | 401 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 330 | 0 | 66 | 200 | 0 | 0 | 35 | 5 | 32 | 67 | 38 | 110 | 0 | 0 | 0 | 43 | 28 | 92 | 0 | 34 | 40 | 52 | 26 | 22 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 80 | 0 | 0 | 418 | 94 | 133 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 216 | 0 | 100 | 0 | 0 | 110 |  | 9576 | 4874 | 14450 | 4032 | 923 | 2284 | 836 | 4451 | 945 | 66 | 200 | 545 | 168 | 0 | 0 | 80.14
21:00 | 0 | 0 | 232 | 0 | 270 | 98 | 0 | 399 | 329 |  | 0 | 225 | 150 | 96 | 76 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 33 | 33 | 49 | 0 | 66 | 35 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 43 | 51 | 0 | 86 | 37 | 0 | 30 | 0 | 0 | 0 | 0 | 175 | 214 | 63 | 91 | 25 | 56 | 0 | 51 | 0 | 50 | 43 | 21 | 10 | 33 | 21 | 170 | 144 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 116 | 55 | 85 | 0 | 219 | 0 | 27 | 10 | 290 | 24 | 11 | 200 | 263 | 301 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 135 | 402 | 115 | 70 | 105 | 0 | 283 | 54 | 110 | 62 | 115 | 100 | 400 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 320 | 0 | 66 | 200 | 0 | 0 | 36 | 0 | 32 | 67 | 40 | 110 | 0 | 0 | 0 | 43 | 31 | 88 | 0 | 34 | 32 | 43 | 26 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 100 | 0 | 0 | 419 | 94 | 168 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 219 | 0 | 134 | 0 | 0 | 110 |  | 9853 | 4929 | 14782 | 4177 | 924 | 2291 | 969 | 4472 | 946 | 101 | 200 | 532 | 170 | 0 | 0 | 80.12
22:00 | 0 | 0 | 232 | 0 | 270 | 97 | 0 | 399 | 329 |  | 0 | 225 | 145 | 96 | 76 | 55 | 326 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 50 | 0 | 67 | 35 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 43 | 51 | 0 | 89 | 38 | 0 | 32 | 0 | 0 | 0 | 0 | 245 | 209 | 63 | 90 | 25 | 55 | 0 | 51 | 0 | 50 | 41 | 21 | 10 | 33 | 21 | 168 | 154 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 126 | 55 | 85 | 0 | 219 | 0 | 27 | 10 | 285 | 23 | 11 | 150 | 275 | 189 | 100 | 180 | 98 | 149 | 0 | 90 | 200 | 138 | 402 | 115 | 70 | 105 | 0 | 285 | 54 | 110 | 62 | 115 | 100 | 401 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 315 | 0 | 66 | 200 | 0 | 0 | 36 | 0 | 32 | 67 | 40 | 110 | 0 | 0 | 0 | 43 | 31 | 88 | 0 | 34 | 32 | 43 | 32 | 22 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 417 | 94 | 130 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 219 | 0 | 134 | 0 | 0 | 115 |  | 9783 | 4790 | 14573 | 4254 | 923 | 2279 | 667 | 4497 | 945 | 102 | 200 | 538 | 168 | 0 | 0 | 80.1
23:00 | 0 | 0 | 232 | 0 | 270 | 98 | 0 | 399 | 329 |  | 0 | 225 | 145 | 96 | 76 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 50 | 0 | 68 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 43 | 51 | 0 | 95 | 38 | 0 | 33 | 0 | 0 | 0 | 0 | 280 | 182 | 45 | 90 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 10 | 33 | 21 | 170 | 139 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 160 | 55 | 86 | 0 | 219 | 0 | 16 | 10 | 290 | 23 | 11 | 100 | 280 | 150 | 100 | 180 | 98 | 149 | 0 | 90 | 200 | 138 | 402 | 115 | 70 | 105 | 0 | 290 | 54 | 110 | 62 | 107 | 100 | 401 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 305 | 0 | 22 | 200 | 0 | 0 | 36 | 0 | 8 | 67 | 40 | 110 | 0 | 0 | 0 | 43 | 31 | 88 | 0 | 34 | 32 | 43 | 32 | 22 | 0 | 11 | 73 | 0 | 249 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 419 | 94 | 50 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 219 | 0 | 150 | 0 | 0 | 115 |  | 9681 | 4639 | 14320 | 4263 | 924 | 2260 | 498 | 4455 | 944 | 68 | 200 | 538 | 170 | 0 | 0 | 80.08
24:00 | 0 | 0 | 232 | 0 | 270 | 98 | 0 | 398 | 329 |  | 0 | 225 | 140 | 96 | 79 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 50 | 0 | 68 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 43 | 0 | 0 | 95 | 38 | 0 | 33 | 0 | 0 | 0 | 0 | 280 | 183 | 45 | 91 | 28 | 56 | 0 | 51 | 0 | 50 | 43 | 22 | 10 | 33 | 20 | 166 | 139 | 0 | 20 | 0 | 0 | 41 | 22 | 15 | 163 | 268 | 55 | 86 | 0 | 219 | 0 | 16 | 10 | 280 | 23 | 11 | 30 | 280 | 70 | 100 | 140 | 98 | 149 | 0 | 90 | 200 | 140 | 402 | 68 | 70 | 105 | 0 | 290 | 54 | 110 | 62 | 34 | 100 | 401 | 92 | 0 | 144 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 300 | 0 | 16 | 200 | 0 | 0 | 36 | 0 | 8 | 67 | 39 | 80 | 0 | 0 | 0 | 43 | 29 | 88 | 0 | 34 | 25 | 43 | 32 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 420 | 94 | 10 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 220 | 0 | 116 | 0 | 0 | 115 |  | 9420 | 4411 | 13831 | 4362 | 924 | 2270 | 308 | 4212 | 843 | 68 | 200 | 478 | 166 | 0 | 0 | 80.06
KWH | 0 | 0 | 5643000 | 0 | 6402200 | 2249818 | 0 | 9487430 | 7400000 |  | 0 | 4922000 | 3380247 | 2074560 | 1756128 | 1074421 | 7618231 | 0 | 0 | 1277760 | 1614096 | 2401440 | 0 | 0 | 0 | 0 | 1222200 | 1223728 | 1191000 | 472428 | 600000 | 626220 | 771480 | 754300 | 1105440 | 0 | 1594287 | 68000 | 0 | 0 | 510174 | 4922134 | 0 | 0 | 0 |  | 501600 | 434544 | 265380 | 0 | 2029440 | 417600 | 0 | 446880 | 0 | 0 | 0 | 0 | 6018000 | 4784000 | 1304727 | 327370 | 625896 | 1294080 | 0 | 1147197 | 0 | 434952 | 1030565 | 448020 | 236160 | 761900 | 476470 | 3520320 | 3977280 | 0 | 440172 | 12200 | 0 | 968640 | 277200 | 79056 | 3605564 | 3283000 | 1377888 | 2034240 | 0 | 4923530 | 0 | 647580 | 249120 | 7089500 | 487464 | 234048 | 777408 | 5221416 | 1590864 | 706772 | 3554400 | 710229 | 3608928 | 118125 | 2081280 | 3705120 | 2264872 | 9334000 | 1914000 | 1658400 | 1984682 | 29400 | 6644073 | 1340849 | 2431298 | 1467180 | 1005480 | 2106240 | 9407700 | 1681920 | 223720 | 2764800 | 2620745 | 0 | 883440 | 155846 | 2365440 | 1305720 |  | 22336727 | 0 | 8810496 | 0 | 488640 | 3767040 | 0 | 0 | 229440 | 151168 | 223125 | 1562000 | 714490 | 1482624 | 0 | 0 | 0 | 373875 | 265315 | 937392 | 0 | 316820 | 244028 | 850560 | 375860 | 487920 | 0 | 212400 | 1756364 | 0 | 5965000 | 0 | 0 | 0 | 0 | 4210245 | 0 | 0 | 300480 | 0 | 0 | 9556290 | 1673280 | 675552 | 2709696 | 1127520 | 2277398 | 0 | 41254 | 2445504 | 15286400 | 4954200 | 0 | 117600 | 30720 | 547920 | 1962732 |  | 204218652 | 99468075 | 303686727 | 100204102 | 22336727 | 51840109 | 4761305 | 85314494 | 23007764 | 1662287 | 3767040 | 6113394 | 3520320 | 1159185 | 0
Fuel Cost | 0 | 0 | 8238780 | 0 | 7106442 | 2969759.76 | 0 | 9582304.3 | 7622000 |  | 0 | 5364980 | 3752074.17 | 15745910.4 | 12099721.92 | 9089601.66 | 7922960.24 | 0 | 0 | 9621532.8 | 14720555.52 | 23630169.6 | 0 | 0 | 0 | 0 | 8922060 | 9459417.44 | 11743260 | 354321 | 450000 | 0 | 0 | 0 | 10689604.8 | 0 | 430457.49 | 18360 | 0 | 0 | 4739516.46 | 5365126.06 | 0 | 0 | 0 |  | 0 | 4202040.48 | 2574186 | 0 | 17656128 | 3307392 | 0 | 1327233.6 | 0 | 0 | 0 | 0 | 6018000 | 4401280 | 1683097.83 | 376475.5 | 707262.48 | 1811712 | 0 | 1961706.87 | 0 | 4393015.2 | 9841895.75 | 568985.4 | 177120 | 1333325 | 357352.5 | 26402400 | 4215916.8 | 0 | 559018.44 | 194468 | 0 | 1549824 | 493416 | 123327.36 | 4110342.96 | 3414320 | 2714439.36 | 3885398.4 | 0 | 8517706.9 | 0 | 757668.6 | 508204.8 | 7160395 | 365598 | 177876.48 | 13223710.08 | 39473904.96 | 27012870.72 | 11817227.84 | 18482880 | 11875028.88 | 35511851.52 | 1380881.25 | 16962432 | 40200552 | 15967347.6 | 8680620 | 17455680 | 15671880 | 17286580.22 | 0 | 50229191.88 | 11678794.79 | 21371109.42 | 14642456.4 | 8616963.6 | 14027558.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128659547.52 | 0 | 9251020.8 | 0 | 3840710.4 | 52211174.4 | 0 | 0 | 2406825.6 | 1584240.64 | 2324962.5 | 1765060 | 1107459.5 | 14470410.24 | 0 | 0 | 0 | 3678930 | 2695600.4 | 8295919.2 | 0 | 4283406.4 | 2364631.32 | 8241926.4 | 3645842 | 936806.4 | 0 | 160786.8 | 10590874.92 | 0 | 32330300 | 0 | 0 | 0 | 0 | 5557523.4 | 0 | 0 | 5111164.8 | 0 | 0 | 9460727.1 | 17469043.2 | 11491139.52 | 25715015.04 | 10643788.8 | 17672608.48 | 0 | 455856.7 | 18072274.56 | 67107296 | 0 | 0 | 0 | 0 | 0 | 0 |  | 729056966.89 | 483602873.04 | 1212659839.93 | 99889445.46 | 128659547.52 | 55036310.35 | 80531141.84 | 597949925.56 | 110028470.92 | 448817.49 | 52211174.4 | 59471400.44 | 26402400 | 2031205.95 | 0
Yesterday Day Peak | 0 | 0 | 232 | 0 | 270 | 95 | 0 | 397 | 260 |  | 0 | 225 | 140 | 66 | 64 | 40 | 322 | 0 | 0 | 20 | 67 | 80 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 68 | 0 | 0 | 0 | 16 | 221 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 330 | 212 | 8 | 0 | 28 | 56 | 0 | 51 | 0 | 0 | 43 | 16 | 9 | 24 | 20 | 146 | 166 | 0 | 20 | 2 | 0 | 41 | 11 | 3 | 163 | 154 | 60 | 83 | 0 | 219 | 0 | 27 | 10 | 285 | 19 | 8 | 0 | 205 | 0 | 0 | 151 | 0 | 149 | 17 | 76 | 36 | 20 | 401 | 72 | 70 | 51 | 3 | 280 | 54 | 92 | 62 | 8 | 100 | 395 | 72 | 11 | 72 | 112 | 0 | 36 | 21 | 82 | 55 |  | 923 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 25 | 0 | 108 | 15 | 110 | 0 | 4 | 113 | 550 | 220 | 0 | 17 | 5 | 86 | 34 |  | 11701 | DayPeak
Yesterday Evening Peak | 0 | 0 | 232 | 0 | 270 | 98 | 0 | 399 | 329 | 0 | 0 | 225 | 150 | 96 | 76 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 33 | 33 | 49 | 0 | 66 | 35 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 22 | 43 | 51 | 0 | 86 | 37 | 0 | 30 | 0 | 0 | 0 | 0 | 175 | 214 | 63 | 91 | 25 | 56 | 0 | 51 | 0 | 50 | 43 | 21 | 10 | 33 | 21 | 170 | 144 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 116 | 55 | 85 | 0 | 219 | 0 | 27 | 10 | 290 | 24 | 11 | 200 | 263 | 301 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 135 | 402 | 115 | 70 | 105 | 0 | 283 | 54 | 110 | 62 | 115 | 100 | 400 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 101 | 55 |  | 924 | 0 | 320 | 0 | 66 | 200 | 0 | 0 | 36 | 0 | 32 | 67 | 40 | 110 | 0 | 0 | 0 | 43 | 31 | 88 | 0 | 34 | 32 | 43 | 26 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 100 | 0 | 0 | 419 | 94 | 168 | 113 | 89 | 109 | 0 | 0 | 113 | 622 | 219 | 0 | 134 | 0 | 0 | 110 |  | 14782 | EvPeak
Forecast for Evening | 0 | 0 | 232 | 0 | 270 | 100 | 0 | 412 | 330 | 0 | 0 | 225 | 150 | 100 | 76 | 55 | 330 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 66 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 22 | 43 | 84 | 0 | 95 | 40 |  | 30 | 0 | 0 | 0 | 300 | 360 | 220 | 26 | 91 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 166 | 150 | 0 | 20 | 0 | 0 | 41 | 11 | 3 | 163 | 280 | 60 | 86 | 0 | 220 | 0 | 27 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 135 | 400 | 115 | 70 | 105 | 0 | 300 | 54 | 110 | 62 | 113 | 100 | 383 | 92 | 0 | 162 | 113 | 0 | 36 |  | 101 | 55 |  | 942 | 0 | 320 | 0 | 66 | 200 | 0 | 0 | 36 | 30 | 32 | 67 | 33 | 110 | 0 | 0 | 0 | 43 | 40 | 88 | 0 | 34 | 40 | 43 | 32 | 22 | 0 | 11 | 74 | 0 | 250 | 17 | 10 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 0 | 414 | 94 | 200 | 113 | 89 | 113 | 0 | 0 | 113 | 660 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 230 | 0 | 270 | 100 | 0 | 400 | 320 | 0 | 0 | 225 | 140 | 100 | 75 | 55 | 330 | 0 | 0 | 90 | 84 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 65 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 22 | 40 | 51 | 0 | 95 | 40 | 0 | 20 | 0 | 0 | 0 | 200 | 360 | 210 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 143 | 140 | 0 | 20 | 1.6 | 0 | 40 | 10 | 3 | 163 | 250 | 60 | 86 | 0 | 220 | 0 | 26 | 10 | 310 | 20 | 11 | 100 | 300 | 300 | 100 | 180 | 100 | 149 | 20 | 90 | 200 | 135 | 370 | 106 | 70 | 105 | 5 | 300 | 54 | 110 | 60 | 113 | 100 | 383 | 90 | 50 | 162 | 113 | 0 | 36 | 30 | 101 | 55 |  | 942 | 0 | 300 | 0 | 66 | 200 | 0 | 0 | 0 | 0 | 32 | 66 | 33 | 50 | 0 | 0 | 0 | 34 | 40 | 88 | 0 | 34 | 0 | 43 | 30 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 0 | 414 | 94 | 100 | 113 | 70 | 113 | 0 | 8 | 113 | 622 | 220 |  | 50 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 233 | 0 | 270 | 98 | 0 | 401 | 332 | 0 | 0 | 225 | 135 | 89 | 78 | 30 | 320 | 0 | 0 | 7 | 76 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 33 | 0 | 70 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 82 | 8 | 0 | 8 | 0 | 0 | 0 | 20 | 260 | 164 | 8 | 90 | 28 | 5 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 32 | 20 | 132 | 109 | 0 | 20 | 1 | 0 | 42 | 11 | 5 | 110 | 268 | 60 | 86 | 0 | 192 | 0 | 7 | 0 | 310 | 14 | 11 | 0 | 148 | 0 | 0 | 142 | 0 | 149 | 9 | 90 | 34 | 13 | 363 | 68 | 70 | 68 | 2 | 300 | 54 | 92 | 62 | 8 | 75 | 401 | 55 | 11 | 108 | 0 | 0 | 36 | 0 | 34 | 55 | 0 | 911 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 66 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 420 | 17 | 0 | 68 | 50 | 50 | 0 | 1 | 50 | 370 | 220 | 0 | 0 | 1 | 27 | 72 | 0 |  |  |  |  | 99956233 |  | 0
99956233
| Minimum Generation |  | 10790 | 7:00
| Highest Generation |  | 14782 | 21:00
| Day Peak Generation |  | 11701 | 12:00
| Evening Peak Generation |  | 14782 | 21:00
| HVDC Max Flow |  | 924 | 5:00
| HVDC EvPeak Flow |  | 924 | 21:00
| Load factor L.F |  | 85.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-17
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11701 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10867 | MW
Evening Peak Generation : |  | 14782 | MW Hour : | 21:00 | Available Max Generation : |  | 15740 | MW
E.P. Demand (at gen end) : |  | 14782 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15000 | MW
Maximum Generation : |  | 14782 | MW Hour : | 21:00 | Reserve(Generation end) |  | 740 | MW
Total Gen. (MKWH) : |  | 303.6867 | System Load Factor : | 85.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -304 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-17
Actual : | 79.96 | Ft.(MSL) , | Rule curve : | 84.8 | Ft.( MSL )
Gas Consumed : | Total = | 1133.56 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 154925755.81
: |  | Coal : | 110028470.92 | Oil : | 790163642.24 | Total : | 1055117868.97
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5297.8858 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1725.2537 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1674.1625 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1499.9519 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1367.0596 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1120.9852 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 550.3477 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 334.4665 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 826.229 |  |  | 0 | 0%
Total | 0 |  | 14396.3418 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari-BSRM 230 kV Ckt was under shut down from 08:12 to 15:10 for A/M.
b) Feni 132/33 kV T-1 transformer was under shut down from 10:15 to 11:01 for C/M. | [5 empty] | About 34 MW power interruption occurred under
Feni S/S area from 10:15 to 11:01.
c) Palashbari 132/33 kV T-1 transformer was under shut down from 09:25 to 11:08 for C/M.
d) Kabirpur 132/33 kV T-2 transformer was under shut down from 09:37 to 11:59 for C/M. | [5 empty] | About 20 MW power interruption occurred under
e) Kabirpur 132/33 kV T-1 transformer was under shut down from 12:03 to 13:27 for C/M. | [5 empty] | Kabirpur S/S area from 09:37 to 11:59.
f) Natore-Bogura 132 kV Ckt was under shut down from 11:52 to 14:54 for C/M.
g) Jholdhaka 132/33 kV T-1 transformer was under shut down from 11:55 to 14:24 for C/M.
h) Joypurhat 132/33 kV T-3 transformer was under shut down from 12:15 to 15:26 for C/M. | [5 empty] | About 30 MW power interruption occurred under
i) Joypurhat 132/33 kV T-2 transformer was under shut down from 12:14 to 13:25 for C/M. | [5 empty] | Joypurhat S/S area from 12:14 to 13:25.
j) Shahjibazar-330 MW CCPP ST tripped at 15:06 showing DEH fault. GT-1 & GT-2 were synchronized at
16:24 & 17:19 respectively.
k) Ashuganj(S)-360 MW tripped at 15:17 due to 230 kV unit breaker open and GT & ST were synchronized
at 17:08 & 19:19 respectively. At the same time Ashuganj midland-150 MW,Ashuganj-51 MW & Ashuganj
modular-195 MW also trip and were synchronized at 15:40,15:50 & 15:33 respectively.
l) Chandpur-150 MW CCPP GT was synchronized at 20:09.
m) Sylhet 132/33 kV T-2 transformer tripped at 02:55(17/4/22) showing E/F relay and was switched on | [5 empty] | About 47 MW power interruption occurred under
at 03:21(17/4/22) and again tripped at 03:31 due to same reason and was switched on at 03:45(17/4/22). | [5 empty] | Sylhet S/S area from 02:55 to 03:45(17/4/22).
n) Payra-Gopalganj 400 kV Ckt-2 was under shut down from 06:13 to 08:43(17/4/22) for C/M.
o) Kaliakoir 400/132 kV T-2 transformer was under shut down from 05:49 to 08:32(17/4/22) for C/M.
p) Baroaulia-Hathazari 132 kV Ckt-2 is under shut down since 06:37(17/4/22) for C/M.
q) Khulna© 132/33 kV T-1 transformer is under shut down since 04:50(17/4/22) for C/M.
r) Ashuganj(N)-360 MW CCPP GT was synchronized at 05:12(17/4/22).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 232 | 5643000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6402200 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2249818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9487430
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 329 | 7400000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4922000 | GT-2 Under S/D
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 96 | 2074560
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3380247 | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 76 | 1756128 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1074421
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 472428
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1277760
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7618231
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1614096 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1222200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2401440 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1223728
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1191000
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1226220 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 771480
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 754300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1105440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 263 | 5221416 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 301 | 1590864
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 706772
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 710229
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3608928
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1658400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1681920 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2764800
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 155846
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1305720
| Dhaka area Total |  |  |  | 5898 | 4212 | 84673022
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 510174
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 118125
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 417600 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 101 | 1662287 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4922134
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1984682
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 434544 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 265380 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2081280 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 446880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 2029440 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29400
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 283 | 6644073 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1340849
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2431298
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2106240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2620745
| Chattogram area Total |  |  |  | 2282 | 1431 | 30045131
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 4784000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 175 | 6018000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 25 | 625896 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1294080
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 63 | 1304727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1147197
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 2264872
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 434952 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 327370 | Sync at 20:09.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3705120
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 448020
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 236160
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3520320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 761900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1030565 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 476470 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 777408
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 1467180 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1005480
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 883440 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 2365440 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1872 | 34878597
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3977280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 440172
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3554400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1914000
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 223720
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 501600
| Mymensingh Area Total |  |  |  | 622 | 481 | 10623372
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 968640 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3605564
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 116 | 3283000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 277200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 3 | 79056 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 234048
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1377888
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2034240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4923530
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 27 | 647580 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 487464
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7089500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9334000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249120
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9407700
| Sylhet Area Total |  |  |  | 2477 | 1857 | 43998530
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 924 | 22336727
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 488640 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 229440 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3767040 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 151168 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8810496 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 223125 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 300480
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 1673280
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 1127520 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 547920
| Khulna Area Total |  |  |  | 2384 | 1861 | 39655836
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1482624
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 40 | 714490
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1562000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15286400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4954200
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 134 | 117600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1192 | 24117314
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 373875 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 265315 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 316820 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 244028 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 190 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Engine problem
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 9556290
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 375860 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 487920
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212400
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 850560 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 937392 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 168 | 675552 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2709696
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2445504
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30720
| Rajshahi Area Total |  |  |  | 2129 | 1333 | 19481932
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 74 | 1756364
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5965000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 109 | 2277398
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41254
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 110 | 1962732
| Rangpur Area Total |  |  |  | 720 | 543 | 12002748
| Total |  |  |  | 21484 | 14782 | 299476482
| Eastern Grid Total |  |  |  | 14293 | 9853 | 204218652
| Western Grid Total |  |  |  | 7191 | 4929 | 95257830
| National Grid Total |  |  |  | 21484 | 14782 | 299476482
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-16
(a) ENTIRE EASTERN GRID : |  | 9373.25 | MW | (b) ENTIRE WESTERN GRID : |  | 4805.2 | MW
i) Dhaka area |  | 4920.95 | MW | i) Khulna area |  | 1843 | MW
ii) Chittagong area |  | 1396.3 | MW | ii) Rajshahi area |  | 1635.2 | MW
iii) Comilla area |  | 1392 | MW | iii) Barisal area |  | 419 | MW
iv) Mymensingh area |  | 1150 | MW | iv) Rangpur area |  | 908 | MW
v) Sylhet area |  | 514 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 14178.45 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 19:00 | Hasnabad | 79 | 22:00 | Palashbari | 136 | 23:00
Agargaon | 91 | 19:00 | Hathazari | 105 | 19:30 | Panchagarh | 61 | 19:30
Agrabad | 84 | 20:00 | Ishurdi | 79 | 21:00 | Patuakhali | 130 | 22:00
AKS | 24 | 13:00 | Jaldhaka | 62 | 19:30 | PHP | 8 | 07:00
AKSML | 18 | 21:00 | Jamalpur | 162 | 08:00 | Purbachal | 20 | 20:00
Amnura | 77 | 21:00 | Jashore | 150 | 21:00 | Purbasadipur | 121 | 22:00
Ashuganj | 36 | 23:00 | Jhenaidah | 134 | 21:00 | Rahim | 17 | 13:00
Bagerhat | 110 | 21:00 | Joydebpur | 174 | 15:00 | Rajbari | 74 | 21:00
Bakulia | 129 | 19:30 | Joypurhat | 74 | 23:00 | Rajendrapur | 115 | 19:30
Banani | 47 | 13:00 | Juldah | 20 | 16:00 | Rajshahi | 182 | 23:00
Bangabhaban | 10 | 11:00 | Kabirpur | 278 | 17:00 | Rajshahi | 50 | 23:00
Barapukuria | 64 | 22:00 | Kachua | 84 | 21:00 | Ramganj | 98 | 21:00
Barguna | 20 | 21:00 | Kallyanpur | 96 | 18:30 | Rampur | 16.5 | 22:00
Barishal | 108 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 12 | 18:30
Barishal | 64 | 23:00 | Kamrangirchar | 73 | 16:00 | Rangpur | 152 | 19:30
Baroaulia | 85 | 23:00 | Kaptai | 4.5 | 19:00 | Ruppur | 3.2 | 01:00
Baroirhat | 48 | 15:00 | Kazla | 86 | 13:00 | Saidpur | 109 | 21:00
Bashundhara | 176 | 15:00 | Keranigonj | 72 | 19:30 | Satkhira | 130 | 21:00
BashundharaCement | 13 | 23:00 | Khagrachori | 26 | 19:00 | Satmasjid | 113 | 19:00
Beanibazar | 52 | 21:00 | Khulna | 91 | 20:00 | Savar | 193 | 16:00
Benapole | 64 | 21:00 | Khulshi | 182 | 19:30 | Shahjadpur | 122 | 21:00
Bhaluka | 140 | 15:00 | Kishoreganj | 146 | 20:00 | Shahjibazar | 122 | 23:00
Bhandaria | 58 | 21:00 | Kodda | 335 | 15:00 | Shahmirpur | 31.6 | 14:00
Bhangura | 46 | 03:00 | KSRM | 25 | 06:00 | Shariatpur | 74 | 21:00
Bheramara(GK) | 71 | 21:00 | Kulaura | 42 | 18:30 | Sherpur | 142 | 20:00
Bhulta | 235 | 15:00 | Kurigram | 58 | 19:30 | Shikalbaha | 46 | 20:00
Bog-Sherpur | 68 | 03:00 | Kushtia | 146 | 19:30 | Shitalakhya | 126 | 16:00
Bogura | 189 | 21:00 | Lalbag | 82 | 16:00 | Sholosohor | N/A | N/A
Borhanuddin | 45 | 00:00 | Lalmonirhat | 45 | 19:30 | Shyampur | 168 | 07:00
Brahmanbaria | 184 | 21:00 | Madanganj | 158 | 01:00 | Siddhirganj | 120 | 14:00
BSRM | 160 | 18:30 | Madaripur | 113 | 21:00 | Sirajganj | 123 | 21:00
Cantonment | 144 | 19:00 | Madartek | 86 | 23:00 | Sonargaon | 92 | 12:00
Chandpur | 78 | 22:00 | Madunaghat | 65 | 19:30 | Sreemongol | 60 | 19:00
Chandraghona | 34 | 19:00 | Magura | 66 | 21:00 | Srinagar | 46.75 | 21:00
Chapai | 76 | 23:00 | Mahasthangarh | 82 | 23:00 | SSM | 0 | 00:00
Charsaidpur | 38 | 15:00 | Manikganj | 93 | 21:00 | Sunamganj | 46 | 22:00
Chauddagram | 64 | 21:00 | Maniknagar | 68 | 13:00 | Sylhet | 136 | 21:00
Chhatak | 20 | 21:00 | Matarbari | 45 | 20:00 | Tangail | 260 | 21:00
Chowmuhani | 229 | 21:00 | Matuail | 68 | 11:00 | Thakurgaon | 95 | 21:00
Chuadanga | 119 | 21:00 | Millgate | 60 | 12:00 | TK | 31 | 23:00
Coxsbazar | 123 | 23:00 | Mirpur | 139 | 19:30 | Tongi | 133 | 13:00
Cumilla(N) | 157 | 21:00 | Mirsorai | N/A | N/A | Ullon | 135 | 13:00
Cumilla(S) | 170 | 19:00 | Mithapukur | 35 | 03:00 | Uttara | 85 | 19:30
Daudkandi | 151 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 24 | 18:30
Dhaka | 30 | 11:00 | Mogbazar | 118 | 14:00 | Zigatola | 46 | 19:00
Dhamrai | 114 | 19:30 | Mongla | 44 | 15:00
Dhanmondi | 183 | 13:00 | Motijheel | 34 | 14:00
Dohazari | 88 | 21:00 | Munshiganj | 104 | 21:00
Faridpur | 157 | 21:00 | Mymensingh | 241 | 19:00
Fatullah | 68 | 16:00 | Naogaon | 128 | 22:00
Fenchuganj | 46 | 21:00 | Narail | 53 | 19:30
Feni | 138 | 21:00 | Narinda | 75 | 13:00
Ghorashal | 79 | 18:00 | Narshingdi | 192 | 21:00
Goalpara | 30 | 21:00 | Natore | 156 | 21:00
Gollamari | 62 | 21:00 | Nawabganj | 59.8 | 21:00
Gopalganj | 107 | 21:00 | Netrakona | 115 | 00:00
GPH | 98 | 01:00 | New | 83.2 | 14:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 23:00 | 395 | 16:00 | Kaliakoir | 383 | 0.33333 | 374 | 0.41667
| Bheramara | 395 | 8:00 | 386 | 12:00 | Bhulta | 387 | 0.95833 | 368 | 0.41667
| Ashuganj(N) | 0 | #NUM! | 0 | #N/A | Gopalganj | 414 | 0.625 | 403 | 0.16667
| Payra | 418 | 18:30 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 237 | 7:00 | 230 | 14:00
| Ishurdi | 232 | 18:00 | 225 | 3:00 | Megnaghat | 228 | 3:00 | 222 | 15:00
| Ashuganj | 240 | 18:30 | 232 | 16:00 | Fenchuganj | 240 | 2:00 | 236 | 17:00
| Serajganj | 233 | 18:00 | 229 | 20:00 | Siddhirganj | 224 | 4:00 | 217 | 10:00
| Baghabari | 230 | 5:00 | 226 | 1:00 | Maniknagar | 222 | 4:00 | 215 | 10:00
| Barapukuria | 225 | 16:00 | 217 | 21:00 | Agargaon | 223 | 8:00 | 213 | 15:00
| Bogra | 227 | 13:00 | 217 | 21:00 | Barisal | 239 | 8:00 | 231 | 21:00
| Rajshahi | 224 | 18:00 | 212 | 4:00 | Bhola 225 MW | 242 | 10:00 | 231 | 21:00
| Khulna South | 236 | 9:00 | 229 | 22:00 | AKSML
| Rampura | 221 | 3:00 | 214 | 10:00 | BSRM | 233 | 5:00 | 225 | 10:00
| Haripur | 221 | 4:00 | 216 | 10:00 | Bibiyana | 240 | 8:00 | 232 | 10:00
| Hasnabad | 223 | 18:30 | 212 | 10:00 | Bhulta | 225 | 23:00 | 216 | 12:00
| Shyampur | 223 | 18:30 | 214 | 10:00 | Ashuganj (S) | 235 | 2:00 | 228 | 16:00
| Aminbazar | 223 | 1:00 | 215 | 2:00 | Kaliakoir | 224 | 2:00 | 216 | 14:00
| Tongi | 230 | 4:00 | 215 | 10:00 | GPH | 236 | 5:00 | 229 | 10:00
| Comilla (N) | 229 | 22:00 | 223 | 10:00 | Jhenaidah | 226 | 8:00 | 218 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 22:00 | 129 | 09:00 | Manikganj | 133 | 05:00 | 124 | 14:00
| Agargaon | 138 | 03:00 | 131 | 10:00 | Maniknagar | 129 | 06:00 | 123 | 12:00
| Agrabad | 134 | 20:00 | 129 | 14:00 | Matarbari | 123 | 08:00 | 114 | 02:00
| AKS | 134 | 08:00 | 130 | 10:00 | Matuail | 133 | 18:30 | 127 | 10:00
| Aminbazar | 138 | 05:00 | 130 | 15:00 | Millgate | 137 | 01:00 | 128 | 15:00
| Amnura | 133 | 17:00 | 121 | 04:00 | Mirpur | 138 | 03:00 | 127 | 15:00
| Ashuganj | 139 | 08:00 | 134 | 00:00 | Mithapukur | 131 | 13:00 | 120 | 21:00
| Bagerhat | 132 | 00:00 | 126 | 22:00 | Modern | 135 | 18:00 | 130 | 10:00
| Bakulia | 135 | 08:00 | 130 | 15:00 | Mogbazar | 136 | 02:00 | 130 | 09:00
| Banani | 137 | 03:00 | 128 | 17:00 | Mongla | 133 | 08:00 | 127 | 23:00
| Bangabhaban | 128 | 01:00 | 123 | 12:00 | Motijheel | 128 | 01:00 | 123 | 12:00
| Barapukuria | 130 | 16:00 | 123 | 21:00 | Munshiganj | 136 | 01:00 | 128 | 10:00
| Barguna | 140 | 18:30 | 131 | 15:00 | Mymensingh | 128 | 09:00 | 114 | 01:00
| Barishal | 142 | 19:30 | 129 | 15:00 | Naogaon | 123 | 13:00 | 110 | 21:00
| Barishal | 139 | 08:00 | 133 | 21:00 | Narail | 136 | 08:00 | 126 | 22:00
| Baroaulia | 136 | 06:00 | 132 | 08:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 17:00 | 126 | 00:00 | Narshingdi | 130 | 18:30 | 123 | 15:00
| Bashundhara | 137 | 02:00 | 128 | 15:00 | Natore | 134 | 18:00 | 127 | 03:00
| BashundharaCement | 134 | 01:00 | 129 | 09:00 | Nawabganj | 137 | 18:30 | 129 | 12:00
| Beanibazar | 137 | 00:00 | 129 | 22:00 | Netrakona | 127 | 09:00 | 113 | 17:00
| Benapole | 133 | 08:00 | 127 | 22:00 | New | 136 | 00:00 | 128 | 14:00
| Bhaluka | 126 | 09:00 | 110 | 00:00 | Niamatpur | 119 | 18:00 | 102 | 21:00
| Bhandaria | 138 | 09:00 | 126 | 22:00 | Noapara | 136 | 08:00 | 131 | 23:00
| Bhangura | 133 | 18:00 | 128 | 00:00 | Pabna | 132 | 18:00 | 127 | 21:00
| Bheramara | 135 | 18:00 | 132 | 00:00 | Palashbari | 128 | 13:00 | 117 | 15:00
| Bheramara(GK) | 138 | 18:00 | 135 | 00:00 | Panchagarh | 133 | 04:00 | 113 | 10:00
| Bhulta | 127 | 03:00 | 123 | 10:00 | Patuakhali | 138 | 19:00 | 133 | 15:00
| Bog-Sherpur | 130 | 13:00 | 122 | 21:00 | PHP | 134 | 17:00 | 125 | 00:00
| Bogura | 132 | 18:00 | 124 | 21:00 | Purbachal | 138 | 03:00 | 127 | 15:00
| Bogura | 132 | 13:00 | 124 | 21:00 | Purbasadipur | 130 | 01:00 | 117 | 10:00
| Brahmanbaria | 134 | 08:00 | 128 | 00:00 | Rahim | 133 | 18:30 | 128 | 10:00
| Cantonment | 137 | 03:00 | 129 | 15:00 | Rajbari | 135 | 08:00 | 129 | 21:00
| Chandpur | 142 | 16:00 | 132 | 07:00 | Rajendrapur | 136 | 04:00 | 128 | 11:00
| Chandraghona | 137 | 08:00 | 132 | 10:00 | Rajshahi | 135 | 18:00 | 125 | 03:00
| Chapai | 134 | 18:00 | 126 | 03:00 | Rajshahi | 136 | 18:00 | 128 | 04:00
| Charsaidpur | 136 | 02:00 | 128 | 10:00 | Ramganj | 137 | 17:00 | 123 | 02:00
| Chauddagram | 134 | 17:00 | 126 | 00:00 | Rampur | 135 | 20:00 | 130 | 15:00
| Chhatak | 135 | 00:00 | 129 | 23:00 | Rampura | 135 | 00:00 | 129 | 10:00
| Chowmuhani | 135 | 16:00 | 123 | 00:00 | Rangamati | 136 | 18:30 | 131 | 12:00
| Chuadanga | 132 | 08:00 | 121 | 21:00 | Rangpur | 130 | 13:00 | 117 | 21:00
| Coxsbazar | 121 | 13:00 | 111 | 00:00 | Ruppur | 136 | 06:00 | 130 | 00:00
| Cumilla(N) | 135 | 17:00 | 131 | 00:00 | Saidpur | 130 | 03:00 | 117 | 21:00
| Cumilla(S) | 135 | 13:00 | 125 | 18:00 | Satkhira | 134 | 09:00 | 126 | 22:00
| Daudkandi | 136 | 19:00 | 127 | 00:00 | Satmasjid | 137 | 02:00 | 130 | 15:00
| Dhaka | 135 | 23:00 | 129 | 09:00 | Savar | 139 | 02:00 | 128 | 15:00
| Dhamrai | 133 | 03:00 | 128 | 15:00 | Shahjadpur | 134 | 01:00 | 130 | 20:00
| Dhanmondi | 133 | 05:00 | 128 | 10:00 | Shahjibazar | 137 | 08:00 | 132 | 19:30
| Dohazari | 130 | 08:00 | 124 | 00:00 | Shahmirpur | 134 | 20:00 | 130 | 12:00
| Faridpur | 135 | 09:00 | 129 | 21:00 | Shariatpur | 137 | 10:00 | 130 | 21:00
| Fatullah | 133 | 18:30 | 126 | 10:00 | Sherpur | 128 | 10:00 | 113 | 02:00
| Fenchuganj | 138 | 06:00 | 134 | 23:00 | Shikalbaha | 135 | 08:00 | 131 | 00:00
| Feni | 135 | 16:00 | 128 | 00:00 | Shikalbaha | 135 | 09:00 | 131 | 00:00
| Ghorashal | 137 | 01:00 | 135 | 00:00 | Shitalakhya | 135 | 01:00 | 128 | 10:00
| Goalpara | 137 | 18:30 | 133 | 04:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 136 | 09:00 | 131 | 04:00 | Shyampur | 133 | 19:30 | 126 | 10:00
| Gopalganj | 140 | 18:30 | 133 | 04:00 | Shyampur | 133 | 23:00 | 126 | 10:00
| Gopalganj_I | 140 | 08:00 | 136 | 00:00 | Siddhirganj | 134 | 18:30 | 127 | 10:00
| Gulshan | 135 | 23:00 | 128 | 09:00 | Sirajganj | 130 | 18:00 | 123 | 21:00
| Halishahar | 135 | 22:00 | 128 | 11:00 | Sonargaon | 135 | 18:30 | 128 | 10:00
| Haripur | 133 | 19:30 | 128 | 10:00 | Sreemongol | 138 | 08:00 | 134 | 00:00
| HaripurSBU | 134 | 23:00 | 128 | 10:00 | Srinagar | 137 | 06:00 | 130 | 12:00
| Hasnabad | 135 | 03:00 | 129 | 10:00 | SSM | 138 | 02:00 | 132 | 11:00
| Hathazari | 138 | 07:00 | 133 | 10:00 | Sunamganj | 135 | 06:00 | 127 | 22:00
| Ishurdi | 134 | 06:00 | 131 | 03:00 | Sylhet | 135 | 00:00 | 132 | 19:00
| Jaldhaka | 128 | 13:00 | 116 | 21:00 | Tangail | 129 | 09:00 | 122 | 16:00
| Jamalpur | 130 | 11:00 | 116 | 02:00 | Thakurgaon | 133 | 13:00 | 113 | 11:00
| Jashore | 134 | 08:00 | 128 | 23:00 | TK | 137 | 18:30 | 131 | 10:00
| Jhenaidah | 137 | 07:00 | 131 | 22:00 | Tongi | 138 | 04:00 | 129 | 16:00
| Jhenaidah | 138 | 08:00 | 131 | 00:00 | Ullon | 136 | 23:00 | 127 | 10:00
| Joydebpur | 138 | 18:30 | 132 | 10:00 | Uttara | 136 | 04:00 | 128 | 15:00
| Joypurhat | 124 | 13:00 | 107 | 21:00 | UttaraNew | 136 | 02:00 | 128 | 15:00
| Juldah | 136 | 08:00 | 130 | 10:00 | Zigatola | 137 | 05:00 | 130 | 11:00
| Kabirpur | 137 | 03:00 | 128 | 15:00
| Kachua | 137 | 16:00 | 130 | 00:00
| Kaliakoir | 133 | 15:00 | 131 | 15:00
| Kallyanpur | 139 | 03:00 | 130 | 15:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 137 | 18:30 | 130 | 12:00
| Kaptai | 134 | 13:00 | 132 | 01:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 184 | 9420 | 4411 | 13831 |  |  |  | QF-LDC-11
0:30 | 180 | 9031 | 4329.5 | 13360.5 | Date: | 2022-04-16
1:00 | 176 | 8642 | 4248 | 12890
1:30 | 188 | 8555 | 4174 | 12729
2:00 | 200 | 8468 | 4100 | 12568
2:30 | 252 | 8514.5 | 4121.5 | 12636 | [5 empty] | Gen. at Eve. Peak | 14782 | 14782 MW (21:00 )
3:00 | 304 | 8561 | 4143 | 12704 | [6 empty] | 21:00
3:30 | 267 | 8538.5 | 4047 | 12585.5 | [5 empty] | Gen. at Day Peak | 11701 | 11701 MW (12:00 )
4:00 | 230 | 8516 | 3951 | 12467 | [6 empty] | 12:00
4:30 | 164 | 8331.5 | 3807 | 12138.5 | [5 empty] | Highest Generation | 14782
5:00 | 98 | 8147 | 3663 | 11810 | [6 empty] | 21:00
5:30 | 116 | 7877 | 3545 | 11422
6:00 | 134 | 7607 | 3427 | 11034
6:30 | 105 | 7478 | 3434 | 10912
7:00 | 76 | 7349 | 3441 | 10790
7:30 | 106 | 7370.5 | 3462 | 10832.5
8:00 | 136 | 7392 | 3483 | 10875
8:30 | 192 | 7351 | 3496.5 | 10847.5
9:00 | 248 | 7310 | 3510 | 10820
9:30 | 216 | 7489 | 3538 | 11027
10:00 | 184 | 7668 | 3566 | 11234
10:30 | 213 | 7728.5 | 3544 | 11272.5
11:00 | 242 | 7789 | 3522 | 11311
11:30 | 244 | 7868.5 | 3637.5 | 11506
12:00 | 246 | 7948 | 3753 | 11701
12:30 | 184 | 8090 | 3846.5 | 11936.5
13:00 | 122 | 8232 | 3940 | 12172
13:30 | 120 | 8403.5 | 3995 | 12398.5
14:00 | 118 | 8575 | 4050 | 12625
14:30 | 193 | 8653.5 | 4175 | 12828.5
15:00 | 268 | 8732 | 4300 | 13032
15:30 | 342 | 8623.5 | 4317.5 | 12941
16:00 | 416 | 8515 | 4335 | 12850
16:30 | 403 | 8455 | 4342 | 12797
17:00 | 390 | 8395 | 4349 | 12744
17:30 | 286 | 8496 | 4255 | 12751
18:00 | 182 | 8597 | 4161 | 12758
18:30 | 141 | 9028 | 4405 | 13433
19:00 | 100 | 9459 | 4649 | 14108
19:30 | 10 | 9609 | 4810 | 14419
20:00 | 10 | 9576 | 4874 | 14450 |  |  |  | Executive Engineer
20:30 | 64 | 9714.5 | 4901.5 | 14616 |  |  |  | Network Operation Division
21:00 | 118 | 9853 | 4929 | 14782
21:30 | 155 | 9818 | 4859.5 | 14677.5
22:00 | 192 | 9783 | 4790 | 14573 |  |  |  |  | Page 6 of 7
22:30 | 170 | 9732 | 4714.5 | 14446.5
23:00 | 148 | 9681 | 4639 | 14320
23:30 | 166 | 9550.5 | 4525 | 14075.5
24:00 | 184 | 9420 | 4411 | 13831
14782 MW (21:00 )
11701 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-16 |  | Energy |  | 303686727
[13 empty] | 2022-04-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4362 | 924 | 2270 | 308 | 4212 | 843 | 68 | 200 | 478 | 166 | 0 | 0
0:30 | 4309.5 | 923.5 | 2229 | 154 | 4093.5 | 894 | 67.5 | 160 | 374.5 | 155 | 0 | 0 | Date: | 2022-04-16
1:00 | 4257 | 923 | 2188 | 0 | 3975 | 945 | 67 | 120 | 271 | 144 | 0 | 0
1:30 | 4220 | 923 | 2146.5 | 0 | 3954 | 943.5 | 66.5 | 120 | 210.5 | 145 | 0 | 0 | [8 empty] | Total Energy | 303.6867 | Total Energy Gen 303.687 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 303.687 MKWHr
2:00 | 4183 | 923 | 2105 | 0 | 3933 | 942 | 66 | 120 | 150 | 146 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4202.5 | 923 | 2138 | 0 | 3948 | 943 | 65.5 | 120 | 149 | 147 | 0 | 0 | [8 empty] | Energy Requirement | 303.6867
3:00 | 4222 | 923 | 2171 | 0 | 3963 | 944 | 65 | 120 | 148 | 148 | 0 | 0
3:30 | 4249 | 923 | 2178.5 | 0 | 3835.5 | 943.5 | 65 | 120 | 123 | 148 | 0 | 0 | [6 empty] | Shortage
4:00 | 4276 | 923 | 2186 | 0 | 3708 | 943 | 65 | 120 | 98 | 148 | 0 | 0
4:30 | 4292.5 | 923.5 | 2178.5 | 0 | 3400.5 | 944 | 65.5 | 120 | 73 | 141 | 0 | 0
5:00 | 4309 | 924 | 2171 | 0 | 3093 | 945 | 66 | 120 | 48 | 134 | 0 | 0
5:30 | 4259 | 923.5 | 2146.5 | 0 | 2820.5 | 915 | 66 | 120 | 40 | 130 | 1.5 | 0
6:00 | 4209 | 923 | 2122 | 0 | 2548 | 885 | 66 | 120 | 32 | 126 | 3 | 0
6:30 | 4210.5 | 923.5 | 2119.5 | 0 | 2413.5 | 885.5 | 66.5 | 120 | 32 | 128 | 13 | 0 |  |  |  |  | Coal
7:00 | 4212 | 924 | 2117 | 0 | 2279 | 886 | 67 | 120 | 32 | 130 | 23 | 0
7:30 | 4183 | 923.5 | 2093 | 0 | 2337 | 885.5 | 67 | 120 | 56 | 130 | 37.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4154 | 923 | 2069 | 0 | 2395 | 885 | 67 | 120 | 80 | 130 | 52 | 0
8:30 | 4123.5 | 923.5 | 2020.5 | 0 | 2439.5 | 865 | 67 | 120 | 80 | 131 | 77.5 | 0
9:00 | 4093 | 924 | 1972 | 0 | 2484 | 845 | 67 | 120 | 80 | 132 | 103 | 0
9:30 | 4203.5 | 923.5 | 2050 | 0 | 2510.5 | 843.5 | 67.5 | 120 | 80 | 135 | 93.5 | 0
10:00 | 4314 | 923 | 2128 | 0 | 2537 | 842 | 68 | 120 | 80 | 138 | 84 | 0
10:30 | 4276.5 | 923 | 2079.5 | 0 | 2596.5 | 852 | 68.5 | 120 | 80 | 142 | 134.5 | 0
11:00 | 4239 | 923 | 2031 | 0 | 2656 | 862 | 69 | 120 | 80 | 146 | 185 | 0
11:30 | 4256.5 | 923 | 2063.5 | 0 | 2803 | 868.5 | 68.5 | 120 | 90 | 146 | 167 | 0
12:00 | 4274 | 923 | 2096 | 0 | 2950 | 875 | 68 | 120 | 100 | 146 | 149 | 0
12:30 | 4244.5 | 923 | 2089 | 0 | 3180 | 874 | 67 | 120 | 131.5 | 147 | 160.5 | 0
13:00 | 4215 | 923 | 2082 | 0 | 3410 | 873 | 66 | 120 | 163 | 148 | 172 | 0
13:30 | 4215 | 923 | 2082 | 0 | 3410 | 873 | 66 | 120 | 163 | 148 | 172 | 0
14:00 | 4215 | 923 | 2082 | 0 | 3410 | 873 | 66 | 120 | 163 | 148 | 172 | 0
14:30 | 4239 | 923 | 2118.5 | 134 | 3539 | 909 | 65 | 155 | 225.5 | 153 | 141 | 0
15:00 | 4263 | 923 | 2155 | 268 | 3668 | 945 | 64 | 190 | 288 | 158 | 110 | 0
15:30 | 4079.5 | 923 | 2141 | 369.5 | 3671 | 918.5 | 64 | 195 | 331 | 156 | 92.5 | 0
16:00 | 3896 | 923 | 2127 | 471 | 3674 | 892 | 64 | 200 | 374 | 154 | 75 | 0
16:30 | 3760 | 923 | 2223 | 260.5 | 3774 | 908 | 64.5 | 200 | 412 | 150 | 54 | 0
17:00 | 3760 | 923 | 2319 | 50 | 3874 | 924 | 65 | 200 | 450 | 146 | 33 | 0
17:30 | 3781 | 923.5 | 2217.5 | 25 | 3968 | 934 | 65 | 200 | 464 | 154 | 19 | 0
18:00 | 3802 | 924 | 2116 | 0 | 4062 | 944 | 65 | 200 | 478 | 162 | 5 | 0
18:30 | 3854 | 923.5 | 2247.5 | 293 | 4226.5 | 944 | 65 | 200 | 511 | 166 | 2.5 | 0
19:00 | 3906 | 923 | 2379 | 586 | 4391 | 944 | 65 | 200 | 544 | 170 | 0 | 0
19:30 | 3993 | 922 | 2296 | 851 | 4436 | 944 | 65 | 200 | 548 | 164 | 0 | 0
20:00 | 4032 | 923 | 2284 | 836 | 4451 | 945 | 66 | 200 | 545 | 168 | 0 | 0
20:30 | 4104.5 | 923.5 | 2287.5 | 902.5 | 4461.5 | 945.5 | 83.5 | 200 | 538.5 | 169 | 0 | 0
21:00 | 4177 | 924 | 2291 | 969 | 4472 | 946 | 101 | 200 | 532 | 170 | 0 | 0
21:30 | 4215.5 | 923.5 | 2285 | 818 | 4484.5 | 945.5 | 101.5 | 200 | 535 | 169 | 0 | 0
22:00 | 4254 | 923 | 2279 | 667 | 4497 | 945 | 102 | 200 | 538 | 168 | 0 | 0
22:30 | 4258.5 | 923.5 | 2269.5 | 582.5 | 4476 | 944.5 | 85 | 200 | 538 | 169 | 0 | 0
23:00 | 4263 | 924 | 2260 | 498 | 4455 | 944 | 68 | 200 | 538 | 170 | 0 | 0
23:30 | 4312.5 | 924 | 2265 | 403 | 4333.5 | 893.5 | 68 | 200 | 508 | 168 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 4362 | 924 | 2270 | 308 | 4212 | 843 | 68 | 200 | 478 | 166 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 303.687 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 303.687 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 67 | 66 | 65 | 65 | 66 | 66 | 67 | 67 | 67 | 68 | 69 | 68 | 66 | 65 | 64 | 64 | 65 | 65 |  | 65 | 65 | 66 | 66 | 67 | 68 | 68 | 1594287
2 | Karnaphuli Hydro PP Unit-4 & 5 | [21 empty] | 0 | 35 | 35 | 0 |  | 68000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 0 | 15 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 510174
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 7 | 12 | 15 | 18 | 17 | 18 | 15 | 11 | 7 | 2 | 0 | [8 empty] | 118125
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 210 | 202 | 203 | 215 | 204 | 221 | 204 | 204 | 203 | 203 | 203 | 213 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4922134
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 51 |  | 265380
12 | Hathazari 100 MW peaking PP | 25 | [12 empty] | 34 | 34 | 25 | 42 | 43 |  | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 434544
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 34 | 34 | 34 | 34 | 41 | 51 | 51 | 51 | 55 | 86 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1984682
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 0 |  | 75 | 200 | 200 | 200 | 150 | 100 | 30 | 777408
14 | Titas 50 MW Peaking PP | [13 empty] | 0 | 13 | 48 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 434952
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 329 | 300 | 336 | 336 | 337 | 280 | 280 | 280 | 280 | 325 | 326 | 322 | 321 | 325 | 325 | 325 | 325 | 300 |  | 325 | 325 | 325 | 325 | 326 | 325 | 325 | 7618231
18 | Kodda 300 MW PP Unit-2 (Summit) | 265 | 278 | 281 | 268 | 145 | 141 | 45 | 48 | 107 | 117 | 122 | 205 | 243 | 265 | 263 | 263 | 247 | 263 |  | 263 | 265 | 263 | 263 | 275 | 280 | 280 | 5221416
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 50 | 185 | 185 |  | 185 | 102 | 63 | 63 | 63 | 45 | 45 | 1304727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 231 | 231 | 231 | 232 | 231 |  | 231 | 230 | 231 | 232 | 232 | 232 | 232 | 5643000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 250 | 250 | 260 |  | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 6402200
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 25 | 28 | 25 | 28 |  | 28 | 28 | 28 | 25 | 25 | 28 | 28 | 625896
33 | Ashuganj 225 MW CCPP | 187 | 194 | 195 | 201 | 198 | 198 | 188 | 174 | 183 | 198 | 203 | 212 | 214 | 211 | 211 | 213 | 212 | 208 |  | 173 | 193 | 192 | 214 | 209 | 182 | 183 | 4784000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 305 | 305 | 330 | 305 | 305 | 330 | 305 | 330 | 305 | 305 | 310 | 0 | 0 | 90 |  | 95 | 95 | 125 | 175 | 245 | 280 | 280 | 6018000
| Ashuganj 450 MW CCPP(North) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 45 | 45 | 45 | 45 | 45 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 57 | 55 | 56 | 53 | 54 | 55 |  | 54 | 54 | 55 | 56 | 55 | 55 | 56 | 1294080
36 | Chandpur 150 MW CCPP | [21 empty] | 0 | 91 | 90 | 90 | 91 | 327370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 360 | 360 | 399 | 399 | 392 | 376 | 377 | 351 | 381 | 401 | 397 | 397 | 393 | 402 | 401 | 400 | 357 |  | 375 | 400 | 399 | 399 | 399 | 399 | 398 | 9487430
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4922000
41 | Haripur 360MW CCPP(HPL) | 333 | 292 | 333 | 333 | 333 | 333 | 282 | 281 | 282 | 312 | 313 | 260 | 272 | 323 | 312 | 312 | 319 | 251 |  | 322 | 330 | 329 | 329 | 329 | 329 | 329 | 7400000
42 | RPCL 210MW CCPP | 195 | 196 | 197 | 202 | 212 | 212 | 210 | 211 | 200 | 199 | 180 | 166 | 161 | 150 | 150 | 142 | 135 | 114 |  | 115 | 124 | 144 | 144 | 154 | 139 | 139 | 3977280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 4 | 11 | 19 | 24 | 34 | 11 | 32 | 26 | 25 | 11 | 7 | 1 |  | 0 | [6 empty] | 223720
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 968640
46 | Shajibazar 330 MW CCPP | 159 | 160 | 159 | 160 | 159 | 159 | 159 | 157 | 159 | 157 | 158 | 154 | 157 | 153 | 153 | 110 | 0 | 108 |  | 108 | 111 | 110 | 116 | 126 | 160 | 268 | 3283000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 62 |  | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 1377888
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 86 | 86 | 84 | 84 | 84 | 84 | 83 | 83 | 85 | 84 | 84 | 84 | 84 | 84 |  | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 2034240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 191 | 191 | 191 | 191 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 219 | 192 | 192 | 192 | 192 | 192 | 192 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4923530
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 16 | 16 | 647580
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234048
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 277200
56 | Shahjahanulla 25 MW PP | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 23 |  | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 487464
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 285 | 285 | 280 | 265 | 295 | 290 | 275 | 300 | 290 | 285 | 280 | 300 | 300 | 290 | 280 | 280 |  | 290 | 285 | 290 | 290 | 285 | 290 | 280 | 7089500
| Bibiyana South 400 MW | 401 | 401 | 401 | 401 | 400 | 401 | 401 | 401 | 340 | 397 | 396 | 395 | 400 | 394 | 391 | 401 | 397 | 350 |  | 388 | 400 | 401 | 400 | 401 | 401 | 401 | 9407700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1191000
59 | Tangail Palli Power Gen 22 MW | 22 | 16 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 3 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501600
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 20 | 19 | 19 | 19 | 472428
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 440172
63 | Impoprt (Tripura) | 144 | 146 | 148 | 148 | 134 | 126 | 130 | 130 | 132 | 138 | 146 | 146 | 148 | 152 | 158 | 154 | 146 | 162 |  | 170 | 164 | 168 | 170 | 168 | 170 | 166 | 3520320
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 42 | 42 | 0 | 0 | 0 | 0 | 3 | 2 | 2 | 4 | 2 | 2 | 2 | 4 | 20 |  | 22 | 20 | 30 | 30 | 32 | 33 | 33 | 446880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 0 | 16 | 16 | 18 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 448020
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 5 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 24 | 25 | 32 | 32 | 32 | 32 | 25 |  | 25 | 30 | 30 | 33 | 33 | 33 | 33 | 761900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 20 | 476470
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 27 | 27 | 27 | 27 |  | 20 | 27 | 27 | 27 | 28 | 28 | 28 | 626220
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 771480
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754300
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 95 | 95 | 98 | 94 | 95 | 92 | 92 | 95 | 95 | 94 | 94 | 94 | 94 | 97 | 97 |  | 98 | 98 | 98 | 98 | 97 | 98 | 98 | 2249818
| Feni Lanka Power | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 52 | 52 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1467180
| Chowmuhani 113 MW | 18 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 31 | 111 | 113 |  | 114 | 114 | 115 | 115 | 115 | 107 | 34 | 1005480
| Manikgonj 162MW PP(MPGL) | 118 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 75 | 72 | 72 | 72 | 72 | 72 | 72 | 84 | 148 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 2764800
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 40 | 40 | 0 |  |  | 0 |  |  |  | 3 | 20 | 60 | 86 | 98 | 98 | 93 | 97 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1277760
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 24 | 24 | 34 | 50 | 44 | 42 | 42 | 49 | 49 | 45 | 41 | 49 | 49 |  | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 1105440
79 | Kodda 150MW PP | 133 | 98 | 98 | 98 | 48 | 32 | 32 | 80 | 80 | 80 | 80 | 80 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 2401440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 38 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 41 | 43 | 43 | 1030565
| Gazipur 100 MW PP | 72 | 72 | 72 | 72 | 35 | 35 | 45 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1658400
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 2 | 5 | 3 | 5 | 3 | 3 | 3 | 1 | 0 | [8 empty] | 29400
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1340849
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 95 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 79 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2431298
82 | Madanganj 102 PP(Summit) | 65 | 79 | 80 | 79 | 79 | 79 | 79 | 80 | 78 | 70 | 64 | 64 | 70 | 75 | 76 | 44 | 44 | 50 |  | 73 | 73 | 76 | 76 | 76 | 76 | 79 | 1756128
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 145 | 140 | 125 | 140 | 132 | 130 | 150 | 120 | 150 | 150 | 120 | 140 | 120 | 140 | 135 | 130 | 145 | 140 |  | 150 | 140 | 150 | 150 | 145 | 145 | 140 | 3380247
87 | Meghnaghat 100 MW(IEL) | 96 | 96 | 97 | 98 | 96 | 98 | 65 | 55 | 55 | 50 | 53 | 66 | 81 | 93 | 94 | 96 | 95 | 95 |  | 96 | 96 | 97 | 96 | 96 | 96 | 96 | 2074560
| Meghnaghat 104 MW PP (OPCL) | 72 | 72 | 72 | 72 | 55 | 34 | 17 | 17 | 51 | 53 | 54 | 72 | 73 | 72 | 72 | 72 | 78 | 92 |  | 93 | 92 | 92 | 92 | 92 | 92 | 92 | 1681920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 15 | 79056
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 40 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1147197
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 84 | 76 | 48 | 24 | 7 | 32 | 33 | 32 | 43 | 67 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1614096
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 27 | 0 | [10 empty] | 0 | 3 |  | 34 | 37 | 37 | 37 | 38 | 38 | 38 | 417600
96 | Chattogram 108 MW PP (ECPV) | 95 | 95 | 95 | 95 | 90 | 88 | 88 | 78 | 87 | 82 | 75 | 77 | 75 | 75 | 75 | 75 | 77 | 75 |  | 82 | 82 | 82 | 86 | 89 | 95 | 95 | 2029440
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 40 | 50 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1074421
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1223728
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3605564
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 12200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1222200
104 | Keranigonj 300 MW PP (APR) | [13 empty] | 56 | 180 | 205 | 0 | 0 |  | 295 | 303 | 223 | 301 | 189 | 150 | 70 | 1590864
105 | Bramhangoan 100 MW PP (Aggreko) | [13 empty] | 25 | 25 | 100 | 25 | 0 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 706772
106 | Mymensingh 200 MW PP (United) | 150 | 151 | 151 | 151 | 152 | 104 | 104 | 104 | 104 | 150 | 151 | 151 | 151 | 151 | 150 | 151 | 151 | 179 |  | 179 | 179 | 180 | 180 | 180 | 180 | 140 | 3554400
112 | Aurahati 100MW PP (Aggreko) | [13 empty] | 25 | 25 | 100 | 25 | 0 |  | 98 | 100 | 100 | 100 | 98 | 98 | 98 | 710229
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3608928
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2081280
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 155 | 120 | 85 | 85 | 34 | 34 | 34 | 36 | 118 | 169 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3705120
117 | Ashuganj 150MW PP (Midland) | 145 | 135 | 147 | 100 | 60 | 30 | 10 | 10 | 10 | 10 | 10 | 20 | 71 | 122 | 128 | 50 | 90 | 127 |  | 142 | 144 | 145 | 135 | 138 | 138 | 140 | 2264872
118 | Bibiyana-III 400 MW CCPP | 369 | 369 | 368 | 368 | 368 | 369 | 369 | 368 | 369 | 400 | 400 | 401 | 402 | 403 | 404 | 402 | 403 | 405 |  | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 9334000
| Jamalpur 115 MW PP (United) | 77 | 77 | 77 | 77 | 78 | 49 | 49 | 49 | 49 | 72 | 72 | 72 | 72 | 72 | 76 | 77 | 76 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 68 | 1914000
| Anwara 300 MW PP (United) | 264 | 265 | 265 | 268 | 268 | 272 | 267 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 283 | 285 | 290 | 290 | 6644073
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 40 | 40 | 40 | 40 | 40 | 90 | 100 | 100 | 90 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2106240
| Anlima Energy Ltd. | 92 | 92 | 95 | 112 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 112 | 113 | 112 | 98 | 97 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2620745
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 883440
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 8 | 9 | 0 | 31 | 21 | 29 | 28 | 18 | 13 | 5 | 1 |  | 0 | [6 empty] | 155846
| Chandpur 115(Doreen) | 101 | 102 | 102 | 102 | 101 | 101 | 101 | 101 | 101 | 101 | 96 | 82 | 86 | 83 | 83 | 99 | 101 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 2365440
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1305720
120 | Eastern Zone Total | 8642 | 8468 | 8561 | 8516 | 8147 | 7607 | 7349 | 7392 | 7310 | 7668 | 7789 | 7948 | 8232 | 8575 | 8732 | 8515 | 8395 | 8597 |  | 9459 | 9609 | 9576 | 9853 | 9783 | 9681 | 9420 | 204218652
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 47 | 16 | 16 | [9 empty] | 16 | 15 | 15 | 16 | 16 | 16 |  | 66 | 66 | 66 | 66 | 66 | 22 | 16 | 488640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [14 empty] | 0 | 4 | 8 | 34 |  | 44 | 35 | 35 | 36 | 36 | 36 | 36 | 229440
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 | 190 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3767040
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 53 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 61 | 72 | 72 | 78 | 94 | 76 |  | 91 | 94 | 94 | 94 | 94 | 94 | 94 | 1673280
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 11 | 20 | 53 | 37 | 87 | 86 | 76 | 66 | 44 | 35 | 16 | 2 | [8 empty] | 547920
131
132 | United Payra Power Ltd. | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 54 | 90 | 100 | 134 | 134 | 150 | 116 | 117600
133 | Bhola Nutan Biddut BD LTD (GAS) | 217 | 217 | 216 | 216 | 215 | 214 | 219 | 180 | 130 | 220 | 120 | 220 | 213 | 220 | 217 | 210 | 214 | 162 |  | 211 | 217 | 216 | 219 | 219 | 219 | 220 | 4954200
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 80 | 80 | 80 | 80 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 |  | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 1482624
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 66 | 67 | 67 | 67 | 67 | 66 | 67 | 65 | 64 | 65 | 65 | 65 | 64 | 64 | 66 | 65 | 65 |  | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 1562000
140 | Bhola 33 MW PP (Venture) | 37 | 36 | 36 | 36 | 34 | 30 | 25 | 24 | 21 | 8 | 18 | 22 | 25 | 26 | 23 | 25 | 24 | 27 |  | 36 | 37 | 38 | 40 | 40 | 40 | 39 | 714490
141 | Noapara 100 MW PP (Bangla Trac) | [12 empty] | 0 | 4 | 20 | 20 | 0 |  |  | 3 | 100 | 80 | 100 |  |  | 0 | 300480
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 223125
143 | Gopalganj 100 MW Peaking PP | [12 empty] | 15 | 25 | 27 | 26 | 21 | 20 |  | 20 | 5 | 5 | 0 |  |  |  | 151168
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 67 | 67 | 67 |  |  |  |  | 8 | 32 | 32 | 15 | 15 | 15 | 37 | 50 | 50 | 50 | 50 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1127520
146 | Bheramara HVDC | 923 | 923 | 923 | 923 | 924 | 923 | 924 | 923 | 924 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 924 |  | 923 | 922 | 923 | 924 | 923 | 924 | 924 | 22336727
147 | Bheramara 410 MW CCPP | 390 | 390 | 395 | 403 | 398 | 360 | 360 | 360 | 390 | 390 | 360 | 360 | 350 | 355 | 350 | 350 | 340 | 300 |  | 340 | 335 | 330 | 320 | 315 | 305 | 300 | 8810496
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 560 | 560 | 560 | 520 | 520 | 540 | 550 | 550 | 550 | 622 | 622 | 622 | 622 |  | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 15286400
149
150 | Barapukuria TPP Unit-1 | 73 | 71 | 72 | 72 | 73 | 75 | 76 | 75 | 75 | 72 | 72 | 75 | 73 | 73 | 73 | 70 | 72 | 72 |  | 72 | 72 | 73 | 74 | 73 | 73 | 72 | 1756364
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 249 | 250 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 214 | 250 | 200 | 230 | 250 |  | 250 | 250 | 250 | 250 | 250 | 249 | 149 | 5965000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 3 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 373875
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 3 | 2 | 4 | 5 | 4 | 5 | 3 | 2 | 0 | 0 | [8 empty] | 30720
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 166 | 144 | 141 | 136 | 136 | 136 | 136 | 133 | 133 | 133 | 134 | 133 | 145 | 200 | 204 | 202 | 205 | 205 |  | 205 | 206 | 200 | 190 | 187 | 176 | 172 | 4210245
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 376 | 345 | 386 | 385 | 385 | 385 | 387 | 414 | 414 | 416 | 414 | 414 | 415 | 408 | 414 | 414 | 414 | 305 |  | 414 | 416 | 418 | 419 | 417 | 419 | 420 | 9556290
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 4 | 5 | 29 | 29 | 28 |  | 28 | 28 | 28 | 31 | 31 | 31 | 29 | 265315
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 487920
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212400
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [13 empty] | 0 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 316820
167 | Katakhali 50 MW Peaking PP | 25 | [12 empty] | 8 | 21 | 12 | 24 | 24 |  | 24 | 40 | 40 | 32 | 32 | 32 | 25 | 244028
168 | Santahar 50 MW Peaking PP | [11 empty] | 20 | 33 | 33 | 32 | 32 | 32 | 33 |  | 34 | 30 | 26 | 26 | 32 | 32 | 32 | 375860
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 20 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 850560
170 | Chapainawabganj 100 MW Peaking PP | 88 | 52 | 50 | [10 empty] | 16 | 38 | 40 | 87 | 88 |  | 93 | 92 | 92 | 88 | 88 | 88 | 88 | 937392
171 | Baghabari 200 MW PP (Paramount) | [13 empty] | 1 | 18 | 46 | 0 |  |  | 15 | 48 | 133 | 168 | 130 | 50 | 10 | 675552
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 94 | 108 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2709696
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2445504
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
176 | Rangpur 113 MW PP (Confidence) | 109 | 109 | 109 | 109 | 53 | 34 | 34 | 39 | 70 | 70 | 79 | 110 | 109 | 109 | 109 | 108 | 108 | 93 |  | 108 | 109 | 109 | 109 | 109 | 109 | 109 | 2277398
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 3 | 3 | 4 | 4 | 6 | 6 | 4 | 3 | 2 | 1 |  | 0 | [6 empty] | 41254
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 45 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 110 | 110 | 109 | 110 | 110 | 110 |  | 111 | 110 | 110 | 110 | 115 | 115 | 115 | 1962732
178