## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-19 | Tuesday
|  |  | Date (day): | 2022-04-19 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14421.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14933 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-18 | 2022-04-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 234 | 233 | 235 | 235
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 100 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 383 | 397 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 331 | 320 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 380 | 380 | 70 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 92 | 91 | 93 | 93 |  | 7 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 130 | 140 | 150 | 185 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 77 | 78 | 80 | 80 |  | 22 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 48 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuelshortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 18 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 90 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 308 | 330 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 76 | 84 | 84 | 84 |  | 18 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 52 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 278 | 270 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 304 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 99 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 104 | 92 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 37 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5998 | 3666 | 4368 | 4439 | 4471 | 931 | 589
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 16 | 37 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 66 | 64 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 204 | 215 | 215
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 48 | 50 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 35 | 80 | 22 | 90
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 88 | 88 | 88 |  | 12 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 5 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 48 | 96 | 95 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 281 | 295 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 108 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1191 | 1493 | 1468 | 1536 | 180 | 646
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 136 | 120 | 190 | 200 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 265 | 290 | 290 | 70 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 205 | 210 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 30 | 30 | 15 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 20 | 20 | 35 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 125 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 49 | 46 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 31 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 42 | 42 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 62 | 62 | 60 | 62 |  | 52 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 38 | 8 | 50 | 63 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 35 | 35 |  |  | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 55 | 101 | 101 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1505 | 1841 | 1655 | 1843 | 993 | 138
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 106 | 120 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 163 | 180 | 190 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 98 | 98 | 98 |  | 17 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 395 | 426 | 501.6 | 450 | 92 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 40 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 265 | 158 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 22 | 22 | 22 | 29 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 55 | 55 | 55
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 140 | 140 | 140 |  | 91 | ST Under maint.
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 15 | 15 | 15 | 35 |  | Gas shortage
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 22 | 22 | 22
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 310 | 330 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 376 | 402 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 391 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1961 | 1834 | 1835 | 1855 | 299 | 310
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 922 | 922 | 940 | 940
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 49 | 66 | 115
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 22 | 33 | 30 | 36 |  | 18 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 125 | 200 | 200 | 200
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 63 | 0 | 63 |  | 46 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 290 | 330 | 330 | 80 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 32 | 32 |  | 8 | Engine problem
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 76 | 75 | 76 | 94 |  | 11 | Engine problem
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 105 | 105 | 105
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1659 | 1869 | 1979 | 2015 | 80 | 83
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 110 | 50 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 23 | 40 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 87 | 66 | 67 | 127 |  | Gas shortage & GT-1 S/D
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 |  | 1244 | Under maint
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 212 | 218 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 116 | 57 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 480 | 512 | 519 | 580 | 127 | 1244
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 29 | 27 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 34 | 34 | 34 |  | 16 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 17 | 40 | 30 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 3 | 198 | 200 | 200 | 10 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 213 | 200 | 210 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 415 | 400 | 414 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 35 | 30 | 32 |  | 18 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 43 | 43 |  | 9 | Engine problem
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 53 | 92 | 92 | 92 |  | 12 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 171 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 997 | 1560 | 1468 | 1607 | 401 | 155
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 76 | 74 | 74
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 249 | 250 | 250
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 77 | 110 | 110 | 110
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 60 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 466 | 567 | 557 | 576 | 0 | 95
|  | Total |  |  |  |  | 22348 | 21734 | 12320 | 14470 | 14421.6 | 14933 | 3103 | 3268
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11912.0862 | 13990.9 | 13944.1025 | 14438.5701
| A. |  | 2022-04-18 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 14509 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11358 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14470 | MW
| 3 | Day peak Generation : |  |  | 12320 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13990.9 | MW
| 4 | Evening peak Generation : |  |  | 14470 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 314.754 | MKWHr | By Solar | 1.2549 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 154.2913 | MKWHr |  | By Oil: | 123.2449 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 8.3786 | MKWHr |  | By Hydro: | 1.6073 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3103 | MW | Dhaka | 5102.9 | 5102.9 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3268 | MW | Chittagong | 1333.6 | 1333.6 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6371 | MW | Khulna | 1812 | 1812 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1125.2 | MMCFD |  |  | Rajshahi | 1618.4 | 1618.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 156603880.54 | ii) Oil : | Taka | 1028005835.42 | Comilla | 1305 | 1305 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 45935972.27 | Total | Taka | 1230545688.23 | Mymensingh | 1058 | 1058 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.028 | MKWHr. | Sylhet | 498 | 498 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -314 | MW (E to W) at | 21:00 | hrs | Barisal | 446 | 446 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -376 | MW at | 20:00 | hrs | Rangpur | 817 | 817 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 13990.9 | 13990.9 |  | 0
| B. |  | 2022-04-19 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 38.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14933 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12500 | MW
| 4 | Reserve(Generation end) |  |  |  | 133 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 321.0668 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10567 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3251 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6518 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.72 |  | (b) Today: | 79.34 |  | (c) Rule Curve: |  | 84.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 233 | 0 | 270 | 96 | 0 | 398 | 0 |  | 0 | 330 | 120 | 94 | 62 | 55 | 310 | 0 | 97 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 68 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 22 | 50 | 0 | 16 | 86 | 38 | 0 | 32 | 0 | 0 | 0 | 290 | 195 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 42 | 22 | 8 | 25 | 20 | 158 | 107 | 0 | 20 | 0 | 0 | 41 | 22 | 15 | 130 | 268 | 55 | 84 | 0 | 207 | 0 | 17 | 10 | 270 | 24 | 8 | 100 | 270 | 107 | 100 | 143 | 100 | 149 | 0 | 90 | 180 | 140 | 401 | 68 | 105 | 51 | 0 | 300 | 54 | 102 | 62 | 18 | 100 | 400 | 104 | 0 | 108 | 113 | 0 | 35 | 0 | 101 | 55 |  | 923 | 0 | 240 | 0 | 0 | 200 | 0 | 0 | 34 | 0 | 8 | 65 | 38 | 48 | 0 | 0 | 0 | 34 | 31 | 90 | 0 | 25 | 17 | 43 | 30 | 22 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 143 | 0 | 30 | 0 | 0 | 420 | 76 | 54 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 219 | 0 | 0 | 0 | 0 | 115 |  | 9175 | 3803 | 12978 | 4386 | 923 | 1876 | 491 | 3940 | 326 | 68 | 343 | 610 | 158 | 0 | 0 | 79.8
2:00 | 0 | 0 | 233 | 0 | 270 | 97 | 0 | 392 | 0 |  | 0 | 330 | 125 | 93 | 62 | 55 | 310 | 0 | 60 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 69 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 50 | 0 | 23 | 91 | 38 | 0 | 32 | 0 | 0 | 0 | 290 | 195 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 25 | 20 | 154 | 107 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 110 | 270 | 55 | 84 | 0 | 140 | 0 | 6 | 0 | 280 | 16 | 8 | 10 | 273 | 33 | 50 | 143 | 50 | 143 | 0 | 90 | 180 | 137 | 400 | 68 | 105 | 51 | 0 | 300 | 54 | 104 | 62 | 8 | 100 | 400 | 104 | 0 | 108 | 113 | 0 | 35 | 0 | 101 | 55 |  | 924 | 0 | 240 | 0 | 0 | 200 | 0 | 0 | 34 | 0 | 8 | 65 | 37 | 48 | 0 | 0 | 0 | 34 | 31 | 90 | 0 | 25 | 17 | 43 | 30 | 22 | 0 | 11 | 76 | 0 | 249 | 0 | 0 | 124 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 366 | 76 | 10 | 113 | 105 | 104 | 0 | 0 | 113 | 90 | 221 | 0 | 48 | 0 | 0 | 115 |  | 8739 | 3809 | 12548 | 4275 | 924 | 1771 | 163 | 3980 | 415 | 69 | 330 | 597 | 154 | 0 | 0 | 79.79
3:00 | 0 | 0 | 235 | 0 | 270 | 97 | 0 | 370 | 0 |  | 0 | 330 | 130 | 94 | 62 | 55 | 306 | 0 | 97 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 69 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 51 | 0 | 22 | 95 | 38 | 0 | 33 | 0 | 0 | 0 | 290 | 205 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 156 | 109 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 110 | 269 | 55 | 84 | 0 | 140 | 0 | 7 | 0 | 300 | 16 | 8 | 10 | 275 | 76 | 25 | 143 | 25 | 149 | 0 | 90 | 178 | 145 | 400 | 68 | 105 | 51 | 0 | 300 | 54 | 110 | 62 | 8 | 100 | 401 | 104 | 0 | 108 | 113 | 0 | 35 | 0 | 101 | 55 |  | 923 | 0 | 245 | 0 | 0 | 200 | 0 | 0 | 29 | 0 | 8 | 65 | 36 | 48 | 0 | 0 | 0 | 34 | 31 | 90 | 0 | 25 | 17 | 43 | 30 | 22 | 0 | 11 | 76 | 0 | 249 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 10 | 0 | 0 | 417 | 76 | 10 | 113 | 105 | 110 | 0 | 0 | 113 | 220 | 217 | 0 | 72 | 0 | 0 | 115 |  | 8818 | 4020 | 12838 | 4318 | 923 | 1844 | 156 | 4034 | 545 | 69 | 330 | 593 | 156 | 0 | 0 | 79.78
4:00 | 0 | 0 | 235 | 0 | 270 | 94 | 0 | 399 | 35 |  | 0 | 330 | 125 | 94 | 63 | 55 | 306 | 0 | 97 | 94 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 67 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 51 | 0 | 22 | 95 | 38 | 0 | 33 | 0 | 0 | 0 | 290 | 205 | 115 | 0 | 101 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 156 | 108 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 163 | 269 | 55 | 84 | 0 | 139 | 0 | 7 | 0 | 290 | 16 | 8 | 0 | 275 | 35 | 25 | 143 | 25 | 149 | 0 | 90 | 178 | 147 | 399 | 68 | 105 | 51 | 0 | 300 | 54 | 110 | 62 | 8 | 100 | 401 | 104 | 0 | 108 | 113 | 0 | 35 | 0 | 101 | 55 |  | 924 | 0 | 245 | 0 | 0 | 200 | 0 | 0 | 29 | 0 | 8 | 65 | 36 | 48 | 0 | 0 | 0 | 34 | 31 | 89 | 0 | 25 | 17 | 43 | 30 | 22 | 0 | 11 | 75 | 0 | 249 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 420 | 76 | 0 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 220 | 0 | 27 | 0 | 0 | 115 |  | 8862 | 3744 | 12606 | 4350 | 924 | 1920 | 85 | 3988 | 324 | 67 | 330 | 592 | 156 | 0 | 0 | 79.6
5:00 | 0 | 0 | 235 | 0 | 270 | 97 | 0 | 386 | 63 |  | 0 | 330 | 125 | 93 | 79 | 55 | 270 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 67 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 22 | 50 | 0 | 22 | 91 | 38 | 0 | 34 | 0 | 0 | 0 | 290 | 205 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 148 | 129 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 110 | 270 | 55 | 84 | 0 | 139 | 0 | 7 | 0 | 270 | 16 | 8 | 0 | 275 | 0 | 0 | 143 | 0 | 149 | 0 | 90 | 178 | 143 | 378 | 69 | 105 | 51 | 0 | 300 | 54 | 97 | 62 | 8 | 100 | 354 | 104 | 0 | 108 | 113 | 0 | 35 | 0 | 99 | 55 |  | 923 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 24 | 0 | 8 | 65 | 33 | 48 | 0 | 0 | 0 | 34 | 31 | 53 | 0 | 25 | 17 | 43 | 30 | 22 | 0 | 11 | 75 | 0 | 249 | 0 | 0 | 133 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 310 | 76 | 0 | 113 | 105 | 115 | 0 | 0 | 113 | 0 | 220 | 0 | 97 | 0 | 0 | 115 |  | 8529 | 3628 | 12157 | 4159 | 923 | 1766 | 0 | 4060 | 324 | 67 | 290 | 550 | 148 | 0 | 0 | 79.74
6:00 | 0 | 0 | 235 | 0 | 270 | 97 | 0 | 286 | 99 |  | 0 | 330 | 125 | 94 | 79 | 55 | 250 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 68 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 0 | 22 | 88 | 38 | 0 | 31 | 0 | 0 | 0 | 290 | 205 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 35 | 22 | 8 | 33 | 20 | 140 | 129 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 110 | 268 | 40 | 84 | 0 | 139 | 0 | 7 | 0 | 280 | 16 | 8 | 0 | 275 | 0 | 0 | 143 | 0 | 149 | 1 | 90 | 178 | 133 | 329 | 69 | 98 | 51 | 0 | 300 | 54 | 95 | 62 | 8 | 93 | 300 | 104 | 1 | 108 | 113 | 0 | 35 | 1 | 51 | 55 |  | 922 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 8 | 65 | 30 | 48 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 30 | 22 | 0 | 11 | 76 | 0 | 249 | 0 | 0 | 96 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 280 | 76 | 0 | 113 | 105 | 73 | 0 | 0 | 70 | 0 | 153 | 0 | 116 | 0 | 1 | 72 |  | 8190 | 3309 | 11499 | 3903 | 922 | 1709 | 0 | 3760 | 325 | 68 | 250 | 548 | 140 | 4 | 0 | 79.72
7:00 | 0 | 0 | 234 | 0 | 270 | 97 | 0 | 272 | 140 |  | 0 | 330 | 130 | 94 | 79 | 55 | 250 | 0 | 0 | 50 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 29 | 50 | 0 | 67 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 50 | 0 | 22 | 90 | 38 | 0 | 4 | 0 | 0 | 0 | 290 | 205 | 115 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 134 | 129 | 0 | 20 | 0 | 0 | 41 | 5 | 5 | 110 | 271 | 40 | 81 | 0 | 139 | 0 | 7 | 0 | 295 | 16 | 8 | 0 | 273 | 0 | 0 | 145 | 0 | 149 | 3 | 90 | 178 | 140 | 322 | 69 | 90 | 51 | 1 | 281 | 54 | 92 | 62 | 8 | 70 | 300 | 104 | 6 | 108 | 113 | 0 | 35 | 5 | 51 | 55 |  | 923 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 8 | 15 | 26 | 48 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 30 | 22 | 0 | 11 | 76 | 0 | 249 | 0 | 0 | 43 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 310 | 76 | 0 | 113 | 105 | 73 | 0 | 0 | 70 | 0 | 152 | 0 | 116 | 0 | 4 | 35 |  | 8140 | 3218 | 11358 | 3801 | 923 | 1765 | 0 | 3656 | 325 | 67 | 250 | 548 | 134 | 19 | 0 | 79.71
8:00 | 0 | 0 | 234 | 0 | 270 | 97 | 0 | 272 | 242 |  | 0 | 330 | 130 | 93 | 79 | 55 | 250 | 0 | 0 | 50 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 30 | 50 | 0 | 70 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 22 | 50 | 0 | 22 | 78 | 18 | 0 | 2 | 0 | 0 | 0 | 290 | 205 | 117 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 132 | 120 | 0 | 20 | 1 | 0 | 41 | 5 | 5 | 110 | 268 | 40 | 81 | 0 | 139 | 0 | 7 | 0 | 280 | 16 | 8 | 0 | 270 | 0 | 0 | 145 | 0 | 149 | 11 | 90 | 178 | 140 | 325 | 69 | 90 | 51 | 2 | 281 | 54 | 92 | 62 | 8 | 40 | 330 | 92 | 13 | 108 | 113 | 0 | 0 | 12 | 51 | 55 |  | 922 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 8 | 15 | 24 | 48 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 30 | 22 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 20 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 311 | 76 | 0 | 113 | 105 | 70 | 0 | 0 | 70 | 0 | 152 | 0 | 116 | 0 | 32 | 35 |  | 8144 | 3238 | 11382 | 3822 | 922 | 1849 | 0 | 3523 | 325 | 70 | 250 | 548 | 132 | 71 | 0 | 79.7
9:00 | 0 | 0 | 233 | 0 | 270 | 90 | 0 | 272 | 242 |  | 0 | 350 | 135 | 93 | 78 | 55 | 255 | 0 | 0 | 50 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 33 | 30 | 50 | 0 | 65 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 22 | 46 | 0 | 22 | 88 | 12 | 0 | 2 | 0 | 0 | 0 | 285 | 205 | 113 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 138 | 120 | 0 | 17 | 1 | 0 | 41 | 5 | 5 | 110 | 270 | 60 | 81 | 0 | 164 | 0 | 7 | 10 | 290 | 16 | 5 | 0 | 273 | 0 | 0 | 146 | 0 | 139 | 12 | 90 | 178 | 140 | 375 | 69 | 90 | 51 | 3 | 281 | 54 | 92 | 62 | 8 | 60 | 330 | 91 | 23 | 72 | 113 | 0 | 26 | 12 | 51 | 49 |  | 921 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 8 | 64 | 23 | 48 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 29 | 22 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 10 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 368 | 76 | 0 | 113 | 105 | 70 | 0 | 2 | 70 | 0 | 154 | 0 | 116 | 1 | 54 | 35 |  | 8295 | 3384 | 11679 | 3972 | 921 | 1945 | 0 | 3541 | 326 | 65 | 250 | 543 | 138 | 108 | 0 | 79.69
10:00 | 0 | 0 | 234 | 0 | 270 | 94 | 0 | 295 | 272 |  | 0 | 370 | 135 | 93 | 78 | 55 | 280 | 0 | 0 | 50 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 28 | 41 | 0 | 65 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 22 | 26 | 0 | 22 | 72 | 12 | 0 | 2 | 0 | 0 | 0 | 275 | 205 | 130 | 0 | 100 | 0 | 0 | 0 | 43 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 144 | 109 | 0 | 17 | 1 | 0 | 41 | 5 | 5 | 130 | 270 | 60 | 78 | 0 | 205 | 0 | 7 | 10 | 300 | 16 | 5 | 0 | 270 | 0 | 0 | 145 | 0 | 133 | 18 | 90 | 178 | 138 | 387 | 69 | 90 | 51 | 4 | 281 | 54 | 92 | 62 | 8 | 100 | 401 | 92 | 15 | 72 | 113 | 0 | 36 | 15 | 51 | 38 |  | 922 | 0 | 340 | 0 | 12 | 120 | 0 | 0 | 24 | 0 | 8 | 65 | 23 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 30 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 8 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 369 | 76 | 0 | 113 | 105 | 70 | 0 | 2 | 70 | 0 | 181 | 0 | 116 | 4 | 39 | 35 |  | 8568 | 3432 | 12000 | 4165 | 922 | 2045 | 0 | 3592 | 325 | 65 | 250 | 524 | 144 | 98 | 0 | 79.68
11:00 | 0 | 0 | 234 | 0 | 270 | 94 | 0 | 341 | 272 |  | 0 | 380 | 140 | 93 | 78 | 40 | 250 | 0 | 0 | 50 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 27 | 33 | 28 | 41 | 0 | 66 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 22 | 26 | 0 | 22 | 49 | 12 | 0 | 2 | 0 | 0 | 0 | 270 | 205 | 136 | 0 | 100 | 0 | 0 | 0 | 43 | 0 | 49 | 42 | 21 | 8 | 31 | 20 | 148 | 109 | 0 | 17 | 2 | 0 | 41 | 15 | 5 | 130 | 269 | 60 | 81 | 0 | 219 | 0 | 7 | 10 | 280 | 16 | 5 | 0 | 265 | 0 | 0 | 145 | 0 | 131 | 19 | 88 | 136 | 137 | 377 | 69 | 90 | 51 | 2 | 281 | 54 | 92 | 62 | 8 | 90 | 400 | 92 | 44 | 72 | 113 | 0 | 36 | 25 | 51 | 37 |  | 922 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 24 | 0 | 8 | 63 | 21 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 8 | 30 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 5 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 416 | 76 | 0 | 113 | 89 | 70 | 0 | 3 | 70 | 0 | 181 | 0 | 116 | 0 | 97 | 35 |  | 8492 | 3482 | 11974 | 4094 | 922 | 2099 | 0 | 3478 | 331 | 66 | 250 | 524 | 148 | 192 | 0 | 79.67
12:00 | 0 | 0 | 234 | 0 | 270 | 94 | 0 | 383 | 323 |  | 0 | 380 | 145 | 92 | 77 | 48 | 305 | 0 | 0 | 50 | 76 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 28 | 41 | 0 | 66 | 0 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 22 | 8 | 0 | 35 | 48 | 16 | 0 | 2 | 0 | 0 | 0 | 270 | 205 | 136 | 0 | 100 | 0 | 0 | 0 | 43 | 0 | 49 | 42 | 21 | 8 | 31 | 20 | 146 | 109 | 0 | 17 | 2 | 0 | 41 | 22 | 5 | 163 | 265 | 60 | 81 | 0 | 219 | 0 | 7 | 10 | 300 | 16 | 5 | 0 | 278 | 0 | 0 | 163 | 0 | 115 | 18 | 88 | 136 | 137 | 376 | 69 | 105 | 51 | 5 | 281 | 54 | 92 | 62 | 8 | 90 | 391 | 91 | 13 | 72 | 113 | 0 | 36 | 22 | 55 | 37 |  | 922 | 0 | 330 | 0 | 16 | 125 | 0 | 0 | 22 | 0 | 8 | 65 | 23 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 16 | 30 | 18 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 3 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 417 | 76 | 0 | 113 | 89 | 77 | 0 | 3 | 113 | 0 | 212 | 0 | 116 | 5 | 71 | 60 |  | 8718 | 3602 | 12320 | 4239 | 922 | 2245 | 0 | 3608 | 326 | 66 | 255 | 504 | 146 | 139 | 0 | 79.66
13:00 | 0 | 0 | 232 | 0 | 270 | 100 | 0 | 400 | 322 |  | 0 | 380 | 150 | 92 | 77 | 55 | 308 | 0 | 0 | 75 | 76 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 28 | 40 | 0 | 66 | 0 | 0 | 0 | 13 | 217 | 0 | 0 | 0 |  | 22 | 0 | 0 | 40 | 48 | 34 | 0 | 10 | 0 | 0 | 0 | 270 | 205 | 128 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 48 | 42 | 21 | 8 | 30 | 20 | 156 | 102 | 0 | 17 | 2 | 0 | 41 | 22 | 5 | 163 | 261 | 60 | 81 | 0 | 220 | 0 | 15 | 10 | 300 | 16 | 5 | 0 | 278 | 47 | 50 | 142 | 44 | 120 | 18 | 88 | 179 | 135 | 376 | 69 | 90 | 51 | 4 | 280 | 55 | 92 | 62 | 8 | 90 | 389 | 91 | 48 | 72 | 113 | 0 | 36 | 11 | 76 | 37 |  | 922 | 0 | 340 | 0 | 16 | 200 | 0 | 0 | 21 | 0 | 8 | 30 | 28 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 34 | 17 | 43 | 30 | 18 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 20 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 414 | 75 | 0 | 113 | 89 | 85 | 0 | 4 | 113 | 0 | 211 | 0 | 116 | 5 | 50 | 115 |  | 9004 | 3809 | 12813 | 4228 | 922 | 2280 | 141 | 3813 | 326 | 66 | 375 | 539 | 156 | 142 | 0 | 79.65
14:00 | 0 | 0 | 230 | 0 | 270 | 95 | 0 | 398 | 322 |  | 0 | 380 | 135 | 93 | 76 | 55 | 305 | 0 | 0 | 80 | 80 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 65 | 0 | 0 | 0 | 20 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 55 | 48 | 37 | 0 | 2 | 0 | 0 | 0 | 265 | 205 | 114 | 0 | 101 | 0 | 0 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 29 | 20 | 166 | 100 | 0 | 17 | 1 | 0 | 41 | 22 | 5 | 163 | 267 | 60 | 79 | 0 | 219 | 0 | 15 | 10 | 290 | 16 | 5 | 100 | 265 | 149 | 100 | 141 | 99 | 140 | 16 | 88 | 200 | 135 | 390 | 69 | 90 | 51 | 2 | 281 | 54 | 92 | 62 | 8 | 90 | 400 | 91 | 38 | 72 | 113 | 0 | 36 | 28 | 67 | 37 |  | 922 | 0 | 340 | 0 | 16 | 200 | 0 | 0 | 22 | 0 | 8 | 30 | 27 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 34 | 24 | 43 | 30 | 18 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 10 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 416 | 75 | 11 | 113 | 89 | 90 | 0 | 6 | 113 | 0 | 190 | 0 | 116 | 4 | 84 | 115 |  | 9325 | 3872 | 13197 | 4210 | 922 | 2220 | 459 | 3870 | 327 | 65 | 408 | 579 | 166 | 179 | 0 | 79.64
15:00 | 0 | 0 | 230 | 0 | 270 | 92 | 0 | 396 | 322 |  | 0 | 380 | 145 | 92 | 76 | 55 | 308 | 0 | 0 | 90 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 62 | 0 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 22 | 28 | 0 | 55 | 55 | 37 | 0 | 2 | 0 | 0 | 0 | 265 | 200 | 113 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 29 | 21 | 8 | 28 | 20 | 164 | 96 | 0 | 17 | 1 | 0 | 40 | 22 | 5 | 163 | 153 | 55 | 79 | 0 | 220 | 0 | 15 | 10 | 300 | 21 | 5 | 60 | 265 | 247 | 100 | 140 | 95 | 149 | 12 | 88 | 200 | 128 | 404 | 69 | 105 | 51 | 3 | 281 | 54 | 92 | 62 | 8 | 91 | 383 | 104 | 12 | 54 | 113 | 0 | 22 | 21 | 86 | 37 |  | 922 | 0 | 335 | 0 | 16 | 198 | 0 | 0 | 22 | 0 | 8 | 45 | 26 | 64 | 0 | 0 | 0 | 34 | 28 | 53 | 0 | 34 | 24 | 43 | 30 | 18 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 20 | 0 | 0 | 208 | 0 | 30 | 0 | 0 | 414 | 75 | 50 | 113 | 88 | 95 | 0 | 4 | 113 | 0 | 213 | 0 | 116 | 2 | 75 | 114 |  | 9298 | 3968 | 13266 | 4117 | 922 | 2257 | 582 | 3902 | 327 | 62 | 406 | 605 | 164 | 130 | 0 | 79.63
16:00 | 0 | 0 | 230 | 0 | 270 | 91 | 0 | 396 | 310 |  | 0 | 380 | 130 | 92 | 76 | 55 | 307 | 0 | 0 | 95 | 82 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 45 | 0 | 62 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 40 | 0 | 52 | 86 | 37 | 0 | 2 | 0 | 0 | 0 | 265 | 200 | 114 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 33 | 21 | 8 | 31 | 20 | 162 | 97 | 0 | 17 | 1 | 0 | 40 | 22 | 5 | 163 | 157 | 55 | 80 | 0 | 219 | 0 | 15 | 10 | 290 | 21 | 8 | 10 | 263 | 210 | 70 | 139 | 70 | 149 | 7 | 88 | 200 | 118 | 403 | 68 | 105 | 80 | 2 | 281 | 54 | 92 | 62 | 15 | 98 | 398 | 104 | 21 | 54 | 113 | 0 | 36 | 6 | 101 | 43 |  | 922 | 0 | 325 | 0 | 16 | 200 | 0 | 0 | 22 | 0 | 8 | 45 | 27 | 110 | 0 | 0 | 0 | 34 | 28 | 52 | 0 | 34 | 24 | 43 | 30 | 18 | 0 | 11 | 72 | 0 | 25 | 0 | 0 | 60 | 0 | 0 | 210 | 0 | 10 | 0 | 0 | 417 | 75 | 10 | 113 | 88 | 100 | 0 | 3 | 113 | 0 | 210 | 0 | 150 | 1 | 41 | 112 |  | 9230 | 3759 | 12989 | 4156 | 922 | 2221 | 380 | 4089 | 97 | 62 | 410 | 618 | 162 | 82 | 0 | 79.62
17:00 | 0 | 0 | 231 | 0 | 270 | 97 | 0 | 395 | 320 |  | 0 | 380 | 145 | 89 | 76 | 55 | 306 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 49 | 0 | 62 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 22 | 47 | 0 | 62 | 88 | 37 | 0 | 3 | 0 | 0 | 0 | 265 | 200 | 114 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 40 | 21 | 8 | 20 | 17 | 162 | 71 | 0 | 17 | 0 | 0 | 40 | 22 | 5 | 163 | 154 | 55 | 80 | 0 | 219 | 0 | 15 | 10 | 290 | 21 | 8 | 10 | 275 | 45 | 25 | 140 | 25 | 134 | 3 | 88 | 200 | 123 | 402 | 68 | 105 | 105 | 1 | 281 | 54 | 92 | 62 | 42 | 100 | 397 | 104 | 9 | 35 | 108 | 0 | 36 | 6 | 100 | 55 |  | 922 | 0 | 310 | 0 | 16 | 180 | 0 | 0 | 29 | 11 | 8 | 45 | 27 | 110 | 0 | 0 | 0 | 34 | 28 | 55 | 0 | 34 | 24 | 43 | 30 | 20 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 85 | 0 | 0 | 195 | 0 | 10 | 0 | 0 | 414 | 75 | 10 | 113 | 93 | 108 | 0 | 2 | 113 | 0 | 212 | 0 | 150 | 0 | 17 | 111 |  | 9021 | 3969 | 12990 | 4122 | 922 | 2254 | 125 | 4170 | 324 | 62 | 375 | 631 | 162 | 38 | 0 | 79.6
18:00 | 0 | 0 | 200 | 0 | 270 | 95 | 0 | 365 | 253 |  | 0 | 380 | 130 | 83 | 76 | 55 | 270 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 49 | 0 | 62 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 47 | 39 | 72 | 89 | 37 | 0 | 16 | 0 | 0 | 0 | 265 | 200 | 114 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 40 | 21 | 8 | 24 | 18 | 164 | 76 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 130 | 156 | 60 | 80 | 0 | 219 | 0 | 15 | 10 | 275 | 21 | 8 | 0 | 275 | 0 | 0 | 178 | 0 | 144 | 0 | 88 | 200 | 133 | 353 | 96 | 105 | 105 | 0 | 282 | 54 | 101 | 62 | 69 | 100 | 360 | 104 | 1 | 144 | 108 | 0 | 36 | 1 | 101 | 55 |  | 922 | 0 | 305 | 0 | 42 | 120 | 0 | 0 | 30 | 55 | 8 | 83 | 30 | 110 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 34 | 27 | 43 | 36 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 122 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 303 | 75 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 0 | 173 | 0 | 150 | 0 | 2 | 114 |  | 8895 | 3890 | 12785 | 4028 | 922 | 1989 | 0 | 4448 | 325 | 62 | 279 | 723 | 164 | 4 | 0 | 79.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 365 | 317 |  | 0 | 380 | 135 | 86 | 79 | 55 | 307 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 49 | 0 | 63 | 0 | 0 | 0 | 25 | 208 | 0 | 0 | 0 |  | 22 | 47 | 51 | 76 | 89 | 37 | 0 | 19 | 0 | 0 | 0 | 265 | 210 | 121 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 37 | 21 | 8 | 33 | 20 | 160 | 80 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 156 | 55 | 80 | 0 | 219 | 0 | 15 | 10 | 295 | 15 | 11 | 100 | 275 | 163 | 100 | 179 | 96 | 149 | 0 | 88 | 200 | 127 | 402 | 98 | 105 | 105 | 0 | 285 | 54 | 110 | 62 | 54 | 100 | 396 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 922 | 0 | 300 | 0 | 49 | 180 | 0 | 0 | 43 | 80 | 32 | 88 | 37 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 36 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 161 | 0 | 20 | 0 | 0 | 415 | 75 | 21 | 113 | 105 | 108 | 0 | 0 | 113 | 0 | 219 | 0 | 0 | 0 | 0 | 115 |  | 9678 | 4152 | 13830 | 4270 | 922 | 2284 | 500 | 4337 | 325 | 63 | 341 | 789 | 160 | 0 | 0 | 79.52
19:30 | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 396 | 327 |  | 0 | 380 | 135 | 90 | 78 | 55 | 308 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 23 | 33 | 33 | 49 | 0 | 64 | 0 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 22 | 48 | 51 | 80 | 89 | 37 | 0 | 25 | 0 | 0 | 0 | 265 | 220 | 121 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 42 | 21 | 8 | 33 | 20 | 160 | 88 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 158 | 55 | 80 | 0 | 219 | 0 | 15 | 10 | 315 | 15 | 11 | 200 | 275 | 301 | 100 | 179 | 99 | 149 | 0 | 88 | 200 | 128 | 403 | 97 | 105 | 105 | 0 | 285 | 54 | 110 | 62 | 39 | 100 | 396 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 300 | 0 | 49 | 200 | 0 | 0 | 38 | 68 | 32 | 88 | 38 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 35 | 21 | 0 | 11 | 75 | 0 | 249 | 0 | 0 | 196 | 0 | 0 | 209 | 0 | 95 | 0 | 0 | 418 | 75 | 80 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 218 | 0 | 0 | 0 | 0 | 115 |  | 10007 | 4354 | 14361 | 4336 | 923 | 2323 | 875 | 4336 | 324 | 64 | 409 | 820 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 232 | 0 | 270 | 100 | 0 | 396 | 330 |  | 0 | 380 | 130 | 91 | 78 | 55 | 308 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 27 | 33 | 33 | 49 | 0 | 64 | 0 | 0 | 0 | 25 | 211 | 0 | 0 | 0 |  | 22 | 48 | 51 | 80 | 91 | 37 | 0 | 21 | 0 | 0 | 0 | 265 | 220 | 121 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 42 | 21 | 8 | 33 | 20 | 160 | 106 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 157 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 305 | 15 | 11 | 200 | 264 | 303 | 100 | 179 | 99 | 149 | 0 | 88 | 200 | 128 | 402 | 98 | 105 | 105 | 0 | 285 | 54 | 110 | 62 | 39 | 100 | 396 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 295 | 0 | 49 | 200 | 0 | 0 | 38 | 60 | 32 | 87 | 39 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 35 | 21 | 0 | 8 | 75 | 0 | 249 | 0 | 0 | 195 | 0 | 0 | 211 | 0 | 100 | 0 | 0 | 417 | 75 | 166 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 218 | 0 | 0 | 0 | 0 | 115 |  | 9921 | 4429 | 14350 | 4260 | 923 | 2308 | 968 | 4329 | 324 | 64 | 411 | 814 | 160 | 0 | 0 | 79.54
21:00 | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 397 | 331 |  | 0 | 380 | 130 | 91 | 78 | 55 | 308 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 27 | 33 | 33 | 49 | 0 | 64 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 48 | 51 | 80 | 96 | 37 | 0 | 28 | 0 | 0 | 0 | 265 | 210 | 120 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 42 | 22 | 8 | 33 | 20 | 162 | 106 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 158 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 310 | 22 | 11 | 200 | 270 | 304 | 100 | 180 | 99 | 149 | 0 | 88 | 200 | 125 | 402 | 98 | 105 | 105 | 0 | 295 | 54 | 110 | 62 | 38 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 922 | 0 | 290 | 0 | 49 | 200 | 0 | 0 | 33 | 63 | 32 | 87 | 40 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 35 | 21 | 0 | 11 | 76 | 0 | 249 | 17 | 0 | 198 | 0 | 0 | 213 | 0 | 100 | 0 | 0 | 415 | 75 | 171 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 218 | 0 | 57 | 0 | 0 | 115 |  | 9962 | 4508 | 14470 | 4266 | 922 | 2320 | 974 | 4406 | 325 | 64 | 430 | 814 | 162 | 0 | 0 | 79.52
22:00 | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 395 | 331 |  | 0 | 380 | 125 | 92 | 78 | 55 | 300 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 27 | 33 | 33 | 49 | 0 | 65 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 47 | 51 | 80 | 91 | 38 | 0 | 29 | 0 | 0 | 0 | 265 | 210 | 120 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 47 | 42 | 22 | 8 | 33 | 20 | 166 | 106 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 160 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 295 | 22 | 11 | 200 | 270 | 301 | 100 | 180 | 97 | 149 | 0 | 88 | 190 | 130 | 400 | 98 | 105 | 105 | 0 | 295 | 54 | 93 | 62 | 39 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 285 | 0 | 49 | 200 | 0 | 0 | 33 | 63 | 32 | 90 | 40 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 35 | 21 | 0 | 11 | 76 | 0 | 249 | 17 | 0 | 196 | 0 | 0 | 216 | 0 | 100 | 0 | 0 | 414 | 75 | 171 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 218 | 0 | 150 | 0 | 0 | 115 |  | 9909 | 4600 | 14509 | 4252 | 923 | 2300 | 969 | 4475 | 325 | 65 | 433 | 817 | 166 | 0 | 0 | 79.5
23:00 | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 394 | 252 |  | 0 | 380 | 125 | 92 | 78 | 55 | 295 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 27 | 33 | 33 | 50 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 48 | 17 | 80 | 89 | 38 | 0 | 30 | 0 | 0 | 0 | 265 | 200 | 136 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 47 | 42 | 22 | 8 | 33 | 21 | 164 | 106 | 0 | 20 | 0 | 0 | 41 | 22 | 5 | 163 | 159 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 280 | 24 | 11 | 200 | 280 | 301 | 100 | 178 | 99 | 149 | 0 | 88 | 178 | 140 | 402 | 98 | 105 | 70 | 0 | 280 | 54 | 93 | 62 | 38 | 90 | 401 | 104 | 0 | 144 | 109 | 0 | 36 | 0 | 101 | 55 |  | 922 | 0 | 280 | 0 | 32 | 200 | 0 | 0 | 33 | 56 | 8 | 90 | 39 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 24 | 43 | 35 | 21 | 0 | 11 | 76 | 0 | 249 | 17 | 0 | 195 | 0 | 0 | 217 | 0 | 100 | 0 | 0 | 414 | 75 | 171 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 216 | 0 | 150 | 0 | 0 | 115 |  | 9733 | 4527 | 14260 | 4251 | 922 | 2204 | 971 | 4379 | 325 | 65 | 434 | 762 | 164 | 0 | 0 | 79.48
24:00 | 0 | 0 | 233 | 0 | 270 | 99 | 0 | 393 | 252 |  | 0 | 380 | 125 | 93 | 78 | 55 | 295 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 28 | 33 | 30 | 50 | 0 | 65 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 46 | 0 | 80 | 90 | 38 | 0 | 32 | 0 | 0 | 0 | 265 | 200 | 139 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 48 | 42 | 22 | 8 | 33 | 21 | 162 | 102 | 0 | 20 | 0 | 0 | 41 | 22 | 5 | 163 | 159 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 280 | 18 | 11 | 160 | 275 | 301 | 100 | 105 | 98 | 149 | 0 | 88 | 184 | 140 | 400 | 48 | 105 | 51 | 0 | 281 | 54 | 94 | 62 | 39 | 100 | 401 | 104 | 0 | 90 | 108 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 275 | 0 | 16 | 200 | 0 | 0 | 33 | 50 | 8 | 90 | 39 | 80 | 0 | 0 | 0 | 34 | 22 | 90 | 0 | 34 | 24 | 43 | 30 | 22 | 0 | 11 | 74 | 0 | 249 | 0 | 0 | 195 | 0 | 0 | 217 | 0 | 60 | 0 | 0 | 414 | 76 | 130 | 113 | 89 | 110 | 0 | 0 | 113 | 0 | 190 | 0 | 150 | 0 | 0 | 115 |  | 9480 | 4319 | 13799 | 4234 | 923 | 2180 | 849 | 4137 | 323 | 65 | 417 | 726 | 162 | 0 | 0 | 79.46
KWH | 0 | 0 | 5565000 | 0 | 6487236 | 2240409 | 0 | 8888320 | 5212000 |  | 0 | 8556050 | 3205615 | 2211840 | 1817784 | 1324538 | 7031939 | 0 | 424000 | 2081981 | 1995552 | 3118080 | 0 | 0 | 0 | 0 | 1295640 | 1209808 | 1321025 | 399384 | 600000 | 623700 | 825800 | 757200 | 1133280 | 0 | 1607302 | 0 | 0 | 0 | 520759 | 4920756 | 0 | 0 | 0 |  | 532800 | 938720 | 254420 | 1043760 | 1918080 | 799200 | 0 | 417130 | 0 | 0 | 0 | 6928300 | 5017000 | 2939000 | 0 | 2370940 | 792 | 0 | 0 | 1194133 | 0 | 1161288 | 977731 | 495540 | 216540 | 745600 | 475040 | 3651840 | 2455680 | 0 | 416700 | 11200 | 0 | 950850 | 370800 | 142920 | 3556636 | 5186000 | 1301184 | 1941120 | 0 | 7577180 | 0 | 286160 | 175860 | 7127500 | 425688 | 181488 | 1322304 | 6543707 | 2546351 | 1104374 | 3607200 | 1072660 | 3501216 | 137430 | 2050560 | 4417920 | 3251781 | 9184000 | 1801200 | 2443200 | 1639272 | 29160 | 6814691 | 1339721 | 2362717 | 1505940 | 527520 | 2217600 | 9098900 | 2488320 | 267160 | 2393280 | 2682218 | 0 | 845640 | 185071 | 2013120 | 1211040 |  | 22325090 | 0 | 7298208 | 0 | 381120 | 4185600 | 0 | 0 | 635040 | 388480 | 282750 | 1999175 | 750774 | 1652448 | 0 | 0 | 0 | 796576 | 682470 | 1654176 | 0 | 558032 | 468909 | 788640 | 738956 | 490800 | 0 | 244710 | 1796509 | 0 | 6026800 | 44000 | 0 | 2498655 | 0 | 0 | 4202318 | 0 | 679680 | 0 | 0 | 9323781 | 1794720 | 1107889 | 2733888 | 2433168 | 2335824 | 0 | 33113 | 2511552 | 555300 | 4769155 | 0 | 2550000 | 25080 | 566640 | 2278848 |  | 220165091 | 94588874 | 314753965 | 104530505 | 22325090 | 49760843 | 7833258 | 96142631 | 8378609 | 1607302 | 8431918 | 10837115 | 3651840 | 1254854 | 0
Fuel Cost | 0 | 0 | 8124900 | 0 | 7200831.96 | 2957339.88 | 0 | 8977203.2 | 5368360 |  | 0 | 9326094.5 | 3558232.65 | 16787865.6 | 12524531.76 | 11205591.48 | 7313216.56 | 0 | 733520 | 15677316.93 | 18199434.24 | 30681907.2 | 0 | 0 | 0 | 0 | 9458172 | 9351815.84 | 13025306.5 | 299538 | 450000 | 0 | 0 | 0 | 10958817.6 | 0 | 433971.54 | 0 | 0 | 0 | 4837851.11 | 5363624.04 | 0 | 0 | 0 |  | 0 | 9077422.4 | 2467874 | 9967908 | 16687296 | 6329664 | 0 | 1238876.1 | 0 | 0 | 0 | 5126942 | 5017000 | 2703880 | 0 | 2726581 | 894.96 | 0 | 0 | 2041967.43 | 0 | 11729008.8 | 9337331.05 | 629335.8 | 162405 | 1304800 | 356280 | 27388800 | 2603020.8 | 0 | 529209 | 178528 | 0 | 1521360 | 660024 | 222955.2 | 4054565.04 | 5393440 | 2563332.48 | 3707539.2 | 0 | 13108521.4 | 0 | 334807.2 | 358754.4 | 7198775 | 319266 | 137930.88 | 22492391.04 | 49470424.92 | 43237039.98 | 18465133.28 | 18757440 | 17934875.2 | 34451965.44 | 1606556.7 | 16712064 | 47934432 | 22925056.05 | 8541120 | 16426944 | 23088240 | 14278059.12 | 0 | 51519063.96 | 11668969.91 | 20768282.43 | 15029281.2 | 4520846.4 | 14769216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128592518.4 | 0 | 7663118.4 | 0 | 2995603.2 | 58012416 | 0 | 0 | 6661569.6 | 4071270.4 | 2946255 | 2259067.75 | 1163699.7 | 16127892.48 | 0 | 0 | 0 | 7838307.84 | 6933895.2 | 14639457.6 | 0 | 7544592.64 | 4543728.21 | 7641921.6 | 7167873.2 | 942336 | 0 | 185245.47 | 10832949.27 | 0 | 32665256 | 1524600 | 0 | 2923426.35 | 0 | 0 | 61858120.96 | 0 | 11561356.8 | 0 | 0 | 9230543.19 | 18736876.8 | 18845191.89 | 25944597.12 | 22969105.92 | 18125994.24 | 0 | 365898.65 | 18560369.28 | 2437767 | 0 | 0 | 0 | 0 | 0 | 0 |  | 844599139.36 | 544512822.16 | 1389111961.52 | 104239011.05 | 128592518.4 | 52364869.49 | 132535988.19 | 668262395.82 | 45935972.27 | 433971.54 | 121395136.96 | 105812314.45 | 27388800 | 2150983.35 | 0
Yesterday Day Peak | 0 | 0 | 234 | 0 | 270 | 94 | 0 | 383 | 323 |  | 0 | 380 | 145 | 92 | 77 | 48 | 305 | 0 | 0 | 50 | 76 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 28 | 41 | 0 | 66 | 0 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 22 | 8 | 0 | 35 | 48 | 16 | 0 | 2 | 0 | 0 | 0 | 270 | 205 | 136 | 0 | 100 | 0 | 0 | 0 | 43 | 0 | 49 | 42 | 21 | 8 | 31 | 20 | 146 | 109 | 0 | 17 | 2 | 0 | 41 | 22 | 5 | 163 | 265 | 60 | 81 | 0 | 219 | 0 | 7 | 10 | 300 | 16 | 5 | 0 | 278 | 0 | 0 | 163 | 0 | 115 | 18 | 88 | 136 | 137 | 376 | 69 | 105 | 51 | 5 | 281 | 54 | 92 | 62 | 8 | 90 | 391 | 91 | 13 | 72 | 113 | 0 | 36 | 22 | 55 | 37 |  | 922 | 0 | 330 | 0 | 16 | 125 | 0 | 0 | 22 | 0 | 8 | 65 | 23 | 64 | 0 | 0 | 0 | 34 | 29 | 53 | 0 | 8 | 17 | 16 | 30 | 18 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 3 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 417 | 76 | 0 | 113 | 89 | 77 | 0 | 3 | 113 | 0 | 212 | 0 | 116 | 5 | 71 | 60 |  | 12320 | DayPeak
Yesterday Evening Peak | 0 | 0 | 233 | 0 | 270 | 100 | 0 | 397 | 331 | 0 | 0 | 380 | 130 | 91 | 78 | 55 | 308 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 27 | 33 | 33 | 49 | 0 | 64 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 22 | 48 | 51 | 80 | 96 | 37 | 0 | 28 | 0 | 0 | 0 | 265 | 210 | 120 | 0 | 100 | 0 | 0 | 0 | 51 | 0 | 46 | 42 | 22 | 8 | 33 | 20 | 162 | 106 | 0 | 20 | 0 | 0 | 40 | 22 | 5 | 163 | 158 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 310 | 22 | 11 | 200 | 270 | 304 | 100 | 180 | 99 | 149 | 0 | 88 | 200 | 125 | 402 | 98 | 105 | 105 | 0 | 295 | 54 | 110 | 62 | 38 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 922 | 0 | 290 | 0 | 49 | 200 | 0 | 0 | 33 | 63 | 32 | 87 | 40 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 34 | 40 | 43 | 35 | 21 | 0 | 11 | 76 | 0 | 249 | 17 | 0 | 198 | 0 | 0 | 213 | 0 | 100 | 0 | 0 | 415 | 75 | 171 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 218 | 0 | 57 | 0 | 0 | 115 |  | 14470 | EvPeak
Forecast for Evening | 0 | 0 | 235 | 0 | 270 | 100 | 0 | 400 | 330 | 0 | 0 | 380 | 150 | 93 | 80 | 55 | 330 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 90 | 95 | 40 |  | 30 | 0 | 0 | 0 | 290 | 0 | 200 | 8 | 100 | 30 | 20 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 166 | 110 | 0 | 20 | 0 | 0 | 41 | 22 | 5 | 163 | 160 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 330 | 22 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 88 | 200 | 150 | 400 | 98 | 105 | 105 | 0 | 300 | 54 | 110 | 62 | 50 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 35 |  | 101 | 55 |  | 940 | 0 | 330 | 0 | 115 | 200 | 0 | 0 | 36 | 63 | 32 | 67 | 33 | 110 | 0 | 0 | 0 | 43 | 40 | 92 | 0 | 34 | 40 | 43 | 32 | 22 | 0 | 11 | 74 | 0 | 250 | 17 | 10 | 200 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 414 | 94 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 0 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 235 | 0 | 270 | 100 | 0 | 400 | 320 | 0 | 0 | 380 | 140 | 93 | 80 | 55 | 330 | 0 | 0 | 90 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 22 | 95 | 40 | 0 | 5 | 0 | 0 | 0 | 290 | 0 | 190 | 8 | 100 | 30 | 20 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 143 | 120 | 0 | 20 | 1.6 | 0 | 41 | 22 | 5 | 163 | 160 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 310 | 22 | 11 | 100 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 88 | 200 | 140 | 400 | 98 | 105 | 105 | 5 | 300 | 54 | 110 | 60 | 8 | 100 | 400 | 92 | 50 | 162 | 113 | 0 | 35 | 30 | 101 | 55 |  | 940 | 0 | 330 | 0 | 66 | 200 | 0 | 0 | 30 | 0 | 32 | 66 | 33 | 50 | 0 | 0 | 0 | 34 | 40 | 92 | 0 | 34 | 30 | 43 | 30 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 400 | 76 | 100 | 113 | 105 | 110 | 0 | 8 | 113 | 0 | 220 |  | 150 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 270 | 102 | 0 | 401 | 253 | 0 | 0 | 380 | 125 | 63 | 63 | 15 | 302 | 0 | 0 | 0 | 76 | 82 | 0 | 0 | 0 | 0 | 54 | 25 | 55 | 0 | 25 | 26 | 33 | 33 | 43 | 0 | 64 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 85 | 24 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 186 | 8 | 30 | 28 | 20 | 0 | 51 | 0 | 0 | 42 | 22 | 8 | 33 | 20 | 134 | 110 | 0 | 0 | 0 | 0 | 41 | 22 | 5 | 163 | 160 | 55 | 81 | 0 | 140 | 0 | 15 | 10 | 300 | 22 | 5 | 0 | 45 | 0 | 0 | 36 | 0 | 102 | 10 | 88 | 69 | 33 | 400 | 48 | 12 | 51 | 2 | 280 | 54 | 74 | 62 | 39 | 72 | 400 | 57 | 25 | 72 | 82 | 0 | 36 | 13 | 101 | 55 | 0 | 923 | 0 | 270 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 421 | 70 | 0 | 60 | 15 | 58 | 0 | 1 | 70 | 0 | 222 | 0 | 100 | 2 | 0 | 17 | 0 |  |  |  |  | 123244922 |  | 0
123244922
| Minimum Generation |  | 11358 | 7:00
| Highest Generation |  | 14509 | 22:00
| Day Peak Generation |  | 12320 | 12:00
| Evening Peak Generation |  | 14470 | 21:00
| HVDC Max Flow |  | 924 | 2:00
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 90.39%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-19
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12320 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10567 | MW
Evening Peak Generation : |  | 14470 | MW Hour : | 21:00 | Available Max Generation : |  | 14933 | MW
E.P. Demand (at gen end) : |  | 14470 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14800 | MW
Maximum Generation : |  | 14509 | MW Hour : | 22:00 | Reserve(Generation end) |  | 133 | MW
Total Gen. (MKWH) : |  | 314.754 | System Load Factor : | 90.39% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -376 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-19
Actual : | 79.34 | Ft.(MSL) , | Rule curve : | 84.6 | Ft.( MSL )
Gas Consumed : | Total = | 1125.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156603880.54
: |  | Coal : | 45935972.27 | Oil : | 1028005835.42 | Total : | 1230545688.23
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5268.6755 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1715.1089 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1665.0352 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1491.6913 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1359.602 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1114.9666 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 547.255 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 332.9241 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 821.5859 |  |  | 0 | 0%
Total | 0 |  | 14316.8444 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensingh-Kishoreganj 132 kV Ckt-2 tripped at 08:00 from both ends showing Dist. B-phase, Z1 at
both ends and was switched on at 08:07.
b) Rampura-Bhulta 230 kV Ckt-1 was under shut down from 08:23 to 10:15 for C/M.
c) Narshingdi-Bhulta 132 kV Ckt was under shut down from 11:10 to 12:34 due to R/H maintenance. | [5 empty] | About 25 MW power interruption occurred under Bhulta
S/S area from 11:10 to 12:34.
d) Shahmirpur 132/33 kV T-1 transformer was under shutdown from 11:31 to 14:35 for D/W.
e) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 11:40 to 12:10 for removing Kite.
f) Rampal 400 kV Bus was under shut down from 12:45 to 19:30 for work.
g) Gopalganj-Rampal 400 kV Ckt was under shut down from 12:50 to 21:31 for Bus maintenance at Rampal.
h) Siddhirganj-Ullon 132 kV Ckt-1 tripped at 13:18 from both ends showing Dist. CN, Z1 at Siddhirganj end
& Dist. B, Z1 at Ullon end and was switched on at 13:46.
i) Ullon-Dhanmondi 132 kV Ckt-2 tripped at 13:18 from Ullon end showing O/C and was switched on at 13:44.
j) Shahjibazar 330 MW CCPP GT-2 was shutdown at 14:56 due to Gas shortage.
k) Bhola CCPP GT-2 was synchronized at 14:14 and ST at 17:51.
l) Bhola CCPP GT-1 was shutdown at 17:50 due to Gas shortage.
m) Sirajganj Unit-1 STG was synchronized at 14:19.
n) Sylhet CCPP ST tripped at 19:35 showing turbine vibration high.
o) Bogura- Naogaon 132 kV Ckt-1 was switched on at 16:08.
p) Dohazari 132/33 T-2 transformer tripped at 18:32 from 33 kV side showing no relay and was switched | [5 empty] | About 80 MW power interruption occurred under
on at 18:50. | [5 empty] | Dohazari S/S area from 18:32 to 18:50.
q) Dohazari 132/33 T-1 transformer tripped at 18:32 showing Diff. & L/O relay and was switched on at 22:54. | [5 empty] | About 30 MW power interruption occurred under
r) Fenchuganj-Bibiyana 230 kV Ckt tripped at 00:52(19/04/2022) from Fenchuganj end showing Dist. | [5 empty] | Dohazari S/S area from 18:32 to 22:54.
Z1,2,3 and was switched on at 01:34(19/04/2022).
s) Ashuganj(S) tripped at 02:32(19/04/2022) due to low gas pressure.
t) Payra-Gopalganj 400 kV Ckt-2 was switched on at 03:23(19/04/2022).
u) Rampura-Bashundhara 132 kV Ckt-1 tripped at 05:48(19/04/2022) from both ends showing Dist. Z1, C-phase
at Rampura end & Dist. Z1 at Bashundhara end and was switched on at 05:56(19/04/2022).
v) Rampura- Gulshan 132 kV Ckt-1 was shutdown at 06:55(19/04/2022) for C/M.
w) Khulna(C)- Noapara 132 kV Ckt-1 was shutdown at 07:00(19/04/2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 233 | 5565000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6487236 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2240409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 8888320
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 331 | 5212000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8556050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 91 | 2211840 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3205615 | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 78 | 1817784 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1324538
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 399384 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 424000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2081981
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 308 | 7031939 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1995552 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1295640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 3118080 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1209808
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1321025
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1223700 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 825800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 757200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1133280 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 6543707 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 2546351
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 1104374
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 1072660
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3501216
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2443200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2488320
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2393280 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 185071
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1211040
| Dhaka area Total |  |  |  | 5998 | 4368 | 91815400
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 520759
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137430
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 799200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 64 | 1607302 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4920756
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1639272
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 938720 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 254420 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1043760 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 2050560 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 417130
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 1918080 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 295 | 6814691
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1339721
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2362717
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2217600
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2682218
| Chattogram area Total |  |  |  | 2382 | 1493 | 31693496
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 120 | 2939000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 6928300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 210 | 5017000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 792 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1194133
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 3251781 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 1161288
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2370940 | Gas shortage
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4417920
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 495540
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 216540 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3651840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 745600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 977731 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 475040 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1322304
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 1505940 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 527520 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 845640 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 2013120 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1841 | 40057969
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2455680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 416700
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3607200 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1801200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 267160
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 532800
| Mymensingh Area Total |  |  |  | 622 | 426 | 9091940
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 950850 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3556636
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 5186000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 370800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 5 | 142920 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 181488
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1301184 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1941120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 7577180 | ST trip
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 15 | 286160 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 22 | 425688
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7127500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9184000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 175860
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9098900
| Sylhet Area Total |  |  |  | 2477 | 1834 | 47506286
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22325090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 381120 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 635040 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 4185600 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 388480 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 7298208 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 282750 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 679680
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 1794720 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2433168
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 566640
| Khulna Area Total |  |  |  | 2384 | 1869 | 40970496
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1652448
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 40 | 750774
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 1999175 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 555300
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 218 | 4769155
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 57 | 2550000 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 512 | 12276852
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 796576 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 27 | 682470 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 558032 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 468909 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 198 | 2498655 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 4202318
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9323781
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 738956 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 490800
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244710
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 788640 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 1654176 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 171 | 1107889 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2733888
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2511552
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25080
| Rajshahi Area Total |  |  |  | 2179 | 1560 | 28826432
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1796509
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 249 | 6026800
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 44000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 2335824
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33113
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2278848
| Rangpur Area Total |  |  |  | 720 | 567 | 12515094
| Total |  |  |  | 21734 | 14470 | 314753965
| Eastern Grid Total |  |  |  | 14493 | 9962 | 220165091
| Western Grid Total |  |  |  | 7241 | 4508 | 94588874
| National Grid Total |  |  |  | 21734 | 14470 | 314753965
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-18
(a) ENTIRE EASTERN GRID : |  | 9297.5 | MW | (b) ENTIRE WESTERN GRID : |  | 4693.4 | MW
i) Dhaka area |  | 5102.9 | MW | i) Khulna area |  | 1812 | MW
ii) Chittagong area |  | 1333.6 | MW | ii) Rajshahi area |  | 1618.4 | MW
iii) Comilla area |  | 1305 | MW | iii) Barisal area |  | 446 | MW
iv) Mymensingh area |  | 1058 | MW | iv) Rangpur area |  | 817 | MW
v) Sylhet area |  | 498 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13990.9 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 19:00 | Hasnabad | 84 | 23:00 | Palashbari | 120 | 01:00
Agargaon | 103 | 13:00 | Hathazari | 106 | 19:00 | Panchagarh | 52 | 19:30
Agrabad | 90 | 15:00 | Ishurdi | 80 | 21:00 | Patuakhali | 142 | 21:00
AKS | 14 | 19:00 | Jaldhaka | 53 | 19:30 | PHP | 10 | 17:00
AKSML | 6 | 07:00 | Jamalpur | 154 | 07:00 | Purbachal | 20 | 20:00
Amnura | 65 | 22:00 | Jashore | 141 | 19:30 | Purbasadipur | 112 | 19:30
Ashuganj | 36 | 21:00 | Jhenaidah | 139 | 21:00 | Rahim | 30 | 12:00
Bagerhat | 109 | 21:00 | Joydebpur | 190 | 09:00 | Rajbari | 74 | 03:00
Bakulia | 131 | 16:00 | Joypurhat | 70 | 00:00 | Rajendrapur | 120 | 23:00
Banani | 51 | 15:00 | Juldah | 31 | 16:00 | Rajshahi | 177 | 00:00
Bangabhaban | 22 | 10:00 | Kabirpur | 319 | 12:00 | Rajshahi | 47 | 23:00
Barapukuria | 88 | 20:00 | Kachua | 82 | 19:30 | Ramganj | 102 | 22:00
Barguna | 20 | 21:00 | Kallyanpur | 96 | 18:30 | Rampur | 17 | 00:00
Barishal | 110 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 14 | 19:00
Barishal | 66 | 21:00 | Kamrangirchar | 74 | 15:00 | Rangpur | 138 | 18:00
Baroaulia | 81 | 03:00 | Kaptai | 5 | 19:00 | Ruppur | 5 | 15:00
Baroirhat | 45 | 21:00 | Kazla | 90 | 19:30 | Saidpur | 98 | 20:00
Bashundhara | 190 | 15:00 | Keranigonj | 72 | 19:30 | Satkhira | 132 | 21:00
BashundharaCement | 12 | 00:00 | Khagrachori | 28 | 19:00 | Satmasjid | 115 | 19:00
Beanibazar | 58 | 18:30 | Khulna | 94 | 19:00 | Savar | 197 | 15:00
Benapole | 64 | 20:00 | Khulshi | 189 | 11:00 | Shahjadpur | 127 | 21:00
Bhaluka | 126 | 11:00 | Kishoreganj | 134 | 04:00 | Shahjibazar | 111 | 23:00
Bhandaria | 62 | 21:00 | Kodda | 310 | 09:00 | Shahmirpur | 44.2 | 16:00
Bhangura | 46 | 21:00 | KSRM | 22.5 | 03:00 | Shariatpur | 74 | 20:00
Bheramara(GK) | 69 | 21:00 | Kulaura | 46 | 21:00 | Sherpur | 134 | 19:00
Bhulta | 244 | 15:00 | Kurigram | 48 | 19:00 | Shikalbaha | 39 | 00:00
Bog-Sherpur | 68 | 03:00 | Kushtia | 146 | 19:30 | Shitalakhya | 128 | 16:00
Bogura | 188 | 21:00 | Lalbag | 95 | 14:00 | Sholosohor | N/A | N/A
Borhanuddin | 48 | 19:30 | Lalmonirhat | 38 | 21:00 | Shyampur | 180 | 10:00
Brahmanbaria | 154 | 02:00 | Madanganj | 159 | 12:00 | Siddhirganj | 118 | 14:00
BSRM | 165 | 02:00 | Madaripur | 113 | 20:00 | Sirajganj | 124 | 20:00
Cantonment | 155 | 14:00 | Madartek | 88 | 22:00 | Sonargaon | 104 | 15:00
Chandpur | 80 | 22:00 | Madunaghat | 65 | 21:00 | Sreemongol | 63 | 21:00
Chandraghona | 32 | 00:00 | Magura | 68 | 21:00 | Srinagar | 46.82 | 22:00
Chapai | 67 | 23:00 | Mahasthangarh | 80 | 00:00 | SSM | 0 | 00:00
Charsaidpur | 34 | 08:00 | Manikganj | 100 | 19:00 | Sunamganj | 46 | 20:00
Chauddagram | 67 | 22:00 | Maniknagar | 83 | 15:00 | Sylhet | 137 | 22:00
Chhatak | 28 | 21:00 | Matarbari | 43 | 22:00 | Tangail | 244 | 18:30
Chowmuhani | 234 | 22:00 | Matuail | 70 | 08:00 | Thakurgaon | 85 | 20:00
Chuadanga | 118 | 21:00 | Millgate | 64 | 14:00 | TK | N/A | N/A
Coxsbazar | 125 | 19:00 | Mirpur | 140 | 19:00 | Tongi | 129 | 13:00
Cumilla(N) | 163 | 22:00 | Mirsorai | N/A | N/A | Ullon | 44 | 21:00
Cumilla(S) | 166 | 14:00 | Mithapukur | 35 | 19:30 | Uttara | 86 | 15:00
Daudkandi | 154 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 25 | 11:00
Dhaka | 39 | 14:00 | Mogbazar | 143 | 15:00 | Zigatola | 46 | 16:00
Dhamrai | 114 | 14:00 | Mongla | 46 | 09:00
Dhanmondi | 372 | 15:00 | Motijheel | 37 | 13:00
Dohazari | 92 | 00:00 | Munshiganj | 110 | 21:00
Faridpur | 155 | 19:30 | Mymensingh | 229 | 22:00
Fatullah | 67 | 10:00 | Naogaon | 134 | 22:00
Fenchuganj | 39 | 00:00 | Narail | 60 | 21:00
Feni | 139 | 21:00 | Narinda | 80 | 13:00
Ghorashal | 86 | 02:00 | Narshingdi | 199 | 23:00
Goalpara | 30 | 21:00 | Natore | 158 | 21:00
Gollamari | 58 | 23:00 | Nawabganj | 62 | 21:00
Gopalganj | 107 | 21:00 | Netrakona | 107 | 03:00
GPH | 87 | 20:00 | New | 87.2 | 10:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 24:00 | 397 | 3:00 | Kaliakoir | 390 | 0.083333 | 376 | 0.66667
| Bheramara | 396 | 8:00 | 387 | 15:00 | Bhulta | 400 | 0.25 | 387 | 0.5
| Ashuganj(N) | 405 | 6:00 | 392 | 12:00 | Gopalganj | 409 | 0.625 | 361 | 0.875
| Payra | 0 | 1:00 | 0 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 7:00 | 230 | 1:00 | Hathazari | 238 | 18:30 | 230 | 13:00
| Ishurdi | 233 | 2:00 | 224 | 19:00 | Megnaghat | 230 | 6:00 | 225 | 10:00
| Ashuganj | 244 | 6:00 | 236 | 11:00 | Fenchuganj | 241 | 6:00 | 235 | 21:00
| Serajganj | 236 | 5:00 | 231 | 19:00 | Siddhirganj | 231 | 6:00 | 222 | 4:00
| Baghabari | 235 | 5:00 | 228 | 19:30 | Maniknagar | 226 | 6:00 | 219 | 12:00
| Barapukuria | 231 | 5:00 | 220 | 19:30 | Agargaon | 226 | 10:00 | 216 | 12:00
| Bogra | 231 | 6:00 | 221 | 19:30 | Barisal | 240 | 10:00 | 228 | 19:00
| Rajshahi | 228 | 9:00 | 216 | 19:00 | Bhola 225 MW | 243 | 10:00 | 228 | 19:00
| Khulna South | 238 | 9:00 | 224 | 19:00 | AKSML
| Rampura | 228 | 6:00 | 220 | 12:00 | BSRM | 238 | 7:00 | 228 | 13:00
| Haripur | 227 | 6:00 | 220 | 11:00 | Bibiyana | 237 | 8:00 | 233 | 14:00
| Hasnabad | 226 | 5:00 | 217 | 13:00 | Bhulta | 231 | 7:00 | 223 | 12:00
| Shyampur | 227 | 6:00 | 218 | 12:00 | Ashuganj (S) | 240 | 6:00 | 233 | 13:00
| Aminbazar | 225 | 1:00 | 213 | 2:00 | Kaliakoir | 227 | 5:00 | 219 | 12:00
| Tongi | 227 | 19:00 | 220 | 10:00 | GPH | 238 | 7:00 | 228 | 4:00
| Comilla (N) | 233 | 6:00 | 226 | 12:00 | Jhenaidah | 229 | 8:00 | 213 | 19:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 139 | 05:00 | 132 | 12:00 | Manikganj | 132 | 04:00 | 126 | 12:00
| Agargaon | 140 | 06:00 | 132 | 12:00 | Maniknagar | 131 | 08:00 | 124 | 13:00
| Agrabad | 136 | 05:00 | 130 | 11:00 | Matarbari | 125 | 12:00 | 112 | 01:00
| AKS | 136 | 06:00 | 130 | 10:00 | Matuail | 135 | 04:00 | 130 | 12:00
| Aminbazar | 140 | 01:00 | 134 | 11:00 | Millgate | 138 | 05:00 | 128 | 13:00
| Amnura | 137 | 08:00 | 129 | 19:00 | Mirpur | 139 | 04:00 | 132 | 10:00
| Ashuganj | 139 | 08:00 | 134 | 15:00 | Mithapukur | 134 | 05:00 | 123 | 19:30
| Bagerhat | 135 | 09:00 | 126 | 00:00 | Modern | 136 | 18:00 | 130 | 11:00
| Bakulia | 134 | 05:00 | 130 | 12:00 | Mogbazar | 139 | 05:00 | 131 | 13:00
| Banani | 137 | 05:00 | 130 | 11:00 | Mongla | 134 | 08:00 | 126 | 00:00
| Bangabhaban | 132 | 06:00 | 122 | 16:00 | Motijheel | 132 | 06:00 | 122 | 16:00
| Barapukuria | 134 | 05:00 | 126 | 19:30 | Munshiganj | 139 | 06:00 | 133 | 12:00
| Barguna | 141 | 10:00 | 123 | 19:00 | Mymensingh | 128 | 08:00 | 113 | 15:00
| Barishal | 139 | 10:00 | 127 | 00:00 | Naogaon | 129 | 06:00 | 117 | 19:30
| Barishal | 139 | 10:00 | 128 | 19:00 | Narail | 136 | 08:00 | 123 | 19:00
| Baroaulia | 138 | 06:00 | 131 | 23:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 136 | 08:00 | 128 | 00:00 | Narshingdi | 130 | 06:00 | 122 | 00:00
| Bashundhara | 137 | 05:00 | 129 | 12:00 | Natore | 136 | 18:00 | 129 | 19:00
| BashundharaCement | 137 | 04:00 | 132 | 12:00 | Nawabganj | 139 | 03:00 | 132 | 11:00
| Beanibazar | 138 | 02:00 | 127 | 20:00 | Netrakona | 125 | 07:00 | 110 | 17:00
| Benapole | 136 | 08:00 | 127 | 19:00 | New | 138 | 06:00 | 131 | 11:00
| Bhaluka | 124 | 08:00 | 108 | 17:00 | Niamatpur | 123 | 05:00 | 110 | 20:00
| Bhandaria | 137 | 11:00 | 121 | 19:00 | Noapara | 137 | 08:00 | 131 | 00:00
| Bhangura | 135 | 05:00 | 128 | 21:00 | Pabna | 134 | 05:00 | 127 | 21:00
| Bheramara | 137 | 08:00 | 131 | 19:00 | Palashbari | 130 | 05:00 | 123 | 19:30
| Bheramara(GK) | 138 | 07:00 | 132 | 19:00 | Panchagarh | 136 | 05:00 | 122 | 19:30
| Bhulta | 128 | 07:00 | 123 | 13:00 | Patuakhali | 139 | 09:00 | 121 | 19:00
| Bog-Sherpur | 134 | 05:00 | 126 | 20:00 | PHP | 135 | 07:00 | 127 | 15:00
| Bogura | 135 | 05:00 | 128 | 20:00 | Purbachal | 137 | 04:00 | 130 | 11:00
| Bogura | 136 | 06:00 | 128 | 19:30 | Purbasadipur | 135 | 05:00 | 121 | 22:00
| Brahmanbaria | 133 | 08:00 | 128 | 02:00 | Rahim | 135 | 03:00 | 131 | 12:00
| Cantonment | 139 | 06:00 | 131 | 12:00 | Rajbari | 136 | 09:00 | 123 | 19:00
| Chandpur | 140 | 07:00 | 133 | 13:00 | Rajendrapur | 138 | 07:00 | 128 | 12:00
| Chandraghona | 138 | 06:00 | 132 | 13:00 | Rajshahi | 138 | 05:00 | 131 | 19:00
| Chapai | 137 | 05:00 | 129 | 21:00 | Rajshahi | 138 | 06:00 | 131 | 19:00
| Charsaidpur | 139 | 07:00 | 132 | 18:00 | Ramganj | 136 | 07:00 | 127 | 21:00
| Chauddagram | 136 | 08:00 | 129 | 15:00 | Rampur | 135 | 19:00 | 129 | 15:00
| Chhatak | 135 | 01:00 | 126 | 20:00 | Rampura | 139 | 06:00 | 132 | 12:00
| Chowmuhani | 130 | 06:00 | 124 | 22:00 | Rangamati | 137 | 06:00 | 131 | 13:00
| Chuadanga | 133 | 08:00 | 118 | 21:00 | Rangpur | 130 | 02:00 | 121 | 19:30
| Coxsbazar | 122 | 09:00 | 109 | 01:00 | Ruppur | 137 | 05:00 | 131 | 18:30
| Cumilla(N) | 137 | 07:00 | 130 | 03:00 | Saidpur | 134 | 05:00 | 123 | 19:30
| Cumilla(S) | 138 | 08:00 | 122 | 14:00 | Satkhira | 135 | 08:00 | 123 | 19:00
| Daudkandi | 136 | 20:00 | 129 | 02:00 | Satmasjid | 139 | 05:00 | 132 | 11:00
| Dhaka | 139 | 06:00 | 131 | 15:00 | Savar | 140 | 04:00 | 132 | 15:00
| Dhamrai | 134 | 04:00 | 128 | 12:00 | Shahjadpur | 136 | 07:00 | 132 | 19:00
| Dhanmondi | 139 | 06:00 | 130 | 12:00 | Shahjibazar | 137 | 10:00 | 133 | 00:00
| Dohazari | 129 | 19:00 | 123 | 01:00 | Shahmirpur | 135 | 04:00 | 130 | 13:00
| Faridpur | 136 | 09:00 | 123 | 19:00 | Shariatpur | 135 | 10:00 | 121 | 19:00
| Fatullah | 135 | 22:00 | 128 | 12:00 | Sherpur | 128 | 08:00 | 112 | 17:00
| Fenchuganj | 138 | 03:00 | 133 | 20:00 | Shikalbaha | 136 | 18:30 | 131 | 13:00
| Feni | 135 | 08:00 | 128 | 13:00 | Shikalbaha | 136 | 07:00 | 130 | 15:00
| Ghorashal | 139 | 08:00 | 135 | 00:00 | Shitalakhya | 139 | 01:00 | 132 | 12:00
| Goalpara | 138 | 08:00 | 133 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 137 | 08:00 | 32 | 01:00 | Shyampur | 134 | 04:00 | 129 | 10:00
| Gopalganj | 138 | 07:00 | 128 | 19:00 | Shyampur | 135 | 18:30 | 128 | 12:00
| Gopalganj_I | 139 | 02:00 | 124 | 19:00 | Siddhirganj | 135 | 04:00 | 131 | 11:00
| Gulshan | 138 | 05:00 | 131 | 12:00 | Sirajganj | 132 | 05:00 | 125 | 19:30
| Halishahar | 136 | 06:00 | 130 | 13:00 | Sonargaon | 135 | 03:00 | 131 | 13:00
| Haripur | 135 | 03:00 | 131 | 12:00 | Sreemongol | 137 | 06:00 | 132 | 23:00
| HaripurSBU | 137 | 06:00 | 131 | 12:00 | Srinagar | 139 | 06:00 | 133 | 00:00
| Hasnabad | 136 | 04:00 | 132 | 00:00 | SSM | 140 | 05:00 | 131 | 13:00
| Hathazari | 138 | 18:30 | 132 | 13:00 | Sunamganj | 135 | 01:00 | 124 | 20:00
| Ishurdi | 137 | 05:00 | 131 | 19:00 | Sylhet | 135 | 02:00 | 130 | 20:00
| Jaldhaka | 133 | 05:00 | 120 | 20:00 | Tangail | 130 | 06:00 | 121 | 17:00
| Jamalpur | 129 | 08:00 | 116 | 17:00 | Thakurgaon | 137 | 05:00 | 121 | 11:00
| Jashore | 136 | 10:00 | 128 | 19:00 | TK | N/A | N/A | N/A | N/A
| Jhenaidah | 140 | 10:00 | 128 | 21:00 | Tongi | 137 | 03:00 | 133 | 11:00
| Jhenaidah | 140 | 08:00 | 129 | 19:00 | Ullon | 139 | 06:00 | 131 | 12:00
| Joydebpur | 141 | 07:00 | 133 | 12:00 | Uttara | 138 | 02:00 | 131 | 17:00
| Joypurhat | 125 | 05:00 | 114 | 19:30 | UttaraNew | 136 | 03:00 | 131 | 11:00
| Juldah | 137 | 05:00 | 132 | 11:00 | Zigatola | 139 | 02:00 | 133 | 12:00
| Kabirpur | 139 | 07:00 | 130 | 12:00
| Kachua | 138 | 07:00 | 130 | 18:30
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 139 | 06:00 | 132 | 13:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 139 | 05:00 | 132 | 12:00
| Kaptai | 135 | 00:00 | 132 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 282 | 9480 | 4319 | 13799 |  |  |  | QF-LDC-11
0:30 | 308 | 9327.5 | 4061 | 13388.5 | Date: | 2022-04-18
1:00 | 334 | 9175 | 3803 | 12978
1:30 | 295 | 8957 | 3806 | 12763
2:00 | 256 | 8739 | 3809 | 12548
2:30 | 307 | 8778.5 | 3914.5 | 12693 | [5 empty] | Gen. at Eve. Peak | 14470 | 14470 MW (21:00 )
3:00 | 358 | 8818 | 4020 | 12838 | [6 empty] | 21:00
3:30 | 330 | 8840 | 3882 | 12722 | [5 empty] | Gen. at Day Peak | 12320 | 12320 MW (12:00 )
4:00 | 302 | 8862 | 3744 | 12606 | [6 empty] | 12:00
4:30 | 260 | 8695.5 | 3686 | 12381.5 | [5 empty] | Highest Generation | 14509
5:00 | 218 | 8529 | 3628 | 12157 | [6 empty] | 22:00
5:30 | 242 | 8359.5 | 3468.5 | 11828
6:00 | 266 | 8190 | 3309 | 11499
6:30 | 258 | 8165 | 3263.5 | 11428.5
7:00 | 250 | 8140 | 3218 | 11358
7:30 | 206 | 8142 | 3228 | 11370
8:00 | 162 | 8144 | 3238 | 11382
8:30 | 111 | 8219.5 | 3311 | 11530.5
9:00 | 60 | 8295 | 3384 | 11679
9:30 | 63 | 8431.5 | 3408 | 11839.5
10:00 | 66 | 8568 | 3432 | 12000
10:30 | 104 | 8530 | 3457 | 11987
11:00 | 142 | 8492 | 3482 | 11974
11:30 | 107 | 8605 | 3542 | 12147
12:00 | 72 | 8718 | 3602 | 12320
12:30 | 73 | 8861 | 3705.5 | 12566.5
13:00 | 74 | 9004 | 3809 | 12813
13:30 | 74 | 9164.5 | 3840.5 | 13005
14:00 | 74 | 9325 | 3872 | 13197
14:30 | 49 | 9311.5 | 3920 | 13231.5
15:00 | 24 | 9298 | 3968 | 13266
15:30 | 37 | 9264 | 3863.5 | 13127.5
16:00 | 50 | 9230 | 3759 | 12989
16:30 | 36 | 9125.5 | 3864 | 12989.5
17:00 | 22 | 9021 | 3969 | 12990
17:30 | 36 | 8958 | 3929.5 | 12887.5
18:00 | 50 | 8895 | 3890 | 12785
18:30 | 184 | 9286.5 | 4021 | 13307.5
19:00 | 318 | 9678 | 4152 | 13830
19:30 | 358 | 10007 | 4354 | 14361
20:00 | 376 | 9921 | 4429 | 14350 |  |  |  | Executive Engineer
20:30 | 345 | 9941.5 | 4468.5 | 14410 |  |  |  | Network Operation Division
21:00 | 314 | 9962 | 4508 | 14470
21:30 | 288 | 9935.5 | 4554 | 14489.5
22:00 | 262 | 9909 | 4600 | 14509 |  |  |  |  | Page 6 of 7
22:30 | 229 | 9821 | 4563.5 | 14384.5
23:00 | 196 | 9733 | 4527 | 14260
23:30 | 239 | 9606.5 | 4423 | 14029.5
24:00 | 282 | 9480 | 4319 | 13799
14470 MW (21:00 )
12320 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-18 |  | Energy |  | 314753965
[13 empty] | 2022-04-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4234 | 923 | 2180 | 849 | 4137 | 323 | 65 | 417 | 726 | 162 | 0 | 0
0:30 | 4310 | 923 | 2028 | 670 | 4038.5 | 324.5 | 66.5 | 380 | 668 | 160 | 0 | 0 | Date: | 2022-04-18
1:00 | 4386 | 923 | 1876 | 491 | 3940 | 326 | 68 | 343 | 610 | 158 | 0 | 0
1:30 | 4330.5 | 923.5 | 1823.5 | 327 | 3960 | 370.5 | 68.5 | 336.5 | 603.5 | 156 | 0 | 0 | [8 empty] | Total Energy | 314.754 | Total Energy Gen 314.754 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 314.754 MKWHr
2:00 | 4275 | 924 | 1771 | 163 | 3980 | 415 | 69 | 330 | 597 | 154 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4296.5 | 923.5 | 1807.5 | 159.5 | 4007 | 480 | 69 | 330 | 595 | 155 | 0 | 0 | [8 empty] | Energy Requirement | 314.754
3:00 | 4318 | 923 | 1844 | 156 | 4034 | 545 | 69 | 330 | 593 | 156 | 0 | 0
3:30 | 4334 | 923.5 | 1882 | 120.5 | 4011 | 434.5 | 68 | 330 | 592.5 | 156 | 0 | 0 | [6 empty] | Shortage
4:00 | 4350 | 924 | 1920 | 85 | 3988 | 324 | 67 | 330 | 592 | 156 | 0 | 0
4:30 | 4254.5 | 923.5 | 1843 | 42.5 | 4024 | 324 | 67 | 310 | 571 | 152 | 0 | 0
5:00 | 4159 | 923 | 1766 | 0 | 4060 | 324 | 67 | 290 | 550 | 148 | 0 | 0
5:30 | 4031 | 922.5 | 1737.5 | 0 | 3910 | 324.5 | 67.5 | 270 | 549 | 144 | 2 | 0
6:00 | 3903 | 922 | 1709 | 0 | 3760 | 325 | 68 | 250 | 548 | 140 | 4 | 0
6:30 | 3852 | 922.5 | 1737 | 0 | 3708 | 325 | 67.5 | 250 | 548 | 137 | 11.5 | 0 |  |  |  |  | Coal
7:00 | 3801 | 923 | 1765 | 0 | 3656 | 325 | 67 | 250 | 548 | 134 | 19 | 0
7:30 | 3811.5 | 922.5 | 1807 | 0 | 3589.5 | 325 | 68.5 | 250 | 548 | 133 | 45 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3822 | 922 | 1849 | 0 | 3523 | 325 | 70 | 250 | 548 | 132 | 71 | 0
8:30 | 3897 | 921.5 | 1897 | 0 | 3532 | 325.5 | 67.5 | 250 | 545.5 | 135 | 89.5 | 0
9:00 | 3972 | 921 | 1945 | 0 | 3541 | 326 | 65 | 250 | 543 | 138 | 108 | 0
9:30 | 4068.5 | 921.5 | 1995 | 0 | 3566.5 | 325.5 | 65 | 250 | 533.5 | 141 | 103 | 0
10:00 | 4165 | 922 | 2045 | 0 | 3592 | 325 | 65 | 250 | 524 | 144 | 98 | 0
10:30 | 4129.5 | 922 | 2072 | 0 | 3535 | 328 | 65.5 | 250 | 524 | 146 | 145 | 0
11:00 | 4094 | 922 | 2099 | 0 | 3478 | 331 | 66 | 250 | 524 | 148 | 192 | 0
11:30 | 4166.5 | 922 | 2172 | 0 | 3543 | 328.5 | 66 | 252.5 | 514 | 147 | 165.5 | 0
12:00 | 4239 | 922 | 2245 | 0 | 3608 | 326 | 66 | 255 | 504 | 146 | 139 | 0
12:30 | 4233.5 | 922 | 2262.5 | 70.5 | 3710.5 | 326 | 66 | 315 | 521.5 | 151 | 140.5 | 0
13:00 | 4228 | 922 | 2280 | 141 | 3813 | 326 | 66 | 375 | 539 | 156 | 142 | 0
13:30 | 4228 | 922 | 2280 | 141 | 3813 | 326 | 66 | 375 | 539 | 156 | 142 | 0
14:00 | 4228 | 922 | 2280 | 141 | 3813 | 326 | 66 | 375 | 539 | 156 | 142 | 0
14:30 | 4172.5 | 922 | 2268.5 | 361.5 | 3857.5 | 326.5 | 64 | 390.5 | 572 | 160 | 136 | 0
15:00 | 4117 | 922 | 2257 | 582 | 3902 | 327 | 62 | 406 | 605 | 164 | 130 | 0
15:30 | 4136.5 | 922 | 2239 | 481 | 3995.5 | 212 | 62 | 408 | 611.5 | 163 | 106 | 0
16:00 | 4156 | 922 | 2221 | 380 | 4089 | 97 | 62 | 410 | 618 | 162 | 82 | 0
16:30 | 4122 | 922 | 2237.5 | 252.5 | 4129.5 | 210.5 | 62 | 392.5 | 624.5 | 162 | 60 | 0
17:00 | 4122 | 922 | 2254 | 125 | 4170 | 324 | 62 | 375 | 631 | 162 | 38 | 0
17:30 | 4075 | 922 | 2121.5 | 62.5 | 4309 | 324.5 | 62 | 327 | 677 | 163 | 21 | 0
18:00 | 4028 | 922 | 1989 | 0 | 4448 | 325 | 62 | 279 | 723 | 164 | 4 | 0
18:30 | 4149 | 922 | 2136.5 | 250 | 4392.5 | 325 | 62.5 | 310 | 756 | 162 | 2 | 0
19:00 | 4270 | 922 | 2284 | 500 | 4337 | 325 | 63 | 341 | 789 | 160 | 0 | 0
19:30 | 4336 | 923 | 2323 | 875 | 4336 | 324 | 64 | 409 | 820 | 160 | 0 | 0
20:00 | 4260 | 923 | 2308 | 968 | 4329 | 324 | 64 | 411 | 814 | 160 | 0 | 0
20:30 | 4263 | 922.5 | 2314 | 971 | 4367.5 | 324.5 | 64 | 420.5 | 814 | 161 | 0 | 0
21:00 | 4266 | 922 | 2320 | 974 | 4406 | 325 | 64 | 430 | 814 | 162 | 0 | 0
21:30 | 4259 | 922.5 | 2310 | 971.5 | 4440.5 | 325 | 64.5 | 431.5 | 815.5 | 164 | 0 | 0
22:00 | 4252 | 923 | 2300 | 969 | 4475 | 325 | 65 | 433 | 817 | 166 | 0 | 0
22:30 | 4251.5 | 922.5 | 2252 | 970 | 4427 | 325 | 65 | 433.5 | 789.5 | 165 | 0 | 0
23:00 | 4251 | 922 | 2204 | 971 | 4379 | 325 | 65 | 434 | 762 | 164 | 0 | 0
23:30 | 4242.5 | 922.5 | 2192 | 910 | 4258 | 324 | 65 | 425.5 | 744 | 163 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 4234 | 923 | 2180 | 849 | 4137 | 323 | 65 | 417 | 726 | 162 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 314.754 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 314.754 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 68 | 69 | 69 | 67 | 67 | 68 | 67 | 70 | 65 | 65 | 66 | 66 | 66 | 65 | 62 | 62 | 62 | 62 |  | 63 | 64 | 64 | 64 | 65 | 65 | 65 | 1607302
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 13 | 20 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 520759
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 3 | 11 | 12 | 18 | 19 | 18 | 18 | 16 | 12 | 7 | 3 | 0 | [8 empty] | 137430
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 204 | 203 | 204 | 202 | 203 | 203 | 203 | 203 | 226 | 203 | 216 | 217 | 203 | 218 | 203 | 205 | 203 |  | 208 | 217 | 211 | 204 | 204 | 203 | 203 | 4920756
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 39 |  | 51 | 51 | 51 | 51 | 51 | 17 | 0 | 254420
12 | Hathazari 100 MW peaking PP | 50 | 50 | 51 | 51 | 50 | 50 | 50 | 50 | 46 | 26 | 26 | 8 | 0 |  | 28 | 40 | 47 | 47 |  | 47 | 48 | 48 | 48 | 47 | 48 | 46 | 938720
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 80 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 70 | 51 | 1639272
| Daudkandi 200 MW PP (B.Trac) | 100 | 10 | 10 | 0 | [8 empty] | 0 | 100 | 60 | 10 | 10 |  |  | 100 | 200 | 200 | 200 | 200 | 200 | 160 | 1322304
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 47 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 47 | 47 | 48 | 1161288
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 60 | 97 | 97 | 0 | [20 empty] | 0 | 424000
17 | Siddhirganj 335 MW CCPP | 310 | 310 | 306 | 306 | 270 | 250 | 250 | 250 | 255 | 280 | 250 | 305 | 308 | 305 | 308 | 307 | 306 | 270 |  | 307 | 308 | 308 | 308 | 300 | 295 | 295 | 7031939
18 | Kodda 300 MW PP Unit-2 (Summit) | 270 | 273 | 275 | 275 | 275 | 275 | 273 | 270 | 273 | 270 | 265 | 278 | 278 | 265 | 265 | 263 | 275 | 275 |  | 275 | 275 | 264 | 270 | 270 | 280 | 275 | 6543707
19 | Ashuganj 195MW PP (APSCL-United) | [24 empty] | 0 | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 233 | 233 | 235 | 235 | 235 | 235 | 234 | 234 | 233 | 234 | 234 | 234 | 232 | 230 | 230 | 230 | 231 | 200 |  | 233 | 233 | 232 | 233 | 233 | 233 | 233 | 5565000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6487236
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [15 empty] | 0 | [9 empty] | 0 | 792
33 | Ashuganj 225 MW CCPP | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 117 | 113 | 130 | 136 | 136 | 128 | 114 | 113 | 114 | 114 | 114 |  | 121 | 121 | 121 | 120 | 120 | 136 | 139 | 2939000
34 | Ashuganj 450 MW CCPP(South) | 195 | 195 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 200 | 200 | 200 | 200 |  | 210 | 220 | 220 | 210 | 210 | 200 | 200 | 5017000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 285 | 275 | 270 | 270 | 270 | 265 | 265 | 265 | 265 | 265 |  | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 6928300
35 | Ashuganj 55 MW PP (Precision) | [24 empty] | 0
36 | Chandpur 150 MW CCPP | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2370940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 392 | 370 | 399 | 386 | 286 | 272 | 272 | 272 | 295 | 341 | 383 | 400 | 398 | 396 | 396 | 395 | 365 |  | 365 | 396 | 396 | 397 | 395 | 394 | 393 | 8888320
40 | Meghnaghat 450 MW CCPP(MPL) | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 350 | 370 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8556050
41 | Haripur 360MW CCPP(HPL) |  |  | 0 | 35 | 63 | 99 | 140 | 242 | 242 | 272 | 272 | 323 | 322 | 322 | 322 | 310 | 320 | 253 |  | 317 | 327 | 330 | 331 | 331 | 252 | 252 | 5212000
42 | RPCL 210MW CCPP | 107 | 107 | 109 | 108 | 129 | 129 | 129 | 120 | 120 | 109 | 109 | 109 | 102 | 100 | 96 | 97 | 71 | 76 |  | 80 | 88 | 106 | 106 | 106 | 106 | 102 | 2455680
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 6 | 13 | 23 | 15 | 44 | 13 | 48 | 38 | 12 | 21 | 9 | 1 | [8 empty] | 267160
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 950850
46 | Shajibazar 330 MW CCPP | 268 | 270 | 269 | 269 | 270 | 268 | 271 | 268 | 270 | 270 | 269 | 265 | 261 | 267 | 153 | 157 | 154 | 156 |  | 156 | 158 | 157 | 158 | 160 | 159 | 159 | 5186000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 60 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1301184
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 78 | 81 | 81 | 81 | 79 | 79 | 80 | 80 | 80 |  | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 1941120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 140 | 140 | 139 | 139 | 139 | 139 | 139 | 164 | 205 | 219 | 219 | 220 | 219 | 220 | 219 | 219 | 219 |  | 219 | 219 | 140 | 140 | 140 | 140 | 140 | 7577180
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 17 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 286160
53 | Sylhet 10MW PP (Desh) | 10 | 0 | [5 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 175860
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 181488
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 370800
56 | Shahjahanulla 25 MW PP | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 |  | 15 | 15 | 15 | 22 | 22 | 24 | 18 | 425688
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 300 | 290 | 270 | 280 | 295 | 280 | 290 | 300 | 280 | 300 | 300 | 290 | 300 | 290 | 290 | 275 |  | 295 | 315 | 305 | 310 | 295 | 280 | 280 | 7127500
| Bibiyana South 400 MW | 400 | 400 | 401 | 401 | 354 | 300 | 300 | 330 | 330 | 401 | 400 | 391 | 389 | 400 | 383 | 398 | 397 | 360 |  | 396 | 396 | 396 | 400 | 400 | 401 | 401 | 9098900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1321025
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 532800
60 | Barabkunda 22 MW PP (Regent) | [25 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 10 | 10 | 18 | 18 | 18 | 18 | 399384
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 416700
63 | Impoprt (Tripura) | 158 | 154 | 156 | 156 | 148 | 140 | 134 | 132 | 138 | 144 | 148 | 146 | 156 | 166 | 164 | 162 | 162 | 164 |  | 160 | 160 | 160 | 162 | 166 | 164 | 162 | 3651840
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 33 | 33 | 34 | 31 | 4 | 2 | 2 | 2 | 2 | 2 | 10 | 2 | 2 | 2 | 3 | 16 |  | 19 | 25 | 21 | 28 | 29 | 30 | 32 | 417130
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 495540
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 216540
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 30 | 29 | 28 | 31 | 20 | 24 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 745600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 18 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 475040
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 26 | 26 | 26 | 26 | 26 | 26 |  | 23 | 23 | 27 | 27 | 27 | 27 | 28 | 623700
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 825800
72 | Rupganj 33 MW PP(Summit) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 757200
73 | Ghorashal 108MW PP (Regent) | 96 | 97 | 97 | 94 | 97 | 97 | 97 | 97 | 90 | 94 | 94 | 94 | 100 | 95 | 92 | 91 | 97 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 2240409
| Feni Lanka Power | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1505940
| Chowmuhani 113 MW | 18 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 42 | 69 |  | 54 | 39 | 39 | 38 | 39 | 38 | 39 | 527520
| Manikgonj 162MW PP(MPGL) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 72 | 72 | 72 | 72 | 72 | 72 | 54 | 54 | 35 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 90 | 2393280
77 | Siddhirganj 100 PP(Dutch Bangla) | 98 | 98 | 98 | 94 | 98 | 98 | 50 | 50 | 50 | 50 | 50 | 50 | 75 | 80 | 90 | 95 | 98 | 98 |  | 98 | 98 | 98 | 100 | 100 | 100 | 100 | 2081981
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 41 | 41 | 41 | 40 | 40 | 40 | 45 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 1133280
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3118080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 42 | 43 | 43 | 43 | 43 | 35 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 29 | 33 | 40 | 40 |  | 37 | 42 | 42 | 42 | 42 | 42 | 42 | 977731
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 98 | 90 | 90 | 90 | 90 | 90 | 105 | 90 | 90 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2443200
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0 | 1 | 2 | 3 | 4 | 2 | 5 | 4 | 2 | 3 | 2 | 1 | 0 | [8 empty] | 29160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 55 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1339721
| Karnaphuli Power Ltd. | 102 | 104 | 110 | 110 | 97 | 95 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 101 |  | 110 | 110 | 110 | 110 | 93 | 93 | 94 | 2362717
82 | Madanganj 102 PP(Summit) | 62 | 62 | 62 | 63 | 79 | 79 | 79 | 79 | 78 | 78 | 78 | 77 | 77 | 76 | 76 | 76 | 76 | 76 |  | 79 | 78 | 78 | 78 | 78 | 78 | 78 | 1817784
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 120 | 125 | 130 | 125 | 125 | 125 | 130 | 130 | 135 | 135 | 140 | 145 | 150 | 135 | 145 | 130 | 145 | 130 |  | 135 | 135 | 130 | 130 | 125 | 125 | 125 | 3205615
87 | Meghnaghat 100 MW(IEL) | 94 | 93 | 94 | 94 | 93 | 94 | 94 | 93 | 93 | 93 | 93 | 92 | 92 | 93 | 92 | 92 | 89 | 83 |  | 86 | 90 | 91 | 91 | 92 | 92 | 93 | 2211840
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 92 | 91 | 92 | 92 | 91 | 91 | 91 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2488320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 16 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 35 | 40 | 55 | 55 | 52 | 62 | 72 |  | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 1043760
92 | Fenchuganj 44MW (Energyprima) | 15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142920
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1194133
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 76 | 76 | 80 | 84 | 82 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1995552
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 18 | 12 | 12 | 12 | 16 | 34 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 799200
96 | Chattogram 108 MW PP (ECPV) | 86 | 91 | 95 | 95 | 91 | 88 | 90 | 78 | 88 | 72 | 49 | 48 | 48 | 48 | 55 | 86 | 88 | 89 |  | 89 | 89 | 91 | 96 | 91 | 89 | 90 | 1918080
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 48 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1324538
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 0 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1209808
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 163 | 110 | 110 | 110 | 110 | 110 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3556636
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1295640
104 | Keranigonj 300 MW PP (APR) | 107 | 33 | 76 | 35 | 0 | [6 empty] | 0 | 47 | 149 | 247 | 210 | 45 |  |  | 163 | 301 | 303 | 304 | 301 | 301 | 301 | 2546351
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | 50 | 25 | 25 | 0 | [6 empty] | 0 | 50 | 100 | 100 | 70 | 25 |  |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1104374
106 | Mymensingh 200 MW PP (United) | 143 | 143 | 143 | 143 | 143 | 143 | 145 | 145 | 146 | 145 | 145 | 163 | 142 | 141 | 140 | 139 | 140 | 178 |  | 179 | 179 | 179 | 180 | 180 | 178 | 105 | 3607200
112 | Aurahati 100MW PP (Aggreko) | 100 | 50 | 25 | 25 | 0 | [6 empty] | 0 | 44 | 99 | 95 | 70 | 25 |  |  | 96 | 99 | 99 | 99 | 97 | 99 | 98 | 1072660
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 143 | 149 | 149 | 149 | 149 | 149 | 149 | 139 | 133 | 131 | 115 | 120 | 140 | 149 | 149 | 134 | 144 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3501216
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2050560
116 | Chandpur 200MW (Desh energy) | 180 | 180 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 136 | 136 | 179 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 190 | 178 | 184 | 4417920
117 | Ashuganj 150MW PP (Midland) | 140 | 137 | 145 | 147 | 143 | 133 | 140 | 140 | 140 | 138 | 137 | 137 | 135 | 135 | 128 | 118 | 123 | 133 |  | 127 | 128 | 128 | 125 | 130 | 140 | 140 | 3251781
118 | Bibiyana-III 400 MW CCPP | 401 | 400 | 400 | 399 | 378 | 329 | 322 | 325 | 375 | 387 | 377 | 376 | 376 | 390 | 404 | 403 | 402 | 353 |  | 402 | 403 | 402 | 402 | 400 | 402 | 400 | 9184000
| Jamalpur 115 MW PP (United) | 68 | 68 | 68 | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 96 |  | 98 | 97 | 98 | 98 | 98 | 98 | 48 | 1801200
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 281 | 281 | 281 | 281 | 281 | 281 | 280 | 281 | 281 | 281 | 281 | 282 |  | 285 | 285 | 285 | 295 | 295 | 280 | 281 | 6814691
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 93 | 70 | 40 | 60 | 100 | 90 | 90 | 90 | 90 | 91 | 98 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 2217600
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 109 | 108 | 2682218
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 26 | 36 | 36 | 36 | 36 | 36 | 22 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 845640
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 5 | 12 | 12 | 15 | 25 | 22 | 11 | 28 | 21 | 6 | 6 | 1 | [8 empty] | 185071
| Chandpur 115(Doreen) | 101 | 101 | 101 | 101 | 99 | 51 | 51 | 51 | 51 | 51 | 51 | 55 | 76 | 67 | 86 | 101 | 100 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 2013120
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 49 | 38 | 37 | 37 | 37 | 37 | 37 | 43 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1211040
120 | Eastern Zone Total | 9175 | 8739 | 8818 | 8862 | 8529 | 8190 | 8140 | 8144 | 8295 | 8568 | 8492 | 8718 | 9004 | 9325 | 9298 | 9230 | 9021 | 8895 |  | 9678 | 10007 | 9921 | 9962 | 9909 | 9733 | 9480 | 220165091
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [9 empty] | 12 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 42 |  | 49 | 49 | 49 | 49 | 49 | 32 | 16 | 381120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 34 | 34 | 29 | 29 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 21 | 22 | 22 | 22 | 29 | 30 |  | 43 | 38 | 38 | 33 | 33 | 33 | 33 | 635040
| Khulna 225 MW CCPP | 200 | 200 | 200 | 200 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 125 | 200 | 200 | 198 | 200 | 180 | 120 |  | 180 | 200 | 200 | 200 | 200 | 200 | 200 | 4185600
129 | Rupsha 105 MW PP (Orion rupsha) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 1794720
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 4 | 32 | 54 | 39 | 97 | 71 | 50 | 84 | 75 | 41 | 17 | 2 | [8 empty] | 566640
131
132 | United Payra Power Ltd. | 0 | 48 | 72 | 27 | 97 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 150 | 150 | 150 |  |  |  |  | 57 | 150 | 150 | 150 | 2550000
133 | Bhola Nutan Biddut BD LTD (GAS) | 219 | 221 | 217 | 220 | 220 | 153 | 152 | 152 | 154 | 181 | 181 | 212 | 211 | 190 | 213 | 210 | 212 | 173 |  | 219 | 218 | 218 | 218 | 218 | 216 | 190 | 4769155
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 1652448
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 15 | 15 | 64 | 65 | 63 | 65 | 30 | 30 | 45 | 45 | 45 | 83 |  | 88 | 88 | 87 | 87 | 90 | 90 | 90 | 1999175
140 | Bhola 33 MW PP (Venture) | 38 | 37 | 36 | 36 | 33 | 30 | 26 | 24 | 23 | 23 | 21 | 23 | 28 | 27 | 26 | 27 | 27 | 30 |  | 37 | 38 | 39 | 40 | 40 | 39 | 39 | 750774
141 | Noapara 100 MW PP (Bangla Trac) | 30 | 10 | 10 | 0 | [10 empty] | 30 | 10 | 10 |  |  | 20 | 95 | 100 | 100 | 100 | 100 | 60 | 679680
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 282750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 11 | 55 |  | 80 | 68 | 60 | 63 | 63 | 56 | 50 | 388480
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 89 | 89 | 88 | 88 | 93 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 2433168
146 | Bheramara HVDC | 923 | 924 | 923 | 924 | 923 | 922 | 923 | 922 | 921 | 922 | 922 | 922 | 922 | 922 | 922 | 922 | 922 | 922 |  | 922 | 923 | 923 | 922 | 923 | 922 | 923 | 22325090
147 | Bheramara 410 MW CCPP | 240 | 240 | 245 | 245 | 250 | 270 | 290 | 310 | 335 | 340 | 300 | 330 | 340 | 340 | 335 | 325 | 310 | 305 |  | 300 | 300 | 295 | 290 | 285 | 280 | 275 | 7298208
148 | Payra 1320 MW | 0 | 90 | 220 | 0 | [21 empty] | 0 | 555300
149
150 | Barapukuria TPP Unit-1 | 76 | 76 | 76 | 75 | 75 | 76 | 76 | 75 | 76 | 75 | 81 | 76 | 76 | 77 | 77 | 72 | 74 | 75 |  | 75 | 75 | 75 | 76 | 76 | 76 | 74 | 1796509
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 249 | 249 | 249 | 249 | 249 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 25 | 250 | 250 |  | 250 | 249 | 249 | 249 | 249 | 249 | 249 | 6026800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 796576
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 25080
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 120 | 124 | 130 | 134 | 133 | 96 | 43 | 20 | 10 | 8 | 5 | 3 | 20 | 10 | 20 | 60 | 85 | 122 |  | 183 | 196 | 195 | 198 | 196 | 195 | 195 | 2498655
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 143 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 175 | 208 | 208 | 210 | 195 | 159 |  | 161 | 209 | 211 | 213 | 216 | 217 | 217 | 4202318
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 366 | 417 | 420 | 310 | 280 | 310 | 311 | 368 | 369 | 416 | 417 | 414 | 416 | 414 | 417 | 414 | 303 |  | 415 | 418 | 417 | 415 | 414 | 414 | 414 | 9323781
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 28 |  | 27 | 27 | 27 | 27 | 27 | 27 | 22 | 682470
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 18 | 18 | 18 | 18 | 18 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 490800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 244710
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 558032
167 | Katakhali 50 MW Peaking PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 24 | 24 | 24 | 27 |  | 40 | 40 | 40 | 40 | 40 | 24 | 24 | 468909
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 36 |  | 36 | 35 | 35 | 35 | 35 | 35 | 30 | 738956
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 788640
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 90 | 89 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 55 | 90 |  | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 1654176
171 | Baghabari 200 MW PP (Paramount) | 54 | 10 | 10 | 0 | [5 empty] | 0 |  |  |  | 11 | 50 | 10 | 10 |  |  | 21 | 80 | 166 | 171 | 171 | 171 | 130 | 1107889
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2733888
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 70 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2511552
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 17 | 17 | 17 | 0 | 44000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 110 | 104 | 110 | 110 | 115 | 73 | 73 | 70 | 70 | 70 | 70 | 77 | 85 | 90 | 95 | 100 | 108 | 107 |  | 108 | 110 | 110 | 110 | 110 | 110 | 110 | 2335824
177 | Sympa Solar Power 8MW |  |  |  |  | 0 | 0 | 0 | 0 | 2 | 2 | 3 | 3 | 4 | 6 | 4 | 3 | 2 | [9 empty] | 33113
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 72 | 35 | 35 | 35 | 35 | 35 | 60 | 115 | 115 | 114 | 112 | 111 | 114 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2278848
178