## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-25 | Monday
|  |  | Date (day): | 2022-04-25 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14757.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14981 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-24 | 2022-04-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 230 | 230 | 240 | 240
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 260 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 97 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 395 | 394 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 267 | 282 | 300 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 260 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 96 | 96 | 96 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 150 | 150 | 150 |  | 185 | GT-1 Under S/D
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 64 | 78 | 80 | 80 |  | 22 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 98 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 84 | 84 | 85 |  | 17 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 31 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 49 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 268 | 278 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 158 | 303 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 90 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 91 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5998 | 3593 | 3881 | 4003 | 4018 | 1201 | 784
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 24 | 25 | 25 |  | 25 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 57 | 57 | 60 | 60 |  | 170 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 147 | 150 | 150
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 5 | 43 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 80 | 90 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 59 | 95 | 95 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 92 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 105 | 105 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1096 | 1428 | 1461 | 1461 | 231 | 605
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 212 | 225 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 200 | 260 | 360 |  | 0
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 28 | 28 | 28 | 17 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 51 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 150 | 145 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 165 | 180 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 164 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 40 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 97 | 96 | 96 |  | 18 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 113 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 0 | 35 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 101 | 101 | 101 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1469 | 1733 | 1845 | 1969 | 827 | 222
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 80 | 95 | 110 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 159 | 178 | 190 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 97 | 115 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 36 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 24 | 24
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 418 | 432 | 510.6 | 459 | 92 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 40 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 153 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 50 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 78 | 81 | 81
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 219 | 220 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 0 | 0 | 25 |  | Gas shortage
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 305 | 310 | 330 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 370 | 394 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 386 | 384 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1690 | 1812 | 1857 | 1877 | 366 | 218
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 918 | 939 | 940
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 31 | 112 | 115 | 115
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 36 | 34 | 34 |  | 20 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 138 | 146 | 150 | 150
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 0 | 80 |  | 29 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 185 | 200 | 200 | 210 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 16 | 32 | 32 |  | 8 | Engine problem
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 92 | 76 | 94 |  | 11 | Engine problem
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 5 | 105 | 105 | 105
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1445 | 1775 | 1851 | 1850 | 210 | 68
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 50 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 24 | 39 | 33 | 37
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 81 | 85 | 90 | 90 | 104 |  | Gas shortage & GT-1 S/D
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 540 | 650 | 650 |  |  | Line over load.
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 212 | 215 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 753 | 944 | 1193 | 1257 | 104 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 43 | 36 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 22 | 30 | 30 |  | 41 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 13 | 32 | 30 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 147 | 143 | 150 | 150 | 60 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 209 | 200 | 200
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 400 | 400 | 410
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 30 | 38 |  | 12 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 87 | 92 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 200 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 55 | 113 | 113 |  | 0 | Engine problem
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1048 | 1451 | 1528 | 1558 | 451 | 140
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 73 | 76 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 |  | 74 | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 94 | 108 | 110 | 110
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 110 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 483 | 519 | 509 | 532 | 0 | 169
|  | Total |  |  |  |  | 22348 | 21734 | 11995 | 13975 | 14757.6 | 14981 | 3482 | 2214
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11559.0257 | 13467.06 | 14221.2154 | 14436.4956
| A. |  | 2022-04-24 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 14078 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10324 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13975 | MW
| 3 | Day peak Generation : |  |  | 11995 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13467.06 | MW
| 4 | Evening peak Generation : |  |  | 13975 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 301.0902 | MKWHr | By Solar | 1.4937 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 133.8478 | MKWHr |  | By Oil: | 118.6826 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.0442 | MKWHr |  | By Hydro: | 1.3739 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3482 | MW | Dhaka | 5029.46 | 5029.46 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2214 | MW | Chittagong | 1322.5 | 1322.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5696 | MW | Khulna | 1533.4 | 1533.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 998.89 | MMCFD |  |  | Rajshahi | 1438.2 | 1438.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 132453104.902 | ii) Oil : | Taka | 1013948043.7 | Comilla | 1345.5 | 1345.5 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 95887670 | Total | Taka | 1242288818.602 | Mymensingh | 1010 | 1010 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.22 | MKWHr. | Sylhet | 551 | 551 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 244 | MW (E to W) at | 21:00 | hrs | Barisal | 448 | 448 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -174 | MW at | 3:00 | hrs | Rangpur | 789 | 789 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.4° C |  |  | Total | 13467.06 | 13467.06 |  | 0
| B. |  | 2022-04-25 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 42.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14981 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12700 | MW
| 4 | Reserve(Generation end) |  |  |  | 181 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 316.5318 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10977 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2669 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3811 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78 |  | (b) Today: | 77.76 |  | (c) Rule Curve: |  | 83.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 232 | 0 | 270 | 88 | 0 | 393 | 238 |  | 0 | 260 | 140 | 97 | 80 | 55 | 0 | 0 | 0 | 100 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 22 | 50 | 0 | 27 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 22 | 40 | 0 | 70 | 96 | 25 | 22 | 27 | 0 | 0 | 0 | 230 | 0 | 216 | 8 | 0 | 28 | 54 | 0 | 51 | 0 | 50 | 43 | 22 | 10 | 33 | 21 | 148 | 93 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 158 | 55 | 78 | 0 | 185 | 0 | 0 | 10 | 280 | 0 | 0 | 50 | 291 | 54 | 100 | 190 | 100 | 149 | 0 | 88 | 200 | 150 | 400 | 107 | 90 | 51 | 0 | 290 | 54 | 110 | 96 | 72 | 100 | 401 | 104 | 0 | 162 | 105 | 0 | 36 | 0 | 101 | 55 |  | 918 | 0 | 170 | 0 | 16 | 65 | 0 | 0 | 33 | 0 | 0 | 88 | 38 | 48 | 0 | 0 | 0 | 43 | 31 | 89 | 0 | 34 | 32 | 52 | 30 | 22 | 0 | 11 | 74 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 148 | 0 | 20 | 0 | 0 | 414 | 94 | 111 | 113 | 15 | 109 | 0 | 0 | 95 | 622 | 217 | 0 | 0 | 0 | 0 | 115 |  | 8747 | 4202 | 12949 | 3566 | 918 | 2088 | 435 | 4165 | 896 | 57 | 213 | 611 | 148 | 0 | 0 | 78.05
2:00 | 0 | 0 | 233 | 0 | 270 | 88 | 0 | 393 | 246 |  | 0 | 260 | 130 | 97 | 80 | 55 | 0 | 0 | 0 | 100 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 22 | 50 | 0 | 28 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 22 | 40 | 0 | 70 | 95 | 25 | 22 | 28 | 0 | 0 | 0 | 230 | 0 | 218 | 8 | 0 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 10 | 33 | 21 | 144 | 98 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 157 | 55 | 81 | 0 | 216 | 0 | 0 | 10 | 275 | 0 | 0 | 50 | 286 | 53 | 50 | 189 | 50 | 149 | 0 | 88 | 200 | 140 | 401 | 107 | 90 | 51 | 0 | 300 | 54 | 110 | 96 | 42 | 100 | 400 | 104 | 0 | 162 | 105 | 0 | 36 | 0 | 101 | 55 |  | 917 | 0 | 175 | 0 | 16 | 35 | 0 | 0 | 33 | 0 | 0 | 87 | 38 | 32 | 0 | 0 | 0 | 43 | 31 | 89 | 0 | 34 | 32 | 52 | 30 | 22 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 135 | 0 | 0 | 54 | 0 | 20 | 0 | 0 | 414 | 94 | 111 | 113 | 15 | 109 | 0 | 0 | 95 | 622 | 212 | 0 | 0 | 0 | 0 | 115 |  | 8641 | 4060 | 12701 | 3607 | 917 | 2081 | 334 | 4112 | 896 | 58 | 89 | 517 | 144 | 0 | 0 | 78.04
3:00 | 0 | 0 | 233 | 0 | 270 | 88 | 0 | 393 | 258 |  | 0 | 260 | 130 | 97 | 80 | 55 | 0 | 0 | 0 | 100 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 22 | 50 | 0 | 28 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 38 | 0 | 70 | 95 | 25 | 22 | 28 | 0 | 0 | 0 | 250 | 0 | 218 | 8 | 0 | 25 | 54 | 0 | 51 | 0 | 50 | 43 | 22 | 10 | 33 | 21 | 142 | 97 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 158 | 55 | 81 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 100 | 286 | 75 | 100 | 189 | 50 | 149 | 0 | 87 | 200 | 142 | 401 | 107 | 90 | 51 | 0 | 300 | 40 | 110 | 96 | 41 | 100 | 400 | 104 | 0 | 162 | 105 | 0 | 36 | 0 | 101 | 55 |  | 918 | 0 | 180 | 0 | 16 | 3 | 0 | 0 | 33 | 0 | 0 | 88 | 36 | 32 | 0 | 0 | 0 | 43 | 29 | 89 | 0 | 34 | 32 | 52 | 30 | 22 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 7 | 0 | 40 | 0 | 0 | 414 | 94 | 111 | 113 | 15 | 109 | 0 | 0 | 95 | 622 | 209 | 0 | 0 | 0 | 0 | 115 |  | 8784 | 4002 | 12786 | 3634 | 918 | 2092 | 476 | 4100 | 897 | 58 | 10 | 466 | 142 | 0 | 0 | 78.03
4:00 | 0 | 0 | 235 | 0 | 270 | 90 | 0 | 393 | 270 |  | 0 | 260 | 130 | 97 | 80 | 55 | 0 | 0 | 0 | 95 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 24 | 50 | 0 | 29 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 17 | 0 | 70 | 95 | 25 | 22 | 28 | 0 | 0 | 0 | 250 | 0 | 218 | 8 | 0 | 25 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 142 | 98 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 157 | 55 | 81 | 0 | 219 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 291 | 0 | 0 | 189 | 0 | 149 | 0 | 87 | 200 | 145 | 401 | 97 | 90 | 51 | 0 | 300 | 54 | 110 | 96 | 38 | 100 | 400 | 104 | 0 | 144 | 105 | 0 | 20 | 0 | 101 | 55 |  | 920 | 0 | 180 | 0 | 16 | 10 | 0 | 0 | 28 | 0 | 0 | 85 | 37 | 32 | 0 | 0 | 0 | 43 | 23 | 89 | 0 | 34 | 12 | 52 | 30 | 22 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 135 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 113 | 0 | 109 | 0 | 0 | 95 | 622 | 206 | 0 | 0 | 0 | 0 | 115 |  | 8360 | 3804 | 12164 | 3635 | 920 | 2087 | 0 | 4055 | 896 | 59 | 13 | 360 | 142 | 0 | 0 | 78.02
5:00 | 0 | 0 | 235 | 0 | 270 | 93 | 0 | 394 | 280 |  | 0 | 260 | 130 | 97 | 79 | 55 | 0 | 0 | 0 | 0 | 84 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 25 | 50 | 0 | 29 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 95 | 25 | 22 | 28 | 0 | 0 | 0 | 250 | 0 | 217 | 8 | 0 | 25 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 128 | 99 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 158 | 55 | 78 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 293 | 0 | 0 | 189 | 0 | 149 | 0 | 76 | 100 | 100 | 400 | 107 | 90 | 51 | 0 | 300 | 54 | 103 | 82 | 38 | 100 | 400 | 104 | 0 | 144 | 105 | 0 | 36 | 0 | 101 | 55 |  | 921 | 0 | 180 | 0 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 88 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 76 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 415 | 94 | 0 | 113 | 0 | 104 | 0 | 0 | 95 | 560 | 218 | 0 | 0 | 0 | 0 | 17 |  | 7989 | 3397 | 11386 | 3642 | 921 | 2116 | 0 | 3608 | 836 | 59 | 12 | 66 | 128 | 0 | 0 | 78.01
6:00 | 0 | 0 | 235 | 0 | 270 | 93 | 0 | 393 | 280 |  | 0 | 260 | 145 | 97 | 79 | 15 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 28 | 33 | 25 | 16 | 0 | 29 | 30 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 95 | 25 | 22 | 24 | 0 | 0 | 0 | 250 | 0 | 218 | 8 | 0 | 25 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 122 | 100 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 159 | 55 | 78 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 145 | 0 | 0 | 100 | 0 | 118 | 1 | 76 | 51 | 50 | 400 | 107 | 90 | 51 | 0 | 300 | 54 | 103 | 78 | 38 | 92 | 400 | 104 | 1 | 144 | 90 | 0 | 36 | 1 | 101 | 55 |  | 920 | 0 | 185 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 94 | 0 | 55 | 0 | 0 | 95 | 520 | 209 | 0 | 0 | 0 | 2 | 17 |  | 7454 | 3183 | 10637 | 3653 | 920 | 2114 | 0 | 2941 | 795 | 59 | 12 | 18 | 122 | 5 | 0 | 78
7:00 | 0 | 0 | 234 | 0 | 270 | 93 | 0 | 394 | 280 |  | 0 | 260 | 130 | 96 | 79 | 15 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 28 | 33 | 25 | 25 | 0 | 28 | 30 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 16 | 0 | 0 | 0 | 96 | 25 | 22 | 5 | 0 | 0 | 0 | 250 | 0 | 216 | 8 | 0 | 25 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 118 | 98 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 159 | 55 | 40 | 0 | 219 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 145 | 0 | 0 | 64 | 0 | 86 | 4 | 76 | 51 | 50 | 402 | 75 | 70 | 51 | 1 | 300 | 54 | 68 | 96 | 39 | 50 | 400 | 71 | 6 | 144 | 51 | 0 | 36 | 5 | 101 | 55 |  | 920 | 0 | 190 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 84 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 146 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 415 | 57 | 0 | 94 | 0 | 70 | 0 | 1 | 50 | 510 | 220 | 0 | 0 | 0 | 19 | 24 |  | 7128 | 3196 | 10324 | 3666 | 920 | 2069 | 0 | 2641 | 785 | 58 | 15 | 21 | 118 | 36 | 0 | 77.99
8:00 | 0 | 0 | 235 | 0 | 270 | 93 | 0 | 401 | 280 |  | 0 | 260 | 130 | 97 | 79 | 15 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 28 | 33 | 25 | 25 | 0 | 27 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 95 | 25 | 22 | 8 | 0 | 0 | 0 | 200 | 0 | 217 | 8 | 0 | 28 | 54 | 0 | 43 | 0 | 0 | 43 | 22 | 0 | 33 | 21 | 118 | 98 | 0 | 20 | 1 | 0 | 42 | 0 | 0 | 163 | 158 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 285 | 0 | 0 | 0 | 145 | 0 | 0 | 64 | 0 | 96 | 3 | 76 | 68 | 50 | 402 | 75 | 70 | 51 | 3 | 300 | 54 | 78 | 96 | 39 | 50 | 401 | 70 | 14 | 144 | 51 | 0 | 36 | 10 | 101 | 55 |  | 924 | 0 | 185 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 76 | 0 | 199 | 0 | 0 | 149 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 94 | 0 | 70 | 0 | 1 | 50 | 450 | 220 | 0 | 0 | 2 | 42 | 52 |  | 7082 | 3275 | 10357 | 3609 | 924 | 2025 | 0 | 2741 | 725 | 57 | 66 | 52 | 118 | 76 | 0 | 77.98
9:00 | 0 | 0 | 235 | 0 | 270 | 91 | 0 | 402 | 278 |  | 0 | 260 | 130 | 97 | 79 | 15 | 0 | 0 | 0 | 5 | 64 | 20 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 27 | 33 | 25 | 27 | 0 | 27 | 30 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 24 | 0 | 0 | 12 | 85 | 25 | 22 | 7 | 0 | 0 | 0 | 200 | 0 | 214 | 8 | 0 | 28 | 54 | 0 | 43 | 0 | 0 | 43 | 22 | 0 | 33 | 21 | 124 | 99 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 158 | 60 | 10 | 0 | 219 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 145 | 0 | 0 | 82 | 0 | 128 | 12 | 76 | 71 | 62 | 403 | 80 | 86 | 51 | 4 | 300 | 54 | 95 | 96 | 38 | 70 | 394 | 80 | 23 | 144 | 51 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 185 | 0 | 6 | 40 | 0 | 0 | 0 | 0 | 0 | 84 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 414 | 76 | 0 | 94 | 0 | 85 | 0 | 2 | 70 | 450 | 216 | 0 | 0 | 3 | 66 | 58 |  | 7246 | 3353 | 10599 | 3609 | 923 | 2011 | 0 | 2931 | 724 | 57 | 88 | 68 | 124 | 112 | 0 | 77.97
10:00 | 0 | 0 | 235 | 0 | 270 | 93 | 0 | 395 | 277 |  | 0 | 260 | 145 | 96 | 79 | 50 | 0 | 0 | 0 | 38 | 76 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 27 | 33 | 28 | 45 | 0 | 26 | 30 | 0 | 0 | 13 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 14 | 0 | 2 | 0 | 0 | 0 | 230 | 0 | 208 | 16 | 0 | 28 | 53 | 0 | 43 | 0 | 0 | 43 | 22 | 0 | 33 | 21 | 128 | 94 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 153 | 60 | 0 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 215 | 30 | 0 | 166 | 0 | 133 | 17 | 76 | 104 | 125 | 395 | 107 | 90 | 37 | 3 | 292 | 0 | 63 | 96 | 39 | 90 | 387 | 104 | 31 | 144 | 81 | 0 | 20 | 29 | 101 | 55 |  | 923 | 0 | 170 | 0 | 31 | 50 | 0 | 0 | 0 | 0 | 0 | 82 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 150 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 94 | 0 | 102 | 0 | 0 | 94 | 430 | 216 | 0 | 0 | 5 | 82 | 76 |  | 7364 | 3498 | 10862 | 3358 | 923 | 2017 | 30 | 3292 | 704 | 56 | 137 | 135 | 128 | 169 | 0 | 77.96
11:00 | 0 | 0 | 232 | 0 | 270 | 90 | 0 | 396 | 272 |  | 0 | 260 | 130 | 96 | 64 | 45 | 0 | 0 | 0 | 67 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 27 | 33 | 28 | 49 | 0 | 26 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 70 | 18 | 18 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 213 | 16 | 0 | 28 | 52 | 0 | 43 | 0 | 0 | 43 | 21 | 0 | 33 | 21 | 134 | 81 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 156 | 60 | 10 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 0 | 25 | 253 | 54 | 50 | 157 | 25 | 138 | 19 | 90 | 154 | 150 | 404 | 107 | 73 | 39 | 5 | 300 | 25 | 58 | 96 | 42 | 90 | 393 | 104 | 39 | 144 | 102 | 0 | 36 | 32 | 101 | 55 |  | 924 | 0 | 175 | 0 | 31 | 140 | 0 | 0 | 2 | 0 | 0 | 85 | 24 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 15 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 150 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 94 | 0 | 101 | 0 | 0 | 95 | 450 | 216 | 0 | 0 | 5 | 92 | 115 |  | 7862 | 3753 | 11615 | 3395 | 924 | 2003 | 154 | 3602 | 724 | 56 | 263 | 289 | 134 | 194 | 0 | 77.95
12:00 | 0 | 0 | 230 | 0 | 270 | 92 | 0 | 395 | 267 |  | 0 | 260 | 145 | 96 | 64 | 40 | 0 | 0 | 0 | 85 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 27 | 33 | 28 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 5 | 0 | 80 | 59 | 24 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 210 | 16 | 0 | 28 | 49 | 0 | 43 | 0 | 0 | 43 | 21 | 10 | 33 | 20 | 140 | 80 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 154 | 55 | 10 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 0 | 40 | 268 | 158 | 90 | 159 | 91 | 149 | 20 | 90 | 165 | 150 | 370 | 97 | 90 | 51 | 5 | 300 | 54 | 105 | 96 | 38 | 92 | 386 | 104 | 36 | 144 | 105 | 0 | 36 | 33 | 101 | 55 |  | 923 | 0 | 155 | 0 | 31 | 138 | 0 | 0 | 4 | 0 | 0 | 81 | 24 | 16 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 13 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 199 | 0 | 0 | 147 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 400 | 94 | 0 | 94 | 5 | 94 | 0 | 6 | 95 | 420 | 212 | 0 | 0 | 5 | 95 | 110 |  | 8266 | 3729 | 11995 | 3322 | 923 | 1990 | 379 | 3800 | 693 | 57 | 308 | 351 | 140 | 202 | 0 | 77.94
13:00 | 0 | 0 | 228 | 0 | 270 | 92 | 0 | 394 | 266 |  | 0 | 260 | 130 | 95 | 64 | 48 | 0 | 0 | 0 | 88 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 26 | 33 | 28 | 42 | 0 | 27 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 26 | 0 | 80 | 79 | 24 | 22 | 5 | 0 | 0 | 0 | 230 | 0 | 211 | 16 | 0 | 28 | 46 | 0 | 51 | 0 | 0 | 43 | 21 | 10 | 33 | 20 | 144 | 81 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 153 | 55 | 10 | 0 | 220 | 0 | 0 | 0 | 285 | 0 | 0 | 150 | 276 | 276 | 90 | 156 | 100 | 149 | 19 | 90 | 180 | 147 | 398 | 96 | 90 | 51 | 5 | 300 | 54 | 109 | 96 | 37 | 100 | 388 | 104 | 31 | 144 | 105 | 0 | 36 | 32 | 101 | 55 |  | 923 | 0 | 168 | 0 | 30 | 138 | 0 | 0 | 4 | 0 | 0 | 84 | 27 | 16 | 0 | 0 | 0 | 43 | 16 | 33 | 0 | 0 | 19 | 52 | 0 | 17 | 0 | 11 | 75 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 202 | 0 | 30 | 0 | 0 | 370 | 94 | 29 | 94 | 58 | 93 | 0 | 0 | 95 | 430 | 211 | 0 | 0 | 5 | 91 | 107 |  | 8583 | 3907 | 12490 | 3361 | 923 | 1949 | 675 | 3896 | 704 | 57 | 340 | 458 | 144 | 185 | 0 | 77.93
14:00 | 0 | 0 | 235 | 0 | 270 | 91 | 0 | 394 | 267 |  | 0 | 260 | 135 | 94 | 64 | 55 | 0 | 0 | 0 | 96 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 26 | 33 | 0 | 42 | 0 | 27 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 25 | 0 | 80 | 85 | 24 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 208 | 16 | 0 | 28 | 48 | 0 | 43 | 0 | 18 | 43 | 21 | 10 | 32 | 20 | 148 | 80 | 0 | 20 | 2 | 0 | 41 | 0 | 0 | 163 | 154 | 50 | 10 | 0 | 220 | 0 | 0 | 0 | 280 | 0 | 0 | 200 | 276 | 300 | 90 | 153 | 97 | 149 | 17 | 90 | 180 | 135 | 404 | 104 | 90 | 51 | 4 | 300 | 54 | 110 | 96 | 34 | 100 | 394 | 104 | 36 | 144 | 105 | 0 | 36 | 28 | 101 | 55 |  | 924 | 0 | 160 | 0 | 30 | 138 | 0 | 0 | 12 | 0 | 0 | 84 | 27 | 32 | 0 | 0 | 0 | 43 | 17 | 49 | 0 | 0 | 24 | 52 | 0 | 17 | 0 | 11 | 75 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 204 | 0 | 80 | 0 | 0 | 370 | 94 | 111 | 94 | 78 | 99 | 0 | 0 | 55 | 440 | 211 | 0 | 0 | 4 | 80 | 107 |  | 8668 | 4060 | 12728 | 3329 | 924 | 1940 | 878 | 3904 | 715 | 57 | 342 | 524 | 148 | 171 | 0 | 77.92
15:00 | 0 | 0 | 227 | 0 | 260 | 91 | 0 | 396 | 267 |  | 0 | 260 | 135 | 94 | 75 | 48 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 24 | 33 | 30 | 48 | 0 | 27 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 5 | 25 | 0 | 80 | 87 | 0 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 212 | 16 | 0 | 27 | 47 | 0 | 43 | 0 | 39 | 43 | 21 | 10 | 30 | 20 | 157 | 81 | 0 | 20 | 2 | 0 | 40 | 0 | 0 | 163 | 151 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 200 | 276 | 304 | 93 | 153 | 99 | 149 | 13 | 90 | 180 | 130 | 405 | 104 | 90 | 56 | 3 | 300 | 54 | 110 | 96 | 44 | 100 | 392 | 104 | 31 | 144 | 105 | 0 | 35 | 22 | 101 | 55 |  | 924 | 0 | 170 | 0 | 30 | 138 | 0 | 0 | 26 | 0 | 0 | 85 | 27 | 32 | 0 | 0 | 0 | 43 | 17 | 49 | 0 | 0 | 24 | 52 | 0 | 17 | 0 | 0 | 76 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 205 | 0 | 100 | 0 | 0 | 367 | 94 | 199 | 93 | 105 | 105 | 0 | 0 | 55 | 480 | 206 | 0 | 0 | 3 | 64 | 104 |  | 8677 | 4227 | 12904 | 3318 | 924 | 1941 | 995 | 3920 | 756 | 57 | 343 | 560 | 157 | 138 | 0 | 77.91
16:00 | 0 | 0 | 227 | 0 | 260 | 91 | 0 | 394 | 262 |  | 0 | 260 | 135 | 89 | 75 | 48 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 16 | 25 | 24 | 33 | 30 | 48 | 0 | 27 | 30 | 0 | 0 | 25 | 80 | 0 | 0 | 0 |  | 14 | 25 | 0 | 80 | 88 | 0 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 210 | 16 | 0 | 27 | 49 | 0 | 51 | 0 | 47 | 43 | 21 | 10 | 25 | 20 | 148 | 80 | 0 | 20 | 1 | 0 | 40 | 0 | 0 | 163 | 153 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 285 | 0 | 0 | 160 | 276 | 231 | 94 | 153 | 99 | 149 | 8 | 90 | 180 | 133 | 405 | 115 | 105 | 74 | 2 | 300 | 54 | 102 | 82 | 52 | 100 | 392 | 104 | 22 | 141 | 105 | 0 | 34 | 15 | 100 | 55 |  | 923 | 0 | 170 | 0 | 28 | 138 | 0 | 0 | 29 | 0 | 0 | 85 | 27 | 32 | 0 | 0 | 0 | 43 | 17 | 49 | 0 | 16 | 24 | 52 | 19 | 16 | 0 | 0 | 77 | 0 | 199 | 0 | 0 | 137 | 0 | 0 | 204 | 0 | 30 | 0 | 0 | 370 | 94 | 194 | 93 | 105 | 105 | 0 | 3 | 55 | 500 | 201 | 0 | 0 | 2 | 50 | 105 |  | 8690 | 4192 | 12882 | 3406 | 923 | 1948 | 808 | 3986 | 776 | 57 | 342 | 589 | 148 | 103 | 0 | 77.9
17:00 | 0 | 0 | 227 | 0 | 260 | 94 | 0 | 396 | 261 |  | 0 | 260 | 135 | 90 | 74 | 55 | 0 | 0 | 0 | 96 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 | 30 | 48 | 0 | 27 | 30 | 0 | 0 | 25 | 82 | 0 | 0 | 0 |  | 18 | 42 | 0 | 80 | 91 | 0 | 22 | 2 | 0 | 0 | 0 | 200 | 0 | 210 | 16 | 0 | 27 | 47 | 0 | 51 | 0 | 47 | 43 | 21 | 10 | 24 | 20 | 144 | 70 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 120 | 152 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 120 | 277 | 197 | 92 | 163 | 60 | 149 | 3 | 90 | 180 | 138 | 399 | 115 | 105 | 87 | 1 | 300 | 54 | 110 | 97 | 112 | 100 | 384 | 104 | 9 | 126 | 105 | 0 | 34 | 6 | 101 | 55 |  | 923 | 0 | 170 | 0 | 28 | 138 | 0 | 0 | 32 | 0 | 0 | 85 | 26 | 32 | 0 | 0 | 0 | 43 | 17 | 50 | 0 | 16 | 16 | 52 | 38 | 18 | 0 | 0 | 77 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 205 | 0 | 40 | 0 | 0 | 370 | 92 | 200 | 94 | 105 | 105 | 0 | 2 | 55 | 480 | 208 | 0 | 0 | 0 | 19 | 109 |  | 8621 | 4183 | 12804 | 3358 | 923 | 1918 | 709 | 4138 | 757 | 57 | 343 | 622 | 144 | 40 | 0 | 77.89
18:00 | 0 | 0 | 230 | 0 | 260 | 94 | 0 | 370 | 261 |  | 0 | 260 | 135 | 94 | 75 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 | 31 | 48 | 0 | 28 | 30 | 0 | 0 | 25 | 80 | 0 | 0 | 0 |  | 21 | 43 | 27 | 80 | 94 | 13 | 22 | 9 | 0 | 0 | 0 | 200 | 0 | 211 | 16 | 0 | 28 | 49 | 0 | 51 | 0 | 48 | 43 | 22 | 8 | 24 | 19 | 146 | 70 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 163 | 153 | 50 | 10 | 0 | 219 | 0 | 0 | 10 | 290 | 0 | 0 | 30 | 275 | 81 | 30 | 164 | 30 | 149 | 0 | 90 | 180 | 135 | 401 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 112 | 100 | 395 | 104 | 1 | 126 | 105 | 0 | 20 | 1 | 101 | 55 |  | 923 | 0 | 165 | 0 | 64 | 140 | 0 | 0 | 34 | 30 | 8 | 85 | 28 | 32 | 0 | 0 | 0 | 43 | 17 | 75 | 0 | 16 | 16 | 52 | 38 | 19 | 0 | 11 | 73 | 0 | 200 | 16 | 8 | 136 | 0 | 0 | 207 | 0 | 30 | 0 | 0 | 370 | 92 | 200 | 94 | 105 | 105 | 0 | 1 | 55 | 480 | 173 | 0 | 16 | 0 | 2 | 110 |  | 8405 | 4269 | 12674 | 3351 | 923 | 1938 | 401 | 4225 | 753 | 58 | 371 | 710 | 146 | 5 | 0 | 77.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 230 | 0 | 260 | 95 | 0 | 382 | 287 |  | 0 | 260 | 135 | 96 | 75 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 18 | 33 | 31 | 48 | 0 | 28 | 30 | 0 | 0 | 25 | 140 | 0 | 0 | 0 |  | 23 | 43 | 51 | 80 | 95 | 24 | 22 | 3 | 0 | 0 | 0 | 200 | 0 | 211 | 16 | 0 | 28 | 49 | 0 | 51 | 0 | 48 | 43 | 22 | 8 | 33 | 19 | 162 | 92 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 163 | 152 | 50 | 20 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 200 | 277 | 302 | 98 | 176 | 98 | 149 | 0 | 90 | 180 | 133 | 390 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 114 | 100 | 389 | 104 | 0 | 132 | 105 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 165 | 0 | 108 | 145 | 0 | 0 | 34 | 50 | 8 | 82 | 33 | 32 | 0 | 0 | 0 | 43 | 20 | 91 | 0 | 43 | 16 | 52 | 37 | 20 | 0 | 11 | 71 | 0 | 200 | 17 | 8 | 137 | 0 | 0 | 208 | 0 | 47 | 0 | 0 | 370 | 92 | 171 | 94 | 105 | 92 | 0 | 0 | 55 | 500 | 220 | 0 | 17 | 0 | 0 | 115 |  | 9122 | 4432 | 13554 | 3428 | 923 | 2012 | 916 | 4341 | 771 | 58 | 378 | 773 | 162 | 0 | 0 | 77.85
19:30 | 0 | 0 | 230 | 0 | 260 | 95 | 0 | 397 | 291 |  | 0 | 260 | 120 | 96 | 75 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 25 | 33 | 31 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 24 | 43 | 51 | 80 | 95 | 24 | 22 | 15 | 0 | 0 | 0 | 200 | 0 | 213 | 16 | 0 | 28 | 50 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 154 | 95 | 0 | 20 | 0 | 0 | 41 | 0 | 0 | 163 | 155 | 50 | 81 | 0 | 219 | 0 | 0 | 10 | 290 | 5 | 0 | 200 | 275 | 207 | 100 | 176 | 100 | 149 | 0 | 90 | 180 | 140 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 113 | 100 | 395 | 104 | 0 | 144 | 105 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 175 | 0 | 115 | 145 | 0 | 0 | 44 | 80 | 16 | 82 | 33 | 48 | 0 | 0 | 0 | 43 | 20 | 91 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 11 | 70 | 0 | 200 | 17 | 8 | 138 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 365 | 92 | 200 | 94 | 105 | 108 | 0 | 0 | 55 | 540 | 220 | 0 | 17 | 0 | 0 | 115 |  | 9163 | 4666 | 13829 | 3487 | 923 | 2082 | 907 | 4406 | 810 | 58 | 380 | 832 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 231 | 0 | 260 | 97 | 0 | 394 | 282 |  | 0 | 260 | 140 | 95 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 31 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 24 | 43 | 51 | 80 | 95 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 213 | 16 | 0 | 28 | 52 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 164 | 95 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 163 | 155 | 50 | 78 | 0 | 219 | 0 | 0 | 10 | 290 | 16 | 0 | 200 | 275 | 300 | 100 | 176 | 100 | 149 | 0 | 90 | 180 | 137 | 405 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 112 | 100 | 390 | 104 | 0 | 144 | 105 | 0 | 36 | 0 | 101 | 55 |  | 923 | 0 | 175 | 0 | 110 | 146 | 0 | 0 | 36 | 70 | 16 | 85 | 37 | 48 | 0 | 0 | 0 | 43 | 22 | 91 | 0 | 43 | 32 | 52 | 38 | 22 | 0 | 11 | 72 | 0 | 200 | 17 | 8 | 139 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 370 | 92 | 200 | 94 | 105 | 108 | 0 | 0 | 55 | 540 | 220 | 0 | 17 | 0 | 0 | 115 |  | 9286 | 4662 | 13948 | 3496 | 923 | 2108 | 1000 | 4399 | 812 | 58 | 381 | 817 | 164 | 0 | 0 | 77.86
21:00 | 0 | 0 | 230 | 0 | 260 | 97 | 0 | 394 | 282 |  | 0 | 260 | 150 | 96 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 31 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 147 | 0 | 0 | 0 |  | 24 | 43 | 51 | 80 | 95 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 212 | 16 | 0 | 28 | 51 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 164 | 95 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 163 | 153 | 50 | 78 | 0 | 219 | 0 | 0 | 10 | 305 | 16 | 0 | 200 | 278 | 303 | 100 | 178 | 100 | 149 | 0 | 90 | 180 | 145 | 394 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 113 | 100 | 384 | 104 | 0 | 144 | 105 | 0 | 0 | 0 | 101 | 55 |  | 918 | 0 | 185 | 0 | 112 | 146 | 0 | 0 | 36 | 65 | 16 | 85 | 39 | 48 | 0 | 0 | 0 | 43 | 22 | 87 | 0 | 43 | 32 | 52 | 38 | 22 | 0 | 11 | 73 | 0 | 200 | 15 | 8 | 143 | 0 | 0 | 209 | 0 | 100 | 0 | 0 | 400 | 92 | 200 | 94 | 105 | 108 | 0 | 0 | 55 | 540 | 215 | 0 | 17 | 0 | 0 | 115 |  | 9286 | 4689 | 13975 | 3505 | 918 | 2159 | 1003 | 4380 | 813 | 57 | 378 | 807 | 164 | 0 | 0 | 77.85
22:00 | 0 | 0 | 231 | 0 | 260 | 100 | 0 | 394 | 277 |  | 0 | 260 | 150 | 95 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 31 | 49 | 0 | 26 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 24 | 43 | 51 | 80 | 96 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 212 | 16 | 0 | 28 | 53 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 30 | 20 | 164 | 95 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 155 | 50 | 78 | 0 | 219 | 0 | 0 | 10 | 310 | 16 | 11 | 200 | 275 | 304 | 100 | 188 | 100 | 149 | 0 | 90 | 180 | 133 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 113 | 100 | 388 | 104 | 0 | 144 | 105 | 0 | 23 | 0 | 101 | 55 |  | 918 | 0 | 190 | 0 | 110 | 147 | 0 | 0 | 36 | 65 | 16 | 84 | 33 | 48 | 0 | 0 | 0 | 43 | 21 | 87 | 0 | 43 | 32 | 52 | 38 | 22 | 0 | 11 | 75 | 0 | 200 | 15 | 8 | 145 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 396 | 94 | 200 | 94 | 105 | 108 | 0 | 0 | 113 | 540 | 215 | 0 | 17 | 0 | 0 | 115 |  | 9332 | 4746 | 14078 | 3541 | 918 | 2154 | 1004 | 4456 | 815 | 56 | 380 | 800 | 164 | 0 | 0 | 77.84
23:00 | 0 | 0 | 231 | 0 | 260 | 98 | 0 | 399 | 276 |  | 0 | 260 | 150 | 96 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 49 | 0 | 26 | 30 | 0 | 0 | 25 | 141 | 0 | 0 | 0 |  | 24 | 43 | 51 | 80 | 95 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 210 | 16 | 0 | 28 | 54 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 158 | 95 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 157 | 50 | 78 | 0 | 219 | 0 | 0 | 10 | 315 | 16 | 0 | 200 | 278 | 300 | 100 | 188 | 100 | 149 | 0 | 90 | 180 | 123 | 404 | 115 | 105 | 92 | 0 | 300 | 54 | 110 | 96 | 113 | 100 | 393 | 104 | 0 | 144 | 0 | 0 | 36 | 0 | 101 | 55 |  | 918 | 0 | 185 | 0 | 66 | 145 | 0 | 0 | 37 | 60 | 8 | 85 | 38 | 48 | 0 | 0 | 0 | 43 | 22 | 87 | 0 | 43 | 32 | 52 | 38 | 22 | 0 | 11 | 74 | 0 | 199 | 16 | 8 | 145 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 387 | 94 | 200 | 94 | 105 | 108 | 0 | 0 | 113 | 540 | 218 | 0 | 17 | 0 | 0 | 115 |  | 9197 | 4683 | 13880 | 3532 | 918 | 2156 | 1000 | 4291 | 813 | 56 | 379 | 787 | 158 | 0 | 0 | 77.83
24:00 | 0 | 0 | 232 | 0 | 260 | 94 | 0 | 398 | 277 |  | 0 | 260 | 135 | 96 | 70 | 55 | 0 | 0 | 0 | 98 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 49 | 0 | 26 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 24 | 43 | 0 | 80 | 95 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 218 | 16 | 0 | 28 | 54 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 154 | 95 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 157 | 50 | 78 | 0 | 219 | 0 | 0 | 0 | 290 | 0 | 11 | 200 | 276 | 301 | 100 | 187 | 100 | 149 | 0 | 90 | 180 | 150 | 400 | 115 | 105 | 57 | 0 | 300 | 54 | 110 | 96 | 107 | 100 | 401 | 104 | 0 | 144 | 0 | 0 | 36 | 0 | 101 | 55 |  | 918 | 0 | 180 | 0 | 32 | 147 | 0 | 0 | 37 | 60 | 8 | 87 | 37 | 48 | 0 | 0 | 0 | 43 | 21 | 87 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 11 | 75 | 0 | 200 | 16 | 8 | 145 | 0 | 0 | 213 | 0 | 100 | 0 | 0 | 388 | 94 | 200 | 94 | 105 | 108 | 0 | 0 | 113 | 550 | 220 | 0 | 17 | 0 | 0 | 115 |  | 9062 | 4663 | 13725 | 3526 | 918 | 2105 | 1001 | 4232 | 825 | 56 | 384 | 737 | 154 | 0 | 0 | 77.82
KWH | 0 | 0 | 5542000 | 0 | 6368500 | 2171408 | 0 | 9592830 | 6486000 |  | 0 | 6119500 | 3255796 | 2314560 | 1819440 | 1156200 | 0 | 0 | 0 | 1830720 | 1955952 | 2367360 | 0 | 0 | 0 | 0 | 1172520 | 1126361 | 596460 | 401472 | 600000 | 598140 | 789840 | 642100 | 1057440 | 0 | 645905 | 728000 | 0 | 0 | 482016 | 2978054 | 0 | 0 | 0 |  | 517920 | 549224 | 265934 | 1452000 | 2048640 | 508320 | 525744 | 322080 | 0 | 0 | 0 | 5528300 | 0 | 5154000 | 334545 | 0 | 646992 | 1243680 | 0 | 1091752 | 0 | 671520 | 1033934 | 499176 | 172980 | 740100 | 482720 | 3381120 | 2091840 | 0 | 411228 | 15300 | 0 | 946472 | 0 | 0 | 3853963 | 3686000 | 1288128 | 1019520 | 0 | 5236420 | 0 | 0 | 178560 | 7151500 | 23671 | 28032 | 2294976 | 6172361 | 3268090 | 1509024 | 3770400 | 1356445 | 3419136 | 137160 | 2029440 | 3879360 | 3059418 | 9595000 | 2486400 | 2270400 | 1615018 | 33480 | 7130836 | 1296388 | 2473117 | 2270880 | 1580040 | 2231040 | 9318000 | 2516160 | 309730 | 3515040 | 2181655 | 0 | 796680 | 234953 | 2444160 | 1360800 |  | 22266909 | 0 | 4420512 | 0 | 904320 | 2343360 | 0 | 0 | 444960 | 358016 | 79875 | 2067998 | 716533 | 798720 | 0 | 0 | 0 | 722864 | 346330 | 1150176 | 0 | 410256 | 367051 | 1112424 | 423974 | 457680 | 0 | 196776 | 1766400 | 0 | 4851200 | 99000 | 48000 | 4390664 | 0 | 0 | 3370182 | 0 | 1046400 | 0 | 0 | 9398218 | 2127840 | 2343951 | 2380800 | 1240416 | 2363049 | 0 | 17486 | 1881312 | 13426600 | 5083418 | 0 | 140400 | 38520 | 707040 | 2325120 |  | 202455476 | 98634750 | 301090226 | 84963689 | 22266909 | 48884153 | 11818886 | 93335744 | 20044200 | 1373905 | 5860542 | 7667409 | 3381120 | 1493669 | 0
Fuel Cost | 0 | 0 | 8091320 | 0 | 7069035 | 2866258.56 | 0 | 9688758.3 | 6680580 |  | 0 | 6670255 | 3613933.56 | 17567510.4 | 12535941.6 | 9781452 | 0 | 0 | 0 | 13785321.6 | 17838282.24 | 23294822.4 | 0 | 0 | 0 | 0 | 8559396 | 8706770.53 | 5881095.6 | 301104 | 450000 | 0 | 0 | 0 | 10225444.8 | 0 | 174394.35 | 196560 | 0 | 0 | 4477928.64 | 3246078.86 | 0 | 0 | 0 |  | 0 | 5310996.08 | 2579559.8 | 13866600 | 17823168 | 4025894.4 | 662437.44 | 956577.6 | 0 | 0 | 0 | 4090942 | 0 | 4741680 | 431563.05 | 0 | 731100.96 | 1741152 | 0 | 1866895.92 | 0 | 6782352 | 9874069.7 | 633953.52 | 129735 | 1295175 | 362040 | 25358400 | 2217350.4 | 0 | 522259.56 | 243882 | 0 | 1514355.2 | 0 | 0 | 4393517.82 | 3833440 | 2537612.16 | 1947283.2 | 0 | 9059006.6 | 0 | 0 | 364262.4 | 7223015 | 17753.25 | 21304.32 | 39037541.76 | 46663049.16 | 55492168.2 | 25230881.28 | 19606080 | 22679760.4 | 33644298.24 | 1603400.4 | 16539936 | 42091056 | 21568896.9 | 8923350 | 22675968 | 21455280 | 14066806.78 | 0 | 53909120.16 | 11291539.48 | 21738698.43 | 22663382.4 | 13540942.8 | 14858726.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128257395.84 | 0 | 4641537.6 | 0 | 7107955.2 | 32478969.6 | 0 | 0 | 4667630.4 | 3752007.68 | 832297.5 | 2336837.74 | 1110626.15 | 7795507.2 | 0 | 0 | 0 | 7112981.76 | 3518712.8 | 10179057.6 | 0 | 5546661.12 | 3556724.19 | 10779388.56 | 4112547.8 | 878745.6 | 0 | 148959.432 | 10651392 | 0 | 26293504 | 3430350 | 1369440 | 5137076.88 | 0 | 0 | 49609079.04 | 0 | 17799264 | 0 | 0 | 9304235.82 | 22214649.6 | 39870606.51 | 22593792 | 11709527.04 | 18337260.24 | 0 | 193220.3 | 13902895.68 | 58942774 | 0 | 0 | 0 | 0 | 0 | 0 |  | 848142460.61 | 550173610.882 | 1398316071.492 | 82404203.222 | 128257395.84 | 50048901.68 | 200110222.15 | 652082590.4 | 95887670 | 370954.35 | 86887838.64 | 74867392.51 | 25358400 | 2040502.7 | 0
Yesterday Day Peak | 0 | 0 | 230 | 0 | 270 | 92 | 0 | 395 | 267 |  | 0 | 260 | 145 | 96 | 64 | 40 | 0 | 0 | 0 | 85 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 27 | 33 | 28 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 5 | 0 | 80 | 59 | 24 | 22 | 2 | 0 | 0 | 0 | 230 | 0 | 210 | 16 | 0 | 28 | 49 | 0 | 43 | 0 | 0 | 43 | 21 | 10 | 33 | 20 | 140 | 80 | 0 | 20 | 2 | 0 | 42 | 0 | 0 | 163 | 154 | 55 | 10 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 0 | 40 | 268 | 158 | 90 | 159 | 91 | 149 | 20 | 90 | 165 | 150 | 370 | 97 | 90 | 51 | 5 | 300 | 54 | 105 | 96 | 38 | 92 | 386 | 104 | 36 | 144 | 105 | 0 | 36 | 33 | 101 | 55 |  | 923 | 0 | 155 | 0 | 31 | 138 | 0 | 0 | 4 | 0 | 0 | 81 | 24 | 16 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 13 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 199 | 0 | 0 | 147 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 400 | 94 | 0 | 94 | 5 | 94 | 0 | 6 | 95 | 420 | 212 | 0 | 0 | 5 | 95 | 110 |  | 11995 | DayPeak
Yesterday Evening Peak | 0 | 0 | 230 | 0 | 260 | 97 | 0 | 394 | 282 | 0 | 0 | 260 | 150 | 96 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 31 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 147 | 0 | 0 | 0 | 0 | 24 | 43 | 51 | 80 | 95 | 24 | 22 | 20 | 0 | 0 | 0 | 200 | 0 | 212 | 16 | 0 | 28 | 51 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 164 | 95 | 0 | 20 | 0 | 0 | 40 | 0 | 0 | 163 | 153 | 50 | 78 | 0 | 219 | 0 | 0 | 10 | 305 | 16 | 0 | 200 | 278 | 303 | 100 | 178 | 100 | 149 | 0 | 90 | 180 | 145 | 394 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 97 | 113 | 100 | 384 | 104 | 0 | 144 | 105 | 0 | 0 | 0 | 101 | 55 |  | 918 | 0 | 185 | 0 | 112 | 146 | 0 | 0 | 36 | 65 | 16 | 85 | 39 | 48 | 0 | 0 | 0 | 43 | 22 | 87 | 0 | 43 | 32 | 52 | 38 | 22 | 0 | 11 | 73 | 0 | 200 | 15 | 8 | 143 | 0 | 0 | 209 | 0 | 100 | 0 | 0 | 400 | 92 | 200 | 94 | 105 | 108 | 0 | 0 | 55 | 540 | 215 | 0 | 17 | 0 | 0 | 115 |  | 13975 | EvPeak
Forecast for Evening | 0 | 0 | 240 | 0 | 270 | 100 | 0 | 400 | 320 | 0 | 0 | 270 | 150 | 100 | 80 | 55 | 0 | 0 | 0 | 100 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 30 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 90 | 95 | 25 | 22 | 20 | 0 | 0 | 0 | 360 | 0 | 225 | 8 | 0 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 166 | 110 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 0 | 0 | 10 | 330 | 0 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 96 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 |  | 101 | 55 |  | 940 | 0 | 200 | 0 | 115 | 150 | 0 | 0 | 34 | 80 | 32 | 90 | 37 | 110 | 0 | 0 | 0 | 43 | 30 | 93 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 80 | 0 | 200 | 17 | 10 | 150 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 410 | 94 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 650 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 240 | 0 | 270 | 100 | 0 | 400 | 300 | 0 | 0 | 270 | 150 | 96 | 80 | 55 | 0 | 0 | 0 | 100 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 30 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 80 | 95 | 25 | 22 | 5 | 0 | 0 | 0 | 260 | 0 | 225 | 8 | 0 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 143 | 110 | 0 | 20 | 1.6 | 0 | 42 | 0 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 0 | 0 | 10 | 310 | 0 | 11 | 200 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 96 | 113 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 35 | 30 | 101 | 55 |  | 939 | 0 | 200 | 0 | 115 | 150 | 0 | 0 | 34 | 0 | 32 | 90 | 33 | 50 | 0 | 0 | 0 | 36 | 30 | 92 | 0 | 43 | 30 | 52 | 30 | 22 | 0 | 11 | 76 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 400 | 76 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 650 | 220 |  | 150 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 233 | 0 | 260 | 97 | 0 | 367 | 302 | 0 | 0 | 270 | 150 | 96 | 79 | 55 | 0 | 0 | 0 | 50 | 84 | 80 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 19 | 25 | 27 | 33 | 33 | 33 | 0 | 28 | 30 | 0 | 0 | 16 | 131 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 91 | 25 | 17 | 4 | 0 | 0 | 0 | 65 | 0 | 213 | 102 | 0 | 25 | 51 | 0 | 43 | 0 | 0 | 25 | 22 | 0 | 33 | 20 | 136 | 104 | 0 | 17 | 1 | 0 | 42 | 0 | 0 | 110 | 156 | 40 | 10 | 0 | 219 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 273 | 0 | 0 | 182 | 0 | 149 | 10 | 90 | 85 | 137 | 354 | 115 | 105 | 51 | 3 | 300 | 54 | 110 | 96 | 29 | 50 | 350 | 104 | 21 | 126 | 108 | 0 | 36 | 12 | 75 | 0 | 0 | 921 | 0 | 180 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 70 | 0 | 113 | 105 | 109 | 0 | 2 | 113 | 480 | 154 | 0 | 0 | 1 | 42 | 52 | 0 |  |  |  |  | 118682581 |  | 0
118682581
| Minimum Generation |  | 10324 | 7:00
| Highest Generation |  | 14078 | 22:00
| Day Peak Generation |  | 11995 | 12:00
| Evening Peak Generation |  | 13975 | 21:00
| HVDC Max Flow |  | 924 | 8:00
| HVDC EvPeak Flow |  | 918 | 21:00
| Load factor L.F |  | 89.11%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-25
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11995 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10977 | MW
Evening Peak Generation : |  | 13975 | MW Hour : | 21:00 | Available Max Generation : |  | 14981 | MW
E.P. Demand (at gen end) : |  | 13975 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14800 | MW
Maximum Generation : |  | 14078 | MW Hour : | 22:00 | Reserve(Generation end) |  | 181 | MW
Total Gen. (MKWH) : |  | 301.0902 | System Load Factor : | 89.11% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -174 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-25
Actual : | 77.76 | Ft.(MSL) , | Rule curve : | 83.2 | Ft.( MSL )
Gas Consumed : | Total = | 998.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 132453104.902
: |  | Coal : | 95887670 | Oil : | 1013948043.7 | Total : | 1242288818.602
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5251.3745 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1709.1001 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1659.6293 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1486.7986 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1355.1849 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1111.4019 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 545.4232 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 332.0105 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 818.8358 |  |  | 0 | 0%
Total | 0 |  | 14269.7587 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rajshahi 132/33 kV T-3 transformer was under shut down from 08:10 to 10:29 for C/M. | [5 empty] | About 25 MW power interruption occurred under Rajshahi
S/S area from 08:10 to 10:29
b) Halishahar-Kulshi 132 kV Ckt-3 was under shut down from 08:55 to 15:10 for C/M.
c) Sikalbaha 132/33 kV T-3 transformer was under shut down from 09:25 to 10:29 for C/M. | [5 empty] | About 20 MW power interruption occurred under Sikalbaha
S/S area from 09:25 to 11:40
d) Fenchuganj-Sreemangal 132 kV Ckt-2 tripped at 09:54 showing Dist C-phase and was switched on at
10:12 Again both Ckt trip 10:14 showing dist Z1 and were switched on at Ckt-1 at 12:23 & Ckt-2 at 18:21.
e) Aminbazar 230/132 kV T-1 transformer was under shut down from 10:08 to 18:03 for C/M.
f) Aminbazar 132 kV bus-2 was under shut down from 10:09 to 18:01 for C/M.
g) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 11:15 to 17:47 for C/M.
h) Rajshahi 132/33 kV T-2 transformer was under shut down from 11:17 to 12:28 for C/M. | [5 empty] | About 20 MW power interruption occurred under Rajshahi
S/S area from 11:17 to 12:28
i) Ramganj 132/33 kV T-2 transformer was under shut down from 11:36 to 12:32 for C/M. | [5 empty] | About 35 MW power interruption occurred under Ramganj
S/S area from 11:36 to 12:32
j) Joydevpur 132/33 kV T-2 transformer was under shut down from 12:21 to 13:07 for C/M. | [5 empty] | About 10 MW power interruption occurred under Joydevpur
S/S area from 12:21 to 13:07
k) Baroaulia-KSRM 132 kV Ckt trip at 12:11 showing E/F relay and was switched on at 12:33.
l) Mohastanghor-Polashbari 132 kV Ckt-2 trip at 12:40 showing dist Z1 and was switched on at 13:11.
m) Sherpur 132 kV bus-B was under shut down from 13:22 to 19:08 for C/M.
n) Gopalganj-Payra 400 kV Ckt-2 was under shut down since at 13:27 for C/M.
o) Keraniganj(new) 132/33 kV T-1 transformer was under shut down from 13:40 to 15:09 for C/M.
p) Madaripur 132/33 kV T-2 transformer was under shut down from 11:15 to 12:49 for C/M. | [5 empty] | About 17 MW power interruption occurred under Joydevpur
S/S area from 11:15 to 12:49
q) Hathazari all 132 kV lines & 132 kV side of auto transformers except MT2 got tripped at 09:33 showing
bus fault while charging Hathazari-Kaptai 132 kV Ckt -1 and were switched on at MT-1,MT-3 & MT-4
are 10:00,10:05,respectively.
r) Sikalbaha 225 MW, KPL,Zodiac,Anlima, Baraka Sikalbaha also got trip due to Above the reason.
s) Choddagram-Feni 132 kV Ckt -2 tripped at 14:47 showing dist B phase,O/C relay and was switched on
at 15:10.
t) Sikalbaha 225 MW CCPP GT was synchronized at 15:23.
u) Sylhet-Bibiyana-Fenchuganj 132 kV Ckt tripped at 01:21(25-04-2022) showing dist Z2,A phase at Sylhet
end & dist Z1,Z2,L-1-N at Fenchuganj end and was switched on at 01:42.
v) Barapukuria #01 tripped at 01:30(25-04-2022).
w) Ashuganj-Shahjibazar 132 kV Ckt-3 tripped at 05:36 and was Switched on at 06:29.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 230 | 5542000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 6368500 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 2171408 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 394 | 9592830
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 282 | 6486000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 6119500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 96 | 2314560
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3255796 | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 78 | 1819440 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1156200
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 401472
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1830720
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1955952 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1172520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2367360 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1126361
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 596460 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1198140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 789840
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 642100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1057440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 6172361 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 303 | 3268090
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 1509024
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1356445
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3419136
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2270400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2516160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3515040 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 234953
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1360800
| Dhaka area Total |  |  |  | 5998 | 3881 | 83587008
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 482016
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137160
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 508320 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 57 | 1373905 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 147 | 2978054 | ST under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1615018
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 549224 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 265934 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1452000 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2029440 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 525744
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 322080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 2048640 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33480
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 7130836
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1296388
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2473117
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2231040
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 105 | 2181655 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1428 | 29634051
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 5154000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 200 | 5528300
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 28 | 646992 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1243680
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 334545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1091752
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 3059418
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 671520
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3879360 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499176
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 172980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3381120
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 740100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1033934 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 482720 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2294976
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 2270880 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1580040
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 796680 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 2444160 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1733 | 37306333
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 95 | 2091840 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 411228
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 178 | 3770400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 2486400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 309730
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 517920
| Mymensingh Area Total |  |  |  | 622 | 432 | 9602818
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 946472 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3853963
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 153 | 3686000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 28032 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1288128 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1019520
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5236420
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 23671
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7151500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 394 | 9595000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 178560
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 384 | 9318000
| Sylhet Area Total |  |  |  | 2477 | 1812 | 42325266
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 22266909
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 112 | 904320
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 444960 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 146 | 2343360 | ST under maint
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 358016 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 185 | 4420512 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 16 | 79875 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 1046400
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 2127840 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1240416
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 707040
| Khulna Area Total |  |  |  | 2384 | 1775 | 35939648
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 798720 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 39 | 716533
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2067998 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 13426600
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 215 | 5083418
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 140400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 944 | 22233669
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 722864 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 22 | 346330 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 410256 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 367051 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 143 | 4390664 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 209 | 3370182
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 400 | 9398218
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 423974 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 457680
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 196776
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1112424
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1150176 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 200 | 2343951
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2380800 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 1881312 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38520
| Rajshahi Area Total |  |  |  | 2179 | 1451 | 28991178
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1766400
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4851200
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 99000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 48000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 2363049
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 17486
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2325120
| Rangpur Area Total |  |  |  | 720 | 519 | 11470255
| Total |  |  |  | 21734 | 13975 | 301090226
| Eastern Grid Total |  |  |  | 14493 | 9286 | 202455476
| Western Grid Total |  |  |  | 7241 | 4689 | 98634750
| National Grid Total |  |  |  | 21734 | 13975 | 301090226
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-24
(a) ENTIRE EASTERN GRID : |  | 9258.46 | MW | (b) ENTIRE WESTERN GRID : |  | 4208.6 | MW
i) Dhaka area |  | 5029.46 | MW | i) Khulna area |  | 1533.4 | MW
ii) Chittagong area |  | 1322.5 | MW | ii) Rajshahi area |  | 1438.2 | MW
iii) Comilla area |  | 1345.5 | MW | iii) Barisal area |  | 448 | MW
iv) Mymensingh area |  | 1010 | MW | iv) Rangpur area |  | 789 | MW
v) Sylhet area |  | 551 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13467.06 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 19:00 | Hasnabad | 75 | 16:00 | Palashbari | 116 | 20:00
Agargaon | 102 | 14:00 | Hathazari | 102 | 19:30 | Panchagarh | 53 | 17:00
Agrabad | 88 | 15:00 | Ishurdi | 79 | 22:00 | Patuakhali | 137 | 21:00
AKS | 7 | 05:00 | Jaldhaka | 53 | 18:30 | PHP | 6 | 00:00
AKSML | 138 | 16:00 | Jamalpur | 151 | 00:00 | Purbachal | 20 | 20:00
Amnura | 59 | 22:00 | Jashore | 130 | 13:00 | Purbasadipur | 104 | 19:00
Ashuganj | 50 | 21:00 | Jhenaidah | 121 | 22:00 | Rahim | 27 | 11:00
Bagerhat | 113 | 21:00 | Joydebpur | 190 | 12:00 | Rajbari | 72 | 23:00
Bakulia | 131 | 19:00 | Joypurhat | 66 | 21:00 | Rajendrapur | 116 | 16:00
Banani | 48 | 14:00 | Juldah | 28 | 00:00 | Rajshahi | 173 | 21:00
Bangabhaban | 20 | 10:00 | Kabirpur | 287 | 02:00 | Rajshahi | 47 | 04:00
Barapukuria | 53 | 14:00 | Kachua | 82 | 21:00 | Ramganj | 100 | 21:00
Barguna | 22 | 23:00 | Kallyanpur | 90 | 18:30 | Rampur | 22 | 18:00
Barishal | 114 | 00:00 | Kalurghat | N/A | N/A | Rangamati | 14 | 19:00
Barishal | 75 | 22:00 | Kamrangirchar | 74 | 13:00 | Rangpur | 131 | 20:00
Baroaulia | 80 | 23:00 | Kaptai | 5 | 19:00 | Ruppur | 4.6 | 17:00
Baroirhat | 44 | 23:00 | Kazla | 84 | 15:00 | Saidpur | 102 | 19:00
Bashundhara | 188 | 14:00 | Keranigonj | 80 | 00:00 | Satkhira | 124 | 00:00
BashundharaCement | 13 | 06:00 | Khagrachori | 30 | 19:00 | Satmasjid | 111 | 19:00
Beanibazar | 70 | 21:00 | Khulna | 102 | 21:00 | Savar | 196 | 15:00
Benapole | 60 | 00:00 | Khulshi | 178 | 15:00 | Shahjadpur | 128 | 21:00
Bhaluka | 148 | 00:00 | Kishoreganj | 138 | 04:00 | Shahjibazar | 115 | 19:00
Bhandaria | 62 | 21:00 | Kodda | 326 | 14:00 | Shahmirpur | 40 | 23:00
Bhangura | 42 | 19:00 | KSRM | 29 | 06:00 | Shariatpur | 70 | 23:00
Bheramara(GK) | 60 | 00:00 | Kulaura | 48 | 20:00 | Sherpur | 124 | 00:00
Bhulta | 242 | 22:00 | Kurigram | 62 | 21:00 | Shikalbaha | 34 | 15:00
Bog-Sherpur | 62 | 03:00 | Kushtia | 130 | 00:00 | Shitalakhya | 137 | 15:00
Bogura | 174 | 03:00 | Lalbag | 81 | 16:00 | Sholosohor | N/A | N/A
Borhanuddin | 47 | 19:00 | Lalmonirhat | 47 | 21:00 | Shyampur | 160 | 12:00
Brahmanbaria | 168 | 00:00 | Madanganj | 156 | 23:00 | Siddhirganj | 122 | 14:00
BSRM | 168 | 13:00 | Madaripur | 99 | 00:00 | Sirajganj | 131 | 21:00
Cantonment | 150 | 14:00 | Madartek | 84 | 19:00 | Sonargaon | 89 | 00:00
Chandpur | 78.5 | 21:00 | Madunaghat | 66 | 21:00 | Sreemongol | 55 | 21:00
Chandraghona | 32 | 19:00 | Magura | 58 | 00:00 | Srinagar | 46.52 | 20:00
Chapai | 59 | 00:00 | Mahasthangarh | 76 | 23:00 | SSM | 2 | 00:00
Charsaidpur | 44 | 17:00 | Manikganj | 100 | 20:00 | Sunamganj | 54 | 21:00
Chauddagram | 61 | 21:00 | Maniknagar | 80 | 13:00 | Sylhet | 148 | 20:00
Chhatak | 30 | 19:30 | Matarbari | 43 | 21:00 | Tangail | 210 | 03:00
Chowmuhani | 227 | 22:00 | Matuail | 68 | 16:00 | Thakurgaon | 99 | 20:00
Chuadanga | 110 | 00:00 | Millgate | 60 | 16:00 | TK | N/A | N/A
Coxsbazar | 123 | 19:00 | Mirpur | 140 | 19:30 | Tongi | 132 | 17:00
Cumilla(N) | 165 | 20:00 | Mirsorai | N/A | N/A | Ullon | 42 | 19:00
Cumilla(S) | 164 | 20:00 | Mithapukur | 44 | 21:00 | Uttara | 96 | 15:00
Daudkandi | 155 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 18:30
Dhaka | 36 | 12:00 | Mogbazar | 133 | 15:00 | Zigatola | 44 | 20:00
Dhamrai | 124 | 19:30 | Mongla | 46 | 12:00
Dhanmondi | 208 | 13:00 | Motijheel | 35 | 13:00
Dohazari | 108 | 19:00 | Munshiganj | 106 | 00:00
Faridpur | 145 | 00:00 | Mymensingh | 237 | 23:00
Fatullah | 72 | 15:00 | Naogaon | 112 | 00:00
Fenchuganj | 57 | 20:00 | Narail | 56 | 23:00
Feni | 140 | 21:00 | Narinda | 80 | 13:00
Ghorashal | 49 | 11:00 | Narshingdi | 187 | 00:00
Goalpara | 32 | 21:00 | Natore | 139 | 00:00
Gollamari | 60 | 19:30 | Nawabganj | 62.2 | 21:00
Gopalganj | 108.4 | 21:00 | Netrakona | 96 | 19:00
GPH | 90 | 19:00 | New | 88.9 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 2:00 | 401 | 17:00 | Kaliakoir | 395 | 0.54167 | 382 | 0.91667
| Bheramara | 400 | 6:00 | 391 | 16:00 | Bhulta | 403 | 0.125 | 385 | 0.45833
| Ashuganj(N) | 406 | 3:00 | 391 | 10:00 | Gopalganj | 411 | 0.625 | 382 | 24:00
| Payra | 415 | 18:30 | 405 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 238 | 18:30 | 228 | 23:00
| Ishurdi | 237 | 8:00 | 231 | 3:00 | Megnaghat | 232 | 4:00 | 226 | 15:00
| Ashuganj | 242 | 1:00 | 235 | 9:00 | Fenchuganj | 243 | 4:00 | 237 | 19:00
| Serajganj | 236 | 6:00 | 232 | 21:00 | Siddhirganj | 230 | 3:00 | 222 | 11:00
| Baghabari | 235 | 5:00 | 232 | 17:00 | Maniknagar | 229 | 3:00 | 220 | 10:00
| Barapukuria | 230 | 4:00 | 222 | 21:00 | Agargaon | 230 | 13:00 | 219 | 10:00
| Bogra | 232 | 8:00 | 224 | 19:00 | Barisal | 241 | 13:00 | 232 | 23:00
| Rajshahi | 237 | 18:00 | 230 | 12:00 | Bhola 225 MW | 244 | 8:00 | 232 | 23:00
| Khulna South | 234 | 13:00 | 222 | 3:00 | AKSML
| Rampura | 230 | 3:00 | 220 | 16:00 | BSRM | 237 | 2:00 | 225 | 10:00
| Haripur | 227 | 1:00 | 221 | 11:00 | Bibiyana | 239 | 2:00 | 234 | 16:00
| Hasnabad | 228 | 1:00 | 218 | 11:00 | Bhulta | 232 | 3:00 | 222 | 15:00
| Shyampur | 230 | 3:00 | 220 | 10:00 | Ashuganj (S) | 240 | 2:00 | 233 | 9:00
| Aminbazar | 229 | 1:00 | 220 | 2:00 | Kaliakoir | 231 | 3:00 | 222 | 12:00
| Tongi | 229 | 1:00 | 220 | 10:00 | GPH | 238 | 2:00 | 230 | 23:00
| Comilla (N) | 234 | 3:00 | 227 | 10:00 | Jhenaidah | 229 | 18:30 | 220 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 02:00 | 124 | 11:00 | Manikganj | 132 | 03:00 | 124 | 00:00
| Agargaon | 133 | 02:00 | 126 | 10:00 | Maniknagar | 130 | 03:00 | 121 | 15:00
| Agrabad | 135 | 01:00 | 127 | 10:00 | Matarbari | 127 | 13:00 | 112 | 21:00
| AKS | 136 | 03:00 | 125 | 10:00 | Matuail | 136.8 | 04:00 | 132.4 | 09:00
| Aminbazar | 140 | 03:00 | 130 | 11:00 | Millgate | 138 | 05:00 | 129 | 11:00
| Amnura | 133 | 18:30 | 127 | 12:00 | Mirpur | 140 | 03:00 | 128 | 14:00
| Ashuganj | 138 | 08:00 | 133 | 21:00 | Mithapukur | 133 | 08:00 | 130 | 04:00
| Bagerhat | 135 | 14:00 | 128 | 00:00 | Modern | 135 | 00:00 | 127 | 10:00
| Bakulia | 135 | 00:00 | 127 | 10:00 | Mogbazar | 136 | 03:00 | 125 | 12:00
| Banani | 137 | 03:00 | 128 | 10:00 | Mongla | 135 | 08:00 | 128 | 01:00
| Bangabhaban | 130 | 05:00 | 121 | 15:00 | Motijheel | 130 | 05:00 | 121 | 15:00
| Barapukuria | 133 | 04:00 | 128 | 18:30 | Munshiganj | 139 | 00:00 | 133 | 10:00
| Barguna | 137 | 14:00 | 129 | 04:00 | Mymensingh | 132 | 05:00 | 114 | 22:00
| Barishal | 139 | 06:00 | 131 | 02:00 | Naogaon | 132 | 04:00 | 125 | 19:00
| Barishal | 140 | 07:00 | 133 | 00:00 | Narail | 137 | 08:00 | 129 | 02:00
| Baroaulia | 137 | 00:00 | 126 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 136 | 07:00 | 129 | 19:00 | Narshingdi | 132 | 02:00 | 125 | 10:00
| Bashundhara | 137 | 03:00 | 128 | 11:00 | Natore | 134 | 06:00 | 131 | 00:00
| BashundharaCement | 138 | 00:00 | 133 | 10:00 | Nawabganj | 136 | 00:00 | 129 | 10:00
| Beanibazar | 134 | 00:00 | 125 | 21:00 | Netrakona | 132 | 09:00 | 114 | 22:00
| Benapole | 135 | 06:00 | 129 | 00:00 | New | 137 | 01:00 | 130 | 10:00
| Bhaluka | 130 | 06:00 | 112 | 22:00 | Niamatpur | 132 | 08:00 | 121 | 22:00
| Bhandaria | 136 | 07:00 | 125 | 22:00 | Noapara | 140 | 19:30 | 131 | 04:00
| Bhangura | 138 | 18:30 | 133 | 00:00 | Pabna | 134 | 06:00 | 131 | 03:00
| Bheramara | 137 | 18:30 | 133 | 03:00 | Palashbari | 134 | 08:00 | 125 | 20:00
| Bheramara(GK) | 140 | 18:30 | 135 | 00:00 | Panchagarh | 132 | 04:00 | 123 | 17:00
| Bhulta | 128 | 00:00 | 125 | 10:00 | Patuakhali | 136 | 13:00 | 130 | 01:00
| Bog-Sherpur | 135 | 04:00 | 131 | 19:00 | PHP | 135 | 07:00 | 128 | 19:00
| Bogura | 136 | 04:00 | 132 | 16:00 | Purbachal | 138 | 03:00 | 127 | 10:00
| Bogura | 136 | 05:00 | 132 | 19:00 | Purbasadipur | 133 | 04:00 | 125 | 17:00
| Brahmanbaria | 133 | 06:00 | 126 | 22:00 | Rahim | 137 | 00:00 | 132 | 11:00
| Cantonment | 134 | 03:00 | 124 | 10:00 | Rajbari | 134 | 12:00 | 127 | 00:00
| Chandpur | 140 | 17:00 | 135 | 23:00 | Rajendrapur | 130 | 05:00 | 120 | 22:00
| Chandraghona | 137 | 06:00 | 131 | 10:00 | Rajshahi | 131 | 18:00 | 126 | 12:00
| Chapai | 134 | 18:30 | 127 | 12:00 | Rajshahi | 139 | 23:00 | 126 | 12:00
| Charsaidpur | 141 | 03:00 | 133 | 10:00 | Ramganj | 137 | 12:00 | 130 | 06:00
| Chauddagram | 137 | 17:00 | 131 | 22:00 | Rampur | 134 | 00:00 | 128 | 10:00
| Chhatak | 133 | 08:00 | 127 | 19:00 | Rampura | 138 | 21:00 | 125 | 12:00
| Chowmuhani | 134 | 12:00 | 125 | 19:00 | Rangamati | 136 | 01:00 | 128 | 10:00
| Chuadanga | 134 | 18:30 | 123 | 00:00 | Rangpur | 138 | 10:00 | 122 | 18:30
| Coxsbazar | 122 | 11:00 | 111 | 23:00 | Ruppur | 136 | 16:00 | 134 | 00:00
| Cumilla(N) | 138 | 03:00 | 133 | 10:00 | Saidpur | 132 | 05:00 | 124 | 19:00
| Cumilla(S) | 137 | 17:00 | 125 | 15:00 | Satkhira | 136 | 19:30 | 127 | 00:00
| Daudkandi | 138 | 00:00 | 130 | 10:00 | Satmasjid | 133 | 03:00 | 125 | 10:00
| Dhaka | 135 | 03:00 | 125 | 14:00 | Savar | 140 | 02:00 | 130 | 12:00
| Dhamrai | 133 | 05:00 | 125 | 14:00 | Shahjadpur | 139 | 03:00 | 135 | 08:00
| Dhanmondi | 138 | 01:00 | 132 | 10:00 | Shahjibazar | 135 | 05:00 | 128 | 19:00
| Dohazari | 130 | 07:00 | 123 | 10:00 | Shahmirpur | 136 | 17:00 | 130 | 23:00
| Faridpur | 134 | 12:00 | 128 | 00:00 | Shariatpur | 137 | 11:00 | 127 | 23:00
| Fatullah | 138 | 03:00 | 131 | 09:00 | Sherpur | 138 | 05:00 | 120 | 22:00
| Fenchuganj | 137 | 00:00 | 131 | 21:00 | Shikalbaha | 136 | 06:00 | 133 | 08:00
| Feni | 136 | 07:00 | 130 | 19:00 | Shikalbaha | 136 | 02:00 | 130 | 10:00
| Ghorashal | 140 | 01:00 | 137 | 13:00 | Shitalakhya | 139 | 01:00 | 131 | 12:00
| Goalpara | 140 | 19:30 | 134 | 02:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 140 | 19:30 | 126 | 00:00 | Shyampur | 136 | 02:00 | 130 | 09:00
| Gopalganj | 139 | 13:00 | 128 | 00:00 | Shyampur | 138 | 03:00 | 130 | 10:00
| Gopalganj_I | 140 | 13:00 | 131 | 23:00 | Siddhirganj | 138 | 03:00 | 132 | 10:00
| Gulshan | 133 | 01:00 | 125 | 12:00 | Sirajganj | 133 | 02:00 | 130 | 12:00
| Halishahar | 136 | 13:00 | 126 | 10:00 | Sonargaon | 138 | 00:00 | 133 | 10:00
| Haripur | 137 | 00:00 | 132 | 11:00 | Sreemongol | 136 | 03:00 | 131 | 23:00
| HaripurSBU | 137 | 04:00 | 132 | 12:00 | Srinagar | 135 | 00:00 | 129 | 10:00
| Hasnabad | 139 | 03:00 | 130 | 09:00 | SSM | 140 | 19:30 | 130 | 10:00
| Hathazari | 138 | 00:00 | 133 | 23:00 | Sunamganj | 131 | 08:00 | 123 | 21:00
| Ishurdi | 137 | 06:00 | 134 | 00:00 | Sylhet | 133 | 00:00 | 130 | 14:00
| Jaldhaka | 131 | 07:00 | 122 | 17:00 | Tangail | 133 | 06:00 | 121 | 22:00
| Jamalpur | 138 | 05:00 | 123 | 22:00 | Thakurgaon | 132 | 11:00 | 124 | 06:00
| Jashore | 136 | 18:00 | 129 | 03:00 | TK | N/A | N/A | N/A | N/A
| Jhenaidah | 138 | 19:30 | 132 | 00:00 | Tongi | 138 | 03:00 | 130 | 10:00
| Jhenaidah | 138 | 06:00 | 132 | 03:00 | Ullon | 134 | 01:00 | 125 | 14:00
| Joydebpur | 141 | 01:00 | 134 | 12:00 | Uttara | 139 | 03:00 | 127 | 13:00
| Joypurhat | 132 | 08:00 | 127 | 07:00 | UttaraNew | 140 | 03:00 | 129 | 14:00
| Juldah | 136 | 01:00 | 131 | 10:00 | Zigatola | 136 | 04:00 | 129 | 11:00
| Kabirpur | 136 | 16:00 | 122 | 19:30
| Kachua | 138 | 16:00 | 133 | 22:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 138 | 04:00 | 129 | 12:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 137 | 02:00 | 129 | 11:00
| Kaptai | 135 | 00:00 | 133 | 10:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 214 | 9062 | 4663 | 13725 |  |  |  | QF-LDC-11
0:30 | 110 | 8904.5 | 4432.5 | 13337 | Date: | 2022-04-24
1:00 | 6 | 8747 | 4202 | 12949
1:30 | 43 | 8694 | 4131 | 12825
2:00 | 80 | 8641 | 4060 | 12701
2:30 | 127 | 8712.5 | 4031 | 12743.5 | [5 empty] | Gen. at Eve. Peak | 13975 | 13975 MW (21:00 )
3:00 | 174 | 8784 | 4002 | 12786 | [6 empty] | 21:00
3:30 | 143 | 8572 | 3903 | 12475 | [5 empty] | Gen. at Day Peak | 11995 | 11995 MW (12:00 )
4:00 | 112 | 8360 | 3804 | 12164 | [6 empty] | 12:00
4:30 | 129 | 8174.5 | 3600.5 | 11775 | [5 empty] | Highest Generation | 14078
5:00 | 146 | 7989 | 3397 | 11386 | [6 empty] | 22:00
5:30 | 76 | 7721.5 | 3290 | 11011.5
6:00 | 6 | 7454 | 3183 | 10637
6:30 | 114 | 7291 | 3189.5 | 10480.5
7:00 | 222 | 7128 | 3196 | 10324
7:30 | 260 | 7105 | 3235.5 | 10340.5
8:00 | 298 | 7082 | 3275 | 10357
8:30 | 330 | 7164 | 3314 | 10478
9:00 | 362 | 7246 | 3353 | 10599
9:30 | 377 | 7305 | 3425.5 | 10730.5
10:00 | 392 | 7364 | 3498 | 10862
10:30 | 419 | 7613 | 3625.5 | 11238.5
11:00 | 446 | 7862 | 3753 | 11615
11:30 | 400 | 8064 | 3741 | 11805
12:00 | 354 | 8266 | 3729 | 11995
12:30 | 316 | 8424.5 | 3818 | 12242.5
13:00 | 278 | 8583 | 3907 | 12490
13:30 | 336 | 8625.5 | 3983.5 | 12609
14:00 | 394 | 8668 | 4060 | 12728
14:30 | 449 | 8672.5 | 4143.5 | 12816
15:00 | 504 | 8677 | 4227 | 12904
15:30 | 502 | 8683.5 | 4209.5 | 12893
16:00 | 500 | 8690 | 4192 | 12882
16:30 | 440 | 8655.5 | 4187.5 | 12843
17:00 | 380 | 8621 | 4183 | 12804
17:30 | 397 | 8513 | 4226 | 12739
18:00 | 414 | 8405 | 4269 | 12674
18:30 | 323 | 8763.5 | 4350.5 | 13114
19:00 | 232 | 9122 | 4432 | 13554
19:30 | 340 | 9163 | 4666 | 13829
20:00 | 300 | 9286 | 4662 | 13948 |  |  |  | Executive Engineer
20:30 | 272 | 9286 | 4675.5 | 13961.5 |  |  |  | Network Operation Division
21:00 | 244 | 9286 | 4689 | 13975
21:30 | 246 | 9309 | 4717.5 | 14026.5
22:00 | 248 | 9332 | 4746 | 14078 |  |  |  |  | Page 6 of 7
22:30 | 266 | 9264.5 | 4714.5 | 13979
23:00 | 284 | 9197 | 4683 | 13880
23:30 | 249 | 9129.5 | 4673 | 13802.5
24:00 | 214 | 9062 | 4663 | 13725
13975 MW (21:00 )
11995 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-24 |  | Energy |  | 301090226
[13 empty] | 2022-04-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3526 | 918 | 2105 | 1001 | 4232 | 825 | 56 | 384 | 737 | 154 | 0 | 0
0:30 | 3546 | 918 | 2096.5 | 718 | 4198.5 | 860.5 | 56.5 | 298.5 | 674 | 151 | 0 | 0 | Date: | 2022-04-24
1:00 | 3566 | 918 | 2088 | 435 | 4165 | 896 | 57 | 213 | 611 | 148 | 0 | 0
1:30 | 3586.5 | 917.5 | 2084.5 | 384.5 | 4138.5 | 896 | 57.5 | 151 | 564 | 146 | 0 | 0 | [8 empty] | Total Energy | 301.0902 | Total Energy Gen 301.090 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 301.090 MKWHr
2:00 | 3607 | 917 | 2081 | 334 | 4112 | 896 | 58 | 89 | 517 | 144 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3620.5 | 917.5 | 2086.5 | 405 | 4106 | 896.5 | 58 | 49.5 | 491.5 | 143 | 0 | 0 | [8 empty] | Energy Requirement | 301.0902
3:00 | 3634 | 918 | 2092 | 476 | 4100 | 897 | 58 | 10 | 466 | 142 | 0 | 0
3:30 | 3634.5 | 919 | 2089.5 | 238 | 4077.5 | 896.5 | 58.5 | 11.5 | 413 | 142 | 0 | 0 | [6 empty] | Shortage
4:00 | 3635 | 920 | 2087 | 0 | 4055 | 896 | 59 | 13 | 360 | 142 | 0 | 0
4:30 | 3638.5 | 920.5 | 2101.5 | 0 | 3831.5 | 866 | 59 | 12.5 | 213 | 135 | 0 | 0
5:00 | 3642 | 921 | 2116 | 0 | 3608 | 836 | 59 | 12 | 66 | 128 | 0 | 0
5:30 | 3647.5 | 920.5 | 2115 | 0 | 3274.5 | 815.5 | 59 | 12 | 42 | 125 | 2.5 | 0
6:00 | 3653 | 920 | 2114 | 0 | 2941 | 795 | 59 | 12 | 18 | 122 | 5 | 0
6:30 | 3659.5 | 920 | 2091.5 | 0 | 2791 | 790 | 58.5 | 13.5 | 19.5 | 120 | 20.5 | 0 |  |  |  |  | Coal
7:00 | 3666 | 920 | 2069 | 0 | 2641 | 785 | 58 | 15 | 21 | 118 | 36 | 0
7:30 | 3637.5 | 922 | 2047 | 0 | 2691 | 755 | 57.5 | 40.5 | 36.5 | 118 | 56 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3609 | 924 | 2025 | 0 | 2741 | 725 | 57 | 66 | 52 | 118 | 76 | 0
8:30 | 3609 | 923.5 | 2018 | 0 | 2836 | 724.5 | 57 | 77 | 60 | 121 | 94 | 0
9:00 | 3609 | 923 | 2011 | 0 | 2931 | 724 | 57 | 88 | 68 | 124 | 112 | 0
9:30 | 3483.5 | 923 | 2014 | 15 | 3111.5 | 714 | 56.5 | 112.5 | 101.5 | 126 | 140.5 | 0
10:00 | 3358 | 923 | 2017 | 30 | 3292 | 704 | 56 | 137 | 135 | 128 | 169 | 0
10:30 | 3376.5 | 923.5 | 2010 | 92 | 3447 | 714 | 56 | 200 | 212 | 131 | 181.5 | 0
11:00 | 3395 | 924 | 2003 | 154 | 3602 | 724 | 56 | 263 | 289 | 134 | 194 | 0
11:30 | 3358.5 | 923.5 | 1996.5 | 266.5 | 3701 | 708.5 | 56.5 | 285.5 | 320 | 137 | 198 | 0
12:00 | 3322 | 923 | 1990 | 379 | 3800 | 693 | 57 | 308 | 351 | 140 | 202 | 0
12:30 | 3341.5 | 923 | 1969.5 | 527 | 3848 | 698.5 | 57 | 324 | 404.5 | 142 | 193.5 | 0
13:00 | 3361 | 923 | 1949 | 675 | 3896 | 704 | 57 | 340 | 458 | 144 | 185 | 0
13:30 | 3361 | 923 | 1949 | 675 | 3896 | 704 | 57 | 340 | 458 | 144 | 185 | 0
14:00 | 3361 | 923 | 1949 | 675 | 3896 | 704 | 57 | 340 | 458 | 144 | 185 | 0
14:30 | 3339.5 | 923.5 | 1945 | 835 | 3908 | 730 | 57 | 341.5 | 509 | 150.5 | 161.5 | 0
15:00 | 3318 | 924 | 1941 | 995 | 3920 | 756 | 57 | 343 | 560 | 157 | 138 | 0
15:30 | 3362 | 923.5 | 1944.5 | 901.5 | 3953 | 766 | 57 | 342.5 | 574.5 | 152.5 | 120.5 | 0
16:00 | 3406 | 923 | 1948 | 808 | 3986 | 776 | 57 | 342 | 589 | 148 | 103 | 0
16:30 | 3358 | 923 | 1933 | 758.5 | 4062 | 766.5 | 57 | 342.5 | 605.5 | 146 | 71.5 | 0
17:00 | 3358 | 923 | 1918 | 709 | 4138 | 757 | 57 | 343 | 622 | 144 | 40 | 0
17:30 | 3354.5 | 923 | 1928 | 555 | 4181.5 | 755 | 57.5 | 357 | 666 | 145 | 22.5 | 0
18:00 | 3351 | 923 | 1938 | 401 | 4225 | 753 | 58 | 371 | 710 | 146 | 5 | 0
18:30 | 3389.5 | 923 | 1975 | 658.5 | 4283 | 762 | 58 | 374.5 | 741.5 | 154 | 2.5 | 0
19:00 | 3428 | 923 | 2012 | 916 | 4341 | 771 | 58 | 378 | 773 | 162 | 0 | 0
19:30 | 3487 | 923 | 2082 | 907 | 4406 | 810 | 58 | 380 | 832 | 154 | 0 | 0
20:00 | 3496 | 923 | 2108 | 1000 | 4399 | 812 | 58 | 381 | 817 | 164 | 0 | 0
20:30 | 3500.5 | 920.5 | 2133.5 | 1001.5 | 4389.5 | 812.5 | 57.5 | 379.5 | 812 | 164 | 0 | 0
21:00 | 3505 | 918 | 2159 | 1003 | 4380 | 813 | 57 | 378 | 807 | 164 | 0 | 0
21:30 | 3523 | 918 | 2156.5 | 1003.5 | 4418 | 814 | 56.5 | 379 | 803.5 | 164 | 0 | 0
22:00 | 3541 | 918 | 2154 | 1004 | 4456 | 815 | 56 | 380 | 800 | 164 | 0 | 0
22:30 | 3536.5 | 918 | 2155 | 1002 | 4373.5 | 814 | 56 | 379.5 | 793.5 | 161 | 0 | 0
23:00 | 3532 | 918 | 2156 | 1000 | 4291 | 813 | 56 | 379 | 787 | 158 | 0 | 0
23:30 | 3529 | 918 | 2130.5 | 1000.5 | 4261.5 | 819 | 56 | 381.5 | 762 | 156 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 36.4° C
24:00 | 3526 | 918 | 2105 | 1001 | 4232 | 825 | 56 | 384 | 737 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 301.090 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 301.090 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 27 | 28 | 28 | 29 | 29 | 29 | 28 | 27 | 27 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 28 |  | 28 | 28 | 28 | 27 | 26 | 26 | 26 | 645905
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 0 |  |  |  |  | 13 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 482016
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 3 | 12 | 17 | 19 | 20 | 19 | 17 | 13 | 8 | 3 | 0 | [8 empty] | 137160
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 204 | 204 | 203 | 204 | 213 | 203 | 206 | [6 empty] | 80 | 82 | 80 |  | 140 | 131 | 131 | 147 | 150 | 141 | 131 | 2978054
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 27 |  | 51 | 51 | 51 | 51 | 51 | 51 |  | 265934
12 | Hathazari 100 MW peaking PP | 40 | 40 | 38 | 17 | 0 | [6 empty] | 5 | 26 | 25 | 25 | 25 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 549224
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 37 | 39 | 51 | 51 | 51 | 56 | 74 | 87 | 105 |  | 105 | 105 | 105 | 105 | 105 | 92 | 57 | 1615018
| Daudkandi 200 MW PP (B.Trac) | 50 | 50 | 100 | 0 | [6 empty] | 25 | 40 | 150 | 200 | 200 | 160 | 120 | 30 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2294976
14 | Titas 50 MW Peaking PP | 50 | 50 | 50 | 0 | [8 empty] | 0 | 18 | 39 | 47 | 47 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 671520
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 291 | 286 | 286 | 291 | 293 | 145 | 145 | 145 | 145 | 215 | 253 | 268 | 276 | 276 | 276 | 276 | 277 | 275 |  | 277 | 275 | 275 | 278 | 275 | 278 | 276 | 6172361
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 334545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 232 | 233 | 233 | 235 | 235 | 235 | 234 | 235 | 235 | 235 | 232 | 230 | 228 | 235 | 227 | 227 | 227 | 230 |  | 230 | 230 | 231 | 230 | 231 | 231 | 232 | 5542000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6368500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 646992
33 | Ashuganj 225 MW CCPP | 216 | 218 | 218 | 218 | 217 | 218 | 216 | 217 | 214 | 208 | 213 | 210 | 211 | 208 | 212 | 210 | 210 | 211 |  | 211 | 213 | 213 | 212 | 212 | 210 | 218 | 5154000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 230 | 230 | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5528300
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 54 | 55 | 55 | 55 | 55 | 54 | 54 | 53 | 52 | 49 | 46 | 48 | 47 | 49 | 47 | 49 |  | 49 | 50 | 52 | 51 | 53 | 54 | 54 | 1243680
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 393 | 393 | 393 | 393 | 394 | 393 | 394 | 401 | 402 | 395 | 396 | 395 | 394 | 394 | 396 | 394 | 396 | 370 |  | 382 | 397 | 394 | 394 | 394 | 399 | 398 | 9592830
40 | Meghnaghat 450 MW CCPP(MPL) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6119500
41 | Haripur 360MW CCPP(HPL) | 238 | 246 | 258 | 270 | 280 | 280 | 280 | 280 | 278 | 277 | 272 | 267 | 266 | 267 | 267 | 262 | 261 | 261 |  | 287 | 291 | 282 | 282 | 277 | 276 | 277 | 6486000
42 | RPCL 210MW CCPP | 93 | 98 | 97 | 98 | 99 | 100 | 98 | 98 | 99 | 94 | 81 | 80 | 81 | 80 | 81 | 80 | 70 | 70 |  | 92 | 95 | 95 | 95 | 95 | 95 | 95 | 2091840
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 6 | 14 | 23 | 31 | 39 | 36 | 31 | 36 | 31 | 22 | 9 | 1 | [8 empty] | 309730
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 40 | 40 | 40 |  | 40 | 41 | 40 | 40 | 42 | 42 | 42 | 946472
46 | Shajibazar 330 MW CCPP | 158 | 157 | 158 | 157 | 158 | 159 | 159 | 158 | 158 | 153 | 156 | 154 | 153 | 154 | 151 | 153 | 152 | 153 |  | 152 | 155 | 155 | 153 | 155 | 157 | 157 | 3686000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 55 | 55 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1288128
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 81 | 81 | 81 | 78 | 78 | 40 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 81 | 78 | 78 | 78 | 78 | 78 | 1019520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 216 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 219 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 5236420
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [6 empty] | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 178560
54 | Hobiganj 11MW PP Cofidence-E | [23 empty] | 11 |  | 11 | 28032
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | [20 empty] | 5 | 16 | 16 | 16 | 16 | 0 | 23671
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 275 | 280 | 270 | 280 | 280 | 300 | 285 | 300 | 290 | 290 | 290 | 285 | 280 | 280 | 285 | 290 | 290 |  | 280 | 290 | 290 | 305 | 310 | 315 | 290 | 7151500
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 400 | 400 | 400 | 401 | 394 | 387 | 393 | 386 | 388 | 394 | 392 | 392 | 384 | 395 |  | 389 | 395 | 390 | 384 | 388 | 393 | 401 | 9318000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 596460
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 24 | 24 | 16 | 21 | 24 | 24 | 24 | 24 | 22 | 17 | 5 | 14 | 18 | 21 |  | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 517920
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 525744
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 401472
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 411228
63 | Impoprt (Tripura) | 148 | 144 | 142 | 142 | 128 | 122 | 118 | 118 | 124 | 128 | 134 | 140 | 144 | 148 | 157 | 148 | 144 | 146 |  | 162 | 154 | 164 | 164 | 164 | 158 | 154 | 3381120
64 | Malancha, Ctg. EPZ (United) | 27 | 28 | 28 | 28 | 28 | 24 | 5 | 8 | 7 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 2 | 9 |  | 3 | 15 | 20 | 20 | 20 | 20 | 20 | 322080
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499176
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 25 | 24 | 24 |  | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 740100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 19 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 482720
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 26 | 26 | 24 | 24 | 24 | 24 |  | 18 | 25 | 26 | 26 | 26 | 26 | 26 | 598140
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789840
72 | Rupganj 33 MW PP(Summit) | 22 | 22 | 22 | 24 | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 0 | 30 | 30 | 30 | 31 |  | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 642100
73 | Ghorashal 108MW PP (Regent) | 88 | 88 | 88 | 90 | 93 | 93 | 93 | 93 | 91 | 93 | 90 | 92 | 92 | 91 | 91 | 91 | 94 | 94 |  | 95 | 95 | 97 | 97 | 100 | 98 | 94 | 2171408
| Feni Lanka Power | 96 | 96 | 96 | 96 | 82 | 78 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 82 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 2270880
| Chowmuhani 113 MW | 72 | 42 | 41 | 38 | 38 | 38 | 39 | 39 | 38 | 39 | 42 | 38 | 37 | 34 | 44 | 52 | 112 | 112 |  | 114 | 113 | 112 | 113 | 113 | 113 | 107 | 1580040
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 141 | 126 | 126 |  | 132 | 144 | 144 | 144 | 144 | 144 | 144 | 3515040
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 95 | 0 |  |  | 0 | 5 | 38 | 67 | 85 | 88 | 96 | 98 | 98 | 96 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1830720
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 16 | 25 | 25 | 27 | 45 | 49 | 49 | 42 | 42 | 48 | 48 | 48 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 1057440
79 | Kodda 150MW PP | 115 | 115 | 115 | 115 | 64 | 16 | 16 | 16 | 20 | 48 | 115 | 115 | 115 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 125 | 115 | 115 | 2367360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1033934
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 86 | 90 | 73 | 90 | 90 | 90 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2270400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 3 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 33480
| Jodiac Power | 54 | 54 | 40 | 54 | 54 | 54 | 54 | 54 | 54 |  | 25 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1296388
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 103 | 103 | 68 | 78 | 95 | 63 | 58 | 105 | 109 | 110 | 110 | 102 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2473117
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 79 | 79 | 64 | 64 | 64 | 64 | 75 | 75 | 74 | 75 |  | 75 | 75 | 78 | 78 | 78 | 78 | 70 | 1819440
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 140 | 130 | 130 | 130 | 130 | 145 | 130 | 130 | 130 | 145 | 130 | 145 | 130 | 135 | 135 | 135 | 135 | 135 |  | 135 | 120 | 140 | 150 | 150 | 150 | 135 | 3255796
87 | Meghnaghat 100 MW(IEL) | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 97 | 97 | 96 | 96 | 96 | 95 | 94 | 94 | 89 | 90 | 94 |  | 96 | 96 | 95 | 96 | 95 | 96 | 96 | 2314560
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 71 | 70 | 80 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2516160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 70 | 70 | 70 | 70 | 30 | 0 |  |  | 12 | 30 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1452000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 43 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1091752
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 84 | 84 | 84 | 84 | 64 | 64 | 64 | 76 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1955952
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 14 | 18 | 24 | 24 | 24 | 0 |  |  | 13 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 508320
96 | Chattogram 108 MW PP (ECPV) | 96 | 95 | 95 | 95 | 95 | 95 | 96 | 95 | 85 | 0 | 18 | 59 | 79 | 85 | 87 | 88 | 91 | 94 |  | 95 | 95 | 95 | 95 | 96 | 95 | 95 | 2048640
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 50 | 45 | 40 | 48 | 55 | 48 | 48 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1156200
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1126361
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3853963
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15300
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1172520
104 | Keranigonj 300 MW PP (APR) | 54 | 53 | 75 | 0 | [5 empty] | 30 | 54 | 158 | 276 | 300 | 304 | 231 | 197 | 81 |  | 302 | 207 | 300 | 303 | 304 | 300 | 301 | 3268090
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | 50 | 100 | 0 | [6 empty] | 50 | 90 | 90 | 90 | 93 | 94 | 92 | 30 |  | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 1509024
106 | Mymensingh 200 MW PP (United) | 190 | 189 | 189 | 189 | 189 | 100 | 64 | 64 | 82 | 166 | 157 | 159 | 156 | 153 | 153 | 153 | 163 | 164 |  | 176 | 176 | 176 | 178 | 188 | 188 | 187 | 3770400
112 | Aurahati 100MW PP (Aggreko) | 100 | 50 | 50 | 0 | [6 empty] | 25 | 91 | 100 | 97 | 99 | 99 | 60 | 30 |  | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 1356445
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 118 | 86 | 96 | 128 | 133 | 138 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3419136
115 | Juldah 100 MW PP Unit-3 (Acorn) | 88 | 88 | 87 | 87 | 76 | 76 | 76 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2029440
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 100 | 51 | 51 | 68 | 71 | 104 | 154 | 165 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3879360
117 | Ashuganj 150MW PP (Midland) | 150 | 140 | 142 | 145 | 100 | 50 | 50 | 50 | 62 | 125 | 150 | 150 | 147 | 135 | 130 | 133 | 138 | 135 |  | 133 | 140 | 137 | 145 | 133 | 123 | 150 | 3059418
118 | Bibiyana-III 400 MW CCPP | 400 | 401 | 401 | 401 | 400 | 400 | 402 | 402 | 403 | 395 | 404 | 370 | 398 | 404 | 405 | 405 | 399 | 401 |  | 390 | 404 | 405 | 394 | 404 | 404 | 400 | 9595000
| Jamalpur 115 MW PP (United) | 107 | 107 | 107 | 97 | 107 | 107 | 75 | 75 | 80 | 107 | 107 | 97 | 96 | 104 | 104 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2486400
| Anwara 300 MW PP (United) | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 292 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7130836
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 92 | 50 | 50 | 70 | 90 | 90 | 92 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2231040
| Anlima Energy Ltd. | 105 | 105 | 105 | 105 | 105 | 90 | 51 | 51 | 51 | 81 | 102 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 |  |  | 2181655
| Bhairob 54.5 MW | 36 | 36 | 36 | 20 | 36 | 36 | 36 | 36 | 36 | 20 | 36 | 36 | 36 | 36 | 35 | 34 | 34 | 20 |  | 36 | 36 | 36 |  | 23 | 36 | 36 | 796680
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 10 |  | 29 | 32 | 33 | 32 | 28 | 22 | 15 | 6 | 1 | [8 empty] | 234953
| Chandpur 115(Doreen) | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 100 | 101 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 2444160
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1360800
120 | Eastern Zone Total | 8747 | 8641 | 8784 | 8360 | 7989 | 7454 | 7128 | 7082 | 7246 | 7364 | 7862 | 8266 | 8583 | 8668 | 8677 | 8690 | 8621 | 8405 |  | 9122 | 9163 | 9286 | 9286 | 9332 | 9197 | 9062 | 202455476
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 0 |  |  | 6 | 31 | 31 | 31 | 30 | 30 | 30 | 28 | 28 | 64 |  | 108 | 115 | 110 | 112 | 110 | 66 | 32 | 904320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 33 | 33 | 28 | 0 | [5 empty] | 2 | 4 | 4 | 12 | 26 | 29 | 32 | 34 |  | 34 | 44 | 36 | 36 | 36 | 37 | 37 | 444960
| Khulna 225 MW CCPP | 65 | 35 | 3 | 10 | 10 | 10 | 10 | 30 | 40 | 50 | 140 | 138 | 138 | 138 | 138 | 138 | 138 | 140 |  | 145 | 145 | 146 | 146 | 147 | 145 | 147 | 2343360
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 94 | 94 | 53 | 57 | 70 | 76 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 92 | 92 |  | 92 | 92 | 92 | 92 | 94 | 94 | 94 | 2127840
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 19 | 42 | 66 | 82 | 92 | 95 | 91 | 80 | 64 | 50 | 19 | 2 | [8 empty] | 707040
131
132 | United Payra Power Ltd. | [17 empty] | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 140400
133 | Bhola Nutan Biddut BD LTD (GAS) | 217 | 212 | 209 | 206 | 218 | 209 | 220 | 220 | 216 | 216 | 216 | 212 | 211 | 211 | 206 | 201 | 208 | 173 |  | 220 | 220 | 220 | 215 | 215 | 218 | 220 | 5083418
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 798720
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 88 | 87 | 88 | 85 | 88 | 86 | 84 | 87 | 84 | 82 | 85 | 81 | 84 | 84 | 85 | 85 | 85 | 85 |  | 82 | 82 | 85 | 85 | 84 | 85 | 87 | 2067998
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 36 | 37 | 33 | 30 | 25 | 25 | 15 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 26 | 28 |  | 33 | 33 | 37 | 39 | 33 | 38 | 37 | 716533
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 20 | 40 | 0 | [5 empty] | 0 |  |  | 30 | 80 | 100 | 30 | 40 | 30 |  | 47 | 100 | 100 | 100 | 100 | 100 | 100 | 1046400
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 16 | 16 | 16 | 16 | 8 | 8 | 79875
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 30 |  | 50 | 80 | 70 | 65 | 65 | 60 | 60 | 358016
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 0 | [7 empty] | 5 | 58 | 78 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1240416
146 | Bheramara HVDC | 918 | 917 | 918 | 920 | 921 | 920 | 920 | 924 | 923 | 923 | 924 | 923 | 923 | 924 | 924 | 923 | 923 | 923 |  | 923 | 923 | 923 | 918 | 918 | 918 | 918 | 22266909
147 | Bheramara 410 MW CCPP | 170 | 175 | 180 | 180 | 180 | 185 | 190 | 185 | 185 | 170 | 175 | 155 | 168 | 160 | 170 | 170 | 170 | 165 |  | 165 | 175 | 175 | 185 | 190 | 185 | 180 | 4420512
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 560 | 520 | 510 | 450 | 450 | 430 | 450 | 420 | 430 | 440 | 480 | 500 | 480 | 480 |  | 500 | 540 | 540 | 540 | 540 | 540 | 550 | 13426600
149
150 | Barapukuria TPP Unit-1 | 74 | 75 | 75 | 75 | 76 | 75 | 75 | 76 | 75 | 75 | 75 | 74 | 75 | 75 | 76 | 77 | 77 | 73 |  | 71 | 70 | 72 | 73 | 75 | 74 | 75 | 1766400
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 199 | 200 | 199 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 199 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 4851200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 43 | 43 | 0 | [5 empty] | 34 | 40 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 722864
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 5 | 5 | 5 | 5 | 4 | 3 | 2 | [10 empty] | 38520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 135 | 135 | 135 | 135 | 138 | 143 | 146 | 149 | 152 | 150 | 150 | 147 | 143 | 138 | 137 | 137 | 138 | 136 |  | 137 | 138 | 139 | 143 | 145 | 145 | 145 | 4390664
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 148 | 54 | 7 | 3 | 2 | 2 | 5 | 36 | 48 | 87 | 123 | 170 | 202 | 204 | 205 | 204 | 205 | 207 |  | 208 | 210 | 210 | 209 | 210 | 210 | 213 | 3370182
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 415 | 414 | 415 | 414 | 414 | 414 | 414 | 400 | 370 | 370 | 367 | 370 | 370 | 370 |  | 370 | 365 | 370 | 400 | 396 | 387 | 388 | 9398218
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 31 | 29 | 23 | 0 | [6 empty] | 4 | 16 | 17 | 17 | 17 | 17 | 17 |  | 20 | 20 | 22 | 22 | 21 | 22 | 21 | 346330
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 17 | 17 | 17 | 17 | 16 | 18 | 19 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 457680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 196776
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | [11 empty] | 16 | 16 | 16 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 410256
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 12 | [6 empty] | 15 | 13 | 19 | 24 | 24 | 24 | 16 | 16 |  | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 367051
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | [11 empty] | 19 | 38 | 38 |  | 37 | 37 | 38 | 38 | 38 | 38 | 37 | 423974
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 8 | 16 | 34 | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1112424
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | [8 empty] | 33 | 49 | 49 | 49 | 50 | 75 |  | 91 | 91 | 91 | 87 | 87 | 87 | 87 | 1150176
171 | Baghabari 200 MW PP (Paramount) | 111 | 111 | 111 | [9 empty] | 29 | 111 | 199 | 194 | 200 | 200 |  | 171 | 200 | 200 | 200 | 200 | 200 | 200 | 2343951
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 93 | 93 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2380800
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 70 | 94 | 95 | 95 | 95 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 113 | 113 | 113 | 1881312
173 | Rangpur 20 MW GTPP | [17 empty] | 16 |  | 17 | 17 | 17 | 15 | 15 | 16 | 16 | 99000
175 | Saidpur 20 MW GTPP | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 48000
176 | Rangpur 113 MW PP (Confidence) | 109 | 109 | 109 | 109 | 104 | 55 | 70 | 70 | 85 | 102 | 101 | 94 | 93 | 99 | 105 | 105 | 105 | 105 |  | 92 | 108 | 108 | 108 | 108 | 108 | 108 | 2363049
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 0 |  | 6 | 0 | 0 | 0 | 3 | 2 | 1 |  | 0 | [6 empty] | 17486
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 17 | 17 | 24 | 52 | 58 | 76 | 115 | 110 | 107 | 107 | 104 | 105 | 109 | 110 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2325120
178