## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-27 | Wednesday
|  |  | Date (day): | 2022-04-27 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15295.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15536 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-26 | 2022-04-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 231 | 231 | 240 | 240
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 93 | 96 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 404 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 301 | 300 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 290 | 290 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 54 | 24 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 130 | 120 | 150 | 150 |  | 185 | GT-1 Under S/D
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 78 | 78 | 80 | 80 |  | 22 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  |  | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 84 | 98 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 84 | 85 | 85 |  | 17 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 146 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 25 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 16 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 49 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 258 | 296 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 111 | 301 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 90 | 98 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 25 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 130 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 6 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5998 | 3415 | 3806 | 4052 | 4062 | 1171 | 767
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 32 | 25 | 35 |  | 15 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 56 | 58 | 60 | 60 |  | 170 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 152 | 151 | 150 | 150
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 50 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 92 | 90 | 90 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 5 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 84 | 96 | 95 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 108 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1325 | 1467 | 1471 | 1476 | 231 | 595
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 216 | 225 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 325 | 300 | 360
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 28 | 28 | 28 | 17 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 48 | 53 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 45 | 45 | 150 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 127 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 47 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 100 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 185 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 154 | 132 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 42 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 30 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 98 | 96 | 96 |  | 18 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 113 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 35 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 101 | 101 | 101 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1545 | 1969 | 2022 | 2106 | 790 | 122
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 117 | 119 | 110 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 183 | 186 | 190 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 105 | 115 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 24 | 24
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 489 | 461 | 507.6 | 456 | 92 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 155 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 50 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 86 | 81 | 81
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 221 | 220 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 17 | 17 | 17 | 25 |  | Gas shortage
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 310 | 310 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 403 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1749 | 1836 | 1874 | 1874 | 366 | 218
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 921 | 914 | 791 | 791 |  |  | Load curtailment from India
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 15 | 16 | 115 | 115
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 37 | 37 |  | 17 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 140 | 200 | 150 | 200
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 64 | 0 | 80 |  | 29 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 190 | 185 | 200 | 200 | 210 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 21 | 32 | 32 |  | 8 | Engine problem
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 17 | 100 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 95 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 67 | 105 | 105 | 105
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1540 | 1747 | 1735 | 1765 | 210 | 54
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 50 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 25 | 38 | 33 | 37
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 67 | 90 | 90 | 104 |  | Gas shortage & GT-1 S/D
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 940 | 1080 | 1060 | 1080
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 210 | 206 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1292 | 1440 | 1603 | 1687 | 104 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 36 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 30 | 30 |  | 41 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 141 | 139 | 150 | 150 | 60 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 211 | 213 | 200 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 414 | 400 | 410
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 30 | 38 |  | 12 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 43 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 92 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 12 | 149 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1058 | 1496 | 1528 | 1578 | 451 | 140
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 70 | 72 | 70 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 |  | 74 | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 99 | 107 | 110 | 110
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 108 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 482 | 494 | 503 | 532 | 0 | 169
|  | Total |  |  |  |  | 22348 | 21734 | 12895 | 14716 | 15295.6 | 15536 | 3415 | 2073
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 12448.398 | 14206.33 | 14765.8563 | 14997.9303
| A. |  | 2022-04-26 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 14716 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11491 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14716 | MW
| 3 | Day peak Generation : |  |  | 12895 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14206.33 | MW
| 4 | Evening peak Generation : |  |  | 14716 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 322.179 | MKWHr | By Solar | 1.4467 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 140.179 | MKWHr |  | By Oil: | 121.1539 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 32.3826 | MKWHr |  | By Hydro: | 1.3484 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3415 | MW | Dhaka | 5055.13 | 5055.13 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2073 | MW | Chittagong | 1449 | 1449 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5488 | MW | Khulna | 1875.8 | 1875.8 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1052.56 | MMCFD |  |  | Rajshahi | 1673.4 | 1673.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 138612835.298 | ii) Oil : | Taka | 1042653862.46 | Comilla | 1366 | 1366 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 149917076.27 | Total | Taka | 1331183774.028 | Mymensingh | 1112 | 1112 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 576 | 576 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 334 | MW (E to W) at | 21:00 | hrs | Barisal | 431 | 431 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 90 | MW at | 3:00 | hrs | Rangpur | 668 | 668 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 14206.33 | 14206.33 |  | 0
| B. |  | 2022-04-27 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 40.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15536 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12500 | MW
| 4 | Reserve(Generation end) |  |  |  | 736 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 324.018 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10409 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 914 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.456 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.32 |  | (b) Today: | 76.97 |  | (c) Rule Curve: |  | 82.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 397 | 294 |  | 0 | 280 | 130 | 8 | 64 | 55 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 25 | 30 | 0 | 0 | 25 | 132 | 0 | 0 | 0 |  | 24 | 43 | 0 | 92 | 94 | 37 | 19 | 27 | 0 | 0 | 0 | 320 | 0 | 213 | 8 | 90 | 28 | 54 | 0 | 51 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 162 | 140 | 0 | 17 | 0 | 0 | 41 | 10 | 0 | 163 | 157 | 50 | 76 | 0 | 219 | 0 | 0 | 10 | 280 | 17 | 0 | 200 | 283 | 103 | 95 | 188 | 100 | 142 | 0 | 90 | 200 | 150 | 403 | 115 | 105 | 51 | 0 | 281 | 54 | 92 | 81 | 36 | 100 | 396 | 99 | 0 | 126 | 108 | 0 | 36 | 0 | 78 | 55 |  | 921 | 0 | 180 | 0 | 110 | 145 | 0 | 0 | 37 | 38 | 0 | 88 | 39 | 32 | 0 | 0 | 0 | 34 | 22 | 90 | 0 | 43 | 22 | 43 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 131 | 0 | 0 | 215 | 0 | 100 | 0 | 0 | 412 | 105 | 122 | 113 | 105 | 108 | 0 | 0 | 113 | 1040 | 206 | 0 | 17 | 0 | 0 | 115 |  | 8931 | 5096 | 14027 | 3764 | 921 | 2163 | 720 | 4075 | 1312 | 55 | 368 | 702 | 162 | 0 | 0 | 77.42
2:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 397 | 292 |  | 0 | 280 | 130 | 7 | 74 | 55 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 25 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 22 | 43 | 0 | 92 | 90 | 37 | 19 | 27 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 90 | 28 | 53 | 0 | 51 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 156 | 150 | 0 | 17 | 0 | 0 | 41 | 10 | 0 | 163 | 158 | 50 | 76 | 0 | 219 | 0 | 0 | 10 | 270 | 17 | 0 | 100 | 273 | 104 | 50 | 188 | 50 | 149 | 0 | 90 | 200 | 150 | 402 | 115 | 105 | 51 | 0 | 300 | 54 | 93 | 81 | 31 | 100 | 400 | 104 | 0 | 126 | 108 | 0 | 36 | 0 | 77 | 55 |  | 921 | 0 | 180 | 0 | 110 | 40 | 0 | 0 | 37 | 38 | 0 | 88 | 39 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 43 | 22 | 43 | 38 | 0 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 132 | 0 | 0 | 216 | 0 | 50 | 0 | 0 | 411 | 105 | 50 | 113 | 105 | 108 | 0 | 0 | 113 | 1040 | 204 | 0 | 17 | 0 | 0 | 115 |  | 8749 | 4848 | 13597 | 3777 | 921 | 2125 | 404 | 4094 | 1312 | 55 | 264 | 705 | 156 | 0 | 0 | 77.4
3:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 398 | 291 |  | 0 | 280 | 130 | 7 | 78 | 55 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 26 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 22 | 43 | 0 | 92 | 90 | 37 | 19 | 35 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 90 | 28 | 54 | 0 | 51 | 0 | 49 | 38 | 22 | 8 | 33 | 20 | 158 | 149 | 0 | 17 | 0 | 0 | 41 | 10 | 0 | 130 | 158 | 50 | 76 | 0 | 191 | 0 | 0 | 0 | 290 | 0 | 0 | 11 | 260 | 107 | 50 | 188 | 50 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 51 | 0 | 300 | 54 | 93 | 81 | 29 | 100 | 400 | 101 | 0 | 126 | 108 | 0 | 36 | 0 | 77 | 55 |  | 921 | 0 | 180 | 0 | 110 | 40 | 0 | 0 | 37 | 38 | 0 | 87 | 38 | 32 | 0 | 0 | 0 | 34 | 21 | 90 | 0 | 43 | 22 | 43 | 36 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 132 | 0 | 0 | 216 | 0 | 10 | 0 | 0 | 414 | 105 | 50 | 113 | 105 | 108 | 0 | 0 | 113 | 1040 | 206 | 0 | 17 | 0 | 0 | 115 |  | 8585 | 4829 | 13414 | 3729 | 921 | 2136 | 278 | 4075 | 1312 | 56 | 264 | 701 | 158 | 0 | 0 | 77.38
4:00 | 0 | 0 | 227 | 0 | 260 | 101 | 0 | 398 | 302 |  | 0 | 280 | 140 | 7 | 78 | 55 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 27 | 30 | 0 | 0 | 25 | 135 | 0 | 0 | 0 |  | 24 | 43 | 0 | 92 | 94 | 37 | 19 | 35 | 0 | 0 | 0 | 330 | 0 | 217 | 8 | 90 | 28 | 54 | 0 | 51 | 0 | 49 | 38 | 22 | 8 | 33 | 20 | 154 | 148 | 0 | 17 | 0 | 0 | 41 | 11 | 0 | 163 | 158 | 50 | 76 | 0 | 212 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 273 | 21 | 0 | 188 | 0 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 51 | 0 | 300 | 54 | 93 | 81 | 27 | 100 | 400 | 104 | 0 | 126 | 108 | 0 | 36 | 0 | 53 | 55 |  | 921 | 0 | 180 | 0 | 110 | 40 | 0 | 0 | 37 | 38 | 0 | 87 | 38 | 32 | 0 | 0 | 0 | 34 | 22 | 30 | 0 | 43 | 22 | 43 | 38 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 132 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 101 | 109 | 0 | 0 | 113 | 1020 | 209 | 0 | 17 | 0 | 0 | 115 |  | 8487 | 4691 | 13178 | 3760 | 921 | 2214 | 21 | 4068 | 1292 | 57 | 263 | 643 | 154 | 0 | 0 | 77.36
5:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 397 | 302 |  | 0 | 280 | 130 | 7 | 78 | 55 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 27 | 30 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 92 | 94 | 37 | 19 | 30 | 0 | 0 | 0 | 280 | 0 | 219 | 8 | 90 | 28 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 20 | 148 | 152 | 0 | 17 | 0 | 0 | 41 | 11 | 0 | 163 | 157 | 50 | 76 | 0 | 218 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 188 | 0 | 149 | 0 | 90 | 200 | 150 | 400 | 105 | 105 | 51 | 0 | 300 | 54 | 93 | 81 | 29 | 100 | 400 | 104 | 0 | 126 | 108 | 0 | 36 | 0 | 54 | 55 |  | 923 | 0 | 185 | 0 | 110 | 10 | 0 | 0 | 9 | 23 | 0 | 88 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 72 | 0 | 199 | 0 | 0 | 131 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 89 | 104 | 0 | 0 | 113 | 990 | 209 | 0 | 17 | 0 | 0 | 72 |  | 8264 | 4274 | 12538 | 3726 | 923 | 2166 | 0 | 3945 | 1261 | 57 | 165 | 302 | 148 | 0 | 0 | 77.34
6:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 350 | 302 |  | 0 | 280 | 125 | 7 | 78 | 30 | 0 | 0 | 0 | 0 | 84 | 80 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 28 | 30 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 96 | 27 | 19 | 29 | 0 | 0 | 0 | 310 | 0 | 219 | 8 | 90 | 28 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 20 | 130 | 153 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 159 | 50 | 10 | 0 | 218 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 230 | 0 | 0 | 188 | 0 | 149 | 1 | 90 | 136 | 50 | 400 | 105 | 105 | 51 | 0 | 300 | 54 | 93 | 72 | 28 | 100 | 400 | 92 | 2 | 126 | 91 | 0 | 36 | 1 | 77 | 55 |  | 922 | 0 | 185 | 0 | 110 | 10 | 0 | 0 | 0 | 0 | 0 | 89 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 105 | 0 | 113 | 89 | 102 | 0 | 0 | 113 | 930 | 213 | 0 | 0 | 0 | 2 | 72 |  | 7720 | 4060 | 11780 | 3714 | 922 | 1966 | 0 | 3562 | 1202 | 58 | 140 | 210 | 130 | 6 | 0 | 77.32
7:00 | 0 | 0 | 232 | 0 | 260 | 101 | 0 | 351 | 301 |  | 0 | 280 | 125 | 7 | 78 | 30 | 0 | 0 | 0 | 0 | 76 | 60 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 28 | 30 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 94 | 18 | 19 | 10 | 0 | 0 | 0 | 310 | 0 | 219 | 8 | 90 | 28 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 20 | 136 | 151 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 159 | 55 | 10 | 0 | 218 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 230 | 0 | 0 | 188 | 0 | 149 | 5 | 90 | 68 | 50 | 400 | 115 | 70 | 51 | 1 | 300 | 54 | 93 | 72 | 28 | 100 | 350 | 76 | 9 | 126 | 108 | 0 | 36 | 6 | 55 | 55 |  | 922 | 0 | 190 | 0 | 110 | 25 | 0 | 0 | 0 | 0 | 0 | 89 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 105 | 0 | 113 | 89 | 88 | 0 | 1 | 70 | 920 | 224 | 0 | 0 | 0 | 17 | 72 |  | 7515 | 4023 | 11538 | 3675 | 922 | 1955 | 0 | 3346 | 1192 | 58 | 155 | 190 | 136 | 39 | 0 | 77.3
8:00 | 0 | 0 | 232 | 0 | 260 | 98 | 0 | 352 | 302 |  | 0 | 280 | 120 | 7 | 78 | 30 | 0 | 0 | 0 | 0 | 84 | 62 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 29 | 30 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 91 | 18 | 19 | 4 | 0 | 0 | 0 | 300 | 0 | 219 | 8 | 90 | 28 | 52 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 20 | 134 | 148 | 0 | 17 | 1 | 0 | 41 | 0 | 0 | 110 | 159 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 260 | 0 | 0 | 0 | 230 | 0 | 0 | 188 | 0 | 143 | 8 | 90 | 68 | 50 | 400 | 106 | 105 | 51 | 2 | 300 | 54 | 88 | 80 | 29 | 100 | 350 | 71 | 22 | 126 | 108 | 0 | 0 | 9 | 50 | 55 |  | 920 | 0 | 190 | 0 | 88 | 78 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 136 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 105 | 0 | 113 | 82 | 74 | 0 | 2 | 70 | 890 | 218 | 0 | 0 | 1 | 30 | 72 |  | 7484 | 4007 | 11491 | 3665 | 920 | 1922 | 0 | 3286 | 1160 | 59 | 208 | 192 | 134 | 75 | 0 | 77.28
9:00 | 0 | 0 | 232 | 0 | 260 | 98 | 0 | 353 | 300 |  | 0 | 290 | 150 | 7 | 78 | 30 | 0 | 0 | 0 | 0 | 84 | 62 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 50 | 0 | 29 | 30 | 0 | 0 | 0 | 149 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 92 | 18 | 19 | 2 | 0 | 0 | 0 | 350 | 0 | 212 | 8 | 90 | 28 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 20 | 136 | 133 | 0 | 17 | 1 | 0 | 41 | 0 | 0 | 110 | 153 | 55 | 10 | 0 | 219 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 230 | 0 | 0 | 188 | 0 | 138 | 13 | 90 | 68 | 50 | 403 | 105 | 105 | 51 | 3 | 300 | 54 | 93 | 80 | 28 | 100 | 391 | 71 | 36 | 126 | 108 | 0 | 7 | 16 | 50 | 55 |  | 920 | 0 | 190 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 82 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 105 | 0 | 113 | 67 | 73 | 0 | 2 | 70 | 890 | 170 | 0 | 0 | 3 | 55 | 72 |  | 7647 | 3986 | 11633 | 3745 | 920 | 1918 | 0 | 3254 | 1160 | 59 | 250 | 192 | 136 | 129 | 0 | 77.26
10:00 | 0 | 0 | 230 | 0 | 260 | 98 | 0 | 393 | 300 |  | 0 | 290 | 130 | 7 | 78 | 36 | 0 | 0 | 0 | 11 | 84 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 27 | 33 | 33 | 41 | 0 | 28 | 30 | 0 | 0 | 1 | 132 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 90 | 20 | 19 | 2 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 90 | 28 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 25 | 20 | 140 | 133 | 0 | 17 | 2 | 0 | 42 | 0 | 0 | 163 | 156 | 55 | 10 | 0 | 219 | 0 | 0 | 9 | 305 | 0 | 0 | 0 | 244 | 57 | 50 | 185 | 92 | 148 | 17 | 76 | 86 | 78 | 402 | 105 | 105 | 59 | 4 | 300 | 54 | 92 | 64 | 28 | 100 | 400 | 83 | 22 | 126 | 108 | 0 | 36 | 31 | 60 | 0 |  | 919 | 0 | 190 | 0 | 45 | 80 | 0 | 0 | 0 | 0 | 0 | 85 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 419 | 105 | 0 | 113 | 67 | 93 | 0 | 2 | 100 | 930 | 220 | 0 | 0 | 3 | 81 | 90 |  | 8003 | 4203 | 12206 | 3744 | 919 | 2101 | 199 | 3360 | 1200 | 58 | 225 | 243 | 140 | 162 | 0 | 77.24
11:00 | 0 | 0 | 231 | 0 | 260 | 93 | 0 | 399 | 300 |  | 0 | 290 | 135 | 16 | 78 | 38 | 0 | 0 | 0 | 64 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 27 | 33 | 33 | 41 | 0 | 27 | 30 | 0 | 0 | 24 | 132 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 86 | 27 | 19 | 2 | 0 | 0 | 0 | 330 | 0 | 213 | 8 | 90 | 28 | 48 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 25 | 20 | 150 | 133 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 155 | 55 | 10 | 0 | 219 | 0 | 0 | 9 | 270 | 0 | 0 | 0 | 259 | 12 | 25 | 185 | 50 | 141 | 17 | 76 | 174 | 120 | 403 | 105 | 90 | 105 | 4 | 300 | 40 | 94 | 64 | 29 | 100 | 395 | 104 | 49 | 126 | 100 | 0 | 36 | 31 | 94 | 0 |  | 920 | 0 | 190 | 0 | 15 | 80 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 417 | 97 | 0 | 94 | 67 | 100 | 0 | 5 | 113 | 940 | 210 | 0 | 2 | 5 | 91 | 108 |  | 8299 | 4266 | 12565 | 3753 | 920 | 2049 | 87 | 3728 | 1210 | 57 | 292 | 327 | 150 | 204 | 0 | 77.22
12:00 | 0 | 0 | 231 | 0 | 260 | 93 | 0 | 400 | 300 |  | 0 | 290 | 130 | 54 | 78 | 40 | 0 | 0 | 0 | 84 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 24 | 22 | 33 | 33 | 41 | 0 | 26 | 30 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 24 | 24 | 0 | 90 | 84 | 31 | 19 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 8 | 91 | 28 | 48 | 0 | 51 | 0 | 0 | 34 | 20 | 8 | 25 | 20 | 154 | 117 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 156 | 50 | 10 | 0 | 219 | 0 | 0 | 9 | 290 | 16 | 0 | 30 | 258 | 111 | 90 | 183 | 25 | 130 | 16 | 90 | 180 | 127 | 403 | 105 | 90 | 105 | 4 | 300 | 54 | 92 | 34 | 28 | 90 | 392 | 104 | 41 | 126 | 91 | 0 | 36 | 28 | 101 | 0 |  | 921 | 0 | 190 | 0 | 15 | 140 | 0 | 0 | 0 | 0 | 0 | 84 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 20 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 211 | 0 | 17 | 0 | 0 | 417 | 95 | 12 | 94 | 67 | 99 | 0 | 5 | 113 | 940 | 210 | 0 | 17 | 5 | 95 | 108 |  | 8523 | 4372 | 12895 | 3741 | 921 | 2066 | 285 | 3776 | 1210 | 56 | 351 | 350 | 154 | 196 | 0 | 77.2
13:00 | 0 | 0 | 231 | 0 | 260 | 93 | 0 | 401 | 300 |  | 0 | 290 | 130 | 71 | 78 | 40 | 0 | 0 | 0 | 78 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 16 | 25 | 25 | 33 | 31 | 48 | 0 | 25 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 24 | 24 | 0 | 90 | 85 | 37 | 19 | 2 | 0 | 0 | 0 | 310 | 0 | 213 | 8 | 90 | 28 | 46 | 0 | 51 | 0 | 47 | 36 | 20 | 8 | 24 | 20 | 158 | 102 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 157 | 50 | 10 | 0 | 219 | 0 | 0 | 9 | 270 | 16 | 0 | 100 | 272 | 55 | 90 | 183 | 98 | 129 | 17 | 90 | 180 | 132 | 404 | 115 | 105 | 105 | 5 | 300 | 54 | 92 | 34 | 28 | 100 | 395 | 104 | 45 | 126 | 105 | 0 | 36 | 30 | 101 | 0 |  | 920 | 0 | 190 | 0 | 15 | 125 | 0 | 0 | 0 | 0 | 8 | 84 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 34 | 10 | 19 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 212 | 0 | 85 | 0 | 0 | 414 | 103 | 99 | 106 | 67 | 98 | 0 | 5 | 113 | 940 | 210 | 0 | 17 | 5 | 91 | 108 |  | 8730 | 4578 | 13308 | 3732 | 920 | 2040 | 527 | 3897 | 1210 | 55 | 337 | 444 | 158 | 200 | 0 | 77.18
14:00 | 0 | 0 | 228 | 0 | 260 | 93 | 0 | 398 | 300 |  | 0 | 290 | 130 | 68 | 76 | 45 | 0 | 0 | 0 | 78 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 16 | 25 | 25 | 33 | 31 | 48 | 0 | 25 | 30 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 24 | 24 | 0 | 90 | 85 | 36 | 19 | 2 | 0 | 0 | 0 | 330 | 0 | 209 | 8 | 90 | 28 | 47 | 0 | 51 | 0 | 47 | 42 | 20 | 8 | 25 | 20 | 158 | 99 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 153 | 50 | 10 | 0 | 215 | 0 | 0 | 10 | 295 | 17 | 0 | 200 | 272 | 303 | 90 | 182 | 97 | 130 | 16 | 90 | 180 | 132 | 406 | 102 | 105 | 105 | 5 | 300 | 54 | 97 | 34 | 28 | 100 | 395 | 104 | 43 | 137 | 104 | 0 | 36 | 27 | 101 | 0 |  | 920 | 0 | 180 | 0 | 15 | 28 | 0 | 0 | 8 | 0 | 8 | 60 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 36 | 35 | 18 | 0 | 11 | 71 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 207 | 0 | 76 | 0 | 0 | 414 | 105 | 125 | 113 | 67 | 98 | 0 | 6 | 113 | 990 | 207 | 0 | 17 | 2 | 83 | 108 |  | 9123 | 4580 | 13703 | 3699 | 920 | 2065 | 891 | 3915 | 1261 | 55 | 235 | 527 | 158 | 184 | 0 | 77.16
15:00 | 0 | 0 | 227 | 0 | 260 | 93 | 0 | 398 | 300 |  | 0 | 290 | 150 | 71 | 76 | 55 | 0 | 0 | 0 | 80 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 16 | 25 | 25 | 33 | 31 | 40 | 0 | 26 | 30 | 0 | 0 | 25 | 141 | 0 | 0 | 0 |  | 24 | 24 | 0 | 90 | 86 | 36 | 19 | 2 | 0 | 0 | 0 | 335 | 0 | 210 | 8 | 90 | 28 | 46 | 0 | 51 | 0 | 47 | 42 | 20 | 8 | 33 | 20 | 162 | 99 | 0 | 17 | 2 | 0 | 40 | 0 | 0 | 163 | 149 | 48 | 86 | 0 | 214 | 0 | 0 | 10 | 305 | 17 | 0 | 200 | 275 | 303 | 90 | 181 | 97 | 132 | 12 | 90 | 180 | 132 | 395 | 102 | 105 | 105 | 3 | 300 | 54 | 110 | 34 | 28 | 90 | 380 | 104 | 23 | 144 | 90 | 0 | 36 | 22 | 101 | 0 |  | 920 | 0 | 180 | 0 | 15 | 37 | 0 | 0 | 16 | 0 | 8 | 50 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 43 | 36 | 18 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 206 | 0 | 98 | 0 | 0 | 414 | 105 | 125 | 113 | 67 | 99 | 0 | 5 | 113 | 1040 | 205 | 0 | 17 | 3 | 62 | 108 |  | 9202 | 4649 | 13851 | 3662 | 920 | 2171 | 913 | 3951 | 1312 | 56 | 243 | 535 | 162 | 132 | 0 | 77.14
16:00 | 0 | 0 | 226 | 0 | 260 | 96 | 0 | 397 | 298 |  | 0 | 290 | 125 | 70 | 76 | 55 | 0 | 0 | 0 | 80 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 25 | 33 | 32 | 40 | 0 | 26 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 14 | 36 | 0 | 90 | 93 | 36 | 19 | 2 | 0 | 0 | 0 | 325 | 0 | 211 | 8 | 90 | 27 | 46 | 0 | 51 | 0 | 46 | 42 | 21 | 8 | 33 | 20 | 156 | 75 | 0 | 17 | 1 | 0 | 40 | 0 | 0 | 163 | 154 | 50 | 10 | 0 | 214 | 0 | 0 | 10 | 285 | 17 | 0 | 200 | 275 | 306 | 90 | 181 | 98 | 132 | 7 | 90 | 180 | 132 | 406 | 112 | 105 | 105 | 2 | 300 | 54 | 110 | 34 | 42 | 90 | 375 | 104 | 12 | 144 | 93 | 0 | 36 | 15 | 90 | 0 |  | 919 | 0 | 180 | 0 | 15 | 44 | 0 | 0 | 22 | 0 | 8 | 65 | 27 | 16 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 24 | 43 | 36 | 18 | 0 | 11 | 73 | 0 | 200 | 0 | 10 | 144 | 0 | 0 | 209 | 0 | 99 | 0 | 0 | 414 | 105 | 125 | 113 | 67 | 98 | 0 | 3 | 95 | 990 | 210 | 0 | 17 | 2 | 44 | 52 |  | 9051 | 4551 | 13602 | 3651 | 919 | 2053 | 918 | 3888 | 1263 | 56 | 263 | 558 | 156 | 86 | 0 | 77.12
17:00 | 0 | 0 | 227 | 0 | 260 | 94 | 0 | 397 | 290 |  | 0 | 290 | 130 | 71 | 75 | 55 | 0 | 0 | 0 | 80 | 84 | 140 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 18 | 25 | 24 | 33 | 32 | 40 | 0 | 26 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 11 | 49 | 0 | 90 | 94 | 36 | 19 | 8 | 0 | 0 | 0 | 330 | 0 | 210 | 8 | 90 | 28 | 50 | 0 | 51 | 0 | 47 | 41 | 21 | 8 | 33 | 20 | 124 | 71 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 152 | 50 | 10 | 0 | 214 | 0 | 0 | 10 | 280 | 17 | 0 | 100 | 275 | 28 | 90 | 181 | 99 | 136 | 2 | 90 | 180 | 132 | 401 | 112 | 105 | 105 | 1 | 300 | 54 | 110 | 98 | 114 | 95 | 390 | 104 | 7 | 144 | 108 | 0 | 36 | 6 | 90 | 0 |  | 918 | 0 | 180 | 0 | 15 | 90 | 0 | 0 | 26 | 0 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 24 | 43 | 36 | 19 | 0 | 11 | 71 | 0 | 200 | 0 | 8 | 141 | 0 | 0 | 210 | 0 | 98 | 0 | 0 | 411 | 105 | 125 | 113 | 85 | 100 | 0 | 1 | 113 | 970 | 210 | 0 | 17 | 1 | 19 | 52 |  | 8792 | 4584 | 13376 | 3675 | 918 | 2052 | 540 | 4048 | 1241 | 56 | 308 | 587 | 124 | 37 | 0 | 77.1
18:00 | 0 | 0 | 228 | 0 | 260 | 94 | 0 | 389 | 288 |  | 0 | 290 | 135 | 71 | 75 | 55 | 0 | 0 | 0 | 85 | 84 | 145 | 0 | 0 | 0 | 0 | 45 | 55 | 55 | 19 | 25 | 24 | 33 | 32 | 48 | 0 | 27 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 20 | 49 | 0 | 50 | 94 | 36 | 19 | 12 | 0 | 0 | 0 | 330 | 0 | 212 | 8 | 90 | 27 | 48 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 25 | 20 | 140 | 75 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 152 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 285 | 17 | 0 | 10 | 278 | 0 | 25 | 182 | 25 | 149 | 0 | 90 | 164 | 142 | 402 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 112 | 100 | 390 | 104 | 1 | 144 | 108 | 0 | 25 | 1 | 101 | 0 |  | 918 | 0 | 175 | 0 | 16 | 155 | 0 | 0 | 28 | 14 | 8 | 65 | 28 | 16 | 0 | 0 | 0 | 43 | 23 | 85 | 0 | 0 | 29 | 43 | 36 | 20 | 0 | 11 | 74 | 0 | 200 | 0 | 8 | 139 | 0 | 0 | 210 | 0 | 60 | 0 | 0 | 395 | 105 | 125 | 113 | 85 | 105 | 0 | 0 | 113 | 930 | 177 | 0 | 17 | 0 | 3 | 52 |  | 8596 | 4624 | 13220 | 3666 | 918 | 2014 | 245 | 4099 | 1204 | 57 | 373 | 709 | 140 | 5 | 0 | 77.09
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 231 | 0 | 260 | 97 | 0 | 388 | 295 |  | 0 | 290 | 140 | 71 | 75 | 55 | 0 | 0 | 0 | 88 | 84 | 145 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 32 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 24 | 49 | 51 | 92 | 93 | 37 | 19 | 12 | 0 | 0 | 0 | 345 | 0 | 211 | 8 | 100 | 28 | 51 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 33 | 20 | 134 | 100 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 150 | 49 | 86 | 0 | 221 | 0 | 0 | 10 | 290 | 17 | 0 | 190 | 290 | 255 | 90 | 182 | 100 | 149 | 0 | 90 | 179 | 143 | 379 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 112 | 100 | 386 | 104 | 0 | 144 | 108 | 0 | 33 | 0 | 95 | 0 |  | 912 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 30 | 20 | 8 | 63 | 38 | 32 | 0 | 0 | 0 | 43 | 24 | 91 | 0 | 16 | 40 | 43 | 37 | 21 | 0 | 11 | 73 | 0 | 200 | 0 | 8 | 136 | 0 | 0 | 210 | 0 | 60 | 0 | 0 | 403 | 105 | 125 | 113 | 85 | 103 | 0 | 0 | 113 | 950 | 214 | 0 | 17 | 0 | 0 | 80 |  | 9427 | 4810 | 14237 | 3681 | 912 | 2169 | 820 | 4246 | 1223 | 57 | 418 | 787 | 134 | 0 | 0 | 77.06
19:30 | 0 | 0 | 231 | 0 | 260 | 97 | 0 | 411 | 300 |  | 0 | 290 | 130 | 24 | 77 | 55 | 0 | 0 | 0 | 98 | 84 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 24 | 49 | 51 | 92 | 94 | 37 | 19 | 18 | 0 | 0 | 0 | 330 | 0 | 213 | 8 | 100 | 28 | 51 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 33 | 20 | 136 | 106 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 156 | 50 | 86 | 0 | 220 | 0 | 0 | 10 | 285 | 17 | 0 | 200 | 290 | 306 | 96 | 185 | 100 | 149 | 0 | 90 | 180 | 147 | 405 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 395 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 0 |  | 911 | 0 | 180 | 0 | 16 | 200 | 0 | 0 | 44 | 25 | 8 | 65 | 39 | 32 | 0 | 0 | 0 | 43 | 24 | 90 | 0 | 34 | 40 | 43 | 36 | 21 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 135 | 0 | 0 | 211 | 0 | 100 | 0 | 0 | 408 | 105 | 125 | 113 | 85 | 99 | 0 | 0 | 113 | 1070 | 215 | 0 | 17 | 0 | 0 | 115 |  | 9546 | 5053 | 14599 | 3757 | 911 | 2172 | 927 | 4279 | 1342 | 58 | 419 | 809 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 231 | 0 | 260 | 97 | 0 | 399 | 300 |  | 0 | 290 | 135 | 40 | 77 | 55 | 0 | 0 | 0 | 94 | 84 | 145 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 32 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 24 | 49 | 51 | 92 | 96 | 35 | 19 | 21 | 0 | 0 | 0 | 330 | 0 | 212 | 8 | 102 | 28 | 52 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 33 | 20 | 138 | 106 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 153 | 50 | 86 | 0 | 221 | 0 | 0 | 10 | 290 | 17 | 0 | 200 | 291 | 221 | 98 | 185 | 100 | 149 | 0 | 90 | 180 | 147 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 388 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 102 | 0 |  | 912 | 0 | 180 | 0 | 16 | 200 | 0 | 0 | 35 | 37 | 8 | 65 | 38 | 32 | 0 | 0 | 0 | 43 | 27 | 90 | 0 | 50 | 40 | 43 | 36 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 8 | 137 | 0 | 0 | 212 | 0 | 99 | 0 | 0 | 414 | 105 | 125 | 113 | 105 | 106 | 0 | 0 | 113 | 1070 | 218 | 0 | 17 | 0 | 0 | 115 |  | 9469 | 5114 | 14583 | 3739 | 912 | 2195 | 843 | 4336 | 1342 | 58 | 420 | 812 | 138 | 0 | 0 | 77.07
21:00 | 0 | 0 | 231 | 0 | 270 | 96 | 0 | 404 | 301 |  | 0 | 290 | 120 | 24 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 0 | 33 | 16 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 24 | 50 | 51 | 92 | 96 | 32 | 19 | 26 | 0 | 0 | 0 | 325 | 0 | 216 | 8 | 100 | 28 | 53 | 0 | 51 | 0 | 47 | 42 | 22 | 8 | 33 | 21 | 132 | 119 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 155 | 50 | 86 | 0 | 221 | 0 | 0 | 10 | 290 | 17 | 0 | 200 | 296 | 301 | 98 | 186 | 100 | 149 | 0 | 90 | 185 | 150 | 403 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 6 |  | 914 | 0 | 185 | 0 | 16 | 200 | 0 | 0 | 37 | 64 | 21 | 67 | 38 | 32 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 43 | 40 | 43 | 35 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 139 | 0 | 0 | 213 | 0 | 100 | 0 | 0 | 414 | 105 | 149 | 113 | 105 | 107 | 0 | 0 | 113 | 1080 | 206 | 0 | 17 | 0 | 0 | 115 |  | 9539 | 5177 | 14716 | 3746 | 914 | 2174 | 948 | 4348 | 1352 | 58 | 413 | 844 | 132 | 0 | 0 | 77.06
22:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 395 | 292 |  | 0 | 290 | 120 | 25 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 16 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 24 | 50 | 51 | 92 | 95 | 37 | 19 | 26 | 0 | 0 | 0 | 325 | 0 | 215 | 8 | 100 | 28 | 53 | 0 | 51 | 0 | 47 | 42 | 21 | 8 | 33 | 21 | 138 | 118 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 157 | 50 | 86 | 0 | 220 | 0 | 0 | 10 | 270 | 17 | 0 | 200 | 293 | 105 | 98 | 186 | 100 | 149 | 0 | 90 | 200 | 150 | 403 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 914 | 0 | 185 | 0 | 16 | 200 | 0 | 0 | 37 | 50 | 24 | 67 | 39 | 32 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 43 | 40 | 43 | 36 | 22 | 0 | 11 | 73 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 215 | 0 | 100 | 0 | 0 | 417 | 105 | 153 | 113 | 105 | 77 | 0 | 0 | 113 | 1080 | 206 | 0 | 17 | 0 | 0 | 115 |  | 9401 | 5150 | 14551 | 3763 | 914 | 2149 | 756 | 4387 | 1353 | 57 | 415 | 834 | 138 | 0 | 0 | 77.05
23:00 | 0 | 0 | 233 | 0 | 270 | 95 | 0 | 394 | 287 |  | 0 | 290 | 130 | 24 | 78 | 55 | 0 | 0 | 0 | 99 | 84 | 145 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 32 | 49 | 0 | 25 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 24 | 50 | 0 | 80 | 96 | 37 | 19 | 27 | 0 | 0 | 0 | 310 | 0 | 215 | 8 | 100 | 28 | 54 | 0 | 51 | 0 | 49 | 42 | 5 | 0 | 33 | 21 | 140 | 121 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 158 | 55 | 86 | 0 | 220 | 0 | 0 | 10 | 275 | 17 | 0 | 150 | 293 | 47 | 98 | 0 | 100 | 149 | 0 | 76 | 200 | 150 | 401 | 0 | 105 | 103 | 0 | 300 | 54 | 110 | 81 | 113 | 100 | 396 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 915 | 0 | 180 | 0 | 16 | 200 | 0 | 0 | 37 | 50 | 8 | 66 | 38 | 32 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 43 | 35 | 25 | 30 | 22 | 0 | 11 | 74 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 216 | 0 | 60 | 0 | 0 | 414 | 105 | 152 | 113 | 105 | 102 | 0 | 0 | 113 | 1060 | 216 | 0 | 17 | 0 | 0 | 115 |  | 8890 | 5072 | 13962 | 3739 | 915 | 2166 | 607 | 4033 | 1334 | 55 | 416 | 773 | 140 | 0 | 0 | 77.04
24:00 | 0 | 0 | 233 | 0 | 270 | 96 | 0 | 395 | 287 |  | 0 | 290 | 130 | 24 | 78 | 55 | 0 | 0 | 0 | 99 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 32 | 49 | 0 | 25 | 30 | 0 | 0 | 2 | 151 | 0 | 0 | 0 |  | 24 | 42 | 0 | 92 | 97 | 37 | 19 | 22 | 0 | 0 | 0 | 310 | 0 | 217 | 63 | 100 | 28 | 54 | 0 | 51 | 0 | 49 | 43 | 21 | 0 | 33 | 20 | 142 | 122 | 0 | 14 | 0 | 0 | 41 | 0 | 0 | 163 | 158 | 55 | 76 | 0 | 219 | 0 | 0 | 10 | 280 | 17 | 0 | 60 | 293 | 17 | 97 | 50 | 50 | 149 | 0 | 76 | 200 | 140 | 402 | 8 | 105 | 51 | 0 | 300 | 54 | 110 | 17 | 56 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 55 |  | 915 | 0 | 180 | 0 | 16 | 200 | 0 | 0 | 37 | 34 | 8 | 67 | 38 | 32 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 43 | 35 | 24 | 30 | 22 | 0 | 11 | 74 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 216 | 0 | 10 | 0 | 0 | 414 | 105 | 152 | 113 | 105 | 102 | 0 | 0 | 113 | 1060 | 217 | 0 | 17 | 0 | 0 | 52 |  | 8647 | 4945 | 13592 | 3762 | 915 | 2213 | 386 | 3835 | 1334 | 55 | 416 | 750 | 142 | 0 | 0 | 77.03
KWH | 0 | 0 | 5534000 | 0 | 6258391 | 2290590 | 0 | 9494530 | 7138000 |  | 0 | 6747300 | 3187549 | 795840 | 1854888 | 1171783 | 0 | 0 | 0 | 1240320 | 1999584 | 2814720 | 0 | 0 | 0 | 0 | 937440 | 1254591 | 1094961 | 394308 | 525000 | 558540 | 788900 | 746400 | 1128960 | 0 | 628364 | 720000 | 0 | 0 | 394664 | 3343972 | 0 | 0 | 0 |  | 553680 | 696120 | 220125 | 1656720 | 2206080 | 788640 | 460608 | 365760 | 0 | 0 | 0 | 8149000 | 0 | 5156000 | 234181 | 2196080 | 668808 | 1222560 | 0 | 1190474 | 0 | 770520 | 1008398 | 472716 | 210660 | 755200 | 495690 | 3456000 | 2817600 | 0 | 368856 | 14250 | 0 | 958664 | 59400 | 0 | 3714709 | 3691000 | 1235808 | 1109760 | 0 | 5225930 | 0 | 0 | 222120 | 6964500 | 238560 | 0 | 2182272 | 6498543 | 2522876 | 1372075 | 4197600 | 1430360 | 3495888 | 126765 | 2069760 | 4027680 | 3019273 | 9609000 | 2470800 | 2496000 | 1967127 | 33000 | 7118291 | 1348276 | 2424608 | 1690620 | 1334760 | 2379840 | 9334100 | 2450880 | 302020 | 3245760 | 2522891 | 0 | 830880 | 220647 | 2045760 | 699120 |  | 22212363 | 0 | 4597920 | 0 | 1206720 | 2528681 | 0 | 0 | 453120 | 439424 | 111375 | 1795553 | 764397 | 599328 | 0 | 0 | 0 | 430752 | 271154 | 1225784 | 0 | 408833 | 389980 | 884645 | 559719 | 469920 | 0 | 252054 | 1686109 | 0 | 4846800 | 3000 | 79000 | 3547464 | 0 | 0 | 4899391 | 0 | 1283520 | 0 | 0 | 9616509 | 2636160 | 1859006 | 2694816 | 2156832 | 2354870 | 0 | 37671 | 2593152 | 25849700 | 4999991 | 0 | 338400 | 34860 | 677520 | 2316288 |  | 208066244 | 114112781 | 322179025 | 89881312 | 22212363 | 50297720 | 10650109 | 94722325 | 32382609 | 1348364 | 7510072 | 8271418 | 3456000 | 1446733 | 0
Fuel Cost | 0 | 0 | 8079640 | 0 | 6946814.01 | 3023578.8 | 0 | 9589475.3 | 7352140 |  | 0 | 7354557 | 3538179.39 | 6040425.6 | 12780178.32 | 9913284.18 | 0 | 0 | 0 | 9339609.6 | 18236206.08 | 27696844.8 | 0 | 0 | 0 | 0 | 6843312 | 9697988.43 | 10796315.46 | 295731 | 393750 | 0 | 0 | 0 | 10917043.2 | 0 | 169658.28 | 194400 | 0 | 0 | 3666428.56 | 3644929.48 | 0 | 0 | 0 |  | 0 | 6731480.4 | 2135212.5 | 15821676 | 19192896 | 6246028.8 | 580366.08 | 1086307.2 | 0 | 0 | 0 | 6030260 | 0 | 4743520 | 302093.49 | 2525492 | 755753.04 | 1711584 | 0 | 2035710.54 | 0 | 7782252 | 9630200.9 | 600349.32 | 157995 | 1321600 | 371767.5 | 25920000 | 2986656 | 0 | 468447.12 | 227145 | 0 | 1533862.4 | 105732 | 0 | 4234768.26 | 3838640 | 2434541.76 | 2119641.6 | 0 | 9040858.9 | 0 | 0 | 453124.8 | 7034145 | 178920 | 0 | 37120446.72 | 49128985.08 | 42838434.48 | 22941094 | 21827520 | 23915619.2 | 34399537.92 | 1481882.85 | 16868544 | 43700328 | 21285874.65 | 8936370 | 22533696 | 23587200 | 17133676.17 | 0 | 53814279.96 | 11743483.96 | 21312304.32 | 16872387.6 | 11438893.2 | 15849734.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127943210.88 | 0 | 4827816 | 0 | 9484819.2 | 35047518.66 | 0 | 0 | 4753228.8 | 4605163.52 | 1160527.5 | 2028974.89 | 1184815.35 | 5849441.28 | 0 | 0 | 0 | 4238599.68 | 2754924.64 | 10848188.4 | 0 | 5527422.16 | 3778906.2 | 8572210.05 | 5429274.3 | 902246.4 | 0 | 190804.878 | 10167237.27 | 0 | 26269656 | 103950 | 2253870 | 4150532.88 | 0 | 0 | 72119035.52 | 0 | 21832675.2 | 0 | 0 | 9520343.91 | 27521510.4 | 31621692.06 | 25573803.84 | 20360494.08 | 18273791.2 | 0 | 416264.55 | 19163393.28 | 113480183 | 0 | 0 | 0 | 0 | 0 | 0 |  | 845579809.61 | 641956525.978 | 1487536335.588 | 86653867.558 | 127943210.88 | 51958967.74 | 180269961.66 | 672105451.38 | 149917076.27 | 364058.28 | 109524374.18 | 80754075.24 | 25920000 | 2125292.4 | 0
Yesterday Day Peak | 0 | 0 | 231 | 0 | 260 | 93 | 0 | 400 | 300 |  | 0 | 290 | 130 | 54 | 78 | 40 | 0 | 0 | 0 | 84 | 84 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 24 | 22 | 33 | 33 | 41 | 0 | 26 | 30 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 24 | 24 | 0 | 90 | 84 | 31 | 19 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 8 | 91 | 28 | 48 | 0 | 51 | 0 | 0 | 34 | 20 | 8 | 25 | 20 | 154 | 117 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 156 | 50 | 10 | 0 | 219 | 0 | 0 | 9 | 290 | 16 | 0 | 30 | 258 | 111 | 90 | 183 | 25 | 130 | 16 | 90 | 180 | 127 | 403 | 105 | 90 | 105 | 4 | 300 | 54 | 92 | 34 | 28 | 90 | 392 | 104 | 41 | 126 | 91 | 0 | 36 | 28 | 101 | 0 |  | 921 | 0 | 190 | 0 | 15 | 140 | 0 | 0 | 0 | 0 | 0 | 84 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 20 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 211 | 0 | 17 | 0 | 0 | 417 | 95 | 12 | 94 | 67 | 99 | 0 | 5 | 113 | 940 | 210 | 0 | 17 | 5 | 95 | 108 |  | 12895 | DayPeak
Yesterday Evening Peak | 0 | 0 | 231 | 0 | 270 | 96 | 0 | 404 | 301 | 0 | 0 | 290 | 120 | 24 | 78 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 0 | 33 | 16 | 49 | 0 | 28 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 | 0 | 24 | 50 | 51 | 92 | 96 | 32 | 19 | 26 | 0 | 0 | 0 | 325 | 0 | 216 | 8 | 100 | 28 | 53 | 0 | 51 | 0 | 47 | 42 | 22 | 8 | 33 | 21 | 132 | 119 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 155 | 50 | 86 | 0 | 221 | 0 | 0 | 10 | 290 | 17 | 0 | 200 | 296 | 301 | 98 | 186 | 100 | 149 | 0 | 90 | 185 | 150 | 403 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 101 | 6 |  | 914 | 0 | 185 | 0 | 16 | 200 | 0 | 0 | 37 | 64 | 21 | 67 | 38 | 32 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 43 | 40 | 43 | 35 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 139 | 0 | 0 | 213 | 0 | 100 | 0 | 0 | 414 | 105 | 149 | 113 | 105 | 107 | 0 | 0 | 113 | 1080 | 206 | 0 | 17 | 0 | 0 | 115 |  | 14716 | EvPeak
Forecast for Evening | 0 | 0 | 240 | 0 | 270 | 100 | 0 | 400 | 320 | 0 | 0 | 300 | 150 | 100 | 80 | 55 | 0 | 0 | 0 | 100 | 85 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 30 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 90 | 95 | 35 | 22 | 25 | 0 | 0 | 0 | 360 | 0 | 225 | 45 | 100 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 166 | 110 | 0 | 17 | 0 | 0 | 42 | 0 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 0 | 0 | 10 | 310 | 17 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 96 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 |  | 101 | 55 |  | 791 | 0 | 200 | 0 | 115 | 200 | 0 | 0 | 37 | 80 | 32 | 90 | 37 | 110 | 0 | 0 | 0 | 43 | 30 | 93 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 80 | 0 | 200 | 17 | 10 | 150 | 0 | 0 | 220 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 1080 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 240 | 0 | 270 | 100 | 0 | 400 | 300 | 0 | 0 | 300 | 150 | 100 | 80 | 55 | 0 | 0 | 0 | 100 | 85 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 30 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 90 | 95 | 25 | 22 | 5 | 0 | 0 | 0 | 300 | 0 | 225 | 45 | 100 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 143 | 110 | 0 | 17 | 1.6 | 0 | 42 | 0 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 0 | 0 | 10 | 310 | 17 | 11 | 200 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 96 | 113 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 35 | 30 | 101 | 55 |  | 791 | 0 | 200 | 0 | 115 | 150 | 0 | 0 | 37 | 0 | 32 | 90 | 33 | 50 | 0 | 0 | 0 | 36 | 30 | 92 | 0 | 43 | 30 | 52 | 30 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 1060 | 220 |  | 150 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 270 | 97 | 0 | 401 | 306 | 0 | 0 | 300 | 120 | 95 | 78 | 15 | 0 | 0 | 0 | 1 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 33 | 40 | 0 | 29 | 30 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 88 | 14 | 19 | 5 | 0 | 0 | 0 | 310 | 0 | 186 | 45 | 100 | 28 | 40 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 20 | 98 | 106 | 0 | 17 | 1 | 0 | 42 | 0 | 0 | 110 | 158 | 55 | 10 | 0 | 178 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 149 | 2 | 90 | 17 | 15 | 352 | 75 | 50 | 51 | 2 | 281 | 54 | 110 | 17 | 29 | 88 | 400 | 35 | 21 | 144 | 105 | 0 | 36 | 13 | 17 | 0 | 0 | 921 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 70 | 0 | 199 | 0 | 0 | 138 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 35 | 0 | 78 | 67 | 38 | 0 | 1 | 35 | 870 | 220 | 0 | 0 | 1 | 44 | 34 | 0 |  |  |  |  | 121153924 |  | 0
121153924
| Minimum Generation |  | 11491 | 8:00
| Highest Generation |  | 14716 | 21:00
| Day Peak Generation |  | 12895 | 12:00
| Evening Peak Generation |  | 14716 | 21:00
| HVDC Max Flow |  | 923 | 5:00
| HVDC EvPeak Flow |  | 914 | 21:00
| Load factor L.F |  | 91.22%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-27
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12895 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10409 | MW
Evening Peak Generation : |  | 14716 | MW Hour : | 21:00 | Available Max Generation : |  | 15536 | MW
E.P. Demand (at gen end) : |  | 14716 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14800 | MW
Maximum Generation : |  | 14716 | MW Hour : | 21:00 | Reserve(Generation end) |  | 736 | MW
Total Gen. (MKWH) : |  | 322.179 | System Load Factor : | 91.22% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 90 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-27
Actual : | 76.97 | Ft.(MSL) , | Rule curve : | 82.8 | Ft.( MSL )
Gas Consumed : | Total = | 1052.56 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 138612835.298
: |  | Coal : | 149917076.27 | Oil : | 1042653862.46 | Total : | 1331183774.028
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5260.5295 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1712.2797 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1662.4899 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1489.3876 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1357.5222 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1113.2882 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 546.3925 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 332.4939 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 820.291 |  |  | 0 | 0%
Total | 0 |  | 14294.6746 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet 132/33 kV T-2 transformer was under shut down from 08:24 to 08:45 due to 33 kV PBS feeder | [5 empty] | About 21 MW power interruption occurred under
fault. | [5 empty] | Sylhet S/S area from 08:24 to 08:45.
b) Ashuganj 132/33 kV T-3 transformer tripped at 07:38 from both end showing E/F relays and was
switched on at 08:06.
c) Rampura 132 kV Bus-2 was under shut down from 07:59 to 12:50 for C/M.
d) Aminbazar 230/132 kV T1 transformer was under shut down from 09:51 to 14:25 for C/M.
e) Keraniganj 132/33 kV T-1 transformer was under shut down from 10:17 to 12:07 for C/M.
f) Khulna 225 MW ST was synchronized at 07:36 and tripped at 10:37.
g) Mithapukur 33 kV Bus of T2 transformer was under shut down from 11:10 to 11:43 for C/M. | [5 empty] | About 12 MW power interruption occurred under
Mithapukur S/S area from 11:10 to 11:43.
h) Sherpur 132/33 kV T-3 transformer was under shut down from 11:51 to 12:51 for C/M.
i) Mymensing-Kishoreganj 132 kV Ckt-2 was under shut down from 12:45 to 13:05 for C/M. | [5 empty] | About 55 MW power interruption occurred under
Mymensing S/S area from 12:45 to 13:05.
j) Sholoshahar 132/33 kV T-2 transformer was under shut down from 13:20 to 15:34 for D/W.
k) Khulna 225 MW ST was synchronized at 15:53.
l) Bhandaria 132/33 kV T1 transformer was under shut down from 14:26 to 17:30 due to oil leakage
maintenance at 33 kV CT.
m) Sholoshahar 132/33 kV T-1 transformer was under shut down from 16:02 to 17:49 for D/W.
n) Shahjibazar 132/33 kV T-4 transformer was under shut down from 15:53 to 16:08 for fuse replacement. | [5 empty] | About 30 MW power interruption occurred under
of PDB auxiliary transformer. | [5 empty] | Shahjibazar S/S area from 15:53 to 16:08.
o) Jhenaidah-Jashore 132 kV Ckt-2 was switched on at 17:35.
p) Haripur-Bhulta 132 kv Ckt tripped at 20:11 from Haripur end showing O/C relays and was switched on | [5 empty] | About 210 MW power interruption occurred under
at 20:20. | [5 empty] | Bhulta & Narshingdi S/S area from 20:11 to 20:20.
q) Barapukuria-Rangpur 132 kV Ckt-1 tripped at 21:17 from Barapukuria end showing Dist. Z1 relays
and was switched on at 21:44.
r) Sylhet-Chatak 132 kv Ckt-2 tripped at 00:29(27-04-2022) from Sylhet end showing Dist. Z2, C-phase
relays and was switched on at 01:17(27-04-2022)
s) Sylhet-Chatak 132 kv Ckt-1 tripped at 01:07(27-04-2022) from Sylhet end showing Dist. Z1, C-phase
relays and was switched on at 01:22(27-04-2022)
t) Sylhet-Chatak 132 kv Ckt-1 tripped at 02:05(27-04-2022) from Sylhet end showing SOTF relays
and was switched on at 09:20(27-04-2022)
u) Fenchuganj-Sylhet 132 kv Ckt-1 tripped at 02:00(27-04-2022) from Sylhet end showing Dist. Z1 relay
and was switched on at 02:10(27-04-2022).
v) Chowmuhuni 132/33 kV T-1 transformer was under shut down from 00:15 to 01:10 for C/M.
w) Kodda-Kabirpur 132 kV Ckt-2 was under shut down at 06:59(27-04-2022) for C/M.
x) Saver 132/33 kV T-1 transformer was under shut down from 07:07 to 09:13 for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 231 | 5534000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6258391 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2290590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 404 | 9494530
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 301 | 7138000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 290 | 6747300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 24 | 795840 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 120 | 3187549 | GT-1 Under S/D & FGNO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 78 | 1854888 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1171783
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 394308
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1240320
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1999584 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 937440 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 2814720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1254591
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1094961
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 1083540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 746400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1128960 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 6498543
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 301 | 2522876
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 98 | 1372075
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1430360
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3495888
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2496000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2450880
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3245760 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 220647
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 6 | 699120 | 33 kV feeder problem.
| Dhaka area Total |  |  |  | 5998 | 3806 | 82388744
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 394664
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126765
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 788640 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 58 | 1348364 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3343972 | ST under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1967127
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 696120 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 220125 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 92 | 1656720 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2069760 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 460608
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 365760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 2206080 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 7118291
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1348276
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2424608
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2379840
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2522891
| Chattogram area Total |  |  |  | 2382 | 1467 | 31471611
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 5156000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 8149000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 28 | 668808 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1222560
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 234181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1190474
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3019273
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 770520
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2196080 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 185 | 4027680 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 472716
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 210660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 3456000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 755200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 1008398 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 495690 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2182272
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1690620 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1334760
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 830880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 2045760 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1969 | 41117532
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 119 | 2817600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 368856
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14250
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 186 | 4197600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 2470800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 302020
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 553680
| Mymensingh Area Total |  |  |  | 622 | 461 | 10724806
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 958664 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3714709
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 155 | 3691000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 59400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1235808 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1109760
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5225930
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 238560
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6964500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9609000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 222120
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9334100
| Sylhet Area Total |  |  |  | 2477 | 1836 | 42363551
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 914 | 22212363
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 1206720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 453120 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 2528681
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 64 | 439424 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 185 | 4597920 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 21 | 111375 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 1283520
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2636160
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2156832
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 677520
| Khulna Area Total |  |  |  | 2384 | 1747 | 38303635
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 599328 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 38 | 764397
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1795553 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 25849700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 206 | 4999991
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 338400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1440 | 34347369
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 430752 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 271154 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 408833 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 389980 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 139 | 3547464 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 4899391
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9616509
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 559719 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 469920
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252054
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 884645
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 1225784 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 149 | 1859006 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2694816
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2593152
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34860
| Rajshahi Area Total |  |  |  | 2179 | 1496 | 30138039
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1686109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4846800
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 3000 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 79000 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2354870
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37671
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2316288
| Rangpur Area Total |  |  |  | 720 | 494 | 11323738
| Total |  |  |  | 21734 | 14716 | 322179025
| Eastern Grid Total |  |  |  | 14493 | 9539 | 208066244
| Western Grid Total |  |  |  | 7241 | 5177 | 114112781
| National Grid Total |  |  |  | 21734 | 14716 | 322179025
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-26
(a) ENTIRE EASTERN GRID : |  | 9558.13 | MW | (b) ENTIRE WESTERN GRID : |  | 4648.2 | MW
i) Dhaka area |  | 5055.13 | MW | i) Khulna area |  | 1875.8 | MW
ii) Chittagong area |  | 1449 | MW | ii) Rajshahi area |  | 1673.4 | MW
iii) Comilla area |  | 1366 | MW | iii) Barisal area |  | 431 | MW
iv) Mymensingh area |  | 1112 | MW | iv) Rangpur area |  | 668 | MW
v) Sylhet area |  | 576 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 14206.33 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 34 | 15:00 | Hasnabad | 82 | 15:00 | Palashbari | 132 | 21:00
Agargaon | 105 | 13:00 | Hathazari | 108 | 21:00 | Panchagarh | 59 | 19:30
Agrabad | 152 | 18:00 | Ishurdi | 81 | 22:00 | Patuakhali | 137.3 | 01:00
AKS | 8 | 17:00 | Jaldhaka | 59 | 00:00 | PHP | 5 | 00:00
AKSML | 144 | 17:00 | Jamalpur | 164 | 04:00 | Purbachal | 20 | 19:30
Amnura | 67 | 22:00 | Jashore | 145 | 21:00 | Purbasadipur | 118 | 22:00
Ashuganj | 40 | 23:00 | Jhenaidah | 144 | 22:00 | Rahim | 23 | 17:00
Bagerhat | 110 | 21:00 | Joydebpur | 202 | 11:00 | Rajbari | 76 | 21:00
Bakulia | 135 | 16:00 | Joypurhat | 77 | 22:00 | Rajendrapur | 116 | 09:00
Banani | 59 | 10:00 | Juldah | 28 | 07:00 | Rajshahi | 201 | 21:00
Bangabhaban | 24 | 10:00 | Kabirpur | 321 | 14:00 | Rajshahi | 40 | 23:00
Barapukuria | 57 | 00:00 | Kachua | 82 | 22:00 | Ramganj | 112 | 21:00
Barguna | 22 | 23:00 | Kallyanpur | 96 | 21:00 | Rampur | 21 | 00:00
Barishal | 111 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 14 | 18:30
Barishal | 74 | 21:00 | Kamrangirchar | 75 | 15:00 | Rangpur | 142 | 18:00
Baroaulia | 78 | 11:00 | Kaptai | 5 | 18:30 | Ruppur | 5.6 | 10:00
Baroirhat | 47 | 22:00 | Kazla | 87 | 15:00 | Saidpur | 109 | 16:00
Bashundhara | 192 | 14:00 | Keranigonj | 78 | 21:00 | Satkhira | 138 | 21:00
BashundharaCement | 13 | 20:00 | Khagrachori | 28 | 18:30 | Satmasjid | 115 | 19:00
Beanibazar | 80 | 19:30 | Khulna | 102 | 19:00 | Savar | 209 | 11:00
Benapole | 66 | 21:00 | Khulshi | 200 | 12:00 | Shahjadpur | 138 | 21:00
Bhaluka | 142 | 12:00 | Kishoreganj | 148 | 04:00 | Shahjibazar | 128 | 23:00
Bhandaria | 64 | 22:00 | Kodda | 333 | 10:00 | Shahmirpur | 43 | 22:00
Bhangura | 42 | 03:00 | KSRM | 26.47 | 07:00 | Shariatpur | 78 | 21:00
Bheramara(GK) | 72 | 21:00 | Kulaura | 52 | 18:30 | Sherpur | 126 | 21:00
Bhulta | 241 | 15:00 | Kurigram | 60 | 00:00 | Shikalbaha | 33 | 00:00
Bog-Sherpur | 70 | 03:00 | Kushtia | 144 | 21:00 | Shitalakhya | 138 | 15:00
Bogura | 193 | 23:00 | Lalbag | 82 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 48 | 19:00 | Lalmonirhat | 49 | 20:00 | Shyampur | 180 | 12:00
Brahmanbaria | 190 | 21:00 | Madanganj | 162 | 14:00 | Siddhirganj | 120 | 15:00
BSRM | 159 | 06:00 | Madaripur | 122 | 22:00 | Sirajganj | 129 | 21:00
Cantonment | 157 | 19:00 | Madartek | 93 | 19:00 | Sonargaon | 90 | 23:00
Chandpur | 70 | 23:00 | Madunaghat | 71 | 19:30 | Sreemongol | 60 | 00:00
Chandraghona | 30 | 18:30 | Magura | 71 | 21:00 | Srinagar | 48.53 | 21:00
Chapai | 76 | 23:00 | Mahasthangarh | 82 | 21:00 | SSM | 9 | 05:00
Charsaidpur | 43 | 17:00 | Manikganj | 96 | 00:00 | Sunamganj | 57 | 22:00
Chauddagram | 69 | 21:00 | Maniknagar | 93 | 13:00 | Sylhet | 145 | 21:00
Chhatak | 32 | 23:00 | Matarbari | 43 | 21:00 | Tangail | 238 | 03:00
Chowmuhani | 214 | 01:00 | Matuail | 70 | 10:00 | Thakurgaon | 99 | 22:00
Chuadanga | 120 | 20:00 | Millgate | 60 | 12:00 | TK | 32 | 19:00
Coxsbazar | 121 | 21:00 | Mirpur | 146 | 19:30 | Tongi | 148 | 15:00
Cumilla(N) | 157 | 19:30 | Mirsorai | N/A | N/A | Ullon | 32 | 00:00
Cumilla(S) | 176 | 18:30 | Mithapukur | 38 | 14:00 | Uttara | 105 | 19:00
Daudkandi | 154 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 21:00
Dhaka | 39 | 13:00 | Mogbazar | 133 | 14:00 | Zigatola | 46 | 19:30
Dhamrai | 128 | 20:00 | Mongla | 44 | 12:00
Dhanmondi | 212 | 12:00 | Motijheel | 41 | 15:00
Dohazari | 96 | 03:00 | Munshiganj | 108 | 21:00
Faridpur | 166 | 21:00 | Mymensingh | 247 | 00:00
Fatullah | 68 | 12:00 | Naogaon | 130 | 22:00
Fenchuganj | 52 | 20:00 | Narail | 63 | 21:00
Feni | 146 | 21:00 | Narinda | 80 | 14:00
Ghorashal | 50 | 19:00 | Narshingdi | 195 | 01:00
Goalpara | 30 | 01:00 | Natore | 156 | 22:00
Gollamari | 61 | 00:00 | Nawabganj | 62.6 | 21:00
Gopalganj | 114.8 | 21:00 | Netrakona | 108 | 02:00
GPH | 88 | 23:00 | New | 84.4 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 3:00 | 397 | 16:00 | Kaliakoir | 395 | 0.29167 | 374 | 0.58333
| Bheramara | 397 | 7:00 | 388 | 12:00 | Bhulta | 396 | 0.25 | 380 | 0.625
| Ashuganj(N) | 400 | 5:00 | 384 | 15:00 | Gopalganj | 416 | 0.625 | 402 | 0.95833
| Payra | 419 | 6:00 | 408 | 14:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 236 | 11:00 | 230 | 23:00
| Ishurdi | 234 | 6:00 | 226 | 14:00 | Megnaghat | 229 | 6:00 | 222 | 11:00
| Ashuganj | 240 | 1:00 | 231 | 11:00 | Fenchuganj | 243 | 3:00 | 236 | 19:30
| Serajganj | 234 | 19:00 | 230 | 3:00 | Siddhirganj | 227 | 6:00 | 219 | 13:00
| Baghabari | 230 | 4:00 | 225 | 21:00 | Maniknagar | 224 | 6:00 | 215 | 11:00
| Barapukuria | 230 | 23:00 | 219 | 18:30 | Agargaon | 226 | 8:00 | 213 | 15:00
| Bogra | 228 | 6:00 | 221 | 16:00 | Barisal | 241 | 8:00 | 232 | 22:00
| Rajshahi | 232 | 7:00 | 222 | 14:00 | Bhola 225 MW | 245 | 9:00 | 232 | 22:00
| Khulna South | 233 | 6:00 | 221 | 23:00 | AKSML
| Rampura | 226 | 5:00 | 216 | 11:00 | BSRM | 236 | 18:30 | 227 | 15:00
| Haripur | 225 | 6:00 | 216 | 11:00 | Bibiyana | 242 | 7:00 | 232 | 15:00
| Hasnabad | 223 | 4:00 | 215 | 15:00 | Bhulta | 229 | 6:00 | 218 | 11:00
| Shyampur | 225 | 6:00 | 215 | 15:00 | Ashuganj (S) | 236 | 5:00 | 228 | 15:00
| Aminbazar | 228 | 1:00 | 216 | 2:00 | Kaliakoir | 228 | 6:00 | 216 | 11:00
| Tongi | 226 | 4:00 | 215 | 11:00 | GPH | 236 | 17:00 | 227 | 15:00
| Comilla (N) | 230 | 7:00 | 224 | 14:00 | Jhenaidah | 226 | 7:00 | 216 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 06:00 | 126 | 12:00 | Manikganj | 132 | 07:00 | 118 | 11:00
| Agargaon | 135 | 06:00 | 124 | 15:00 | Maniknagar | 131 | 18:30 | 119 | 11:00
| Agrabad | 134 | 07:00 | 129 | 15:00 | Matarbari | 122 | 09:00 | 111 | 23:00
| AKS | 135 | 05:00 | 130 | 23:00 | Matuail | 133 | 05:00 | 127 | 11:00
| Aminbazar | 138 | 06:00 | 126 | 14:00 | Millgate | 135 | 01:00 | 125 | 14:00
| Amnura | 131 | 18:30 | 120 | 11:00 | Mirpur | 137 | 03:00 | 125 | 12:00
| Ashuganj | 136 | 08:00 | 131 | 17:00 | Mithapukur | 136 | 23:00 | 122 | 17:00
| Bagerhat | 135 | 09:00 | 127 | 22:00 | Modern | 135 | 17:00 | 131 | 15:00
| Bakulia | 134 | 01:00 | 129 | 15:00 | Mogbazar | 136 | 06:00 | 126 | 15:00
| Banani | 135 | 05:00 | 125 | 14:00 | Mongla | 135 | 08:00 | 127 | 23:00
| Bangabhaban | 130 | 19:00 | 119 | 11:00 | Motijheel | 130 | 19:00 | 119 | 11:00
| Barapukuria | 134 | 23:00 | 124 | 17:00 | Munshiganj | 136 | 19:00 | 129 | 15:00
| Barguna | 135 | 07:00 | 130 | 10:00 | Mymensingh | 130 | 08:00 | 113 | 23:00
| Barishal | 139 | 09:00 | 130 | 23:00 | Naogaon | 129 | 07:00 | 122 | 03:00
| Barishal | 140 | 08:00 | 133 | 22:00 | Narail | 134 | 07:00 | 124 | 22:00
| Baroaulia | 137 | 12:00 | 131 | 14:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 135 | 17:00 | 126 | 23:00 | Narshingdi | 128 | 06:00 | 120 | 11:00
| Bashundhara | 135 | 02:00 | 124 | 13:00 | Natore | 138 | 17:00 | 126 | 00:00
| BashundharaCement | 135 | 05:00 | 129 | 09:00 | Nawabganj | 134 | 01:00 | 127 | 14:00
| Beanibazar | 135 | 03:00 | 124 | 19:00 | Netrakona | 128 | 06:00 | 111 | 23:00
| Benapole | 135 | 07:00 | 127 | 14:00 | New | 136 | 06:00 | 126 | 11:00
| Bhaluka | 127 | 07:00 | 111 | 23:00 | Niamatpur | 127 | 03:00 | 112 | 19:00
| Bhandaria | 137 | 08:00 | 126 | 19:30 | Noapara | 137 | 07:00 | 131 | 16:00
| Bhangura | 135 | 06:00 | 131 | 21:00 | Pabna | 133 | 06:00 | 128 | 13:00
| Bheramara | 135 | 06:00 | 131 | 14:00 | Palashbari | 134 | 23:00 | 121 | 19:00
| Bheramara(GK) | 136 | 06:00 | 132 | 14:00 | Panchagarh | 134 | 11:00 | 113 | 17:00
| Bhulta | 127 | 03:00 | 120 | 09:00 | Patuakhali | 135 | 08:00 | 131 | 00:00
| Bog-Sherpur | 133 | 05:00 | 128 | 03:00 | PHP | 135 | 17:00 | 126 | 15:00
| Bogura | 135 | 06:00 | 130 | 00:00 | Purbachal | 135 | 05:00 | 124 | 14:00
| Bogura | 135 | 05:00 | 131 | 16:00 | Purbasadipur | 135 | 23:00 | 117 | 17:00
| Brahmanbaria | 131 | 08:00 | 125 | 14:00 | Rahim | 134 | 01:00 | 128 | 11:00
| Cantonment | 133 | 06:00 | 123 | 15:00 | Rajbari | 133 | 06:00 | 126 | 21:00
| Chandpur | 140 | 17:00 | 135 | 02:00 | Rajendrapur | 135 | 07:00 | 119 | 11:00
| Chandraghona | 137 | 07:00 | 133 | 14:00 | Rajshahi | 130 | 18:30 | 122 | 12:00
| Chapai | 130 | 18:00 | 120 | 12:00 | Rajshahi | 130 | 18:30 | 123 | 09:00
| Charsaidpur | 136 | 01:00 | 129 | 09:00 | Ramganj | 135 | 16:00 | 127 | 15:00
| Chauddagram | 135 | 17:00 | 129 | 14:00 | Rampur | 134 | 04:00 | 129 | 15:00
| Chhatak | 135 | 02:00 | 125 | 23:00 | Rampura | 134 | 05:00 | 126 | 15:00
| Chowmuhani | 132 | 17:00 | 123 | 14:00 | Rangamati | 135 | 02:00 | 132 | 14:00
| Chuadanga | 131 | 07:00 | 119 | 21:00 | Rangpur | 135 | 23:00 | 119 | 18:00
| Coxsbazar | 122 | 10:00 | 111 | 02:00 | Ruppur | 135 | 07:00 | 131 | 14:00
| Cumilla(N) | 138 | 18:00 | 132 | 14:00 | Saidpur | 136 | 23:00 | 118 | 17:00
| Cumilla(S) | 136 | 16:00 | 126 | 12:00 | Satkhira | 134 | 07:00 | 125 | 21:00
| Daudkandi | 135 | 21:00 | 128 | 11:00 | Satmasjid | 134 | 06:00 | 124 | 15:00
| Dhaka | 135 | 06:00 | 125 | 15:00 | Savar | 139 | 07:00 | 126 | 14:00
| Dhamrai | 132 | 06:00 | 122 | 15:00 | Shahjadpur | 138 | 19:30 | 134 | 00:00
| Dhanmondi | 134 | 02:00 | 126 | 15:00 | Shahjibazar | 132 | 06:00 | 125 | 17:00
| Dohazari | 137 | 03:00 | 123 | 14:00 | Shahmirpur | 135 | 17:00 | 131 | 09:00
| Faridpur | 134 | 08:00 | 128 | 19:30 | Shariatpur | 139 | 09:00 | 129 | 21:00
| Fatullah | 134 | 02:00 | 127 | 11:00 | Sherpur | 134 | 06:00 | 120 | 04:00
| Fenchuganj | 137 | 05:00 | 132 | 01:00 | Shikalbaha | 136 | 02:00 | 129 | 15:00
| Feni | 135 | 17:00 | 128 | 14:00 | Shikalbaha | 135 | 08:00 | 130 | 15:00
| Ghorashal | 136 | 00:00 | 135 | 01:00 | Shitalakhya | 136 | 05:00 | 130 | 11:00
| Goalpara | 139 | 08:00 | 132 | 14:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 06:00 | 132 | 14:00 | Shyampur | 132 | 00:00 | 129 | 07:00
| Gopalganj | 138 | 09:00 | 134 | 15:00 | Shyampur | 133 | 01:00 | 123 | 18:00
| Gopalganj_I | 138 | 05:00 | 132 | 21:00 | Siddhirganj | 134 | 03:00 | 128 | 11:00
| Gulshan | 134 | 03:00 | 125 | 15:00 | Sirajganj | 132 | 05:00 | 129 | 23:00
| Halishahar | 135 | 22:00 | 130 | 14:00 | Sonargaon | 135 | 19:00 | 128 | 09:00
| Haripur | 134 | 01:00 | 128 | 11:00 | Sreemongol | 135 | 08:00 | 130 | 17:00
| HaripurSBU | 134 | 02:00 | 128 | 09:00 | Srinagar | 134 | 01:00 | 127 | 12:00
| Hasnabad | 135 | 01:00 | 128 | 12:00 | SSM | 140 | 19:00 | 132 | 14:00
| Hathazari | 137 | 07:00 | 134 | 23:00 | Sunamganj | 134 | 02:00 | 122 | 21:00
| Ishurdi | 135 | 06:00 | 131 | 12:00 | Sylhet | 134 | 03:00 | 129 | 20:00
| Jaldhaka | 134 | 23:00 | 115 | 17:00 | Tangail | 132 | 06:00 | 122 | 04:00
| Jamalpur | 135 | 06:00 | 110 | 23:00 | Thakurgaon | 134 | 11:00 | 114 | 17:00
| Jashore | 135 | 08:00 | 128 | 14:00 | TK | 136 | 17:00 | 132 | 09:00
| Jhenaidah | 138 | 07:00 | 129 | 21:00 | Tongi | 135 | 04:00 | 126 | 13:00
| Jhenaidah | 137 | 07:00 | 130 | 22:00 | Ullon | 136 | 05:00 | 126 | 14:00
| Joydebpur | 140 | 03:00 | 134 | 10:00 | Uttara | 137 | 05:00 | 125 | 12:00
| Joypurhat | 126 | 06:00 | 117 | 21:00 | UttaraNew | 131 | 21:00 | 131 | 21:00
| Juldah | 136 | 17:00 | 131 | 15:00 | Zigatola | 133 | 02:00 | 126 | 12:00
| Kabirpur | 136 | 06:00 | 122 | 11:00
| Kachua | 137 | 17:00 | 132 | 04:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 134 | 00:00 | 126 | 14:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 134 | 01:00 | 127 | 10:00
| Kaptai | 135 | 00:00 | 135 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 488 | 8647 | 4945 | 13592 |  |  |  | QF-LDC-11
0:30 | 447 | 8789 | 5020.5 | 13809.5 | Date: | 2022-04-26
1:00 | 406 | 8931 | 5096 | 14027
1:30 | 318 | 8840 | 4972 | 13812
2:00 | 230 | 8749 | 4848 | 13597
2:30 | 160 | 8667 | 4838.5 | 13505.5 | [5 empty] | Gen. at Eve. Peak | 14716 | 14716 MW (21:00 )
3:00 | 90 | 8585 | 4829 | 13414 | [6 empty] | 21:00
3:30 | 147 | 8536 | 4760 | 13296 | [5 empty] | Gen. at Day Peak | 12895 | 12895 MW (12:00 )
4:00 | 204 | 8487 | 4691 | 13178 | [6 empty] | 12:00
4:30 | 195 | 8375.5 | 4482.5 | 12858 | [5 empty] | Highest Generation | 14716
5:00 | 186 | 8264 | 4274 | 12538 | [6 empty] | 21:00
5:30 | 244 | 7992 | 4167 | 12159
6:00 | 302 | 7720 | 4060 | 11780
6:30 | 372 | 7617.5 | 4041.5 | 11659
7:00 | 442 | 7515 | 4023 | 11538
7:30 | 499 | 7499.5 | 4015 | 11514.5
8:00 | 556 | 7484 | 4007 | 11491
8:30 | 593 | 7565.5 | 3996.5 | 11562
9:00 | 630 | 7647 | 3986 | 11633
9:30 | 650 | 7825 | 4094.5 | 11919.5
10:00 | 670 | 8003 | 4203 | 12206
10:30 | 666 | 8151 | 4234.5 | 12385.5
11:00 | 662 | 8299 | 4266 | 12565
11:30 | 656 | 8411 | 4319 | 12730
12:00 | 650 | 8523 | 4372 | 12895
12:30 | 607 | 8626.5 | 4475 | 13101.5
13:00 | 564 | 8730 | 4578 | 13308
13:30 | 486 | 8926.5 | 4579 | 13505.5
14:00 | 408 | 9123 | 4580 | 13703
14:30 | 476 | 9162.5 | 4614.5 | 13777
15:00 | 544 | 9202 | 4649 | 13851
15:30 | 486 | 9126.5 | 4600 | 13726.5
16:00 | 428 | 9051 | 4551 | 13602
16:30 | 476 | 8921.5 | 4567.5 | 13489
17:00 | 524 | 8792 | 4584 | 13376
17:30 | 531 | 8694 | 4604 | 13298
18:00 | 538 | 8596 | 4624 | 13220
18:30 | 366 | 9011.5 | 4717 | 13728.5
19:00 | 194 | 9427 | 4810 | 14237
19:30 | 282 | 9546 | 5053 | 14599
20:00 | 332 | 9469 | 5114 | 14583 |  |  |  | Executive Engineer
20:30 | 333 | 9504 | 5145.5 | 14649.5 |  |  |  | Network Operation Division
21:00 | 334 | 9539 | 5177 | 14716
21:30 | 404 | 9470 | 5163.5 | 14633.5
22:00 | 474 | 9401 | 5150 | 14551 |  |  |  |  | Page 6 of 7
22:30 | 520 | 9145.5 | 5111 | 14256.5
23:00 | 566 | 8890 | 5072 | 13962
23:30 | 527 | 8768.5 | 5008.5 | 13777
24:00 | 488 | 8647 | 4945 | 13592
14716 MW (21:00 )
12895 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-26 |  | Energy |  | 322179025
[13 empty] | 2022-04-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3762 | 915 | 2213 | 386 | 3835 | 1334 | 55 | 416 | 750 | 142 | 0 | 0
0:30 | 3763 | 918 | 2188 | 553 | 3955 | 1323 | 55 | 392 | 726 | 152 | 0 | 0 | Date: | 2022-04-26
1:00 | 3764 | 921 | 2163 | 720 | 4075 | 1312 | 55 | 368 | 702 | 162 | 0 | 0
1:30 | 3770.5 | 921 | 2144 | 562 | 4084.5 | 1312 | 55 | 316 | 703.5 | 159 | 0 | 0 | [8 empty] | Total Energy | 322.179 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3777 | 921 | 2125 | 404 | 4094 | 1312 | 55 | 264 | 705 | 156 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3753 | 921 | 2130.5 | 341 | 4084.5 | 1312 | 55.5 | 264 | 703 | 157 | 0 | 0 | [8 empty] | Energy Requirement | 322.179
3:00 | 3729 | 921 | 2136 | 278 | 4075 | 1312 | 56 | 264 | 701 | 158 | 0 | 0
3:30 | 3744.5 | 921 | 2175 | 149.5 | 4071.5 | 1302 | 56.5 | 263.5 | 672 | 156 | 0 | 0 | [6 empty] | Shortage
4:00 | 3760 | 921 | 2214 | 21 | 4068 | 1292 | 57 | 263 | 643 | 154 | 0 | 0
4:30 | 3743 | 922 | 2190 | 10.5 | 4006.5 | 1276.5 | 57 | 214 | 472.5 | 151 | 0 | 0
5:00 | 3726 | 923 | 2166 | 0 | 3945 | 1261 | 57 | 165 | 302 | 148 | 0 | 0
5:30 | 3720 | 922.5 | 2066 | 0 | 3753.5 | 1231.5 | 57.5 | 152.5 | 256 | 139 | 3 | 0
6:00 | 3714 | 922 | 1966 | 0 | 3562 | 1202 | 58 | 140 | 210 | 130 | 6 | 0
6:30 | 3694.5 | 922 | 1960.5 | 0 | 3454 | 1197 | 58 | 147.5 | 200 | 133 | 22.5 | 0 |  |  |  |  | Coal
7:00 | 3675 | 922 | 1955 | 0 | 3346 | 1192 | 58 | 155 | 190 | 136 | 39 | 0
7:30 | 3670 | 921 | 1938.5 | 0 | 3316 | 1176 | 58.5 | 181.5 | 191 | 135 | 57 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3665 | 920 | 1922 | 0 | 3286 | 1160 | 59 | 208 | 192 | 134 | 75 | 0
8:30 | 3705 | 920 | 1920 | 0 | 3270 | 1160 | 59 | 229 | 192 | 135 | 102 | 0
9:00 | 3745 | 920 | 1918 | 0 | 3254 | 1160 | 59 | 250 | 192 | 136 | 129 | 0
9:30 | 3744.5 | 919.5 | 2009.5 | 99.5 | 3307 | 1180 | 58.5 | 237.5 | 217.5 | 138 | 145.5 | 0
10:00 | 3744 | 919 | 2101 | 199 | 3360 | 1200 | 58 | 225 | 243 | 140 | 162 | 0
10:30 | 3748.5 | 919.5 | 2075 | 143 | 3544 | 1205 | 57.5 | 258.5 | 285 | 145 | 183 | 0
11:00 | 3753 | 920 | 2049 | 87 | 3728 | 1210 | 57 | 292 | 327 | 150 | 204 | 0
11:30 | 3747 | 920.5 | 2057.5 | 186 | 3752 | 1210 | 56.5 | 321.5 | 338.5 | 152 | 200 | 0
12:00 | 3741 | 921 | 2066 | 285 | 3776 | 1210 | 56 | 351 | 350 | 154 | 196 | 0
12:30 | 3736.5 | 920.5 | 2053 | 406 | 3836.5 | 1210 | 55.5 | 344 | 397 | 156 | 198 | 0
13:00 | 3732 | 920 | 2040 | 527 | 3897 | 1210 | 55 | 337 | 444 | 158 | 200 | 0
13:30 | 3732 | 920 | 2040 | 527 | 3897 | 1210 | 55 | 337 | 444 | 158 | 200 | 0
14:00 | 3732 | 920 | 2040 | 527 | 3897 | 1210 | 55 | 337 | 444 | 158 | 200 | 0
14:30 | 3697 | 920 | 2105.5 | 720 | 3924 | 1261 | 55.5 | 290 | 489.5 | 160 | 166 | 0
15:00 | 3662 | 920 | 2171 | 913 | 3951 | 1312 | 56 | 243 | 535 | 162 | 132 | 0
15:30 | 3656.5 | 919.5 | 2112 | 915.5 | 3919.5 | 1287.5 | 56 | 253 | 546.5 | 159 | 109 | 0
16:00 | 3651 | 919 | 2053 | 918 | 3888 | 1263 | 56 | 263 | 558 | 156 | 86 | 0
16:30 | 3675 | 918.5 | 2052.5 | 729 | 3968 | 1252 | 56 | 285.5 | 572.5 | 140 | 61.5 | 0
17:00 | 3675 | 918 | 2052 | 540 | 4048 | 1241 | 56 | 308 | 587 | 124 | 37 | 0
17:30 | 3670.5 | 918 | 2033 | 392.5 | 4073.5 | 1222.5 | 56.5 | 340.5 | 648 | 132 | 21 | 0
18:00 | 3666 | 918 | 2014 | 245 | 4099 | 1204 | 57 | 373 | 709 | 140 | 5 | 0
18:30 | 3673.5 | 915 | 2091.5 | 532.5 | 4172.5 | 1213.5 | 57 | 395.5 | 748 | 137 | 2.5 | 0
19:00 | 3681 | 912 | 2169 | 820 | 4246 | 1223 | 57 | 418 | 787 | 134 | 0 | 0
19:30 | 3757 | 911 | 2172 | 927 | 4279 | 1342 | 58 | 419 | 809 | 136 | 0 | 0
20:00 | 3739 | 912 | 2195 | 843 | 4336 | 1342 | 58 | 420 | 812 | 138 | 0 | 0
20:30 | 3742.5 | 913 | 2184.5 | 895.5 | 4342 | 1347 | 58 | 416.5 | 828 | 135 | 0 | 0
21:00 | 3746 | 914 | 2174 | 948 | 4348 | 1352 | 58 | 413 | 844 | 132 | 0 | 0
21:30 | 3754.5 | 914 | 2161.5 | 852 | 4367.5 | 1352.5 | 57.5 | 414 | 839 | 135 | 0 | 0
22:00 | 3763 | 914 | 2149 | 756 | 4387 | 1353 | 57 | 415 | 834 | 138 | 0 | 0
22:30 | 3751 | 914.5 | 2157.5 | 681.5 | 4210 | 1343.5 | 56 | 415.5 | 803.5 | 139 | 0 | 0
23:00 | 3739 | 915 | 2166 | 607 | 4033 | 1334 | 55 | 416 | 773 | 140 | 0 | 0
23:30 | 3750.5 | 915 | 2189.5 | 496.5 | 3934 | 1334 | 55 | 416 | 761.5 | 141 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.5° C
24:00 | 3762 | 915 | 2213 | 386 | 3835 | 1334 | 55 | 416 | 750 | 142 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 26 | 27 | 27 | 28 | 28 | 29 | 29 | 28 | 27 | 26 | 25 | 25 | 26 | 26 | 26 | 27 |  | 27 | 28 | 28 | 28 | 27 | 25 | 25 | 628364
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | [5 empty] | 1 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 2 | 394664
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 8 | 13 | 17 | 17 | 16 | 17 | 16 | 12 | 7 | 2 | 0 | [8 empty] | 126765
6 | Sikalbaha 225MW CCPP (Gas) | 132 | 131 | 131 | 135 | 131 | 131 | 131 | 131 | 149 | 132 | 132 | 152 | 150 | 148 | 141 | 151 | 151 | 151 |  | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 3343972
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 0 |  | 220125
12 | Hathazari 100 MW peaking PP | 43 | 43 | 43 | 43 | 0 | [5 empty] | 0 | 24 | 24 | 24 | 24 | 36 | 49 | 49 |  | 49 | 49 | 49 | 50 | 50 | 50 | 42 | 696120
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 59 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 103 | 51 | 1967127
| Daudkandi 200 MW PP (B.Trac) | 200 | 100 | 11 | [7 empty] | 0 | 30 | 100 | 200 | 200 | 200 | 100 | 10 |  | 190 | 200 | 200 | 200 | 200 | 150 | 60 | 2182272
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | [7 empty] | 0 | 47 | 47 | 47 | 46 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 49 | 49 | 770520
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 283 | 273 | 260 | 273 | 280 | 230 | 230 | 230 | 230 | 244 | 259 | 258 | 272 | 272 | 275 | 275 | 275 | 278 |  | 290 | 290 | 291 | 296 | 293 | 293 | 293 | 6498543
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 63 | 234181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 232 | 232 | 232 | 227 | 232 | 232 | 232 | 232 | 232 | 230 | 231 | 231 | 231 | 228 | 227 | 226 | 227 | 228 |  | 231 | 231 | 231 | 231 | 232 | 233 | 233 | 5534000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 6258391
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 28 | 27 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 668808
33 | Ashuganj 225 MW CCPP | 213 | 215 | 215 | 217 | 219 | 219 | 219 | 219 | 212 | 215 | 213 | 212 | 213 | 209 | 210 | 211 | 210 | 212 |  | 211 | 213 | 212 | 216 | 215 | 215 | 217 | 5156000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 330 | 280 | 310 | 310 | 300 | 350 | 320 | 330 | 310 | 310 | 330 | 335 | 325 | 330 | 330 |  | 345 | 330 | 330 | 325 | 325 | 310 | 310 | 8149000
35 | Ashuganj 55 MW PP (Precision) | 54 | 53 | 54 | 54 | 54 | 53 | 54 | 52 | 52 | 52 | 48 | 48 | 46 | 47 | 46 | 46 | 50 | 48 |  | 51 | 51 | 52 | 53 | 53 | 54 | 54 | 1222560
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 102 | 100 | 100 | 100 | 100 | 2196080
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 397 | 397 | 398 | 398 | 397 | 350 | 351 | 352 | 353 | 393 | 399 | 400 | 401 | 398 | 398 | 397 | 397 | 389 |  | 388 | 411 | 399 | 404 | 395 | 394 | 395 | 9494530
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 6747300
41 | Haripur 360MW CCPP(HPL) | 294 | 292 | 291 | 302 | 302 | 302 | 301 | 302 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 298 | 290 | 288 |  | 295 | 300 | 300 | 301 | 292 | 287 | 287 | 7138000
42 | RPCL 210MW CCPP | 140 | 150 | 149 | 148 | 152 | 153 | 151 | 148 | 133 | 133 | 133 | 117 | 102 | 99 | 99 | 75 | 71 | 75 |  | 100 | 106 | 106 | 119 | 118 | 121 | 122 | 2817600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 9 | 22 | 36 | 22 | 49 | 41 | 45 | 43 | 23 | 12 | 7 | 1 |  | 0 | [6 empty] | 302020
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 |  | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 958664
46 | Shajibazar 330 MW CCPP | 157 | 158 | 158 | 158 | 157 | 159 | 159 | 159 | 153 | 156 | 155 | 156 | 157 | 153 | 149 | 154 | 152 | 152 |  | 150 | 156 | 153 | 155 | 157 | 158 | 158 | 3691000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 55 | 55 | 55 | 55 | 50 | 50 | 50 | 48 | 50 | 50 | 50 |  | 49 | 50 | 50 | 50 | 50 | 55 | 55 | 1235808
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 76 | 76 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 86 | 10 | 10 | 10 |  | 86 | 86 | 86 | 86 | 86 | 86 | 76 | 1109760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 191 | 212 | 218 | 218 | 218 | 219 | 219 | 219 | 219 | 219 | 219 | 215 | 214 | 214 | 214 | 220 |  | 221 | 220 | 221 | 221 | 220 | 220 | 219 | 5225930
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 0 | 10 | 0 | 10 | 10 | 10 | 0 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 222120
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 10 | 10 | 10 | 11 | 11 | 0 | 0 | [19 empty] | 59400
56 | Shahjahanulla 25 MW PP | 17 | 17 | [9 empty] | 16 | 16 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 238560
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 290 | 300 | 280 | 270 | 270 | 260 | 280 | 305 | 270 | 290 | 270 | 295 | 305 | 285 | 280 | 285 |  | 290 | 285 | 290 | 290 | 270 | 275 | 280 | 6964500
| Bibiyana South 400 MW | 396 | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 391 | 400 | 395 | 392 | 395 | 395 | 380 | 375 | 390 | 390 |  | 386 | 395 | 388 | 400 | 400 | 396 | 400 | 9334100
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1094961
59 | Tangail Palli Power Gen 22 MW | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14 | 11 | 20 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 553680
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 460608
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 394308
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 368856
63 | Impoprt (Tripura) | 162 | 156 | 158 | 154 | 148 | 130 | 136 | 134 | 136 | 140 | 150 | 154 | 158 | 158 | 162 | 156 | 124 | 140 |  | 134 | 136 | 138 | 132 | 138 | 140 | 142 | 3456000
64 | Malancha, Ctg. EPZ (United) | 27 | 27 | 35 | 35 | 30 | 29 | 10 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 12 |  | 12 | 18 | 21 | 26 | 26 | 27 | 22 | 365760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 21 | 5 | 21 | 472716
66 | Feni 11 MW PP (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 210660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 24 | 25 | 33 | 33 | 33 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 755200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 20 | 495690
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 525000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 22 | 25 | 25 | 25 | 25 | 24 | 24 |  | 18 | 26 | 26 | 0 | 25 | 27 | 28 | 558540
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 32 | 32 | 32 |  | 32 | 32 | 32 | 16 | 16 | 32 | 32 | 746400
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 98 | 98 | 98 | 93 | 93 | 93 | 93 | 93 | 96 | 94 | 94 |  | 97 | 97 | 97 | 96 | 96 | 95 | 96 | 2290590
| Feni Lanka Power | 81 | 81 | 81 | 81 | 81 | 72 | 72 | 80 | 80 | 64 | 64 | 34 | 34 | 34 | 34 | 34 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 81 | 17 | 1690620
| Chowmuhani 113 MW | 36 | 31 | 29 | 27 | 29 | 28 | 28 | 29 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 42 | 114 | 112 |  | 112 | 113 | 113 | 113 | 113 | 113 | 56 | 1334760
| Manikgonj 162MW PP(MPGL) | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 137 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3245760
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 11 | 64 | 84 | 78 | 78 | 80 | 80 | 80 | 85 |  | 88 | 98 | 94 | 98 | 98 | 99 | 99 | 1240320
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 41 | 41 | 41 | 48 | 48 | 40 | 40 | 40 | 48 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1128960
79 | Kodda 150MW PP | 115 | 115 | 115 | 115 | 115 | 80 | 60 | 62 | 62 | 98 | 115 | 115 | 115 | 132 | 132 | 132 | 140 | 145 |  | 145 | 149 | 145 | 146 | 147 | 145 | 146 | 2814720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 38 | 38 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 36 | 42 | 42 | 42 | 41 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 1008398
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 105 | 105 | 105 | 90 | 90 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2496000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 5 | 5 | 3 | 2 | 1 | 0 | [8 empty] | 33000
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1348276
| Karnaphuli Power Ltd. | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 88 | 93 | 92 | 94 | 92 | 92 | 97 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2424608
82 | Madanganj 102 PP(Summit) | 64 | 74 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 76 | 76 | 76 | 75 | 75 |  | 75 | 77 | 77 | 78 | 78 | 78 | 78 | 1854888
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 130 | 130 | 130 | 140 | 130 | 125 | 125 | 120 | 150 | 130 | 135 | 130 | 130 | 130 | 150 | 125 | 130 | 135 |  | 140 | 130 | 135 | 120 | 120 | 130 | 130 | 3187549
87 | Meghnaghat 100 MW(IEL) | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 54 | 71 | 68 | 71 | 70 | 71 | 71 |  | 71 | 24 | 40 | 24 | 25 | 24 | 24 | 795840
| Meghnaghat 104 MW PP (OPCL) | 99 | 104 | 101 | 104 | 104 | 92 | 76 | 71 | 71 | 83 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2450880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 10 | 0 |  |  | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 |  | 92 | 92 | 92 | 92 | 92 | 80 | 92 | 1656720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1190474
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 84 | 84 | 84 | 84 | 76 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1999584
95 | Patenga 50MW PP (Baraka) | 37 | 37 | 37 | 37 | 37 | 27 | 18 | 18 | 18 | 20 | 27 | 31 | 37 | 36 | 36 | 36 | 36 | 36 |  | 37 | 37 | 35 | 32 | 37 | 37 | 37 | 788640
96 | Chattogram 108 MW PP (ECPV) | 94 | 90 | 90 | 94 | 94 | 96 | 94 | 91 | 92 | 90 | 86 | 84 | 85 | 85 | 86 | 93 | 94 | 94 |  | 93 | 94 | 96 | 96 | 95 | 96 | 97 | 2206080
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 36 | 38 | 40 | 40 | 45 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1171783
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1254591
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 163 | 163 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3714709
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14250
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 45 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 937440
104 | Keranigonj 300 MW PP (APR) | 103 | 104 | 107 | 21 | [5 empty] | 57 | 12 | 111 | 55 | 303 | 303 | 306 | 28 | 0 |  | 255 | 306 | 221 | 301 | 105 | 47 | 17 | 2522876
105 | Bramhangoan 100 MW PP (Aggreko) | 95 | 50 | 50 | [6 empty] | 50 | 25 | 90 | 90 | 90 | 90 | 90 | 90 | 25 |  | 90 | 96 | 98 | 98 | 98 | 98 | 97 | 1372075
106 | Mymensingh 200 MW PP (United) | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 185 | 185 | 183 | 183 | 182 | 181 | 181 | 181 | 182 |  | 182 | 185 | 185 | 186 | 186 | 0 | 50 | 4197600
112 | Aurahati 100MW PP (Aggreko) | 100 | 50 | 50 | [6 empty] | 92 | 50 | 25 | 98 | 97 | 97 | 98 | 99 | 25 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1430360
114 | Kodda 149 MW PP Unit-1 (Summit) | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 143 | 138 | 148 | 141 | 130 | 129 | 130 | 132 | 132 | 136 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3495888
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 2069760
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 136 | 68 | 68 | 68 | 86 | 174 | 180 | 180 | 180 | 180 | 180 | 180 | 164 |  | 179 | 180 | 180 | 185 | 200 | 200 | 200 | 4027680
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 150 | 150 | 50 | 50 | 50 | 50 | 78 | 120 | 127 | 132 | 132 | 132 | 132 | 132 | 142 |  | 143 | 147 | 147 | 150 | 150 | 150 | 140 | 3019273
118 | Bibiyana-III 400 MW CCPP | 403 | 402 | 400 | 400 | 400 | 400 | 400 | 400 | 403 | 402 | 403 | 403 | 404 | 406 | 395 | 406 | 401 | 402 |  | 379 | 405 | 404 | 403 | 403 | 401 | 402 | 9609000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 105 | 105 | 115 | 106 | 105 | 105 | 105 | 105 | 115 | 102 | 102 | 112 | 112 | 115 |  | 115 | 115 | 115 | 115 | 115 | 0 | 8 | 2470800
| Anwara 300 MW PP (United) | 281 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7118291
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 90 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2379840
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 91 | 108 | 108 | 108 | 108 | 100 | 91 | 105 | 104 | 90 | 93 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2522891
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | 7 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 25 |  | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 830880
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 9 | 16 | 31 | 31 | 28 | 30 | 27 | 22 | 15 | 6 | 1 |  | 0 | [6 empty] | 220647
| Chandpur 115(Doreen) | 78 | 77 | 77 | 53 | 54 | 77 | 55 | 50 | 50 | 60 | 94 | 101 | 101 | 101 | 101 | 90 | 90 | 101 |  | 95 | 101 | 102 | 101 | 101 | 101 | 101 | 2045760
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | [12 empty] | 6 | 55 | 55 | 55 | 699120
120 | Eastern Zone Total | 8931 | 8749 | 8585 | 8487 | 8264 | 7720 | 7515 | 7484 | 7647 | 8003 | 8299 | 8523 | 8730 | 9123 | 9202 | 9051 | 8792 | 8596 |  | 9427 | 9546 | 9469 | 9539 | 9401 | 8890 | 8647 | 208066244
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 88 | 66 | 45 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1206720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 37 | 37 | 37 | 37 | 9 | [8 empty] | 8 | 16 | 22 | 26 | 28 |  | 30 | 44 | 35 | 37 | 37 | 37 | 37 | 453120
| Khulna 225 MW CCPP | 145 | 40 | 40 | 40 | 10 | 10 | 25 | 78 | 120 | 80 | 80 | 140 | 125 | 28 | 37 | 44 | 90 | 155 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2528681
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 97 | 95 | 103 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2636160
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 17 | 30 | 55 | 81 | 91 | 95 | 91 | 83 | 62 | 44 | 19 | 3 |  | 0 | [6 empty] | 677520
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | [5 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 338400
133 | Bhola Nutan Biddut BD LTD (GAS) | 206 | 204 | 206 | 209 | 209 | 213 | 224 | 218 | 170 | 220 | 210 | 210 | 210 | 207 | 205 | 210 | 210 | 177 |  | 214 | 215 | 218 | 206 | 206 | 216 | 217 | 4999991
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 599328
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 88 | 88 | 87 | 87 | 88 | 89 | 89 | 88 | 82 | 85 | 84 | 84 | 84 | 60 | 50 | 65 | 65 | 65 |  | 63 | 65 | 65 | 67 | 67 | 66 | 67 | 1795553
140 | Bhola 33 MW PP (Venture) | 39 | 39 | 38 | 38 | 35 | 32 | 29 | 27 | 25 | 22 | 22 | 25 | 25 | 27 | 30 | 27 | 28 | 28 |  | 38 | 39 | 38 | 38 | 39 | 38 | 38 | 764397
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 50 | 10 | [6 empty] | 0 | 0 | 17 | 85 | 76 | 98 | 99 | 98 | 60 |  | 60 | 100 | 99 | 100 | 100 | 60 | 10 | 1283520
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 21 | 24 | 8 | 8 | 111375
143 | Gopalganj 100 MW Peaking PP | 38 | 38 | 38 | 38 | 23 | [12 empty] | 14 |  | 20 | 25 | 37 | 64 | 50 | 50 | 34 | 439424
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 101 | 89 | 89 | 89 | 82 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 85 | 85 |  | 85 | 85 | 105 | 105 | 105 | 105 | 105 | 2156832
146 | Bheramara HVDC | 921 | 921 | 921 | 921 | 923 | 922 | 922 | 920 | 920 | 919 | 920 | 921 | 920 | 920 | 920 | 919 | 918 | 918 |  | 912 | 911 | 912 | 914 | 914 | 915 | 915 | 22212363
147 | Bheramara 410 MW CCPP | 180 | 180 | 180 | 180 | 185 | 185 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 180 | 180 | 180 | 180 | 175 |  | 170 | 180 | 180 | 185 | 185 | 180 | 180 | 4597920
148 | Payra 1320 MW | 1040 | 1040 | 1040 | 1020 | 990 | 930 | 920 | 890 | 890 | 930 | 940 | 940 | 940 | 990 | 1040 | 990 | 970 | 930 |  | 950 | 1070 | 1070 | 1080 | 1080 | 1060 | 1060 | 25849700
149
150 | Barapukuria TPP Unit-1 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 70 | 70 | 71 | 72 | 73 | 71 | 74 |  | 73 | 72 | 72 | 72 | 73 | 74 | 74 | 1686109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4846800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 0 | [12 empty] | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 430752
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 3 | 5 | 5 | 5 | 2 | 3 | 2 | 1 | 0 | [8 empty] | 34860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 131 | 132 | 132 | 132 | 131 | 132 | 134 | 136 | 140 | 141 | 142 | 141 | 142 | 142 | 143 | 144 | 141 | 139 |  | 136 | 135 | 137 | 139 | 141 | 141 | 142 | 3547464
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 215 | 216 | 216 | 215 | 155 | 130 | 130 | 130 | 130 | 145 | 212 | 211 | 212 | 207 | 206 | 209 | 210 | 210 |  | 210 | 211 | 212 | 213 | 215 | 216 | 216 | 4899391
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 412 | 411 | 414 | 414 | 414 | 350 | 350 | 350 | 350 | 419 | 417 | 417 | 414 | 414 | 414 | 414 | 411 | 395 |  | 403 | 408 | 414 | 414 | 417 | 414 | 414 | 9616509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 22 | 23 | 21 | 22 | 0 | [10 empty] | 3 | 5 | 23 |  | 24 | 24 | 27 | 28 | 28 | 28 | 28 | 271154
162 | Bogra 22 MW PP (GBB) | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 18 | 18 | 19 | 20 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 469920
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252054
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 43 | 0 | [14 empty] | 16 | 34 | 50 | 43 | 43 | 43 | 43 | 408833
167 | Katakhali 50 MW Peaking PP | 22 | 22 | 22 | 22 | 0 | [8 empty] | 24 | 24 | 24 | 24 | 29 |  | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 389980
168 | Santahar 50 MW Peaking PP | 37 | 38 | 36 | 38 | 0 | [7 empty] | 10 | 35 | 36 | 36 | 36 | 36 |  | 37 | 36 | 36 | 35 | 36 | 30 | 30 | 559719
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 24 | 24 | 24 | 24 | 34 | 34 | 34 | 34 | 36 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 25 | 24 | 884645
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 90 | 30 | 0 | [7 empty] | 36 | 50 | 50 | 50 | 50 | 85 |  | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 1225784
171 | Baghabari 200 MW PP (Paramount) | 122 | 50 | 50 | 0 | [7 empty] | 12 | 99 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 149 | 153 | 152 | 152 | 1859006
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 94 | 94 | 106 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2694816
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 113 | 113 | 95 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2593152
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  |  |  | 3000
175 | Saidpur 20 MW GTPP | 8 | 8 | 8 | 8 | 0 | [10 empty] | 10 | 8 | 8 |  | 8 | 8 | 8 | 0 |  |  |  | 79000
176 | Rangpur 113 MW PP (Confidence) | 108 | 108 | 108 | 109 | 104 | 102 | 88 | 74 | 73 | 93 | 100 | 99 | 98 | 98 | 99 | 98 | 100 | 105 |  | 103 | 99 | 106 | 107 | 77 | 102 | 102 | 2354870
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 2 | 5 | 5 | 5 | 6 | 5 | 3 | 1 | [8 empty] | 0 | 37671
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 72 | 72 | 72 | 72 | 72 | 90 | 108 | 108 | 108 | 108 | 108 | 52 | 52 | 52 |  | 80 | 115 | 115 | 115 | 115 | 115 | 52 | 2316288
178