## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-04-29 | Friday
|  |  | Date (day): | 2022-04-29 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15257.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15495 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-28 | 2022-04-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 232 | 230 | 230 | 230
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 98 | 94 | 94
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 399 | 406 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 265 | 350 | 350 | 10
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 320 | 320 | 130 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 94 | 87 | 97 | 97
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 130 | 150 | 150 |  | 185 | GT-1 Under S/D
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 75 | 76 | 76 | 76 |  | 26 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 84 | 98 | 96 | 96
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 84 | 85 | 85 |  | 17 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 146 | 146 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 50 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 48 | 49 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 263 | 288 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 116 | 203 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 94 | 98 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 95 | 99 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 144 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 33 | 33 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5998 | 3583 | 3816 | 4096 | 4086 | 1021 | 874
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 37 | 37 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 56 | 57 | 35 | 35 |  | 195 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 33 | 203 | 200 | 200
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 28 | 44 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 17 | 17 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 42 | 40 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 87 | 96 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 82 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1172 | 1529 | 1539 | 1506 | 231 | 617
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 210 | 225 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 280 | 330 | 350
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 28 | 28 | 28 | 17 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 53 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 138 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 5 | 47 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 136 | 136 | 136 |  | 27 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 130 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 41 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 100 | 150 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 80 | 80 | 80 |  | 34 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 68 | 113 | 57 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 36 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 82 | 82 | 82 | 82 |  | 33 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1647 | 1863 | 1958 | 2057 | 827 | 121
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 74 | 131 | 100 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 174 | 177 | 190 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 115 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 24 | 24
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 431 | 464 | 497.6 | 446 | 102 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 155 | 156 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 50 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 220 | 220 | 220
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 10 | 0 | 0 | 50 |  | Gas shortage
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 17 | 17 | 17
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 310 | 310 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 404 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 393 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1762 | 1853 | 1876 | 1876 | 341 | 219
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 922 | 923 | 943 | 943
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 37 | 37 |  | 17 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 170 | 200
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 0 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 160 | 175 | 170 | 170 | 240 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 32 |  | 8 | Engine problem
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 1 | 50 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 89 | 105 | 105
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1493 | 1657 | 1778 | 1768 | 339 | 74
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 50 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 27 | 39 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 30 | 65 | 65 | 65 | 129 |  | Gas shortage & GT-2 S/D
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1100 | 1080 | 1120
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 209 | 217 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1229 | 1486 | 1598 | 1698 | 129 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 36 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 28 | 30 | 30 |  | 41 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 50 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 10 | 40 | 30 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 134 | 114 | 130 | 120 | 90 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 176 | 214 | 200 | 220 |  |  | Running on HSD
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 386 | 400 | 410
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 30 | 38 |  | 12 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 43 | 43
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 90 | 90 |  | 14 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 66 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1018 | 1369 | 1497 | 1536 | 481 | 143
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 73 | 70 | 70
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 |  | 74 | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 101 | 111 | 110 | 110
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 115 | 30 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 429 | 507 | 418 | 522 | 0 | 169
|  | Total |  |  |  |  | 22348 | 21734 | 12764 | 14544 | 15257.6 | 15495 | 3471 | 2225
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 12394.841 | 14123.36 | 14816.3213 | 15046.8553
| A. |  | 2022-04-28 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 14666 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11088 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14544 | MW
| 3 | Day peak Generation : |  |  | 12764 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14123.36 | MW
| 4 | Evening peak Generation : |  |  | 14544 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 316.7995 | MKWHr | By Solar | 1.4549 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 136.4484 | MKWHr |  | By Oil: | 120.2069 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 32.1783 | MKWHr |  | By Hydro: | 1.3497 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3471 | MW | Dhaka | 4867.26 | 4867.26 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2225 | MW | Chittagong | 1381.7 | 1381.7 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5696 | MW | Khulna | 1897 | 1897 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1026.06 | MMCFD |  |  | Rajshahi | 1591.4 | 1591.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 135884895.368 | ii) Oil : | Taka | 1034039517.82 | Comilla | 1404 | 1404 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 149054498.27 | Total | Taka | 1318978911.458 | Mymensingh | 1096 | 1096 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 590 | 590 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 66 | MW (E to W) at | 21:00 | hrs | Barisal | 451 | 451 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 66 | MW at | 21:00 | hrs | Rangpur | 845 | 845 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.0° C |  |  | Total | 14123.36 | 14123.36 |  | 0
| B. |  | 2022-04-29 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 26.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15495 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1795 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 295.933 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10975 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3062 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.855 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.59 |  | (b) Today: | 76.33 |  | (c) Rule Curve: |  | 82.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 396 | 256 |  | 0 | 300 | 130 | 96 | 76 | 55 | 0 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 41 | 0 | 26 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 10 | 51 | 0 | 90 | 91 | 37 | 19 | 29 | 0 | 0 | 0 | 270 | 0 | 214 | 8 | 90 | 28 | 56 | 0 | 51 | 0 | 47 | 43 | 19 | 8 | 33 | 21 | 128 | 136 | 0 | 0 | 0 | 0 | 41 | 11 | 10 | 163 | 160 | 50 | 74 | 0 | 220 | 0 | 0 | 10 | 280 | 17 | 11 | 120 | 278 | 158 | 98 | 182 | 98 | 149 | 0 | 90 | 200 | 150 | 403 | 106 | 105 | 51 | 0 | 300 | 54 | 97 | 17 | 28 | 100 | 394 | 93 | 0 | 127 | 108 | 0 | 36 | 0 | 83 | 33 |  | 921 | 0 | 175 | 0 | 16 | 206 | 0 | 0 | 34 | 60 | 0 | 67 | 39 | 32 | 0 | 0 | 0 | 43 | 28 | 86 | 0 | 43 | 24 | 25 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 220 | 0 | 10 | 0 | 0 | 395 | 105 | 20 | 113 | 89 | 110 | 0 | 0 | 113 | 1040 | 220 | 0 | 54 | 0 | 0 | 34 |  | 8967 | 4798 | 13765 | 3679 | 921 | 2150 | 504 | 4029 | 1312 | 56 | 426 | 780 | 128 | 0 | 0 | 76.69
2:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 397 | 267 |  | 0 | 300 | 120 | 96 | 62 | 55 | 0 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 41 | 0 | 26 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 18 | 51 | 0 | 92 | 96 | 37 | 19 | 21 | 0 | 0 | 0 | 270 | 0 | 216 | 8 | 91 | 28 | 55 | 0 | 51 | 0 | 49 | 35 | 19 | 8 | 33 | 21 | 106 | 150 | 0 | 0 | 0 | 0 | 41 | 11 | 10 | 163 | 157 | 50 | 74 | 0 | 220 | 0 | 0 | 10 | 280 | 17 | 11 | 80 | 272 | 127 | 98 | 182 | 98 | 149 | 0 | 90 | 200 | 150 | 402 | 115 | 105 | 51 | 0 | 300 | 54 | 92 | 17 | 28 | 100 | 401 | 90 | 0 | 115 | 108 | 0 | 36 | 0 | 83 | 33 |  | 921 | 0 | 175 | 0 | 16 | 206 | 0 | 0 | 34 | 60 | 0 | 67 | 39 | 32 | 0 | 0 | 0 | 43 | 29 | 86 | 0 | 43 | 24 | 25 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 219 | 0 | 10 | 0 | 0 | 396 | 105 | 20 | 113 | 89 | 110 | 0 | 0 | 113 | 1030 | 210 | 0 | 54 | 0 | 0 | 34 |  | 8845 | 4779 | 13624 | 3700 | 921 | 2133 | 433 | 3985 | 1302 | 56 | 425 | 782 | 106 | 0 | 0 | 76.67
3:00 | 0 | 0 | 231 | 0 | 270 | 96 | 0 | 397 | 272 |  | 0 | 300 | 120 | 96 | 62 | 55 | 0 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 41 | 0 | 26 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 24 | 51 | 0 | 90 | 97 | 37 | 19 | 25 | 0 | 0 | 0 | 270 | 0 | 218 | 8 | 90 | 28 | 55 | 0 | 51 | 0 | 49 | 43 | 19 | 8 | 33 | 21 | 106 | 150 | 0 | 17 | 0 | 0 | 41 | 11 | 10 | 163 | 157 | 50 | 74 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 11 | 30 | 285 | 51 | 50 | 182 | 50 | 149 | 0 | 90 | 200 | 132 | 402 | 115 | 105 | 51 | 0 | 300 | 54 | 92 | 17 | 28 | 100 | 400 | 89 | 0 | 126 | 108 | 0 | 36 | 0 | 83 | 33 |  | 920 | 0 | 175 | 0 | 16 | 206 | 0 | 0 | 34 | 60 | 0 | 68 | 39 | 32 | 0 | 0 | 0 | 43 | 29 | 86 | 0 | 43 | 24 | 25 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 219 | 0 | 10 | 0 | 0 | 401 | 105 | 20 | 113 | 89 | 110 | 0 | 0 | 113 | 1030 | 210 | 0 | 54 | 0 | 0 | 34 |  | 8679 | 4784 | 13463 | 3700 | 920 | 2157 | 211 | 4023 | 1302 | 56 | 425 | 782 | 106 | 0 | 0 | 76.65
4:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 397 | 277 |  | 0 | 300 | 145 | 96 | 62 | 55 | 0 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 41 | 0 | 24 | 30 | 0 | 0 | 25 | 141 | 0 | 0 | 0 |  | 24 | 51 | 0 | 90 | 97 | 37 | 19 | 30 | 0 | 0 | 0 | 270 | 0 | 214 | 8 | 90 | 28 | 55 | 0 | 51 | 0 | 49 | 43 | 19 | 8 | 33 | 21 | 106 | 150 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 156 | 50 | 10 | 0 | 191 | 0 | 0 | 10 | 290 | 8 | 11 | 0 | 288 | 0 | 0 | 182 | 0 | 149 | 0 | 90 | 200 | 150 | 404 | 115 | 105 | 51 | 0 | 300 | 54 | 92 | 17 | 28 | 100 | 394 | 90 | 0 | 126 | 108 | 0 | 36 | 0 | 83 | 33 |  | 921 | 0 | 175 | 0 | 16 | 150 | 0 | 0 | 12 | 12 | 0 | 66 | 39 | 32 | 0 | 0 | 0 | 43 | 21 | 70 | 0 | 43 | 24 | 25 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 403 | 105 | 0 | 113 | 89 | 110 | 0 | 0 | 113 | 1010 | 210 | 0 | 35 | 0 | 0 | 0 |  | 8396 | 4491 | 12887 | 3679 | 921 | 2056 | 0 | 3992 | 1282 | 54 | 328 | 647 | 106 | 0 | 0 | 76.63
5:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 392 | 276 |  | 0 | 300 | 125 | 96 | 62 | 55 | 0 | 0 | 0 | 91 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 42 | 0 | 24 | 30 | 0 | 0 | 25 | 131 | 0 | 0 | 0 |  | 24 | 8 | 0 | 60 | 98 | 37 | 19 | 40 | 0 | 0 | 0 | 270 | 0 | 217 | 8 | 91 | 28 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 100 | 150 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 157 | 50 | 10 | 0 | 192 | 0 | 0 | 10 | 290 | 14 | 0 | 0 | 288 | 0 | 0 | 182 | 0 | 149 | 0 | 90 | 190 | 150 | 370 | 115 | 90 | 51 | 0 | 300 | 54 | 92 | 17 | 28 | 100 | 398 | 91 | 0 | 126 | 95 | 0 | 36 | 0 | 79 | 33 |  | 921 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 36 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 370 | 99 | 0 | 113 | 89 | 105 | 0 | 0 | 113 | 960 | 210 | 0 | 35 | 0 | 0 | 0 |  | 8222 | 4075 | 12297 | 3635 | 921 | 2061 | 0 | 3864 | 1232 | 54 | 272 | 310 | 100 | 0 | 0 | 76.61
6:00 | 0 | 0 | 231 | 0 | 270 | 96 | 0 | 380 | 277 |  | 0 | 300 | 130 | 96 | 65 | 55 | 0 | 0 | 0 | 0 | 84 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 42 | 0 | 26 | 30 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 98 | 37 | 19 | 31 | 0 | 0 | 0 | 270 | 0 | 215 | 8 | 70 | 28 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 21 | 98 | 137 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 160 | 50 | 10 | 0 | 178 | 0 | 0 | 10 | 280 | 14 | 0 | 0 | 288 | 0 | 0 | 182 | 0 | 149 | 1 | 90 | 51 | 50 | 371 | 115 | 81 | 51 | 0 | 300 | 54 | 68 | 17 | 28 | 100 | 400 | 79 | 2 | 127 | 68 | 0 | 0 | 1 | 69 | 33 |  | 923 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 71 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 340 | 17 | 0 | 50 | 89 | 93 | 0 | 0 | 35 | 910 | 210 | 0 | 17 | 0 | 3 | 0 |  | 7524 | 3707 | 11231 | 3587 | 923 | 2017 | 0 | 3031 | 1180 | 56 | 250 | 212 | 98 | 7 | 0 | 76.59
7:00 | 0 | 0 | 232 | 0 | 270 | 96 | 0 | 395 | 272 |  | 0 | 300 | 145 | 96 | 76 | 55 | 0 | 0 | 0 | 0 | 82 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 42 | 0 | 26 | 30 | 0 | 0 | 0 | 70 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 91 | 37 | 19 | 5 | 0 | 0 | 0 | 270 | 0 | 216 | 8 | 30 | 28 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 98 | 116 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 163 | 159 | 50 | 10 | 0 | 178 | 0 | 0 | 10 | 310 | 14 | 0 | 0 | 288 | 0 | 0 | 182 | 0 | 149 | 4 | 90 | 54 | 50 | 373 | 115 | 81 | 51 | 1 | 300 | 54 | 68 | 17 | 28 | 60 | 390 | 23 | 9 | 126 | 68 | 0 | 7 | 0 | 54 | 33 |  | 923 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 72 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 417 | 17 | 0 | 60 | 89 | 39 | 0 | 0 | 70 | 910 | 215 | 0 | 17 | 0 | 19 | 0 |  | 7292 | 3796 | 11088 | 3454 | 923 | 2113 | 0 | 2898 | 1181 | 56 | 250 | 212 | 98 | 33 | 0 | 76.57
8:00 | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 400 | 272 |  | 0 | 300 | 130 | 97 | 66 | 55 | 0 | 0 | 0 | 3 | 84 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 42 | 0 | 26 | 30 | 0 | 0 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 91 | 37 | 19 | 5 | 0 | 0 | 0 | 270 | 0 | 218 | 8 | 30 | 28 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 112 | 108 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 160 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 285 | 15 | 0 | 0 | 288 | 0 | 0 | 181 | 0 | 149 | 9 | 90 | 71 | 50 | 374 | 115 | 90 | 51 | 3 | 300 | 54 | 85 | 17 | 33 | 80 | 401 | 30 | 9 | 126 | 68 | 0 | 36 | 13 | 78 | 33 |  | 922 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 71 | 0 | 200 | 0 | 0 | 133 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 354 | 25 | 0 | 113 | 89 | 39 | 0 | 1 | 100 | 930 | 190 | 0 | 17 | 1 | 30 | 8 |  | 7392 | 3831 | 11223 | 3481 | 922 | 1923 | 0 | 3130 | 1201 | 56 | 250 | 212 | 112 | 66 | 0 | 76.55
9:00 | 0 | 0 | 232 | 0 | 270 | 91 | 0 | 400 | 274 |  | 0 | 300 | 150 | 97 | 69 | 55 | 0 | 0 | 0 | 7 | 84 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 42 | 0 | 26 | 30 | 0 | 0 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 77 | 37 | 19 | 7 | 0 | 0 | 0 | 270 | 0 | 215 | 8 | 30 | 28 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 110 | 106 | 0 | 17 | 1 | 0 | 41 | 0 | 0 | 110 | 154 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 270 | 15 | 0 | 0 | 288 | 0 | 0 | 181 | 0 | 149 | 14 | 90 | 100 | 50 | 374 | 115 | 90 | 51 | 4 | 300 | 54 | 93 | 52 | 66 | 100 | 388 | 88 | 21 | 126 | 68 | 0 | 22 | 20 | 83 | 33 |  | 923 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 63 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 11 | 71 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 351 | 65 | 0 | 113 | 89 | 39 | 0 | 4 | 113 | 930 | 216 | 0 | 17 | 3 | 67 | 34 |  | 7564 | 3968 | 11532 | 3454 | 923 | 1946 | 0 | 3376 | 1201 | 56 | 250 | 212 | 110 | 134 | 0 | 76.54
10:00 | 0 | 0 | 232 | 0 | 270 | 91 | 0 | 402 | 253 |  | 0 | 300 | 135 | 96 | 76 | 55 | 0 | 0 | 0 | 20 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 42 | 0 | 29 | 30 | 0 | 0 | 6 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 81 | 37 | 19 | 5 | 0 | 0 | 0 | 320 | 0 | 215 | 26 | 30 | 28 | 54 | 0 | 51 | 0 | 0 | 17 | 0 | 8 | 33 | 20 | 114 | 103 | 0 | 17 | 1 | 0 | 41 | 0 | 0 | 130 | 157 | 50 | 10 | 0 | 219 | 0 | 0 | 9 | 290 | 17 | 0 | 0 | 288 | 0 | 25 | 180 | 25 | 149 | 16 | 90 | 147 | 83 | 371 | 105 | 90 | 51 | 4 | 300 | 54 | 91 | 70 | 70 | 100 | 399 | 89 | 40 | 126 | 95 | 0 | 17 | 24 | 84 | 33 |  | 922 | 0 | 175 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 0 | 63 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 19 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 384 | 92 | 0 | 113 | 89 | 92 | 0 | 5 | 111 | 930 | 200 | 0 | 17 | 4 | 82 | 49 |  | 7969 | 4160 | 12129 | 3498 | 922 | 1981 | 50 | 3687 | 1200 | 59 | 309 | 282 | 114 | 176 | 0 | 76.53
11:00 | 0 | 0 | 232 | 0 | 270 | 91 | 0 | 396 | 252 |  | 0 | 300 | 145 | 91 | 75 | 40 | 0 | 0 | 0 | 71 | 76 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 18 | 33 | 33 | 42 | 0 | 28 | 30 | 0 | 0 | 25 | 27 | 0 | 0 | 0 |  | 0 | 8 | 0 | 90 | 82 | 37 | 19 | 7 | 0 | 0 | 0 | 320 | 0 | 210 | 26 | 30 | 28 | 54 | 0 | 51 | 0 | 0 | 34 | 0 | 8 | 33 | 20 | 114 | 74 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 153 | 45 | 10 | 0 | 219 | 0 | 0 | 9 | 270 | 17 | 0 | 0 | 283 | 0 | 25 | 179 | 25 | 149 | 18 | 90 | 192 | 125 | 379 | 105 | 90 | 51 | 5 | 300 | 54 | 88 | 65 | 73 | 90 | 380 | 89 | 39 | 126 | 108 | 0 | 17 | 30 | 83 | 32 |  | 921 | 0 | 160 | 0 | 16 | 125 | 0 | 0 | 0 | 0 | 0 | 63 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 18 | 0 | 11 | 71 | 0 | 200 | 0 | 0 | 133 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 373 | 93 | 0 | 113 | 89 | 102 | 0 | 6 | 111 | 930 | 213 | 0 | 17 | 2 | 94 | 52 |  | 8037 | 4157 | 12194 | 3413 | 921 | 1955 | 50 | 3837 | 1201 | 58 | 295 | 324 | 114 | 196 | 0 | 76.52
12:00 | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 399 | 252 |  | 0 | 300 | 140 | 94 | 75 | 40 | 0 | 0 | 0 | 84 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 18 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 33 | 0 | 0 | 0 |  | 0 | 28 | 0 | 90 | 87 | 37 | 19 | 12 | 0 | 0 | 0 | 325 | 0 | 211 | 45 | 30 | 28 | 53 | 0 | 51 | 0 | 5 | 34 | 0 | 8 | 33 | 20 | 120 | 74 | 0 | 17 | 2 | 0 | 40 | 0 | 0 | 163 | 155 | 55 | 10 | 0 | 219 | 0 | 0 | 9 | 300 | 17 | 0 | 100 | 263 | 116 | 94 | 174 | 95 | 144 | 19 | 76 | 200 | 137 | 404 | 115 | 90 | 51 | 5 | 300 | 54 | 82 | 80 | 68 | 90 | 390 | 92 | 49 | 126 | 108 | 0 | 17 | 0 | 82 | 33 |  | 922 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 27 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 16 | 10 | 16 | 0 | 19 | 0 | 11 | 71 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 176 | 0 | 1 | 0 | 0 | 402 | 93 | 0 | 113 | 89 | 101 | 0 | 6 | 113 | 930 | 209 | 0 | 17 | 4 | 92 | 52 |  | 8595 | 4169 | 12764 | 3442 | 922 | 2086 | 406 | 3866 | 1200 | 56 | 296 | 369 | 120 | 177 | 0 | 76.51
13:00 | 0 | 0 | 230 | 0 | 270 | 90 | 0 | 398 | 245 |  | 0 | 300 | 145 | 95 | 75 | 45 | 0 | 0 | 0 | 82 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 40 | 0 | 0 | 0 |  | 0 | 28 | 0 | 90 | 87 | 37 | 19 | 20 | 0 | 0 | 0 | 330 | 0 | 210 | 45 | 29 | 28 | 51 | 0 | 51 | 0 | 47 | 40 | 19 | 8 | 33 | 20 | 126 | 72 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 163 | 151 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 295 | 17 | 0 | 100 | 258 | 100 | 96 | 155 | 100 | 132 | 18 | 90 | 200 | 137 | 406 | 115 | 90 | 51 | 5 | 300 | 54 | 92 | 80 | 73 | 100 | 384 | 92 | 28 | 126 | 108 | 0 | 17 | 32 | 83 | 33 |  | 922 | 0 | 165 | 0 | 16 | 140 | 0 | 0 | 0 | 0 | 0 | 45 | 29 | 16 | 0 | 0 | 0 | 0 | 22 | 28 | 0 | 16 | 16 | 16 | 0 | 18 | 0 | 11 | 71 | 0 | 199 | 0 | 0 | 131 | 0 | 0 | 207 | 0 | 10 | 0 | 0 | 392 | 93 | 9 | 113 | 89 | 101 | 0 | 6 | 113 | 930 | 207 | 0 | 17 | 4 | 91 | 52 |  | 8699 | 4295 | 12994 | 3484 | 922 | 2071 | 415 | 3900 | 1200 | 56 | 347 | 494 | 126 | 186 | 0 | 76.5
14:00 | 0 | 0 | 226 | 0 | 270 | 91 | 0 | 398 | 250 |  | 0 | 300 | 120 | 90 | 75 | 55 | 0 | 0 | 0 | 96 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 33 | 33 | 40 | 0 | 25 | 30 | 0 | 0 | 25 | 62 | 0 | 0 | 0 |  | 0 | 32 | 0 | 90 | 87 | 25 | 19 | 20 | 0 | 0 | 0 | 320 | 0 | 178 | 45 | 56 | 27 | 50 | 0 | 51 | 0 | 40 | 43 | 19 | 8 | 31 | 20 | 128 | 71 | 0 | 17 | 2 | 0 | 40 | 0 | 0 | 163 | 152 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 285 | 17 | 0 | 200 | 260 | 301 | 95 | 156 | 99 | 131 | 16 | 90 | 200 | 137 | 402 | 105 | 90 | 51 | 4 | 300 | 54 | 92 | 80 | 73 | 100 | 390 | 104 | 37 | 126 | 108 | 0 | 25 | 28 | 82 | 33 |  | 922 | 0 | 170 | 0 | 16 | 165 | 0 | 0 | 0 | 0 | 0 | 63 | 30 | 16 | 0 | 0 | 0 | 0 | 26 | 36 | 0 | 16 | 16 | 16 | 0 | 18 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 129 | 0 | 0 | 210 | 0 | 27 | 0 | 0 | 378 | 93 | 38 | 113 | 88 | 101 | 0 | 6 | 113 | 940 | 210 | 0 | 17 | 1 | 81 | 52 |  | 8979 | 4390 | 13369 | 3503 | 922 | 2031 | 760 | 3912 | 1212 | 55 | 375 | 506 | 128 | 175 | 0 | 0
15:00 | 0 | 0 | 227 | 0 | 270 | 89 | 0 | 396 | 244 |  | 0 | 300 | 150 | 90 | 75 | 55 | 0 | 0 | 0 | 97 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 40 | 0 | 25 | 30 | 0 | 0 | 25 | 138 | 0 | 0 | 0 |  | 0 | 32 | 0 | 90 | 87 | 25 | 19 | 20 | 0 | 0 | 0 | 280 | 0 | 203 | 8 | 57 | 27 | 51 | 0 | 51 | 0 | 47 | 43 | 19 | 8 | 12 | 19 | 130 | 68 | 0 | 17 | 1 | 0 | 40 | 0 | 0 | 163 | 154 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 290 | 17 | 0 | 200 | 270 | 260 | 95 | 156 | 99 | 131 | 12 | 90 | 200 | 127 | 391 | 95 | 70 | 60 | 3 | 300 | 54 | 92 | 80 | 73 | 100 | 389 | 104 | 33 | 126 | 108 | 0 | 36 | 22 | 82 | 33 |  | 922 | 0 | 165 | 0 | 16 | 195 | 0 | 0 | 0 | 0 | 0 | 63 | 31 | 32 | 0 | 0 | 0 | 0 | 25 | 45 | 0 | 16 | 31 | 16 | 0 | 18 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 127 | 0 | 0 | 210 | 0 | 80 | 0 | 0 | 388 | 93 | 149 | 95 | 88 | 99 | 0 | 4 | 113 | 980 | 205 | 0 | 17 | 3 | 65 | 0 |  | 8919 | 4572 | 13491 | 3502 | 922 | 2028 | 883 | 3847 | 1250 | 55 | 405 | 536 | 130 | 143 | 0 | 0
16:00 | 0 | 0 | 225 | 0 | 270 | 89 | 0 | 396 | 237 |  | 0 | 300 | 140 | 88 | 75 | 55 | 0 | 0 | 0 | 97 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 40 | 0 | 26 | 30 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 3 | 32 | 0 | 90 | 87 | 25 | 19 | 30 | 0 | 0 | 0 | 280 | 0 | 209 | 8 | 54 | 27 | 50 | 0 | 51 | 0 | 45 | 43 | 18 | 8 | 33 | 19 | 126 | 70 | 0 | 17 | 1 | 0 | 40 | 0 | 0 | 163 | 152 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 270 | 17 | 0 | 100 | 270 | 50 | 50 | 165 | 55 | 130 | 7 | 90 | 200 | 135 | 405 | 95 | 80 | 90 | 2 | 300 | 54 | 103 | 80 | 86 | 100 | 385 | 104 | 21 | 144 | 108 | 0 | 36 | 12 | 82 | 33 |  | 922 | 0 | 160 | 0 | 16 | 195 | 0 | 0 | 5 | 0 | 0 | 63 | 30 | 32 | 0 | 0 | 0 | 0 | 24 | 42 | 0 | 16 | 40 | 16 | 0 | 18 | 0 | 11 | 70 | 0 | 199 | 0 | 0 | 124 | 0 | 0 | 212 | 0 | 70 | 0 | 0 | 358 | 105 | 100 | 110 | 89 | 96 | 0 | 3 | 113 | 960 | 183 | 0 | 17 | 2 | 43 | 0 |  | 8668 | 4444 | 13112 | 3604 | 922 | 1947 | 425 | 3971 | 1229 | 56 | 407 | 546 | 126 | 91 | 0 | 0
17:00 | 0 | 0 | 227 | 0 | 270 | 89 | 0 | 396 | 238 |  | 0 | 300 | 130 | 95 | 75 | 55 | 0 | 0 | 0 | 97 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 45 | 0 | 25 | 30 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 17 | 51 | 0 | 90 | 87 | 29 | 19 | 38 | 0 | 0 | 0 | 280 | 0 | 210 | 8 | 71 | 27 | 51 | 0 | 51 | 0 | 47 | 43 | 19 | 8 | 33 | 19 | 126 | 102 | 0 | 14 | 0 | 0 | 40 | 0 | 0 | 163 | 155 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 270 | 17 | 0 | 20 | 270 | 20 | 25 | 165 | 25 | 134 | 2 | 90 | 200 | 142 | 406 | 114 | 90 | 105 | 1 | 300 | 54 | 104 | 80 | 113 | 100 | 395 | 104 | 8 | 144 | 108 | 0 | 36 | 3 | 82 | 33 |  | 923 | 0 | 160 | 0 | 16 | 198 | 0 | 0 | 22 | 20 | 0 | 63 | 29 | 32 | 0 | 0 | 0 | 0 | 25 | 42 | 0 | 16 | 40 | 16 | 32 | 18 | 0 | 11 | 72 | 0 | 199 | 0 | 0 | 122 | 0 | 0 | 212 | 0 | 20 | 0 | 0 | 349 | 105 | 30 | 113 | 88 | 107 | 0 | 2 | 113 | 960 | 161 | 0 | 17 | 0 | 20 | 0 |  | 8689 | 4353 | 13042 | 3684 | 923 | 1915 | 140 | 4097 | 1231 | 55 | 410 | 637 | 126 | 36 | 0 | 0
18:00 | 0 | 0 | 227 | 0 | 270 | 89 | 0 | 366 | 235 |  | 0 | 300 | 150 | 95 | 76 | 38 | 0 | 0 | 0 | 97 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 206 | 0 | 0 | 0 |  | 24 | 51 | 2 | 50 | 95 | 37 | 19 | 32 | 0 | 0 | 0 | 280 | 0 | 208 | 8 | 136 | 28 | 51 | 0 | 51 | 0 | 48 | 41 | 19 | 8 | 22 | 19 | 124 | 107 | 0 | 14 | 0 | 0 | 40 | 0 | 0 | 110 | 152 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 265 | 17 | 0 | 10 | 283 | 0 | 0 | 175 | 0 | 147 | 0 | 90 | 200 | 142 | 405 | 115 | 95 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 50 | 351 | 104 | 1 | 144 | 108 | 0 | 36 | 1 | 82 | 33 |  | 923 | 0 | 155 | 0 | 16 | 175 | 0 | 0 | 26 | 40 | 0 | 63 | 29 | 32 | 0 | 0 | 0 | 43 | 25 | 85 | 0 | 16 | 40 | 43 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 119 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 351 | 105 | 10 | 70 | 89 | 108 | 0 | 0 | 70 | 900 | 165 | 0 | 17 | 0 | 3 | 0 |  | 8488 | 4220 | 12708 | 3646 | 923 | 1878 | 20 | 4006 | 1172 | 56 | 335 | 703 | 124 | 5 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 230 | 0 | 270 | 93 | 0 | 355 | 242 |  | 0 | 300 | 140 | 87 | 76 | 42 | 0 | 0 | 0 | 97 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 24 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 24 | 51 | 51 | 90 | 96 | 37 | 19 | 32 | 0 | 0 | 0 | 280 | 0 | 214 | 8 | 137 | 28 | 52 | 0 | 51 | 0 | 48 | 41 | 19 | 8 | 33 | 19 | 128 | 107 | 0 | 14 | 0 | 0 | 40 | 0 | 0 | 163 | 157 | 50 | 84 | 0 | 220 | 0 | 11 | 10 | 275 | 17 | 11 | 30 | 288 | 220 | 80 | 176 | 96 | 149 | 0 | 90 | 200 | 143 | 391 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 110 | 61 | 378 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 922 | 0 | 155 | 0 | 16 | 200 | 0 | 0 | 27 | 72 | 0 | 63 | 37 | 32 | 0 | 0 | 0 | 43 | 24 | 89 | 0 | 50 | 40 | 43 | 37 | 22 | 0 | 11 | 73 | 0 | 200 | 16 | 0 | 120 | 0 | 0 | 180 | 0 | 10 | 0 | 0 | 350 | 105 | 12 | 90 | 88 | 109 | 0 | 0 | 100 | 970 | 190 | 0 | 17 | 0 | 0 | 108 |  | 9204 | 4621 | 13825 | 3682 | 922 | 2060 | 448 | 4262 | 1243 | 56 | 396 | 808 | 128 | 0 | 0 | 0
19:30 | 0 | 0 | 230 | 0 | 270 | 95 | 0 | 409 | 253 |  | 0 | 300 | 130 | 88 | 76 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 210 | 8 | 136 | 28 | 52 | 0 | 51 | 0 | 47 | 41 | 19 | 8 | 33 | 19 | 128 | 116 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 155 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 280 | 17 | 11 | 150 | 288 | 218 | 95 | 173 | 99 | 149 | 0 | 90 | 200 | 143 | 405 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 922 | 0 | 165 | 0 | 16 | 200 | 0 | 0 | 44 | 65 | 0 | 65 | 37 | 48 | 0 | 0 | 0 | 43 | 24 | 90 | 0 | 50 | 40 | 43 | 37 | 22 | 0 | 11 | 72 | 0 | 200 | 15 | 8 | 115 | 0 | 0 | 217 | 0 | 50 | 0 | 0 | 365 | 105 | 30 | 113 | 88 | 109 | 0 | 0 | 113 | 1100 | 200 | 0 | 17 | 0 | 0 | 115 |  | 9504 | 4954 | 14458 | 3783 | 922 | 2102 | 642 | 4375 | 1372 | 56 | 440 | 855 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 230 | 0 | 270 | 95 | 0 | 401 | 258 |  | 0 | 300 | 140 | 87 | 76 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 27 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 211 | 8 | 136 | 28 | 53 | 0 | 51 | 0 | 47 | 41 | 19 | 8 | 33 | 20 | 130 | 121 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 155 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 270 | 17 | 11 | 120 | 288 | 124 | 98 | 176 | 100 | 149 | 0 | 90 | 200 | 143 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 394 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 922 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 37 | 62 | 0 | 65 | 39 | 48 | 0 | 0 | 0 | 43 | 28 | 90 | 0 | 50 | 40 | 43 | 39 | 22 | 0 | 11 | 73 | 0 | 199 | 0 | 8 | 115 | 0 | 0 | 216 | 0 | 50 | 0 | 0 | 371 | 105 | 50 | 113 | 89 | 109 | 0 | 0 | 113 | 1080 | 210 | 0 | 17 | 0 | 0 | 115 |  | 9388 | 4958 | 14346 | 3781 | 922 | 2126 | 542 | 4378 | 1352 | 57 | 424 | 850 | 130 | 0 | 0 | 0
21:00 | 0 | 0 | 230 | 0 | 270 | 98 | 0 | 406 | 265 |  | 0 | 300 | 130 | 87 | 76 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 44 | 51 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 210 | 8 | 136 | 28 | 53 | 0 | 51 | 0 | 47 | 41 | 19 | 8 | 33 | 20 | 130 | 131 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 156 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 295 | 17 | 11 | 150 | 288 | 203 | 98 | 177 | 99 | 149 | 0 | 90 | 200 | 138 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 393 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 923 | 0 | 175 | 0 | 16 | 200 | 0 | 0 | 37 | 62 | 0 | 65 | 39 | 48 | 0 | 0 | 0 | 43 | 28 | 91 | 0 | 50 | 40 | 43 | 35 | 22 | 0 | 11 | 73 | 0 | 200 | 0 | 8 | 114 | 0 | 0 | 214 | 0 | 50 | 0 | 0 | 386 | 105 | 66 | 113 | 89 | 111 | 0 | 0 | 113 | 1100 | 217 | 0 | 17 | 0 | 0 | 115 |  | 9525 | 5019 | 14544 | 3799 | 923 | 2173 | 666 | 4377 | 1373 | 57 | 422 | 838 | 130 | 0 | 0 | 0
22:00 | 0 | 0 | 231 | 0 | 270 | 98 | 0 | 406 | 265 |  | 0 | 300 | 130 | 96 | 76 | 55 | 0 | 0 | 0 | 98 | 85 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 40 | 0 | 28 | 30 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 24 | 51 | 51 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 212 | 8 | 136 | 28 | 54 | 0 | 51 | 0 | 47 | 42 | 19 | 8 | 33 | 20 | 132 | 132 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 156 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 280 | 17 | 11 | 150 | 288 | 255 | 98 | 177 | 100 | 149 | 0 | 90 | 200 | 145 | 403 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 394 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 923 | 0 | 180 | 0 | 16 | 205 | 0 | 0 | 37 | 61 | 0 | 65 | 40 | 48 | 0 | 0 | 0 | 43 | 28 | 91 | 0 | 50 | 40 | 34 | 35 | 22 | 0 | 11 | 73 | 0 | 200 | 0 | 8 | 129 | 0 | 0 | 215 | 0 | 50 | 0 | 0 | 391 | 105 | 80 | 113 | 89 | 111 | 0 | 0 | 113 | 1120 | 217 | 0 | 17 | 0 | 0 | 115 |  | 9591 | 5075 | 14666 | 3827 | 923 | 2165 | 733 | 4377 | 1393 | 58 | 428 | 845 | 132 | 0 | 0 | 76.41
23:00 | 0 | 0 | 231 | 0 | 270 | 98 | 0 | 401 | 290 |  | 0 | 300 | 150 | 93 | 76 | 55 | 0 | 0 | 0 | 92 | 82 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 40 | 0 | 27 | 30 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 51 | 0 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 212 | 8 | 136 | 28 | 53 | 0 | 51 | 0 | 47 | 43 | 19 | 8 | 33 | 20 | 134 | 136 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 158 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 285 | 17 | 11 | 150 | 288 | 253 | 98 | 178 | 99 | 149 | 0 | 90 | 200 | 145 | 404 | 115 | 105 | 94 | 0 | 280 | 54 | 110 | 80 | 111 | 100 | 388 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 81 | 33 |  | 925 | 0 | 180 | 0 | 16 | 205 | 0 | 0 | 37 | 60 | 0 | 65 | 40 | 48 | 0 | 0 | 0 | 43 | 30 | 88 | 0 | 50 | 40 | 16 | 35 | 22 | 0 | 11 | 73 | 0 | 200 | 0 | 8 | 134 | 0 | 0 | 216 | 0 | 10 | 0 | 0 | 400 | 105 | 50 | 113 | 89 | 109 | 0 | 0 | 113 | 1120 | 215 | 0 | 17 | 0 | 0 | 115 |  | 9550 | 4998 | 14548 | 3839 | 925 | 2221 | 660 | 4313 | 1393 | 57 | 429 | 793 | 134 | 0 | 0 | 76.4
24:00 | 0 | 0 | 231 | 0 | 270 | 97 | 0 | 399 | 290 |  | 0 | 300 | 135 | 90 | 76 | 55 | 0 | 0 | 0 | 90 | 85 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 40 | 0 | 25 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 0 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 310 | 0 | 214 | 8 | 138 | 28 | 55 | 0 | 51 | 0 | 47 | 43 | 19 | 8 | 33 | 21 | 136 | 135 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 156 | 50 | 81 | 0 | 220 | 0 | 11 | 10 | 300 | 17 | 11 | 200 | 288 | 305 | 99 | 169 | 99 | 149 | 0 | 90 | 200 | 150 | 404 | 115 | 105 | 56 | 0 | 282 | 54 | 108 | 80 | 79 | 100 | 398 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 81 | 33 |  | 924 | 0 | 180 | 0 | 16 | 205 | 0 | 0 | 31 | 60 | 0 | 67 | 40 | 48 | 0 | 0 | 0 | 43 | 30 | 88 | 0 | 50 | 40 | 16 | 36 | 20 | 0 | 11 | 71 | 0 | 200 | 0 | 8 | 134 | 0 | 0 | 214 | 0 | 30 | 0 | 0 | 380 | 105 | 98 | 113 | 89 | 108 | 0 | 0 | 113 | 1100 | 219 | 0 | 17 | 0 | 0 | 0 |  | 9604 | 4904 | 14508 | 3869 | 924 | 2202 | 831 | 4121 | 1371 | 55 | 427 | 786 | 136 | 0 | 0 | 76.39
KWH | 0 | 0 | 5533000 | 0 | 6426236 | 2218454 | 0 | 9598980 | 6248000 |  | 0 | 6954000 | 3247113 | 2260800 | 1747656 | 1277615 | 0 | 0 | 0 | 1829760 | 2011968 | 3172800 | 0 | 0 | 0 | 0 | 1295280 | 1327212 | 1256166 | 392796 | 600000 | 586440 | 77680 | 799400 | 1025280 | 0 | 621731 | 728000 | 0 | 0 | 484801 | 2999301 | 0 | 0 | 0 |  | 333840 | 775120 | 232703 | 1711560 | 2203200 | 859200 | 447840 | 665840 | 0 | 0 | 0 | 7386200 | 0 | 5108000 | 351272 | 1915610 | 656424 | 1284480 | 0 | 1186174 | 0 | 766088 | 855154 | 389016 | 232380 | 755300 | 472200 | 2855040 | 2608320 | 0 | 307620 | 10950 | 0 | 957328 | 43200 | 44352 | 3675190 | 3737000 | 1201248 | 912000 | 0 | 5165740 | 0 | 52680 | 240660 | 7021511 | 304856 | 109912 | 1788096 | 6761998 | 2390280 | 1308574 | 4176000 | 1300062 | 3544130 | 133245 | 2076480 | 4256640 | 3041018 | 9469000 | 2626800 | 2323200 | 1693636 | 35279 | 7093200 | 1353474 | 2356026 | 1356600 | 1690920 | 2262720 | 9281300 | 2267520 | 289340 | 3206880 | 2458909 | 0 | 747720 | 210395 | 1934400 | 793080 |  | 22306181 | 0 | 4269312 | 0 | 364800 | 4153920 | 0 | 0 | 363360 | 606080 | 0 | 1511000 | 789477 | 725760 | 0 | 0 | 0 | 478480 | 403816 | 1104992 | 0 | 588528 | 415490 | 600480 | 420592 | 471600 | 0 | 247104 | 1686109 | 0 | 4880100 | 22000 | 38000 | 3336600 | 0 | 0 | 4694036 | 0 | 553920 | 0 | 0 | 9104654 | 2268480 | 893863 | 2624352 | 2146464 | 2302886 | 0 | 48140 | 2568096 | 25612100 | 5054564 | 0 | 606000 | 30540 | 697060 | 1027968 |  | 206782599 | 110016904 | 316799503 | 86883143 | 22306181 | 49565221 | 8234795 | 94324657 | 32178309 | 1349731 | 8907956 | 8739521 | 2855040 | 1454949 | 0
Fuel Cost | 0 | 0 | 8078180 | 0 | 7133121.96 | 2928359.28 | 0 | 9694969.8 | 6435440 |  | 0 | 7579860 | 3604295.43 | 17159472 | 12041349.84 | 10808622.9 | 0 | 0 | 0 | 13778092.8 | 18349148.16 | 31220352 | 0 | 0 | 0 | 0 | 9455544 | 10259348.76 | 12385796.76 | 294597 | 450000 | 0 | 0 | 0 | 9914457.6 | 0 | 167867.37 | 196560 | 0 | 0 | 4503801.29 | 3269238.09 | 0 | 0 | 0 |  | 0 | 7495410.4 | 2257219.1 | 16345398 | 19167840 | 6804864 | 564278.4 | 1977544.8 | 0 | 0 | 0 | 5465788 | 0 | 4699360 | 453140.88 | 2202951.5 | 741759.12 | 1798272 | 0 | 2028357.54 | 0 | 7737488.8 | 8166720.7 | 494050.32 | 174285 | 1321775 | 354150 | 21412800 | 2764819.2 | 0 | 390677.4 | 174543 | 0 | 1531724.8 | 76896 | 69189.12 | 4189716.6 | 3886480 | 2366458.56 | 1741920 | 0 | 8936730.2 | 0 | 61635.6 | 490946.4 | 7091726.11 | 228642 | 83533.12 | 30415512.96 | 51120704.88 | 40586954.4 | 21879357.28 | 21715200 | 21737036.64 | 34874239.2 | 1557634.05 | 16923312 | 46184544 | 21439176.9 | 8806170 | 23956416 | 21954240 | 14751569.56 | 0 | 53624592 | 11788758.54 | 20709468.54 | 13538868 | 14491184.4 | 15069715.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128483602.56 | 0 | 4482777.6 | 0 | 2867328 | 57573331.2 | 0 | 0 | 3811646.4 | 6351718.4 | 0 | 1707430 | 1223689.35 | 7083417.6 | 0 | 0 | 0 | 4708243.2 | 4102770.56 | 9779179.2 | 0 | 7956898.56 | 4026098.1 | 5818651.2 | 4079742.4 | 905472 | 0 | 187057.728 | 10167237.27 | 0 | 26450142 | 762300 | 1084140 | 3903822 | 0 | 0 | 69096209.92 | 0 | 9422179.2 | 0 | 0 | 9013607.46 | 23682931.2 | 15204609.63 | 24905100.48 | 20262620.16 | 17870395.36 | 0 | 531947 | 18978229.44 | 112437119 | 0 | 0 | 0 | 0 | 0 | 0 |  | 852582221.26 | 618921644.178 | 1471503865.438 | 84214826.798 | 128483602.56 | 51670068.57 | 139245650.11 | 680708018.03 | 149054498.27 | 364427.37 | 128515981.12 | 85569868.56 | 21412800 | 2264124.05 | 0
Yesterday Day Peak | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 399 | 252 |  | 0 | 300 | 140 | 94 | 75 | 40 | 0 | 0 | 0 | 84 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 18 | 33 | 33 | 48 | 0 | 26 | 30 | 0 | 0 | 25 | 33 | 0 | 0 | 0 |  | 0 | 28 | 0 | 90 | 87 | 37 | 19 | 12 | 0 | 0 | 0 | 325 | 0 | 211 | 45 | 30 | 28 | 53 | 0 | 51 | 0 | 5 | 34 | 0 | 8 | 33 | 20 | 120 | 74 | 0 | 17 | 2 | 0 | 40 | 0 | 0 | 163 | 155 | 55 | 10 | 0 | 219 | 0 | 0 | 9 | 300 | 17 | 0 | 100 | 263 | 116 | 94 | 174 | 95 | 144 | 19 | 76 | 200 | 137 | 404 | 115 | 90 | 51 | 5 | 300 | 54 | 82 | 80 | 68 | 90 | 390 | 92 | 49 | 126 | 108 | 0 | 17 | 0 | 82 | 33 |  | 922 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 27 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 16 | 10 | 16 | 0 | 19 | 0 | 11 | 71 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 176 | 0 | 1 | 0 | 0 | 402 | 93 | 0 | 113 | 89 | 101 | 0 | 6 | 113 | 930 | 209 | 0 | 17 | 4 | 92 | 52 |  | 12764 | DayPeak
Yesterday Evening Peak | 0 | 0 | 230 | 0 | 270 | 98 | 0 | 406 | 265 | 0 | 0 | 300 | 130 | 87 | 76 | 55 | 0 | 0 | 0 | 98 | 84 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 49 | 0 | 27 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 44 | 51 | 90 | 96 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 0 | 210 | 8 | 136 | 28 | 53 | 0 | 51 | 0 | 47 | 41 | 19 | 8 | 33 | 20 | 130 | 131 | 0 | 17 | 0 | 0 | 40 | 0 | 0 | 163 | 156 | 50 | 84 | 0 | 220 | 0 | 10 | 10 | 295 | 17 | 11 | 150 | 288 | 203 | 98 | 177 | 99 | 149 | 0 | 90 | 200 | 138 | 404 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 393 | 104 | 0 | 144 | 108 | 0 | 36 | 0 | 82 | 33 |  | 923 | 0 | 175 | 0 | 16 | 200 | 0 | 0 | 37 | 62 | 0 | 65 | 39 | 48 | 0 | 0 | 0 | 43 | 28 | 91 | 0 | 50 | 40 | 43 | 35 | 22 | 0 | 11 | 73 | 0 | 200 | 0 | 8 | 114 | 0 | 0 | 214 | 0 | 50 | 0 | 0 | 386 | 105 | 66 | 113 | 89 | 111 | 0 | 0 | 113 | 1100 | 217 | 0 | 17 | 0 | 0 | 115 |  | 14544 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 270 | 94 | 0 | 400 | 350 | 0 | 0 | 320 | 150 | 97 | 76 | 55 | 0 | 0 | 0 | 96 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 90 | 96 | 37 | 19 | 30 | 0 | 0 | 0 | 350 | 0 | 225 | 8 | 136 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 8 | 33 | 21 | 166 | 100 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 0 | 0 | 10 | 310 | 17 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 |  | 82 | 55 |  | 943 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 37 | 60 | 32 | 65 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 90 | 0 | 43 | 40 | 43 | 38 | 22 | 0 | 11 | 70 | 0 | 200 | 17 | 10 | 120 | 0 | 0 | 220 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 1120 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 230 | 0 | 270 | 94 | 0 | 400 | 350 | 0 | 0 | 320 | 150 | 97 | 76 | 55 | 0 | 0 | 0 | 96 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 90 | 96 | 37 | 17 | 40 | 0 | 0 | 0 | 330 | 0 | 225 | 8 | 136 | 28 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 8 | 33 | 21 | 143 | 100 | 0 | 17 | 1.6 | 0 | 41 | 0 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 0 | 0 | 10 | 310 | 17 | 11 | 200 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 80 | 57 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 36 | 30 | 82 | 55 |  | 943 | 0 | 170 | 0 | 16 | 170 | 0 | 0 | 37 | 0 | 32 | 65 | 33 | 50 | 0 | 0 | 0 | 36 | 30 | 90 | 0 | 43 | 30 | 43 | 30 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 1080 | 220 |  | 150 | 6 | 100 | 30
Generation at 08:00(Today) | 0 | 0 | 232 | 0 | 270 | 94 | 0 | 397 | 332 | 0 | 0 | 310 | 130 | 54 | 76 | 15 | 0 | 0 | 0 | 0 | 24 | 80 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 27 | 33 | 33 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 90 | 37 | 17 | 40 | 0 | 0 | 0 | 260 | 0 | 216 | 8 | 137 | 28 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 20 | 112 | 106 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 130 | 158 | 60 | 10 | 0 | 218 | 0 | 0 | 10 | 270 | 17 | 0 | 0 | 95 | 0 | 0 | 140 | 0 | 70 | 10 | 90 | 17 | 30 | 402 | 115 | 105 | 51 | 2 | 300 | 54 | 68 | 80 | 57 | 20 | 400 | 58 | 19 | 108 | 51 | 0 | 36 | 14 | 81 | 0 | 0 | 925 | 0 | 175 | 0 | 8 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 129 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 388 | 17 | 0 | 50 | 50 | 54 | 0 | 1 | 50 | 920 | 218 | 0 | 17 | 1 | 32 | 0 | 0 |  |  |  |  | 120206929 |  | 0
120206929
| Minimum Generation |  | 11088 | 7:00
| Highest Generation |  | 14666 | 22:00
| Day Peak Generation |  | 12764 | 12:00
| Evening Peak Generation |  | 14544 | 21:00
| HVDC Max Flow |  | 925 | 23:00
| HVDC EvPeak Flow |  | 923 | 21:00
| Load factor L.F |  | 90%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-04-29
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12764 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10975 | MW
Evening Peak Generation : |  | 14544 | MW Hour : | 21:00 | Available Max Generation : |  | 15495 | MW
E.P. Demand (at gen end) : |  | 14544 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13700 | MW
Maximum Generation : |  | 14666 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1795 | MW
Total Gen. (MKWH) : |  | 316.7995 | System Load Factor : | 90% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 66 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-04-29
Actual : | 76.33 | Ft.(MSL) , | Rule curve : | 82.4 | Ft.( MSL )
Gas Consumed : | Total = | 1026.06 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 135884895.368
: |  | Coal : | 149054498.27 | Oil : | 1034039517.82 | Total : | 1318978911.458
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4898.6116 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1586.5837 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1549.4029 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1387.038 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1265.1219 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1038.7177 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 508.0729 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 313.3834 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 762.7624 |  |  | 0 | 0%
Total | 0 |  | 13309.6945 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensingh-Jamalpur 132 kV Ckt-1 was under shut down from 09:07 to 18:04 for C/M.
b) Sherpur 132/33 kV T-1 transformer was under shut down from 09:32 to 11:16 for C/M.
c) Nawabganj 132/33 kV T-2 transformer was under shut down from 12:42 to 14:55 for R/H maintenance.
d) Narail 132/33 kV T-1 transformer was under shut down from 08:15 to 10:09 for C/M.
e) Jhenaidah 132 kV Bus-Coupler Breaker was under shut down from 08:24 to 13:32 for C/M.
f) Sikalbaha 225 MW STG was synchronized at 13:37.
g) Bheramara GK 132/33 kV T-2 transformer was under shut down from 14:11 to 14:55 for C/M.
h) Kachua 132 kV Bus-2 tripped at 16:45 showing protection Lock out,CB close block relay and was
switched on at 17:31.
i) Daudkandi 132/33 kV T-1 transformer was under shut down from 07:16(29/4/2022) to 09:21 for C/M.
j) Bottail 132/33 kV T-2 transformer along with 33 kV Bus were under shut down from 07:00(29/4/2022) to | [5 empty] | About 48 MW power interruption occurred under
10:01 for C/M. | [5 empty] | Bottail S/S area from 07:00(29/4/2022) to 10:01.
k) Narail 132/33 kV T-2 transformer was under shut down from 07:12(29/4/2022) to 09:39 for C/M. | [5 empty] | About 15 MW power interruption occurred under
Narail S/S area from 07:12(29/4/2022) to 09:39.
l) Faridpur 132/33 kV T-2 transformer was under shut down from 07:47(29/4/2022) to 09:49 for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 230 | 5533000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6426236 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2218454 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 406 | 9598980
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 265 | 6248000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 6954000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 87 | 2260800 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3247113 | GT-1 Under S/D & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 76 | 1747656 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1277615
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 392796
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1829760
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 2011968 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1295280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 3172800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1327212
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1256166
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1186440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 77680
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 799400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1025280 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 288 | 6761998 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 203 | 2390280
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 98 | 1308574
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 1300062
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3544130
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2323200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2267520
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3206880 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 210395
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 33 | 793080 | 33 kV feeder problem.
| Dhaka area Total |  |  |  | 5998 | 3816 | 83992755
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 484801
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 133245
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 859200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 57 | 1349731 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 2999301 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1693636
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 44 | 775120 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 232703 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1711560 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2076480 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 447840
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 665840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 2203200 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35279
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 7093200
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1353474
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2356026
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2262720
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2458909 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1529 | 31192265
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 5108000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7386200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 28 | 656424 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1284480
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 351272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1186174
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 3041018 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 766088 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 1915610 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4256640
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 389016
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 232380
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2855040
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 755300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 41 | 855154 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 472200 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 1788096
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1356600 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1690920
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 747720 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 82 | 1934400 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1863 | 39028732
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 2608320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 307620
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 177 | 4176000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 2626800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 289340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 333840
| Mymensingh Area Total |  |  |  | 622 | 464 | 10352870
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 957328 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3675190
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 156 | 3737000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 43200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 44352 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 109912
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1201248 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 912000
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5165740
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 10 | 52680 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 304856
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7021511 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9469000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240660
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 393 | 9281300
| Sylhet Area Total |  |  |  | 2477 | 1853 | 42215977
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22306181
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 364800 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 363360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 4153920
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 62 | 606080 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 4269312 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 553920
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2268480
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 2146464 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 697060
| Khulna Area Total |  |  |  | 2384 | 1657 | 37729577
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 725760 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 39 | 789477
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1511000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 25612100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 217 | 5054564
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 606000 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1486 | 34298901
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 478480 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 403816 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 588528
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 415490 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 114 | 3336600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 214 | 4694036
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 386 | 9104654 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 420592 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 471600
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 247104
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 600480
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 1104992 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 66 | 893863
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2624352
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2568096
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30540
| Rajshahi Area Total |  |  |  | 2179 | 1369 | 27983223
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1686109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4880100
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 22000 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 38000 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 2302886
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48140
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1027968
| Rangpur Area Total |  |  |  | 720 | 507 | 10005203
| Total |  |  |  | 21734 | 14544 | 316799503
| Eastern Grid Total |  |  |  | 14493 | 9525 | 206782599
| Western Grid Total |  |  |  | 7241 | 5019 | 110016904
| National Grid Total |  |  |  | 21734 | 14544 | 316799503
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-28
(a) ENTIRE EASTERN GRID : |  | 9338.96 | MW | (b) ENTIRE WESTERN GRID : |  | 4784.4 | MW
i) Dhaka area |  | 4867.26 | MW | i) Khulna area |  | 1897 | MW
ii) Chittagong area |  | 1381.7 | MW | ii) Rajshahi area |  | 1591.4 | MW
iii) Comilla area |  | 1404 | MW | iii) Barisal area |  | 451 | MW
iv) Mymensingh area |  | 1096 | MW | iv) Rangpur area |  | 845 | MW
v) Sylhet area |  | 590 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 14123.36 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 13:00 | Hasnabad | 76 | 00:00 | Palashbari | 126 | 22:00
Agargaon | 114 | 14:00 | Hathazari | 105 | 19:00 | Panchagarh | 60 | 19:30
Agrabad | 92 | 15:00 | Ishurdi | 81 | 21:00 | Patuakhali | 146 | 22:00
AKS | 9 | 06:00 | Jaldhaka | 60 | 19:00 | PHP | 8 | 11:00
AKSML | 150 | 06:00 | Jamalpur | 179 | 19:30 | Purbachal | 20 | 00:00
Amnura | 64 | 00:00 | Jashore | 140 | 21:00 | Purbasadipur | 112 | 20:00
Ashuganj | 46 | 06:00 | Jhenaidah | 140 | 21:00 | Rahim | 28 | 11:00
Bagerhat | 114 | 21:00 | Joydebpur | 210 | 13:00 | Rajbari | 78 | 22:00
Bakulia | 131 | 16:00 | Joypurhat | 59 | 21:00 | Rajendrapur | 111 | 20:00
Banani | 51 | 13:00 | Juldah | 29 | 08:00 | Rajshahi | 192 | 00:00
Bangabhaban | 24 | 10:00 | Kabirpur | 301 | 12:00 | Rajshahi | 36 | 03:00
Barapukuria | 56 | 20:00 | Kachua | 88 | 22:00 | Ramganj | 124 | 22:00
Barguna | 22 | 22:00 | Kallyanpur | 120 | 19:00 | Rampur | 18 | 18:30
Barishal | 110 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 14 | 19:00
Barishal | 68 | 00:00 | Kamrangirchar | 71 | 12:00 | Rangpur | 131 | 19:00
Baroaulia | 82 | 00:00 | Kaptai | 5 | 18:30 | Ruppur | 4.8 | 10:00
Baroirhat | 49 | 22:00 | Kazla | 88 | 05:00 | Saidpur | 98 | 19:30
Bashundhara | 188 | 19:00 | Keranigonj | 84 | 21:00 | Satkhira | 136 | 22:00
BashundharaCement | 13 | 00:00 | Khagrachori | 28 | 18:30 | Satmasjid | 106 | 15:00
Beanibazar | 83 | 22:00 | Khulna | 102 | 19:00 | Savar | 185 | 15:00
Benapole | 64 | 21:00 | Khulshi | 196 | 15:00 | Shahjadpur | 131 | 21:00
Bhaluka | 138 | 00:00 | Kishoreganj | 150 | 00:00 | Shahjibazar | 149 | 22:00
Bhandaria | 64 | 22:00 | Kodda | 320 | 12:00 | Shahmirpur | 40 | 04:00
Bhangura | 41 | 03:00 | KSRM | 32 | 07:00 | Shariatpur | 84 | 22:00
Bheramara(GK) | 69 | 23:00 | Kulaura | 54 | 19:00 | Sherpur | 124 | 23:00
Bhulta | 245 | 00:00 | Kurigram | 56 | 19:30 | Shikalbaha | 35 | 20:00
Bog-Sherpur | 66 | 19:30 | Kushtia | 150 | 00:00 | Shitalakhya | 138 | 15:00
Bogura | 174 | 22:00 | Lalbag | 78 | 12:00 | Sholosohor | N/A | N/A
Borhanuddin | 48 | 21:00 | Lalmonirhat | 43 | 19:00 | Shyampur | 184 | 11:00
Brahmanbaria | 170 | 01:00 | Madanganj | 162 | 23:00 | Siddhirganj | 116 | 12:00
BSRM | 156 | 02:00 | Madaripur | 125 | 21:00 | Sirajganj | 125 | 21:00
Cantonment | 148 | 13:00 | Madartek | 91 | 23:00 | Sonargaon | 93 | 19:30
Chandpur | 85 | 23:00 | Madunaghat | 65 | 19:00 | Sreemongol | 61 | 00:00
Chandraghona | 34 | 19:00 | Magura | 69 | 19:30 | Srinagar | 49.66 | 21:00
Chapai | 77 | 03:00 | Mahasthangarh | 76 | 22:00 | SSM | 8 | 00:00
Charsaidpur | 30 | 00:00 | Manikganj | 102 | 22:00 | Sunamganj | 50 | 22:00
Chauddagram | 71 | 22:00 | Maniknagar | 82 | 15:00 | Sylhet | 144 | 18:30
Chhatak | 26 | 22:00 | Matarbari | 43 | 20:00 | Tangail | 237 | 22:00
Chowmuhani | 218 | 00:00 | Matuail | 70 | 11:00 | Thakurgaon | 94 | 21:00
Chuadanga | 119 | 03:00 | Millgate | 52 | 12:00 | TK | 32 | 22:00
Coxsbazar | 124 | 21:00 | Mirpur | 137 | 19:30 | Tongi | 142 | 15:00
Cumilla(N) | 163 | 23:00 | Mirsorai | N/A | N/A | Ullon | 39 | 23:00
Cumilla(S) | 174 | 23:00 | Mithapukur | 39 | 03:00 | Uttara | 102 | 19:00
Daudkandi | 156 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 18 | 00:00
Dhaka | 37 | 13:00 | Mogbazar | 129 | 15:00 | Zigatola | 47 | 22:00
Dhamrai | 122 | 00:00 | Mongla | 42 | 00:00
Dhanmondi | 206 | 13:00 | Motijheel | 39 | 13:00
Dohazari | 104 | 22:00 | Munshiganj | 112 | 21:00
Faridpur | 167 | 23:00 | Mymensingh | 246 | 03:00
Fatullah | 67 | 00:00 | Naogaon | 132 | 21:00
Fenchuganj | 49 | 21:00 | Narail | 64 | 22:00
Feni | 150 | 22:00 | Narinda | 77 | 13:00
Ghorashal | 50 | 23:00 | Narshingdi | 195 | 00:00
Goalpara | 30 | 00:00 | Natore | 151 | 21:00
Gollamari | 56 | 19:00 | Nawabganj | 62.6 | 21:00
Gopalganj | 113 | 22:00 | Netrakona | 116 | 19:00
GPH | 89 | 00:00 | New | 80.3 | 10:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 5:00 | 399 | 12:00 | Kaliakoir | 388 | 0.41667 | 376 | 0.45833
| Bheramara | 401 | 8:00 | 380 | 22:00 | Bhulta | 394 | 0.083333 | 382 | 0.375
| Ashuganj(N) | 399 | 3:00 | 387 | 11:00 | Gopalganj | 418 | 0.625 | 397 | 0.95833
| Payra | 419 | 6:00 | 408 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 15:00 | Hathazari | 237 | 17:00 | 231 | 1:00
| Ishurdi | 232 | 5:00 | 225 | 23:00 | Megnaghat | 229 | 2:00 | 225 | 17:00
| Ashuganj | 237 | 3:00 | 233 | 11:00 | Fenchuganj | 240 | 2:00 | 236 | 9:00
| Serajganj | 234 | 5:00 | 229 | 22:00 | Siddhirganj | 226 | 6:00 | 219 | 10:00
| Baghabari | 232 | 4:00 | 225 | 15:00 | Maniknagar | 224 | 6:00 | 216 | 11:00
| Barapukuria | 229 | 5:00 | 217 | 24:00 | Agargaon | 225 | 10:00 | 215 | 11:00
| Bogra | 230 | 5:00 | 220 | 15:00 | Barisal | 240 | 10:00 | 232 | 22:00
| Rajshahi | 231 | 18:30 | 220 | 22:00 | Bhola 225 MW | 245 | 8:00 | 232 | 22:00
| Khulna South | 230 | 8:00 | 219 | 23:00 | AKSML
| Rampura | 225 | 5:00 | 217 | 11:00 | BSRM | 235 | 5:00 | 228 | 9:00
| Haripur | 224 | 19:00 | 217 | 11:00 | Bibiyana | 239 | 18:30 | 233 | 6:00
| Hasnabad | 224 | 24:00 | 215 | 11:00 | Bhulta | 227 | 3:00 | 220 | 9:00
| Shyampur | 225 | 3:00 | 22 | 21:00 | Ashuganj (S) | 236 | 5:00 | 228 | 9:00
| Aminbazar | 225 | 1:00 | 218 | 2:00 | Kaliakoir | 226 | 5:00 | 217 | 11:00
| Tongi | 225 | 4:00 | 217 | 9:00 | GPH | 236 | 18:30 | 229 | 9:00
| Comilla (N) | 230 | 19:00 | 224 | 9:00 | Jhenaidah | 225 | 8:00 | 213 | 23:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 02:00 | 127 | 11:00 | Manikganj | 132 | 05:00 | 124 | 11:00
| Agargaon | 134 | 03:00 | 126 | 11:00 | Maniknagar | 133 | 03:00 | 127 | 11:00
| Agrabad | 135 | 10:00 | 130 | 00:00 | Matarbari | 122 | 09:00 | 111 | 00:00
| AKS | 135 | 03:00 | 128 | 01:00 | Matuail | 134.2 | 19:00 | 129.4 | 09:00
| Aminbazar | 136 | 01:00 | 131 | 10:00 | Millgate | 135 | 03:00 | 127 | 09:00
| Amnura | 132 | 18:00 | 124 | 14:00 | Mirpur | 136 | 03:00 | 129 | 11:00
| Ashuganj | 135 | 06:00 | 130 | 15:00 | Mithapukur | 134 | 05:00 | 123 | 12:00
| Bagerhat | 135 | 10:00 | 124 | 23:00 | Modern | 135 | 17:00 | 130 | 00:00
| Bakulia | 135 | 17:00 | 129 | 00:00 | Mogbazar | 136 | 05:00 | 128 | 11:00
| Banani | 135 | 06:00 | 126 | 12:00 | Mongla | 135 | 10:00 | 125 | 23:00
| Bangabhaban | 133 | 04:00 | 127 | 11:00 | Motijheel | 133 | 04:00 | 127 | 11:00
| Barapukuria | 132 | 05:00 | 125 | 15:00 | Munshiganj | 137 | 18:30 | 131 | 11:00
| Barguna | 135 | 18:00 | 128 | 00:00 | Mymensingh | 131 | 08:00 | 114 | 21:00
| Barishal | 139 | 10:00 | 126 | 00:00 | Naogaon | 132 | 04:00 | 121 | 23:00
| Barishal | 140 | 09:00 | 132 | 22:00 | Narail | 134 | 08:00 | 123 | 23:00
| Baroaulia | 138 | 17:00 | 130 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 133 | 16:00 | 124 | 00:00 | Narshingdi | 130 | 18:00 | 122 | 00:00
| Bashundhara | 135 | 05:00 | 127 | 10:00 | Natore | 133 | 08:00 | 127 | 22:00
| BashundharaCement | 137 | 19:00 | 130 | 11:00 | Nawabganj | 133 | 01:00 | 126 | 11:00
| Beanibazar | 132 | 03:00 | 124 | 21:00 | Netrakona | 126 | 05:00 | 110 | 18:00
| Benapole | 134 | 08:00 | 125 | 23:00 | New | 136 | 05:00 | 127 | 11:00
| Bhaluka | 128 | 06:00 | 110 | 16:00 | Niamatpur | 130 | 04:00 | 116 | 23:00
| Bhandaria | 137 | 08:00 | 125 | 21:00 | Noapara | 136 | 08:00 | 128 | 23:00
| Bhangura | 136 | 04:00 | 130 | 23:00 | Pabna | 133 | 06:00 | 127 | 23:00
| Bheramara | 134 | 04:00 | 130 | 23:00 | Palashbari | 134 | 05:00 | 121 | 23:00
| Bheramara(GK) | 137 | 18:00 | 133 | 21:00 | Panchagarh | 129 | 03:00 | 110 | 17:00
| Bhulta | 126 | 04:00 | 120 | 14:00 | Patuakhali | 136 | 05:00 | 131 | 00:00
| Bog-Sherpur | 137 | 05:00 | 128 | 21:00 | PHP | 132 | 10:00 | 123 | 00:00
| Bogura | 139 | 05:00 | 130 | 15:00 | Purbachal | 135 | 05:00 | 126 | 11:00
| Bogura | 139 | 05:00 | 130 | 15:00 | Purbasadipur | 129 | 05:00 | 114 | 16:00
| Brahmanbaria | 130 | 07:00 | 124 | 15:00 | Rahim | 134 | 19:00 | 130 | 09:00
| Cantonment | 133 | 05:00 | 125 | 10:00 | Rajbari | 133 | 08:00 | 125 | 23:00
| Chandpur | 137 | 10:00 | 132 | 00:00 | Rajendrapur | 132 | 06:00 | 125 | 14:00
| Chandraghona | 137 | 17:00 | 133 | 00:00 | Rajshahi | 130 | 02:00 | 126 | 13:00
| Chapai | 132 | 18:00 | 126 | 06:00 | Rajshahi | 132 | 18:30 | 126 | 22:00
| Charsaidpur | 137 | 03:00 | 131 | 11:00 | Ramganj | 135 | 10:00 | 122 | 00:00
| Chauddagram | 132 | 10:00 | 125 | 00:00 | Rampur | 135 | 04:00 | 130 | 00:00
| Chhatak | 134 | 06:00 | 126 | 21:00 | Rampura | 134 | 05:00 | 127 | 11:00
| Chowmuhani | 131 | 18:30 | 121 | 00:00 | Rangamati | 136 | 17:00 | 132 | 00:00
| Chuadanga | 130 | 08:00 | 118 | 23:00 | Rangpur | 131 | 06:00 | 121 | 15:00
| Coxsbazar | 120 | 08:00 | 108 | 00:00 | Ruppur | 135 | 10:00 | 130 | 22:00
| Cumilla(N) | 134 | 12:00 | 130 | 07:00 | Saidpur | 132 | 06:00 | 116 | 15:00
| Cumilla(S) | 134 | 10:00 | 125 | 18:30 | Satkhira | 134 | 08:00 | 123 | 23:00
| Daudkandi | 136 | 13:00 | 126 | 07:00 | Satmasjid | 134 | 18:30 | 126 | 11:00
| Dhaka | 135 | 05:00 | 128 | 11:00 | Savar | 137 | 01:00 | 130 | 16:00
| Dhamrai | 134 | 04:00 | 129 | 09:00 | Shahjadpur | 137 | 04:00 | 133 | 22:00
| Dhanmondi | 134 | 02:00 | 128 | 11:00 | Shahjibazar | 133 | 07:00 | 127 | 21:00
| Dohazari | 130 | 10:00 | 121 | 00:00 | Shahmirpur | 135 | 04:00 | 131 | 09:00
| Faridpur | 133 | 08:00 | 126 | 19:30 | Shariatpur | 137 | 08:00 | 128 | 23:00
| Fatullah | 135 | 22:00 | 128 | 11:00 | Sherpur | 136 | 06:00 | 117 | 21:00
| Fenchuganj | 136 | 06:00 | 131 | 15:00 | Shikalbaha | 136 | 17:00 | 131 | 00:00
| Feni | 134 | 10:00 | 125 | 00:00 | Shikalbaha | 135 | 18:00 | 131 | 00:00
| Ghorashal | 138 | 01:00 | 135 | 11:00 | Shitalakhya | 137 | 18:30 | 131 | 11:00
| Goalpara | 137 | 08:00 | 131 | 23:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 136 | 07:00 | 130 | 23:00 | Shyampur | 134 | 19:00 | 127 | 11:00
| Gopalganj | 139 | 08:00 | 131 | 23:00 | Shyampur | 135 | 03:00 | 126 | 12:00
| Gopalganj_I | 140 | 10:00 | 130 | 23:00 | Siddhirganj | 134 | 21:00 | 129 | 11:00
| Gulshan | 134 | 05:00 | 126 | 11:00 | Sirajganj | 135 | 00:00 | 127 | 21:00
| Halishahar | 135 | 17:00 | 130 | 00:00 | Sonargaon | 135 | 00:00 | 130 | 09:00
| Haripur | 134 | 19:00 | 130 | 09:00 | Sreemongol | 134 | 08:00 | 130 | 14:00
| HaripurSBU | 135 | 18:30 | 129 | 10:00 | Srinagar | 133 | 02:00 | 128 | 11:00
| Hasnabad | 136 | 19:00 | 130 | 12:00 | SSM | 140 | 20:00 | 131 | 00:00
| Hathazari | 138 | 17:00 | 134 | 01:00 | Sunamganj | 131 | 05:00 | 124 | 21:00
| Ishurdi | 135 | 06:00 | 130 | 23:00 | Sylhet | 133 | 03:00 | 129 | 21:00
| Jaldhaka | 130 | 06:00 | 115 | 15:00 | Tangail | 134 | 05:00 | 122 | 22:00
| Jamalpur | 138 | 10:00 | 121 | 18:30 | Thakurgaon | 129 | 23:00 | 110 | 15:00
| Jashore | 135 | 08:00 | 126 | 23:00 | TK | 136 | 18:30 | 130 | 14:00
| Jhenaidah | 136 | 08:00 | 127 | 23:00 | Tongi | 136 | 04:00 | 130 | 09:00
| Jhenaidah | 137 | 06:00 | 128 | 23:00 | Ullon | 134 | 02:00 | 127 | 11:00
| Joydebpur | 139 | 03:00 | 134 | 08:00 | Uttara | 134 | 02:00 | 129 | 11:00
| Joypurhat | 132 | 02:00 | 120 | 21:00 | UttaraNew | 135 | 03:00 | 129 | 11:00
| Juldah | 136 | 17:00 | 129 | 07:00 | Zigatola | 133 | 02:00 | 127 | 11:00
| Kabirpur | 131 | 00:00 | 124 | 15:00
| Kachua | 136 | 10:00 | 127 | 06:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 136 | 03:00 | 130 | 16:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 133 | 19:00 | 127 | 09:00
| Kaptai | 135 | 00:00 | 132 | 01:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 114 | 9604 | 4904 | 14508 |  |  |  | QF-LDC-11
0:30 | 265 | 9285.5 | 4851 | 14136.5 | Date: | 2022-04-28
1:00 | 416 | 8967 | 4798 | 13765
1:30 | 415 | 8906 | 4788.5 | 13694.5
2:00 | 414 | 8845 | 4779 | 13624
2:30 | 395 | 8762 | 4781.5 | 13543.5 | [5 empty] | Gen. at Eve. Peak | 14544 | 14544 MW (21:00 )
3:00 | 376 | 8679 | 4784 | 13463 | [6 empty] | 21:00
3:30 | 369 | 8537.5 | 4637.5 | 13175 | [5 empty] | Gen. at Day Peak | 12764 | 12764 MW (12:00 )
4:00 | 362 | 8396 | 4491 | 12887 | [6 empty] | 12:00
4:30 | 333 | 8309 | 4283 | 12592 | [5 empty] | Highest Generation | 14666
5:00 | 304 | 8222 | 4075 | 12297 | [6 empty] | 22:00
5:30 | 345 | 7873 | 3891 | 11764
6:00 | 386 | 7524 | 3707 | 11231
6:30 | 450 | 7408 | 3751.5 | 11159.5
7:00 | 514 | 7292 | 3796 | 11088
7:30 | 586 | 7342 | 3813.5 | 11155.5
8:00 | 658 | 7392 | 3831 | 11223
8:30 | 725 | 7478 | 3899.5 | 11377.5
9:00 | 792 | 7564 | 3968 | 11532
9:30 | 797 | 7766.5 | 4064 | 11830.5
10:00 | 802 | 7969 | 4160 | 12129
10:30 | 769 | 8003 | 4158.5 | 12161.5
11:00 | 736 | 8037 | 4157 | 12194
11:30 | 652 | 8316 | 4163 | 12479
12:00 | 568 | 8595 | 4169 | 12764
12:30 | 515 | 8647 | 4232 | 12879
13:00 | 462 | 8699 | 4295 | 12994
13:30 | 487 | 8839 | 4342.5 | 13181.5
14:00 | 512 | 8979 | 4390 | 13369
14:30 | 498 | 8949 | 4481 | 13430
15:00 | 484 | 8919 | 4572 | 13491
15:30 | 487 | 8793.5 | 4508 | 13301.5
16:00 | 490 | 8668 | 4444 | 13112
16:30 | 443 | 8678.5 | 4398.5 | 13077
17:00 | 396 | 8689 | 4353 | 13042
17:30 | 359 | 8588.5 | 4286.5 | 12875
18:00 | 322 | 8488 | 4220 | 12708
18:30 | 213 | 8846 | 4420.5 | 13266.5
19:00 | 104 | 9204 | 4621 | 13825
19:30 | 168 | 9504 | 4954 | 14458
20:00 | 102 | 9388 | 4958 | 14346 |  |  |  | Executive Engineer
20:30 | 84 | 9456.5 | 4988.5 | 14445 |  |  |  | Network Operation Division
21:00 | 66 | 9525 | 5019 | 14544
21:30 | 85 | 9558 | 5047 | 14605
22:00 | 104 | 9591 | 5075 | 14666 |  |  |  |  | Page 6 of 7
22:30 | 116 | 9570.5 | 5036.5 | 14607
23:00 | 128 | 9550 | 4998 | 14548
23:30 | 121 | 9577 | 4951 | 14528
24:00 | 114 | 9604 | 4904 | 14508
14544 MW (21:00 )
12764 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-28 |  | Energy |  | 316799503
[13 empty] | 2022-04-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3869 | 924 | 2202 | 831 | 4121 | 1371 | 55 | 427 | 786 | 136 | 0 | 0
0:30 | 3774 | 922.5 | 2176 | 667.5 | 4075 | 1341.5 | 55.5 | 426.5 | 783 | 132 | 0 | 0 | Date: | 2022-04-28
1:00 | 3679 | 921 | 2150 | 504 | 4029 | 1312 | 56 | 426 | 780 | 128 | 0 | 0
1:30 | 3689.5 | 921 | 2141.5 | 468.5 | 4007 | 1307 | 56 | 425.5 | 781 | 117 | 0 | 0 | [8 empty] | Total Energy | 316.7995 | Total Energy Gen 316.800 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 316.800 MKWHr
2:00 | 3700 | 921 | 2133 | 433 | 3985 | 1302 | 56 | 425 | 782 | 106 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3700 | 920.5 | 2145 | 322 | 4004 | 1302 | 56 | 425 | 782 | 106 | 0 | 0 | [8 empty] | Energy Requirement | 316.7995
3:00 | 3700 | 920 | 2157 | 211 | 4023 | 1302 | 56 | 425 | 782 | 106 | 0 | 0
3:30 | 3689.5 | 920.5 | 2106.5 | 105.5 | 4007.5 | 1292 | 55 | 376.5 | 714.5 | 106 | 0 | 0 | [6 empty] | Shortage
4:00 | 3679 | 921 | 2056 | 0 | 3992 | 1282 | 54 | 328 | 647 | 106 | 0 | 0
4:30 | 3657 | 921 | 2058.5 | 0 | 3928 | 1257 | 54 | 300 | 478.5 | 103 | 0 | 0
5:00 | 3635 | 921 | 2061 | 0 | 3864 | 1232 | 54 | 272 | 310 | 100 | 0 | 0
5:30 | 3611 | 922 | 2039 | 0 | 3447.5 | 1206 | 55 | 261 | 261 | 99 | 3.5 | 0
6:00 | 3587 | 923 | 2017 | 0 | 3031 | 1180 | 56 | 250 | 212 | 98 | 7 | 0
6:30 | 3520.5 | 923 | 2065 | 0 | 2964.5 | 1180.5 | 56 | 250 | 212 | 98 | 20 | 0 |  |  |  |  | Coal
7:00 | 3454 | 923 | 2113 | 0 | 2898 | 1181 | 56 | 250 | 212 | 98 | 33 | 0
7:30 | 3467.5 | 922.5 | 2018 | 0 | 3014 | 1191 | 56 | 250 | 212 | 105 | 49.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3481 | 922 | 1923 | 0 | 3130 | 1201 | 56 | 250 | 212 | 112 | 66 | 0
8:30 | 3467.5 | 922.5 | 1934.5 | 0 | 3253 | 1201 | 56 | 250 | 212 | 111 | 100 | 0
9:00 | 3454 | 923 | 1946 | 0 | 3376 | 1201 | 56 | 250 | 212 | 110 | 134 | 0
9:30 | 3476 | 922.5 | 1963.5 | 25 | 3531.5 | 1200.5 | 57.5 | 279.5 | 247 | 112 | 155 | 0
10:00 | 3498 | 922 | 1981 | 50 | 3687 | 1200 | 59 | 309 | 282 | 114 | 176 | 0
10:30 | 3455.5 | 921.5 | 1968 | 50 | 3762 | 1200.5 | 58.5 | 302 | 303 | 114 | 186 | 0
11:00 | 3413 | 921 | 1955 | 50 | 3837 | 1201 | 58 | 295 | 324 | 114 | 196 | 0
11:30 | 3427.5 | 921.5 | 2020.5 | 228 | 3851.5 | 1200.5 | 57 | 295.5 | 346.5 | 117 | 186.5 | 0
12:00 | 3442 | 922 | 2086 | 406 | 3866 | 1200 | 56 | 296 | 369 | 120 | 177 | 0
12:30 | 3463 | 922 | 2078.5 | 410.5 | 3883 | 1200 | 56 | 321.5 | 431.5 | 123 | 181.5 | 0
13:00 | 3484 | 922 | 2071 | 415 | 3900 | 1200 | 56 | 347 | 494 | 126 | 186 | 0
13:30 | 3484 | 922 | 2071 | 415 | 3900 | 1200 | 56 | 347 | 494 | 126 | 186 | 0
14:00 | 3484 | 922 | 2071 | 415 | 3900 | 1200 | 56 | 347 | 494 | 126 | 186 | 0
14:30 | 3493 | 922 | 2049.5 | 649 | 3873.5 | 1225 | 55.5 | 376 | 515 | 128 | 164.5 | 0
15:00 | 3502 | 922 | 2028 | 883 | 3847 | 1250 | 55 | 405 | 536 | 130 | 143 | 0
15:30 | 3553 | 922 | 1987.5 | 654 | 3909 | 1239.5 | 55.5 | 406 | 541 | 128 | 117 | 0
16:00 | 3604 | 922 | 1947 | 425 | 3971 | 1229 | 56 | 407 | 546 | 126 | 91 | 0
16:30 | 3684 | 922.5 | 1931 | 282.5 | 4034 | 1230 | 55.5 | 408.5 | 591.5 | 126 | 63.5 | 0
17:00 | 3684 | 923 | 1915 | 140 | 4097 | 1231 | 55 | 410 | 637 | 126 | 36 | 0
17:30 | 3665 | 923 | 1896.5 | 80 | 4051.5 | 1201.5 | 55.5 | 372.5 | 670 | 125 | 20.5 | 0
18:00 | 3646 | 923 | 1878 | 20 | 4006 | 1172 | 56 | 335 | 703 | 124 | 5 | 0
18:30 | 3664 | 922.5 | 1969 | 234 | 4134 | 1207.5 | 56 | 365.5 | 755.5 | 126 | 2.5 | 0
19:00 | 3682 | 922 | 2060 | 448 | 4262 | 1243 | 56 | 396 | 808 | 128 | 0 | 0
19:30 | 3783 | 922 | 2102 | 642 | 4375 | 1372 | 56 | 440 | 855 | 128 | 0 | 0
20:00 | 3781 | 922 | 2126 | 542 | 4378 | 1352 | 57 | 424 | 850 | 130 | 0 | 0
20:30 | 3790 | 922.5 | 2149.5 | 604 | 4377.5 | 1362.5 | 57 | 423 | 844 | 130 | 0 | 0
21:00 | 3799 | 923 | 2173 | 666 | 4377 | 1373 | 57 | 422 | 838 | 130 | 0 | 0
21:30 | 3813 | 923 | 2169 | 699.5 | 4377 | 1383 | 57.5 | 425 | 841.5 | 131 | 0 | 0
22:00 | 3827 | 923 | 2165 | 733 | 4377 | 1393 | 58 | 428 | 845 | 132 | 0 | 0
22:30 | 3833 | 924 | 2193 | 696.5 | 4345 | 1393 | 57.5 | 428.5 | 819 | 133 | 0 | 0
23:00 | 3839 | 925 | 2221 | 660 | 4313 | 1393 | 57 | 429 | 793 | 134 | 0 | 0
23:30 | 3854 | 924.5 | 2211.5 | 745.5 | 4217 | 1382 | 56 | 428 | 789.5 | 135 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.0° C
24:00 | 3869 | 924 | 2202 | 831 | 4121 | 1371 | 55 | 427 | 786 | 136 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 316.800 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 316.800 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 26 | 26 | 26 | 24 | 24 | 26 | 26 | 26 | 26 | 29 | 28 | 26 | 26 | 25 | 25 | 26 | 25 | 26 |  | 26 | 26 | 27 | 27 | 28 | 27 | 25 | 621731
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 0 |  |  |  | 6 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 484801
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 4 | 9 | 14 | 16 | 18 | 19 | 18 | 16 | 12 | 7 | 2 | 0 | [8 empty] | 133245
6 | Sikalbaha 225MW CCPP (Gas) | 131 | 131 | 131 | 141 | 131 | 131 | 70 | 26 | 26 | 26 | 27 | 33 | 40 | 62 | 138 | 217 | 216 | 206 |  | 205 | 203 | 203 | 203 | 205 | 216 | 204 | 2999301
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 2 |  | 51 | 51 | 51 | 51 | 51 | 0 |  | 232703
12 | Hathazari 100 MW peaking PP | 51 | 51 | 51 | 51 | 8 | 0 |  |  |  |  | 8 | 28 | 28 | 32 | 32 | 32 | 51 | 51 |  | 51 | 51 | 51 | 44 | 51 | 51 | 51 | 775120
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 60 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 94 | 56 | 1693636
| Daudkandi 200 MW PP (B.Trac) | 120 | 80 | 30 | 0 | [7 empty] | 100 | 100 | 200 | 200 | 100 | 20 | 10 |  | 30 | 150 | 120 | 150 | 150 | 150 | 200 | 1788096
14 | Titas 50 MW Peaking PP | 47 | 49 | 49 | 49 | 0 | [6 empty] | 5 | 47 | 40 | 47 | 45 | 47 | 48 |  | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 766088
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 278 | 272 | 285 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 283 | 263 | 258 | 260 | 270 | 270 | 270 | 283 |  | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 6761998
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 45 | 45 | 45 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 351272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 232 | 232 | 231 | 232 | 232 | 231 | 232 | 232 | 232 | 232 | 232 | 232 | 230 | 226 | 227 | 225 | 227 | 227 |  | 230 | 230 | 230 | 230 | 231 | 231 | 231 | 5533000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6426236
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 656424
33 | Ashuganj 225 MW CCPP | 214 | 216 | 218 | 214 | 217 | 215 | 216 | 218 | 215 | 215 | 210 | 211 | 210 | 178 | 203 | 209 | 210 | 208 |  | 214 | 210 | 211 | 210 | 212 | 212 | 214 | 5108000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 320 | 320 | 325 | 330 | 320 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 310 | 7386200
35 | Ashuganj 55 MW PP (Precision) | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 53 | 51 | 50 | 51 | 50 | 51 | 51 |  | 52 | 52 | 53 | 53 | 54 | 53 | 55 | 1284480
36 | Chandpur 150 MW CCPP | 90 | 91 | 90 | 90 | 91 | 70 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 56 | 57 | 54 | 71 | 136 |  | 137 | 136 | 136 | 136 | 136 | 136 | 138 | 1915610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 397 | 397 | 397 | 392 | 380 | 395 | 400 | 400 | 402 | 396 | 399 | 398 | 398 | 396 | 396 | 396 | 366 |  | 355 | 409 | 401 | 406 | 406 | 401 | 399 | 9598980
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6954000
41 | Haripur 360MW CCPP(HPL) | 256 | 267 | 272 | 277 | 276 | 277 | 272 | 272 | 274 | 253 | 252 | 252 | 245 | 250 | 244 | 237 | 238 | 235 |  | 242 | 253 | 258 | 265 | 265 | 290 | 290 | 6248000
42 | RPCL 210MW CCPP | 136 | 150 | 150 | 150 | 150 | 137 | 116 | 108 | 106 | 103 | 74 | 74 | 72 | 71 | 68 | 70 | 102 | 107 |  | 107 | 116 | 121 | 131 | 132 | 136 | 135 | 2608320
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 9 | 9 | 21 | 40 | 39 | 49 | 28 | 37 | 33 | 21 | 8 | 1 | [8 empty] | 289340
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 957328
46 | Shajibazar 330 MW CCPP | 160 | 157 | 157 | 156 | 157 | 160 | 159 | 160 | 154 | 157 | 153 | 155 | 151 | 152 | 154 | 152 | 155 | 152 |  | 157 | 155 | 155 | 156 | 156 | 158 | 156 | 3737000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 55 | 55 | 55 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1201248
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 912000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 191 | 192 | 178 | 178 | 220 | 220 | 219 | 219 | 219 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5165740
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [19 empty] | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 52680
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240660
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 0 | [14 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 109912
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 0 | [21 empty] | 0 | 43200
56 | Shahjahanulla 25 MW PP | 17 | 17 | 0 | 8 | 14 | 14 | 14 | 15 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 304856
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 290 | 290 | 280 | 310 | 285 | 270 | 290 | 270 | 300 | 295 | 285 | 290 | 270 | 270 | 265 |  | 275 | 280 | 270 | 295 | 280 | 285 | 300 | 7021511
| Bibiyana South 400 MW | 394 | 401 | 400 | 394 | 398 | 400 | 390 | 401 | 388 | 399 | 380 | 390 | 384 | 390 | 389 | 385 | 395 | 351 |  | 378 | 400 | 394 | 393 | 394 | 388 | 398 | 9281300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1256166
59 | Tangail Palli Power Gen 22 MW | 10 | 18 | 24 | 24 | 24 | 24 | 0 | [8 empty] | 3 | 17 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 333840
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 447840
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 |  |  | 19 | 19 |  | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 392796
62 | Tangail 22 MW PP (Doreen) |  | 0 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 |  | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 307620
63 | Impoprt (Tripura) | 128 | 106 | 106 | 106 | 100 | 98 | 98 | 112 | 110 | 114 | 114 | 120 | 126 | 128 | 130 | 126 | 126 | 124 |  | 128 | 128 | 130 | 130 | 132 | 134 | 136 | 2855040
64 | Malancha, Ctg. EPZ (United) | 29 | 21 | 25 | 30 | 40 | 31 | 5 | 5 | 7 | 5 | 7 | 12 | 20 | 20 | 20 | 30 | 38 | 32 |  | 32 | 42 | 42 | 42 | 42 | 42 | 42 | 665840
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 19 | 19 | 19 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 389016
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 232380
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 12 | 33 | 33 | 22 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 755300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | 20 | 20 | 20 | 21 | 472200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 27 | 18 | 18 | 25 | 25 | 24 | 24 | 24 | 24 |  | 24 | 24 | 25 | 25 | 26 | 26 | 26 | 586440
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 77680
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 799400
73 | Ghorashal 108MW PP (Regent) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 94 | 91 | 91 | 91 | 94 | 90 | 91 | 89 | 89 | 89 | 89 |  | 93 | 95 | 95 | 98 | 98 | 98 | 97 | 2218454
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 70 | 65 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1356600
| Chowmuhani 113 MW | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 66 | 70 | 73 | 68 | 73 | 73 | 73 | 86 | 113 | 113 |  | 110 | 113 | 113 | 113 | 113 | 111 | 79 | 1690920
| Manikgonj 162MW PP(MPGL) | 127 | 115 | 126 | 126 | 126 | 127 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3206880
77 | Siddhirganj 100 PP(Dutch Bangla) | 96 | 96 | 96 | 96 | 91 | 0 |  | 3 | 7 | 20 | 71 | 84 | 82 | 96 | 97 | 97 | 97 | 97 |  | 97 | 98 | 98 | 98 | 98 | 92 | 90 | 1829760
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 48 | 48 | 40 | 40 | 40 | 45 | 48 |  | 48 | 48 | 48 | 49 | 40 | 40 | 40 | 1025280
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 82 | 82 | 82 | 82 | 133 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 |  | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 3172800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 35 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 17 | 34 | 34 | 40 | 43 | 43 | 43 | 43 | 41 |  | 41 | 41 | 41 | 41 | 42 | 43 | 43 | 855154
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 90 | 81 | 81 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 80 | 90 | 95 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2323200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 35279
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1353474
| Karnaphuli Power Ltd. | 97 | 92 | 92 | 92 | 92 | 68 | 68 | 85 | 93 | 91 | 88 | 82 | 92 | 92 | 92 | 103 | 104 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 108 | 2356026
82 | Madanganj 102 PP(Summit) | 76 | 62 | 62 | 62 | 62 | 65 | 76 | 66 | 69 | 76 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1747656
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 130 | 120 | 120 | 145 | 125 | 130 | 145 | 130 | 150 | 135 | 145 | 140 | 145 | 120 | 150 | 140 | 130 | 150 |  | 140 | 130 | 140 | 130 | 130 | 150 | 135 | 3247113
87 | Meghnaghat 100 MW(IEL) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 96 | 91 | 94 | 95 | 90 | 90 | 88 | 95 | 95 |  | 87 | 88 | 87 | 87 | 96 | 93 | 90 | 2260800
| Meghnaghat 104 MW PP (OPCL) | 93 | 90 | 89 | 90 | 91 | 79 | 23 | 30 | 88 | 89 | 89 | 92 | 92 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2267520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 92 | 90 | 90 | 60 | 0 |  | 10 | 10 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1711560
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 0 | [22 empty] | 44352
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1186174
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 84 | 84 | 84 | 84 | 82 | 84 | 84 | 84 | 76 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 85 | 82 | 85 | 2011968
95 | Patenga 50MW PP (Baraka) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 25 | 25 | 25 | 29 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 859200
96 | Chattogram 108 MW PP (ECPV) | 91 | 96 | 97 | 97 | 98 | 98 | 91 | 91 | 77 | 81 | 82 | 87 | 87 | 87 | 87 | 87 | 87 | 95 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2203200
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 45 | 55 | 55 | 55 | 55 | 38 |  | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 1277615
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1327212
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 110 | 163 | 163 | 163 | 110 | 110 | 130 | 110 | 163 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3675190
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 10950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1295280
104 | Keranigonj 300 MW PP (APR) | 158 | 127 | 51 | 0 | [7 empty] | 116 | 100 | 301 | 260 | 50 | 20 |  |  | 220 | 218 | 124 | 203 | 255 | 253 | 305 | 2390280
105 | Bramhangoan 100 MW PP (Aggreko) | 98 | 98 | 50 | 0 | [5 empty] | 25 | 25 | 94 | 96 | 95 | 95 | 50 | 25 |  |  | 80 | 95 | 98 | 98 | 98 | 98 | 99 | 1308574
106 | Mymensingh 200 MW PP (United) | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 181 | 181 | 180 | 179 | 174 | 155 | 156 | 156 | 165 | 165 | 175 |  | 176 | 173 | 176 | 177 | 177 | 178 | 169 | 4176000
112 | Aurahati 100MW PP (Aggreko) | 98 | 98 | 50 | 0 | [5 empty] | 25 | 25 | 95 | 100 | 99 | 99 | 55 | 25 |  |  | 96 | 99 | 100 | 99 | 100 | 99 | 99 | 1300062
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 144 | 132 | 131 | 131 | 130 | 134 | 147 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3544130
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2076480
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 190 | 51 | 54 | 71 | 100 | 147 | 192 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4256640
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 132 | 150 | 150 | 50 | 50 | 50 | 50 | 83 | 125 | 137 | 137 | 137 | 127 | 135 | 142 | 142 |  | 143 | 143 | 143 | 138 | 145 | 145 | 150 | 3041018
118 | Bibiyana-III 400 MW CCPP | 403 | 402 | 402 | 404 | 370 | 371 | 373 | 374 | 374 | 371 | 379 | 404 | 406 | 402 | 391 | 405 | 406 | 405 |  | 391 | 405 | 404 | 404 | 403 | 404 | 404 | 9469000
| Jamalpur 115 MW PP (United) | 106 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 105 | 105 | 115 | 115 | 105 | 95 | 95 | 114 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2626800
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 280 | 282 | 7093200
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 80 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 50 |  | 61 | 100 | 100 | 100 | 100 | 100 | 100 | 2262720
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 95 | 68 | 68 | 68 | 68 | 95 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2458909
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 0 | 7 | 36 | 22 | 17 | 17 | 17 | 17 | 25 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 747720
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 0 | 13 | 20 | 24 | 30 | 0 | 32 | 28 | 22 | 12 | 3 | 1 | [8 empty] | 210395
| Chandpur 115(Doreen) | 83 | 83 | 83 | 83 | 79 | 69 | 54 | 78 | 83 | 84 | 83 | 82 | 83 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 81 | 81 | 1934400
| Kanchan Purbachal Power Generation Ltd. | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793080
120 | Eastern Zone Total | 8967 | 8845 | 8679 | 8396 | 8222 | 7524 | 7292 | 7392 | 7564 | 7969 | 8037 | 8595 | 8699 | 8979 | 8919 | 8668 | 8689 | 8488 |  | 9204 | 9504 | 9388 | 9525 | 9591 | 9550 | 9604 | 206782599
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 364800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 34 | 34 | 34 | 12 | 0 | [10 empty] | 5 | 22 | 26 |  | 27 | 44 | 37 | 37 | 37 | 37 | 31 | 363360
| Khulna 225 MW CCPP | 206 | 206 | 206 | 150 | 120 | 120 | 120 | 120 | 120 | 160 | 125 | 120 | 140 | 165 | 195 | 195 | 198 | 175 |  | 200 | 200 | 200 | 200 | 205 | 205 | 205 | 4153920
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 99 | 17 | 17 | 25 | 65 | 92 | 93 | 93 | 93 | 93 | 93 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2268480
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 19 | 30 | 67 | 82 | 94 | 92 | 91 | 81 | 65 | 43 | 20 | 3 | [8 empty] | 697060
131
132 | United Payra Power Ltd. | 54 | 54 | 54 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 606000
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 210 | 210 | 210 | 210 | 210 | 215 | 190 | 216 | 200 | 213 | 209 | 207 | 210 | 205 | 183 | 161 | 165 |  | 190 | 200 | 210 | 217 | 217 | 215 | 219 | 5054564
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 725760
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 67 | 67 | 68 | 66 | 66 | 67 | 66 | 66 | 63 | 63 | 63 | 30 | 45 | 63 | 63 | 63 | 63 | 63 |  | 63 | 65 | 65 | 65 | 65 | 65 | 67 | 1511000
140 | Bhola 33 MW PP (Venture) | 39 | 39 | 39 | 39 | 36 | 34 | 34 | 28 | 24 | 24 | 26 | 27 | 29 | 30 | 31 | 30 | 29 | 29 |  | 37 | 37 | 39 | 39 | 40 | 40 | 40 | 789477
141 | Noapara 100 MW PP (Bangla Trac) | 10 | 10 | 10 | 0 | [5 empty] | 0 |  | 1 | 10 | 27 | 80 | 70 | 20 |  |  | 10 | 50 | 50 | 50 | 50 | 10 | 30 | 553920
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 60 | 60 | 60 | 12 | 0 | [11 empty] | 20 | 40 |  | 72 | 65 | 62 | 62 | 61 | 60 | 60 | 606080
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 88 | 89 | 88 | 89 |  | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 2146464
146 | Bheramara HVDC | 921 | 921 | 920 | 921 | 921 | 923 | 923 | 922 | 923 | 922 | 921 | 922 | 922 | 922 | 922 | 922 | 923 | 923 |  | 922 | 922 | 922 | 923 | 923 | 925 | 924 | 22306181
147 | Bheramara 410 MW CCPP | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 160 | 160 | 165 | 170 | 165 | 160 | 160 | 155 |  | 155 | 165 | 170 | 175 | 180 | 180 | 180 | 4269312
148 | Payra 1320 MW | 1040 | 1030 | 1030 | 1010 | 960 | 910 | 910 | 930 | 930 | 930 | 930 | 930 | 930 | 940 | 980 | 960 | 960 | 900 |  | 970 | 1100 | 1080 | 1100 | 1120 | 1120 | 1100 | 25612100
149
150 | Barapukuria TPP Unit-1 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 71 | 71 | 70 | 71 | 71 | 71 | 72 | 70 | 70 | 72 | 72 |  | 73 | 72 | 73 | 73 | 73 | 73 | 71 | 1686109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 200 | 200 | 200 | 200 | 199 | 199 | 200 | 200 | 199 | 199 | 200 |  | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 4880100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 43 | 43 | 0 | [12 empty] | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 478480
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 4 | 2 | 4 | 4 | 1 | 3 | 2 | 0 | 0 | [8 empty] | 30540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 134 | 135 | 133 | 134 | 131 | 129 | 127 | 124 | 122 | 119 |  | 120 | 115 | 115 | 114 | 129 | 134 | 134 | 3336600
158 | Sirajgonj 225MW CCPP Unit-1(Oil) | 0 | 0 | 0 | 0 | 0 | 0
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 220 | 219 | 219 | 178 | 152 | 130 | 130 | 130 | 130 | 149 | 170 | 176 | 207 | 210 | 210 | 212 | 212 | 160 |  | 180 | 217 | 216 | 214 | 215 | 216 | 214 | 4694036
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 396 | 401 | 403 | 370 | 340 | 417 | 354 | 351 | 384 | 373 | 402 | 392 | 378 | 388 | 358 | 349 | 351 |  | 350 | 365 | 371 | 386 | 391 | 400 | 380 | 9104654
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 28 | 29 | 29 | 21 | 0 | [6 empty] | 4 | 22 | 26 | 25 | 24 | 25 | 25 |  | 24 | 24 | 28 | 28 | 28 | 30 | 30 | 403816
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 21 | 19 | 19 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 471600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247104
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 43 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 588528
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 0 | [6 empty] | 10 | 16 | 16 | 31 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 415490
168 | Santahar 50 MW Peaking PP | 37 | 37 | 37 | 37 | 0 | [11 empty] | 32 | 37 |  | 37 | 37 | 39 | 35 | 35 | 35 | 36 | 420592
169 | Natore 52 MW PP (Rajlanka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 43 |  | 43 | 43 | 43 | 43 | 34 | 16 | 16 | 600480
170 | Chapainawabganj 100 MW Peaking PP | 86 | 86 | 86 | 70 | 0 | [7 empty] | 28 | 36 | 45 | 42 | 42 | 85 |  | 89 | 90 | 90 | 91 | 91 | 88 | 88 | 1104992
171 | Baghabari 200 MW PP (Paramount) | 20 | 20 | 20 | 0 | [8 empty] | 9 | 38 | 149 | 100 | 30 | 10 |  | 12 | 30 | 50 | 66 | 80 | 50 | 98 | 893863
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 50 | 60 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 95 | 110 | 113 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2624352
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 70 | 100 | 113 | 111 | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2568096
173 | Rangpur 20 MW GTPP | [19 empty] | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 22000
175 | Saidpur 20 MW GTPP | [20 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 38000
176 | Rangpur 113 MW PP (Confidence) | 110 | 110 | 110 | 110 | 105 | 93 | 39 | 39 | 39 | 92 | 102 | 101 | 101 | 101 | 99 | 96 | 107 | 108 |  | 109 | 109 | 109 | 111 | 111 | 109 | 108 | 2302886
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 | 5 | 6 | 6 | 6 | 6 | 4 | 3 | 2 | 0 | [8 empty] | 48140
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 0 |  |  |  | 8 | 34 | 49 | 52 | 52 | 52 | 52 | 0 |  |  | 0 |  | 108 | 115 | 115 | 115 | 115 | 115 | 0 | 1027968
178