## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-01 | Sunday
|  |  | Date (day): | 2022-05-01 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14849.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15821 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-04-30 | 2022-05-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 230 | 233 | 230 | 230
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 77 | 101 | 94 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 399 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 271 | 343 | 350 | 350 | 10
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 320 | 320 | 130 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 1 | 80 | 90 | 90
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 125 | 140 | 150 | 150 |  | 185 | GT-1 Under S/D
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 90 | 96 | 94 | 94 |  | 8 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 96 | 96
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 300 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 3 | 16 | 84 | 84 |  | 18 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 6 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 31 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 24 | 12 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 95 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 55 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 50 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 13 | 19 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 2292 | 2741 | 4406 | 4437 | 686 | 757
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 16 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 37 | 37 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 |  | 195 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 210 | 215 | 200 | 200
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 32 | 42 | 30 | 42
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 14 | 95 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 282 | 190 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 30 | 50 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 42 | 68 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 6 | 20 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 57 | 51 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2282 | 842 | 1033 | 1444 | 1431 | 231 | 607
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 199 | 225 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 335 | 330 | 350 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 31 | 31 | 31 | 14 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 53 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 16 | 8 | 16 | 179 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 22 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 134 | 136 | 136 |  | 27 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 34 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 122 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 0 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 80 | 80 | 80 |  | 34 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 57 | 114 | 113 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 36 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 50 | 82 | 82 |  | 33 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1147 | 1352 | 2019 | 2070 | 816 | 121
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 157 | 209 | 165 | 210
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 2 | 45 | 190 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 13 | 115 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 24 | 24
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 238 | 410 | 562.6 | 556 | 0 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 42 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 155 | 158 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 17 | 5 | 17 | 34 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 15 | 5 | 15 | 35 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 56 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 219 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 16 | 5 | 16 | 34 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 17 | 17 | 17
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 310 | 310 | 310 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 378 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 396 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1677 | 1917 | 1892 | 1925 | 293 | 218
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 925 | 943 | 943
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 37 | 37 |  | 17 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 170 | 200
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 305 | 220 | 220 | 190 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 8 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 89 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1435 | 1500 | 1828 | 1818 | 289 | 74
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 27 | 39 | 33 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 60 | 65 | 65 | 129 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 970 | 450 | 1000
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 195 | 219 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 656 | 1320 | 818 | 1578 | 129 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 36 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  | 50 | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 196 | 179 | 165 | 165 | 45 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 139 | 130 | 200 | 220 |  |  | Running on HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 321 | 414 | 400 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 43 | 43
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 22 | 90 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 200 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 6 | 35 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 16 | 35 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 699 | 882 | 1532 | 1581 | 436 | 143
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Reserve
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 |  | 74 | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 110 | 110 | 110
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 30 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 200 | 309 | 348 | 425 | 0 | 179
|  | Total |  |  |  |  | 22348 | 21484 | 9186 | 11464 | 14849.6 | 15821 | 2880 | 2107
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9031.5912 | 11271.3 | 14599.991 | 15555.0626
| A. |  | 2022-04-30 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 11464 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7683 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11464 | MW
| 3 | Day peak Generation : |  |  | 9186 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11271.3 | MW
| 4 | Evening peak Generation : |  |  | 11464 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 230.7404 | MKWHr | By Solar | 1.285 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 138.0928 | MKWHr |  | By Oil: | 47.0148 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 18.5462 | MKWHr |  | By Hydro: | 0.84 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2880 | MW | Dhaka | 3676.4 | 3676.4 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2107 | MW | Chittagong | 1330.7 | 1330.7 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4987 | MW | Khulna | 1550 | 1550 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1054.79 | MMCFD |  |  | Rajshahi | 1162.2 | 1162.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 138018267.466 | ii) Oil : | Taka | 381579357.11 | Comilla | 1248 | 1248 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 87132702.43 | Total | Taka | 606730327.006 | Mymensingh | 867 | 867 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 476 | 476 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 282 | MW (E to W) at | 21:00 | hrs | Barisal | 444 | 444 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 92 | MW at | 19:00 | hrs | Rangpur | 517 | 517 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 11271.3 | 11271.3 |  | 0
| B. |  | 2022-05-01 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 36.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15821 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3821 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 241.5287 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7413 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.36 | MKWHr. | ii) HVDC Flow at Peak Time |  | 925 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6016 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.91 |  | (b) Today: | 75.66 |  | (c) Rule Curve: |  | 82
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-04-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 180 | 0 | 220 | 101 | 0 | 385 | 325 |  | 0 | 320 | 140 | 49 | 70 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 26 | 28 | 33 | 7 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 83 | 37 | 19 | 42 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 25 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 10 | 33 | 20 | 126 | 161 | 0 | 0 | 0 | 0 | 40 | 11 | 10 | 130 | 159 | 55 | 50 | 0 | 158 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 0 | 90 | 85 | 0 | 304 | 0 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 61 | 100 | 350 | 17 | 0 | 72 | 112 | 0 | 3 | 0 | 77 | 55 |  | 925 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 36 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 165 | 0 | 35 | 0 | 0 | 0 |  | 6650 | 2679 | 9329 | 3473 | 925 | 1995 | 0 | 1974 | 551 | 35 | 250 | 130 | 126 | 0 | 0 | 76.01
2:00 | 0 | 0 | 180 | 0 | 220 | 101 | 0 | 377 | 300 |  | 0 | 320 | 130 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 27 | 28 | 33 | 16 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 93 | 30 | 19 | 37 | 0 | 0 | 0 | 295 | 0 | 186 | 8 | 137 | 25 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 10 | 33 | 20 | 122 | 162 | 0 | 0 | 0 | 0 | 40 | 11 | 10 | 110 | 160 | 55 | 50 | 0 | 158 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 0 | 90 | 51 | 0 | 328 | 0 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 62 | 100 | 350 | 0 | 0 | 17 | 113 | 0 | 17 | 0 | 80 | 55 |  | 924 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 135 | 0 | 17 | 0 | 0 | 0 |  | 6400 | 2597 | 8997 | 3554 | 924 | 1867 | 0 | 1714 | 531 | 35 | 250 | 130 | 122 | 0 | 0 | 75.99
3:00 | 0 | 0 | 180 | 0 | 220 | 101 | 0 | 370 | 300 |  | 0 | 320 | 120 | 7 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 28 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 91 | 18 | 19 | 40 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 135 | 25 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 10 | 33 | 20 | 122 | 163 | 0 | 0 | 0 | 0 | 40 | 11 | 10 | 110 | 159 | 55 | 50 | 0 | 158 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 399 | 0 | 70 | 105 | 0 | 300 | 54 | 110 | 80 | 59 | 100 | 350 | 0 | 0 | 17 | 113 | 0 | 17 | 0 | 77 | 55 |  | 924 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 38 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 134 | 0 | 17 | 0 | 0 | 0 |  | 6353 | 2604 | 8957 | 3623 | 924 | 1875 | 0 | 1606 | 522 | 35 | 250 | 130 | 122 | 0 | 0 | 75.97
4:00 | 0 | 0 | 180 | 0 | 220 | 101 | 0 | 339 | 300 |  | 0 | 320 | 125 | 7 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 88 | 6 | 19 | 42 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 137 | 25 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 10 | 33 | 20 | 124 | 163 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 130 | 158 | 55 | 10 | 0 | 159 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 401 | 0 | 17 | 105 | 0 | 300 | 35 | 110 | 80 | 57 | 66 | 350 | 0 | 0 | 17 | 111 | 0 | 17 | 0 | 80 | 17 |  | 924 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 38 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 156 | 0 | 17 | 0 | 0 | 0 |  | 6099 | 2627 | 8726 | 3582 | 924 | 1857 | 0 | 1431 | 523 | 35 | 250 | 130 | 124 | 0 | 0 | 75.95
5:00 | 0 | 0 | 180 | 0 | 220 | 14 | 0 | 334 | 300 |  | 0 | 320 | 130 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 49 | 0 | 19 | 42 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 25 | 55 | 0 | 5 | 0 | 0 | 43 | 19 | 10 | 0 | 20 | 88 | 162 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 110 | 159 | 40 | 10 | 0 | 159 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 401 | 0 | 17 | 17 | 0 | 260 | 35 | 34 | 80 | 57 | 0 | 350 | 0 | 0 | 0 | 60 | 0 | 17 | 0 | 80 | 0 |  | 924 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 37 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 155 | 0 | 17 | 0 | 0 | 0 |  | 5408 | 2664 | 8072 | 3575 | 924 | 1715 | 0 | 980 | 505 | 35 | 250 | 130 | 88 | 0 | 0 | 75.93
6:00 | 0 | 0 | 180 | 0 | 220 | 14 | 0 | 310 | 251 |  | 0 | 320 | 130 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 19 | 42 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 136 | 25 | 55 | 0 | 5 | 0 | 0 | 26 | 19 | 10 | 33 | 20 | 86 | 165 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 110 | 160 | 40 | 10 | 0 | 160 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 70 | 17 | 0 | 400 | 0 | 17 | 0 | 0 | 260 | 35 | 17 | 80 | 57 | 0 | 350 | 0 | 2 | 0 | 17 | 0 | 17 | 0 | 78 | 0 |  | 925 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 135 | 0 | 17 | 0 | 5 | 0 |  | 5225 | 2527 | 7752 | 3499 | 925 | 1648 | 0 | 812 | 487 | 35 | 250 | 132 | 86 | 8 | 0 | 75.91
7:00 | 0 | 0 | 150 | 0 | 220 | 13 | 0 | 305 | 251 |  | 0 | 320 | 135 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 25 | 33 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 42 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 137 | 25 | 55 | 0 | 5 | 0 | 0 | 35 | 19 | 10 | 33 | 15 | 88 | 164 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 110 | 160 | 40 | 10 | 0 | 159 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 4 | 50 | 17 | 0 | 352 | 0 | 70 | 0 | 1 | 230 | 35 | 17 | 80 | 57 | 0 | 350 | 0 | 5 | 0 | 17 | 0 | 17 | 4 | 50 | 0 |  | 924 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 135 | 0 | 0 | 1 | 16 | 0 |  | 5196 | 2487 | 7683 | 3379 | 924 | 1648 | 0 | 809 | 487 | 35 | 250 | 162 | 88 | 31 | 0 | 75.89
8:00 | 0 | 0 | 149 | 0 | 220 | 13 | 0 | 309 | 254 |  | 0 | 320 | 120 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 32 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 22 | 55 | 0 | 5 | 0 | 0 | 34 | 19 | 10 | 33 | 20 | 90 | 163 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 110 | 158 | 40 | 10 | 0 | 159 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 9 | 50 | 17 | 0 | 352 | 0 | 70 | 0 | 2 | 230 | 35 | 17 | 80 | 57 | 0 | 350 | 0 | 20 | 0 | 17 | 0 | 9 | 10 | 50 | 0 |  | 925 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 170 | 0 | 0 | 165 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 130 | 0 | 0 | 1 | 40 | 0 |  | 5258 | 2504 | 7762 | 3404 | 925 | 1619 | 0 | 880 | 461 | 35 | 250 | 146 | 90 | 82 | 0 | 75.88
9:00 | 0 | 0 | 150 | 0 | 220 | 12 | 0 | 320 | 257 |  | 0 | 320 | 140 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 32 | 0 | 0 | 0 | 325 | 0 | 208 | 8 | 135 | 24 | 55 | 0 | 5 | 0 | 0 | 34 | 19 | 10 | 33 | 19 | 96 | 157 | 0 | 0 | 2 | 0 | 41 | 0 | 0 | 110 | 157 | 40 | 10 | 0 | 160 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 50 | 17 | 0 | 352 | 0 | 70 | 0 | 3 | 230 | 35 | 17 | 80 | 57 | 0 | 385 | 0 | 39 | 0 | 17 | 0 | 17 | 23 | 50 | 0 |  | 925 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 130 | 0 | 0 | 2 | 56 | 0 |  | 5484 | 2487 | 7971 | 3536 | 925 | 1638 | 0 | 918 | 420 | 35 | 250 | 146 | 96 | 137 | 0 | 75.87
10:00 | 0 | 0 | 150 | 0 | 220 | 12 | 0 | 335 | 286 |  | 0 | 320 | 138 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 23 | 33 | 33 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 32 | 0 | 0 | 0 | 350 | 0 | 187 | 8 | 137 | 25 | 55 | 0 | 5 | 0 | 0 | 34 | 19 | 10 | 33 | 20 | 88 | 157 | 0 | 0 | 1 | 0 | 41 | 0 | 0 | 110 | 156 | 40 | 10 | 0 | 220 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 16 | 50 | 17 | 0 | 401 | 0 | 70 | 0 | 4 | 230 | 35 | 17 | 80 | 61 | 0 | 396 | 0 | 48 | 0 | 17 | 0 | 17 | 27 | 50 | 0 |  | 925 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 4 | 73 | 0 |  | 5691 | 2717 | 8408 | 3672 | 925 | 1906 | 0 | 923 | 420 | 35 | 250 | 146 | 88 | 173 | 0 | 75.86
11:00 | 0 | 0 | 230 | 0 | 220 | 29 | 0 | 380 | 322 |  | 0 | 320 | 132 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 23 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 24 | 0 | 0 | 0 | 280 | 0 | 213 | 8 | 137 | 25 | 54 | 0 | 5 | 0 | 0 | 34 | 19 | 10 | 30 | 20 | 98 | 156 | 0 | 0 | 2 | 0 | 41 | 0 | 0 | 163 | 150 | 55 | 10 | 0 | 218 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 8 | 50 | 17 | 0 | 404 | 0 | 70 | 0 | 5 | 230 | 30 | 17 | 80 | 57 | 0 | 393 | 0 | 37 | 0 | 17 | 0 | 17 | 32 | 50 | 0 |  | 925 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 62 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 210 | 0 | 0 | 5 | 50 | 0 |  | 5869 | 2794 | 8663 | 3817 | 925 | 2045 | 0 | 914 | 424 | 35 | 250 | 146 | 98 | 139 | 0 | 75.85
12:00 | 0 | 0 | 230 | 0 | 250 | 77 | 0 | 398 | 271 |  | 0 | 320 | 125 | 1 | 90 | 0 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 54 | 6 | 35 | 19 | 25 | 23 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 14 | 0 | 19 | 32 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 28 | 53 | 0 | 22 | 0 | 0 | 34 | 19 | 10 | 25 | 20 | 108 | 157 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 155 | 40 | 50 | 0 | 218 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 114 | 18 | 76 | 17 | 0 | 378 | 13 | 70 | 17 | 4 | 282 | 30 | 42 | 80 | 57 | 6 | 396 | 17 | 47 | 17 | 57 | 0 | 17 | 30 | 50 | 13 |  | 925 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 196 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 16 | 370 | 195 | 0 | 0 | 5 | 70 | 0 |  | 6196 | 2990 | 9186 | 3921 | 925 | 1916 | 0 | 1260 | 570 | 35 | 259 | 155 | 108 | 176 | 0 | 75.84
13:00 | 0 | 0 | 231 | 0 | 260 | 95 | 0 | 352 | 271 |  | 0 | 320 | 130 | 38 | 90 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 25 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 54 | 0 | 19 | 38 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 137 | 28 | 52 | 0 | 51 | 0 | 0 | 34 | 19 | 10 | 32 | 20 | 108 | 162 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 153 | 40 | 50 | 0 | 219 | 0 | 0 | 9 | 270 | 0 | 0 | 0 | 11 | 0 | 0 | 40 | 0 | 115 | 17 | 76 | 17 | 0 | 378 | 40 | 70 | 34 | 4 | 300 | 30 | 68 | 80 | 58 | 20 | 398 | 17 | 50 | 54 | 80 | 0 | 17 | 30 | 50 | 55 |  | 923 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 460 | 180 | 0 | 0 | 3 | 72 | 0 |  | 6619 | 3087 | 9706 | 3871 | 923 | 1955 | 0 | 1710 | 660 | 35 | 250 | 146 | 108 | 178 | 0 | 75.83
14:00 | 0 | 0 | 230 | 0 | 270 | 96 | 0 | 386 | 321 |  | 0 | 320 | 130 | 23 | 90 | 25 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 25 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 50 | 0 | 19 | 38 | 0 | 0 | 0 | 310 | 0 | 183 | 8 | 137 | 27 | 52 | 0 | 51 | 0 | 0 | 34 | 19 | 10 | 32 | 20 | 116 | 177 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 152 | 40 | 50 | 0 | 219 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 15 | 0 | 0 | 58 | 0 | 114 | 15 | 90 | 17 | 0 | 378 | 64 | 70 | 30 | 4 | 300 | 30 | 54 | 80 | 57 | 32 | 400 | 24 | 30 | 66 | 51 | 0 | 17 | 20 | 50 | 55 |  | 925 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 57 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 70 | 600 | 196 | 0 | 0 | 4 | 46 | 0 |  | 6819 | 3334 | 10153 | 3966 | 925 | 2100 | 0 | 1825 | 799 | 35 | 250 | 146 | 116 | 121 | 0 | 75.82
15:00 | 0 | 0 | 230 | 0 | 270 | 99 | 0 | 396 | 171 |  | 0 | 320 | 122 | 31 | 92 | 41 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 31 | 24 | 0 | 0 | 33 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 56 | 0 | 19 | 38 | 0 | 0 | 0 | 310 | 0 | 184 | 8 | 137 | 27 | 52 | 0 | 51 | 0 | 0 | 34 | 19 | 0 | 32 | 20 | 110 | 187 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 153 | 40 | 50 | 0 | 219 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 72 | 0 | 0 | 70 | 0 | 115 | 11 | 90 | 17 | 0 | 365 | 97 | 70 | 68 | 2 | 300 | 30 | 68 | 80 | 57 | 60 | 360 | 35 | 36 | 108 | 68 | 0 | 17 | 18 | 35 | 55 |  | 923 | 0 | 305 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 70 | 600 | 208 | 0 | 0 | 3 | 36 | 0 |  | 6903 | 3316 | 10219 | 3924 | 923 | 1911 | 0 | 2145 | 799 | 33 | 250 | 146 | 110 | 108 | 0 | 75.81
16:00 | 0 | 0 | 230 | 0 | 270 | 100 | 0 | 377 | 193 |  | 0 | 320 | 126 | 31 | 92 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 31 | 8 | 0 | 0 | 33 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 57 | 0 | 22 | 40 | 0 | 0 | 0 | 310 | 0 | 183 | 8 | 136 | 24 | 51 | 0 | 51 | 0 | 0 | 38 | 19 | 0 | 32 | 20 | 98 | 188 | 0 | 17 | 1 | 0 | 41 | 0 | 0 | 110 | 156 | 40 | 50 | 0 | 219 | 0 | 0 | 9 | 270 | 0 | 0 | 0 | 110 | 0 | 0 | 45 | 0 | 115 | 7 | 90 | 17 | 0 | 367 | 97 | 70 | 68 | 2 | 300 | 30 | 68 | 70 | 57 | 60 | 360 | 17 | 21 | 108 | 68 | 0 | 17 | 8 | 17 | 28 |  | 925 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 45 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 660 | 188 | 0 | 0 | 1 | 35 | 0 |  | 6742 | 3292 | 10034 | 3884 | 925 | 1906 | 0 | 1988 | 859 | 33 | 250 | 146 | 98 | 75 | 0 | 75.8
17:00 | 0 | 0 | 231 | 0 | 270 | 100 | 0 | 377 | 213 |  | 0 | 320 | 130 | 31 | 92 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 33 | 31 | 8 | 0 | 0 | 34 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 50 | 0 | 22 | 42 | 0 | 0 | 0 | 340 | 0 | 204 | 8 | 135 | 21 | 51 | 0 | 51 | 0 | 0 | 25 | 19 | 0 | 32 | 20 | 102 | 187 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 153 | 50 | 50 | 0 | 192 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 110 | 0 | 0 | 45 | 0 | 115 | 2 | 90 | 17 | 0 | 370 | 55 | 70 | 34 | 0 | 245 | 30 | 51 | 51 | 107 | 20 | 360 | 17 | 4 | 54 | 34 | 0 | 17 | 2 | 17 | 0 |  | 924 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 177 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 414 | 10 | 0 | 35 | 20 | 0 | 0 | 0 | 35 | 690 | 213 | 0 | 0 | 0 | 16 | 0 |  | 6497 | 3393 | 9890 | 3933 | 924 | 2060 | 0 | 1658 | 889 | 34 | 250 | 146 | 102 | 24 | 0 | 75.79
18:00 | 0 | 0 | 231 | 0 | 270 | 101 | 0 | 377 | 272 |  | 0 | 320 | 140 | 31 | 92 | 15 | 0 | 0 | 0 | 7 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 33 | 31 | 8 | 0 | 0 | 35 | 0 | 0 | 6 | 212 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 52 | 5 | 22 | 42 | 0 | 0 | 0 | 325 | 0 | 198 | 8 | 135 | 27 | 52 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 0 | 20 | 104 | 185 | 0 | 17 | 0 | 0 | 41 | 0 | 0 | 110 | 156 | 60 | 50 | 0 | 192 | 0 | 10 | 9 | 295 | 0 | 0 | 0 | 110 | 0 | 0 | 50 | 0 | 115 | 0 | 90 | 17 | 11 | 383 | 55 | 70 | 34 | 0 | 180 | 30 | 51 | 51 | 114 | 20 | 360 | 17 | 1 | 54 | 34 | 0 | 17 | 0 | 17 | 4 |  | 924 | 0 | 285 | 0 | 20 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 171 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 360 | 17 | 0 | 35 | 38 | 5 | 0 | 0 | 35 | 760 | 211 | 0 | 0 | 0 | 2 | 0 |  | 6550 | 3478 | 10028 | 3904 | 924 | 2084 | 0 | 1739 | 959 | 35 | 250 | 156 | 104 | 3 | 0 | 75.78
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 180 | 0 | 210 | 101 | 0 | 348 | 242 |  | 0 | 320 | 135 | 59 | 94 | 25 | 0 | 0 | 0 | 30 | 70 | 80 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 18 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 13 | 203 | 0 | 0 | 0 |  | 24 | 10 | 51 | 20 | 74 | 21 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 188 | 16 | 136 | 27 | 52 | 0 | 51 | 0 | 0 | 35 | 19 | 11 | 31 | 20 | 110 | 198 | 0 | 17 | 0 | 0 | 42 | 16 | 15 | 110 | 158 | 40 | 50 | 0 | 192 | 0 | 16 | 9 | 265 | 17 | 11 | 0 | 160 | 0 | 0 | 100 | 0 | 127 | 0 | 90 | 41 | 50 | 366 | 108 | 70 | 47 | 0 | 180 | 48 | 65 | 80 | 114 | 40 | 400 | 76 | 0 | 134 | 47 | 0 | 17 | 0 | 28 | 0 |  | 925 | 0 | 230 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 8 | 57 | 38 | 32 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 30 | 25 | 37 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 328 | 91 | 0 | 35 | 67 | 95 | 0 | 0 | 35 | 790 | 211 | 0 | 0 | 0 | 0 | 16 |  | 7239 | 3784 | 11023 | 3676 | 925 | 2039 | 0 | 2745 | 989 | 35 | 250 | 384 | 110 | 0 | 0 | 75.75
19:30 | 0 | 0 | 200 | 0 | 260 | 101 | 0 | 385 | 275 |  | 0 | 320 | 120 | 80 | 91 | 15 | 0 | 0 | 0 | 7 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 24 | 33 | 31 | 8 | 0 | 0 | 35 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 80 | 36 | 22 | 42 | 0 | 0 | 0 | 270 | 0 | 182 | 16 | 136 | 27 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 31 | 20 | 110 | 210 | 0 | 17 | 0 | 0 | 42 | 16 | 15 | 110 | 160 | 40 | 70 | 0 | 219 | 0 | 16 | 9 | 285 | 17 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 80 | 0 | 90 | 34 | 50 | 365 | 108 | 70 | 51 | 0 | 190 | 54 | 68 | 80 | 114 | 40 | 400 | 89 | 0 | 162 | 51 | 0 | 17 | 0 | 35 | 0 |  | 924 | 0 | 230 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 51 | 38 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 37 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 162 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 414 | 91 | 0 | 35 | 67 | 100 | 0 | 0 | 35 | 800 | 205 | 0 | 0 | 0 | 0 | 17 |  | 7370 | 3791 | 11161 | 3829 | 924 | 2177 | 0 | 2711 | 999 | 35 | 250 | 256 | 110 | 0 | 0 | 0
20:00 | 0 | 0 | 233 | 0 | 270 | 101 | 0 | 367 | 334 |  | 0 | 320 | 140 | 78 | 96 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 27 | 33 | 31 | 8 | 0 | 0 | 35 | 0 | 0 | 16 | 209 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 95 | 34 | 22 | 42 | 0 | 0 | 0 | 310 | 0 | 190 | 16 | 136 | 28 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 0 | 110 | 204 | 0 | 17 | 0 | 0 | 42 | 17 | 15 | 110 | 157 | 45 | 84 | 0 | 219 | 0 | 16 | 9 | 290 | 17 | 11 | 0 | 95 | 0 | 0 | 45 | 0 | 92 | 0 | 90 | 34 | 10 | 413 | 115 | 50 | 51 | 0 | 192 | 54 | 68 | 80 | 114 | 20 | 400 | 34 | 0 | 162 | 51 | 0 | 17 | 0 | 45 | 0 |  | 925 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 38 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 168 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 360 | 53 | 0 | 35 | 78 | 97 | 0 | 0 | 35 | 860 | 218 | 0 | 0 | 0 | 0 | 0 |  | 7301 | 3735 | 11036 | 3953 | 925 | 2235 | 0 | 2380 | 1059 | 35 | 250 | 219 | 110 | 0 | 0 | 75.76
21:00 | 0 | 0 | 233 | 0 | 270 | 101 | 0 | 399 | 343 |  | 0 | 320 | 140 | 80 | 96 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 31 | 12 | 0 | 0 | 35 | 0 | 0 | 16 | 215 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 95 | 37 | 22 | 42 | 0 | 0 | 0 | 335 | 0 | 199 | 16 | 134 | 31 | 53 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 0 | 122 | 209 | 0 | 17 | 0 | 0 | 42 | 17 | 15 | 163 | 158 | 56 | 84 | 0 | 219 | 0 | 16 | 9 | 310 | 17 | 11 | 0 | 95 | 0 | 0 | 45 | 0 | 55 | 0 | 90 | 34 | 10 | 400 | 115 | 50 | 51 | 0 | 190 | 50 | 68 | 80 | 114 | 20 | 400 | 17 | 0 | 162 | 51 | 0 | 17 | 0 | 50 | 19 |  | 925 | 0 | 305 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 39 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 179 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 89 | 110 | 0 | 0 | 35 | 970 | 219 | 0 | 0 | 0 | 0 | 0 |  | 7453 | 4011 | 11464 | 4123 | 925 | 2374 | 0 | 2377 | 1169 | 35 | 250 | 219 | 122 | 0 | 0 | 75.75
22:00 | 0 | 0 | 234 | 0 | 270 | 98 | 0 | 398 | 342 |  | 0 | 320 | 125 | 88 | 96 | 15 | 92 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 94 | 30 | 22 | 42 | 0 | 0 | 0 | 310 | 0 | 183 | 16 | 136 | 31 | 54 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 120 | 213 | 0 | 17 | 0 | 0 | 42 | 17 | 15 | 130 | 156 | 57 | 84 | 0 | 219 | 0 | 16 | 9 | 270 | 17 | 11 | 0 | 15 | 0 | 0 | 45 | 0 | 49 | 0 | 90 | 34 | 0 | 367 | 115 | 50 | 51 | 0 | 190 | 50 | 68 | 80 | 114 | 20 | 401 | 17 | 0 | 162 | 51 | 0 | 17 | 0 | 50 | 55 |  | 925 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 51 | 38 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 185 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 89 | 72 | 0 | 0 | 35 | 960 | 210 | 0 | 0 | 0 | 0 | 0 |  | 7344 | 3911 | 11255 | 4157 | 925 | 2273 | 0 | 2247 | 1159 | 35 | 250 | 219 | 120 | 0 | 0 | 75.74
23:00 | 0 | 0 | 234 | 0 | 270 | 98 | 0 | 397 | 332 |  | 0 | 320 | 135 | 97 | 96 | 15 | 300 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 15 | 12 | 22 | 42 | 0 | 0 | 0 | 310 | 0 | 182 | 16 | 137 | 31 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 21 | 20 | 122 | 211 | 0 | 17 | 0 | 0 | 41 | 28 | 15 | 130 | 157 | 57 | 84 | 0 | 219 | 0 | 17 | 9 | 265 | 17 | 11 | 0 | 15 | 0 | 0 | 45 | 0 | 14 | 0 | 90 | 34 | 0 | 367 | 115 | 50 | 51 | 0 | 190 | 48 | 68 | 80 | 113 | 20 | 400 | 17 | 0 | 126 | 51 | 0 | 17 | 0 | 50 | 35 |  | 924 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 53 | 38 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 0 | 39 | 0 | 0 | 35 | 770 | 182 | 0 | 0 | 0 | 0 | 0 |  | 7326 | 3484 | 10810 | 4356 | 924 | 2224 | 0 | 1862 | 970 | 35 | 250 | 197 | 122 | 0 | 0 | 75.73
24:00 | 0 | 0 | 235 | 0 | 270 | 100 | 0 | 373 | 332 |  | 0 | 320 | 140 | 59 | 90 | 15 | 300 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 27 | 33 | 31 | 25 | 0 | 0 | 35 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 6 | 12 | 22 | 42 | 0 | 0 | 0 | 310 | 0 | 182 | 16 | 136 | 31 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 14 | 20 | 114 | 211 | 0 | 17 | 0 | 0 | 42 | 48 | 15 | 130 | 157 | 55 | 84 | 0 | 219 | 0 | 20 | 9 | 275 | 17 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 90 | 34 | 0 | 367 | 115 | 35 | 51 | 0 | 240 | 48 | 68 | 80 | 100 | 20 | 400 | 17 | 0 | 90 | 51 | 0 | 17 | 0 | 50 | 35 |  | 924 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 58 | 38 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 191 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 600 | 152 | 0 | 0 | 0 | 0 | 0 |  | 7123 | 3226 | 10349 | 4300 | 924 | 2231 | 0 | 1679 | 800 | 35 | 250 | 146 | 114 | 0 | 0 | 75.72
KWH | 0 | 0 | 4821000 | 0 | 5791500 | 1738590 | 0 | 8837120 | 6828000 |  | 0 | 7557850 | 3180858 | 745920 | 1575360 | 258060 | 543637 | 0 | 0 | 47040 | 340416 | 350400 | 0 | 0 | 0 | 0 | 801360 | 585769 | 603616 | 403272 | 600000 | 556200 | 801700 | 731400 | 409440 | 0 | 0 | 840000 | 0 | 0 | 106632 | 4889433 | 0 | 0 | 0 |  | 366960 | 10032 | 273319 | 25080 | 1210560 | 261600 | 474768 | 920160 | 0 | 0 | 0 | 7525900 | 0 | 4537000 | 267636 | 3256470 | 613368 | 1285920 | 0 | 913832 | 0 | 0 | 905611 | 443736 | 207360 | 702900 | 430440 | 2601600 | 4147200 | 0 | 192852 | 13300 | 0 | 671064 | 165600 | 135504 | 3129463 | 3723000 | 1141920 | 1073280 | 0 | 4577500 | 0 | 105980 | 131040 | 7050500 | 111984 | 87800 | 0 | 1159199 | 0 | 0 | 705600 | 0 | 1658450 | 123390 | 1908480 | 683040 | 138836 | 8832000 | 1108800 | 1502400 | 1110686 | 32039 | 6029345 | 961696 | 1527193 | 1867320 | 1830360 | 780480 | 8870800 | 408000 | 321250 | 1575360 | 1333582 | 0 | 417600 | 200718 | 1355520 | 642600 |  | 22360000 | 0 | 6075936 | 0 | 79680 | 2992320 | 0 | 0 | 0 | 0 | 29625 | 1277000 | 797899 | 309216 | 0 | 0 | 0 | 0 | 0 | 130664 | 0 | 0 | 19192 | 140640 | 47258 | 260160 | 0 | 119178 | 602181 | 0 | 4589700 | 0 | 0 | 4379482 | 0 | 0 | 3347036 | 0 | 0 | 0 | 0 | 7939600 | 286560 | 0 | 553056 | 393984 | 416572 | 0 | 526 | 517152 | 13354300 | 4235973 | 0 | 140400 | 32940 | 560880 | 29760 |  | 154721556 | 76018870 | 230740426 | 90374920 | 22360000 | 47717845 | 0 | 39844616 | 18546181 | 840000 | 6339356 | 830865 | 2601600 | 1285043 | 0
Fuel Cost | 0 | 0 | 7038660 | 0 | 6428565 | 2294938.8 | 0 | 8925491.2 | 7032840 |  | 0 | 8238056.5 | 3530752.38 | 5661532.8 | 10854230.4 | 2183187.6 | 565382.48 | 0 | 0 | 354211.2 | 3104593.92 | 3447936 | 0 | 0 | 0 | 0 | 5849928 | 4527994.37 | 5951653.76 | 302454 | 450000 | 0 | 0 | 0 | 3959284.8 | 0 | 0 | 226800 | 0 | 0 | 990611.28 | 5329481.97 | 0 | 0 | 0 |  | 0 | 97009.44 | 2651194.3 | 239514 | 10531872 | 2071872 | 598207.68 | 2732875.2 | 0 | 0 | 0 | 5569166 | 0 | 4174040 | 345250.44 | 3744940.5 | 693105.84 | 1800288 | 0 | 1562652.72 | 0 | 0 | 8648585.05 | 563544.72 | 155520 | 1230075 | 322830 | 19512000 | 4396032 | 0 | 244922.04 | 212002 | 0 | 1073702.4 | 294768 | 211386.24 | 3567587.82 | 3871920 | 2249582.4 | 2049964.8 | 0 | 7919075 | 0 | 123996.6 | 267321.6 | 7121005 | 83988 | 66728 | 0 | 8763544.44 | 0 | 0 | 3669120 | 0 | 16319148 | 1442429.1 | 15554112 | 7410984 | 978793.8 | 8213760 | 10112256 | 14197680 | 9674075.06 | 0 | 45581848.2 | 8376372.16 | 13424026.47 | 18635853.6 | 15686185.2 | 5197996.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128793600 | 0 | 6379732.8 | 0 | 626284.8 | 41473555.2 | 0 | 0 | 0 | 0 | 308692.5 | 1443010 | 1236743.45 | 3017948.16 | 0 | 0 | 0 | 0 | 0 | 1156376.4 | 0 | 0 | 185970.48 | 1362801.6 | 458402.6 | 499507.2 | 0 | 90217.746 | 3631151.43 | 0 | 24876174 | 0 | 0 | 5123993.94 | 0 | 0 | 49268369.92 | 0 | 0 | 0 | 0 | 7860204 | 2991686.4 | 0 | 5248501.44 | 3719208.96 | 3232598.72 | 0 | 5812.3 | 3821753.28 | 58625377 | 0 | 0 | 0 | 0 | 0 | 0 |  | 401485296.08 | 355437674.326 | 756922970.406 | 87248128.716 | 128793600 | 50770138.75 | 0 | 282840542.77 | 87132702.43 | 226800 | 90741925.12 | 7996889.22 | 19512000 | 1660243.4 | 0
Yesterday Day Peak | 0 | 0 | 230 | 0 | 250 | 77 | 0 | 398 | 271 |  | 0 | 320 | 125 | 1 | 90 | 0 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 54 | 6 | 35 | 19 | 25 | 23 | 33 | 31 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 14 | 0 | 19 | 32 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 28 | 53 | 0 | 22 | 0 | 0 | 34 | 19 | 10 | 25 | 20 | 108 | 157 | 0 | 17 | 2 | 0 | 41 | 0 | 0 | 110 | 155 | 40 | 50 | 0 | 218 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 114 | 18 | 76 | 17 | 0 | 378 | 13 | 70 | 17 | 4 | 282 | 30 | 42 | 80 | 57 | 6 | 396 | 17 | 47 | 17 | 57 | 0 | 17 | 30 | 50 | 13 |  | 925 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 196 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 16 | 370 | 195 | 0 | 0 | 5 | 70 | 0 |  | 9186 | DayPeak
Yesterday Evening Peak | 0 | 0 | 233 | 0 | 270 | 101 | 0 | 399 | 343 | 0 | 0 | 320 | 140 | 80 | 96 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 31 | 12 | 0 | 0 | 35 | 0 | 0 | 16 | 215 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 0 | 95 | 37 | 22 | 42 | 0 | 0 | 0 | 335 | 0 | 199 | 16 | 134 | 31 | 53 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 0 | 122 | 209 | 0 | 17 | 0 | 0 | 42 | 17 | 15 | 163 | 158 | 56 | 84 | 0 | 219 | 0 | 16 | 9 | 310 | 17 | 11 | 0 | 95 | 0 | 0 | 45 | 0 | 55 | 0 | 90 | 34 | 10 | 400 | 115 | 50 | 51 | 0 | 190 | 50 | 68 | 80 | 114 | 20 | 400 | 17 | 0 | 162 | 51 | 0 | 17 | 0 | 50 | 19 |  | 925 | 0 | 305 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 60 | 39 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 179 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 89 | 110 | 0 | 0 | 35 | 970 | 219 | 0 | 0 | 0 | 0 | 0 |  | 11464 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 270 | 100 | 0 | 400 | 350 | 0 | 0 | 320 | 150 | 90 | 94 | 55 | 335 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 0 | 96 | 37 | 22 | 42 | 0 | 0 | 0 | 350 | 0 | 225 | 16 | 136 | 31 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 166 | 210 | 0 | 17 | 0 | 0 | 42 | 17 | 15 | 163 | 160 | 60 | 84 | 0 | 220 | 0 | 16 | 10 | 310 | 17 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 36 |  | 82 | 55 |  | 943 | 0 | 220 | 0 | 16 | 200 | 0 | 0 | 37 | 60 | 32 | 65 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 90 | 0 | 43 | 40 | 43 | 38 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 220 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 1000 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 230 | 0 | 270 | 94 | 0 | 400 | 350 | 0 | 0 | 320 | 150 | 90 | 94 | 55 | 300 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 0 | 96 | 37 | 22 | 30 | 0 | 0 | 0 | 330 | 0 | 225 | 8 | 136 | 31 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 143 | 165 | 0 | 17 | 1.6 | 0 | 42 | 5 | 5 | 163 | 160 | 60 | 84 | 0 | 220 | 0 | 5 | 10 | 310 | 17 | 11 | 200 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 36 | 30 | 82 | 55 |  | 943 | 0 | 220 | 0 | 16 | 170 | 0 | 0 | 37 | 0 | 32 | 65 | 33 | 50 | 0 | 0 | 0 | 36 | 30 | 90 | 0 | 43 | 30 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 200 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 450 | 220 |  | 0 | 6 | 100 | 30
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 250 | 12 | 0 | 282 | 223 | 0 | 0 | 320 | 140 | 0 | 14 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 19 | 33 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 153 | 8 | 137 | 31 | 5 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 25 | 20 | 88 | 185 | 0 | 0 | 1 | 0 | 42 | 5 | 5 | 110 | 133 | 40 | 5 | 0 | 192 | 0 | 5 | 9 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 20 | 0 | 0 | 340 | 0 | 0 | 0 | 2 | 80 | 54 | 17 | 17 | 57 | 0 | 320 | 0 | 25 | 0 | 17 | 0 | 17 | 12 | 0 | 0 | 0 | 924 | 0 | 200 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 56 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 152 | 0 | 0 | 2 | 46 | 0 | 0 |  |  |  |  | 47014837 |  | 0
47014837
| Minimum Generation |  | 7683 | 7:00
| Highest Generation |  | 11464 | 21:00
| Day Peak Generation |  | 9186 | 12:00
| Evening Peak Generation |  | 11464 | 21:00
| HVDC Max Flow |  | 925 | 1:00
| HVDC EvPeak Flow |  | 925 | 21:00
| Load factor L.F |  | 83.86%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-01
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-04-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9186 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7413 | MW
Evening Peak Generation : |  | 11464 | MW Hour : | 21:00 | Available Max Generation : |  | 15821 | MW
E.P. Demand (at gen end) : |  | 11464 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11464 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3821 | MW
Total Gen. (MKWH) : |  | 230.7404 | System Load Factor : | 83.86% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 92 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-01
Actual : | 75.66 | Ft.(MSL) , | Rule curve : | 82 | Ft.( MSL )
Gas Consumed : | Total = | 1054.79 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 138018267.466
: |  | Coal : | 87132702.43 | Oil : | 381579357.11 | Total : | 606730327.006
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4344.3858 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1394.0981 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1376.2261 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1230.304 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1123.6238 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 924.5237 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 449.392 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 284.1184 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 674.6656 |  |  | 0 | 0%
Total | 0 |  | 11801.3373 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barapukuria Unit-1 was shutdown at 08:15 due to low demand.
b) Saidpur 132/33 kV T-3 transformer was switched on at 12:50..
c) Kabirpur 132/33 kV T-2 transformer was under shut down from 07:32 to 11:58 for D/W.
d) Natore 132/33 kV T-3 transformer was under shut down from 08:15 to 10:30 for C/M. | [5 empty] | About 20 MW power interruption occurred under
Natore S/S area from 08:15 to 10:30.
e) Benapole 132/33 kV T-1 transformer was under shut down from 08:23 to 10:09 due to 33 kV Bakhra feeder fault.
f) Manikganj 132/33 kV T-4 transformer was under shut down from 09:30 to 10:50 for C/M.
g) B.Baria 132/33 kV T-2 transformer was under shut down from 08:09 to 10:18 for C/M.
h) Sherpur 132/33 kV T-2 transformer was under shut down from 09:54 to 13:00 for C/M.
i) Mithapukur 132/33 kV T-1 transformer was under shut down from 10:55 to 12:01 for C/M.
j) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 11:29 to 13:13 for tree trimming.
k) Kabirpur 132/33 kV T-1 transformer was under shut down from 11:59 to 16:28 for D/W.
l) Hasnabad 132/33 kV T-5 transformer was under shut down from 10:15 to 12:41 for C/M.
m) Shyampur 230/132 kV T-02 transformer was under shut down from 13:36 to 13:28 for C/M.
n) Sreemangal 132/33 kV T-3 transformer was under shut down from 14:51 to 15:14 for 33 kV CB gas filling.
o) Payra 400 kV Bus splited at 15:00.
p) Bagerhat-Mongla 132 kV Ckt-1 tripped at 15:59 from Mongla end showing dist. Z1 and was switched on at 16:22.
q) Meghnaghat-Cumilla(N) 230 kV Ckt-1 tripped at 18:31 showing dist. Z1, B,C-phases and was switched on at 19:10.
r) Chattak 132/33 kV T-1 transformer tripped at 20:25 showing O/C and was switched on at 20:30.
s) Siddhirganj 335 MW CCPP GT was synchronize at 18:07 and ST at 20:55.
t) Sikalbaha-TK.Chemical 132 kV Ckt tripped at 01:45(01/05/2022) from Sikalbaha end showing dist. Z1, Y,B
and was switched on at 02:27(01/05/2022).
u) Rampura-Bashundhara 132 kV Ckt-1 tripped at 05:50(01/05/2022) from both ends showing dist Z1, C
at Rampura end & dist Z1, C, GT at Bashundhara end and was switched on at 06:19(01/05/2022).
v) Sirajganj Unit-1 tripped at 06:27(01/05/2022) due to GBC problem and GT was synchronized at 08:06(01/05/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-04-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 233 | 4821000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 5791500 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 1738590
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 8837120
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 6828000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7557850 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 80 | 745920 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3180858 | GT-1 Under S/D & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 1575360 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 258060 | Low Demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 403272
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 47040 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 543637 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 340416 | Low Demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 801360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 350400 | Low Demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 585769
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 603616
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1156200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 731400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 12 | 409440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 1159199 | Low Demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 55 | 1658450 | Low Demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 1502400 | Low Demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 408000 | Low Demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1575360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 200718
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 19 | 642600 | Engine problem
| Dhaka area Total |  |  |  | 5898 | 2741 | 55255235
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 106632 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123390
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 261600 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 840000 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 215 | 4889433
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1110686 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 10032 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 273319 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 0 | 0 | 25080 | Contract Expired
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1908480 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 474768
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 920160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 1210560 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 6029345 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 50 | 961696
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1527193 | Low Demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 20 | 780480 | Low Demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 1333582 | Low Demand
| Chattogram area Total |  |  |  | 2282 | 1033 | 22818475
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4537000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7525900 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 31 | 613368 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1285920
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 267636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 913832
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 138836 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 134 | 3256470 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 683040 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 443736
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 207360
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2601600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 702900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 905611 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 430440 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1867320 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 1830360
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 417600 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 1355520 | Low Demand
| Cumilla Area Total |  |  |  | 3014 | 1352 | 29984449
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 209 | 4147200 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 192852
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 45 | 705600 | Low Demand
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1108800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 321250
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 366960
| Mymensingh Area Total |  |  |  | 622 | 410 | 6855962
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Gas shortage
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 671064 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3129463
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3723000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 17 | 165600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 15 | 135504 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 87800
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1141920 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1073280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4577500
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 16 | 105980 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 111984
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7050500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 8832000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 131040
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8870800
| Sylhet Area Total |  |  |  | 2477 | 1917 | 39807435
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 925 | 22360000
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 79680 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 2992320 | Low Demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 6075936 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 8 | 29625 | Low Demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 286560 | Low Demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 393984 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 560880
| Khulna Area Total |  |  |  | 2384 | 1500 | 32778985
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 309216 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 39 | 797899
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1277000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 970 | 13354300
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4235973
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 140400 | Reserve.
| Barisal Area Total |  |  |  | 1958 | 1320 | 20114788
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 19192 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 179 | 4379482 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3347036
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7939600
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 47258 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 260160
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 119178
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 140640
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 22 | 130664 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 553056 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 517152 | Low Demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32940
| Rajshahi Area Total |  |  |  | 2129 | 882 | 17486358
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 602181
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4589700
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 416572
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 526
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 29760
| Rangpur Area Total |  |  |  | 720 | 309 | 5638739
| Total |  |  |  | 21484 | 11464 | 230740426
| Eastern Grid Total |  |  |  | 14293 | 7453 | 154721556
| Western Grid Total |  |  |  | 7191 | 4011 | 76018870
| National Grid Total |  |  |  | 21484 | 11464 | 230740426
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-04-30
(a) ENTIRE EASTERN GRID : |  | 7598.1 | MW | (b) ENTIRE WESTERN GRID : |  | 3673.2 | MW
i) Dhaka area |  | 3676.4 | MW | i) Khulna area |  | 1550 | MW
ii) Chittagong area |  | 1330.7 | MW | ii) Rajshahi area |  | 1162.2 | MW
iii) Comilla area |  | 1248 | MW | iii) Barisal area |  | 444 | MW
iv) Mymensingh area |  | 867 | MW | iv) Rangpur area |  | 517 | MW
v) Sylhet area |  | 476 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11271.3 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 28 | 00:00 | Hasnabad | 55 | 03:00 | Palashbari | 90 | 22:00
Agargaon | 69 | 13:00 | Hathazari | 98 | 19:00 | Panchagarh | 36 | 19:30
Agrabad | 78 | 19:00 | Ishurdi | 64 | 21:00 | Patuakhali | 135 | 21:00
AKS | 27 | 17:00 | Jaldhaka | 38 | 19:00 | PHP | 7 | 14:00
AKSML | 131 | 14:00 | Jamalpur | 94 | 23:00 | Purbachal | 17 | 00:00
Amnura | 53 | 22:00 | Jashore | 128 | 21:00 | Purbasadipur | 89 | 19:30
Ashuganj | 51 | 23:00 | Jhenaidah | 122 | 20:00 | Rahim | 0 | 00:00
Bagerhat | 106 | 21:00 | Joydebpur | 145 | 02:00 | Rajbari | 70 | 21:00
Bakulia | 117 | 00:00 | Joypurhat | 31 | 20:00 | Rajendrapur | 80 | 15:00
Banani | 36 | 00:00 | Juldah | 30 | 00:00 | Rajshahi | 145 | 00:00
Bangabhaban | 10 | 11:00 | Kabirpur | 171 | 01:00 | Rajshahi | 28 | 22:00
Barapukuria | 51 | 22:00 | Kachua | 86 | 23:00 | Ramganj | 120 | 18:30
Barguna | 22 | 22:00 | Kallyanpur | 93 | 01:00 | Rampur | 17 | 00:00
Barishal | 108 | 21:00 | Kalurghat | N/A | N/A | Rangamati | 12 | 18:30
Barishal | 70 | 23:00 | Kamrangirchar | 52 | 00:00 | Rangpur | 89 | 21:00
Baroaulia | 59 | 00:00 | Kaptai | 4.4 | 18:30 | Ruppur | 3.2 | 00:00
Baroirhat | 67 | 21:00 | Kazla | 73 | 00:00 | Saidpur | 44 | 22:00
Bashundhara | 144 | 00:00 | Keranigonj | 66 | 01:00 | Satkhira | 130 | 20:00
BashundharaCement | 12 | 00:00 | Khagrachori | 26 | 18:00 | Satmasjid | 86 | 19:00
Beanibazar | 52 | 19:00 | Khulna | 96 | 21:00 | Savar | 127 | 02:00
Benapole | 68 | 19:00 | Khulshi | 171 | 01:00 | Shahjadpur | 108 | 19:30
Bhaluka | 106 | 18:00 | Kishoreganj | 148 | 22:00 | Shahjibazar | 113 | 21:00
Bhandaria | 65 | 21:00 | Kodda | 196 | 15:00 | Shahmirpur | 31 | 22:00
Bhangura | 38 | 21:00 | KSRM | 0.5 | 00:00 | Shariatpur | 76 | 20:00
Bheramara(GK) | 59 | 22:00 | Kulaura | 48 | 00:00 | Sherpur | 96 | 19:00
Bhulta | 229 | 15:00 | Kurigram | 40 | 19:00 | Shikalbaha | 34 | 19:30
Bog-Sherpur | 44 | 23:00 | Kushtia | 132 | 21:00 | Shitalakhya | 104 | 12:00
Bogura | 100 | 20:00 | Lalbag | 52 | 00:00 | Sholosohor | N/A | N/A
Borhanuddin | 48 | 21:00 | Lalmonirhat | 31 | 18:30 | Shyampur | 124 | 00:00
Brahmanbaria | 190 | 00:00 | Madanganj | 160 | 14:00 | Siddhirganj | 92 | 00:00
BSRM | 165 | 04:00 | Madaripur | 106 | 19:00 | Sirajganj | 85 | 19:30
Cantonment | 117 | 19:00 | Madartek | 74 | 00:00 | Sonargaon | 66 | 00:00
Chandpur | 75 | 00:00 | Madunaghat | 60 | 19:00 | Sreemongol | 56 | 19:00
Chandraghona | 32 | 19:00 | Magura | 63 | 21:00 | Srinagar | 52.44 | 00:00
Chapai | 61 | 00:00 | Mahasthangarh | 46 | 22:00 | SSM | 4 | 03:00
Charsaidpur | 26 | 17:00 | Manikganj | 86 | 21:00 | Sunamganj | 38 | 19:30
Chauddagram | 68 | 23:00 | Maniknagar | 63 | 13:00 | Sylhet | 124 | 23:00
Chhatak | 20 | 21:00 | Matarbari | 41 | 19:30 | Tangail | 192 | 22:00
Chowmuhani | 210 | 21:00 | Matuail | 48 | 01:00 | Thakurgaon | 27 | 00:00
Chuadanga | 113 | 21:00 | Millgate | 40 | 10:00 | TK | 30.3 | 21:00
Coxsbazar | 120 | 23:00 | Mirpur | 108 | 00:00 | Tongi | 115 | 03:00
Cumilla(N) | 167 | 21:00 | Mirsorai | N/A | N/A | Ullon | 42 | 21:00
Cumilla(S) | 167 | 00:00 | Mithapukur | 40 | 19:30 | Uttara | 76 | 13:00
Daudkandi | 136 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 15 | 00:00
Dhaka | 24 | 13:00 | Mogbazar | 98 | 14:00 | Zigatola | 44 | 00:00
Dhamrai | 94 | 21:00 | Mongla | 40 | 12:00
Dhanmondi | 148 | 13:00 | Motijheel | 30 | 00:00
Dohazari | 100 | 21:00 | Munshiganj | 110 | 03:00
Faridpur | 113 | 15:00 | Mymensingh | 188 | 18:30
Fatullah | 51 | 00:00 | Naogaon | 90 | 21:00
Fenchuganj | 45 | 21:00 | Narail | 57 | 19:30
Feni | 135 | 00:00 | Narinda | 53 | 14:00
Ghorashal | 42 | 03:00 | Narshingdi | 164 | 23:00
Goalpara | 28 | 21:00 | Natore | 126 | 21:00
Gollamari | 52 | 19:30 | Nawabganj | 55.6 | 21:00
Gopalganj | 105 | 21:00 | Netrakona | 102 | 19:00
GPH | 91 | 05:00 | New | 58 | 00:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-04-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 18:30 | 399 | 22:00 | Kaliakoir | 395 | 0.20833 | 378 | 0.45833
| Bheramara | 419 | 8:00 | 395 | 16:00 | Bhulta | 400 | 0.77083 | 379 | 0.45833
| Ashuganj(N) | 402 | 18:30 | 385 | 11:00 | Gopalganj | 420 | 0.625 | 406 | 0.875
| Payra | 423 | 6:00 | 413 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 232 | 16:00 | 217 | 11:00
| Ishurdi | 236 | 6:00 | 226 | 20:00 | Megnaghat | 230 | 18:30 | 225 | 11:00
| Ashuganj | 240 | 19:00 | 230 | 10:00 | Fenchuganj | 240 | 13:00 | 236 | 24:00
| Serajganj | 236 | 3:00 | 230 | 24:00 | Siddhirganj | 226 | 18:30 | 223 | 2:00
| Baghabari | 234 | 3:00 | 228 | 22:00 | Maniknagar | 228 | 18:30 | 217 | 11:00
| Barapukuria | 236 | 1:00 | 221 | 24:00 | Agargaon | 227 | 24:00 | 215 | 11:00
| Bogra | 232 | 1:00 | 224 | 2:00 | Barisal | 244 | 24:00 | 232 | 15:00
| Rajshahi | 236 | 2:00 | 219 | 24:00 | Bhola 225 MW | 247 | 24:00 | 232 | 15:00
| Khulna South | 236 | 5:00 | 222 | 20:00 | AKSML
| Rampura | 226 | 19:00 | 219 | 11:00 | BSRM | 231 | 18:30 | 216 | 11:00
| Haripur | 226 | 19:00 | 219 | 10:00 | Bibiyana | 239 | 7:00 | 232 | 11:00
| Hasnabad | 226 | 18:30 | 215 | 11:00 | Bhulta | 229 | 18:30 | 219 | 11:00
| Shyampur | 225 | 19:00 | 215 | 11:00 | Ashuganj (S) | 236 | 18:30 | 226 | 11:00
| Aminbazar | 225 | 1:00 | 218 | 2:00 | Kaliakoir | 229 | 18:30 | 217 | 11:00
| Tongi | 230 | 7:00 | 220 | 11:00 | GPH | 232 | 18:30 | 217 | 11:00
| Comilla (N) | 231 | 18:30 | 218 | 11:00 | Jhenaidah | 235 | 6:00 | 216 | 19:30
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 03:00 | 130 | 10:00 | Manikganj | 136 | 18:30 | 126 | 00:00
| Agargaon | 135 | 18:30 | 128 | 11:00 | Maniknagar | 136 | 19:30 | 130 | 11:00
| Agrabad | 130 | 14:00 | 123 | 10:00 | Matarbari | 121 | 03:00 | 107 | 11:00
| AKS | 134 | 00:00 | 119 | 18:00 | Matuail | 133.6 | 22:00 | 129.7 | 10:00
| Aminbazar | 135 | 00:00 | 129 | 10:00 | Millgate | 138 | 19:30 | 133 | 00:00
| Amnura | 132 | 02:00 | 121 | 01:00 | Mirpur | 136 | 18:30 | 127 | 11:00
| Ashuganj | 137 | 00:00 | 134 | 11:00 | Mithapukur | 141 | 03:00 | 128 | 18:00
| Bagerhat | 138 | 23:00 | 127 | 20:00 | Modern | 131 | 18:30 | 124 | 09:00
| Bakulia | 130 | 03:00 | 122 | 11:00 | Mogbazar | 135 | 00:00 | 130 | 11:00
| Banani | 137 | 18:30 | 132 | 00:00 | Mongla | 138 | 23:00 | 126 | 21:00
| Bangabhaban | 137 | 18:30 | 129 | 11:00 | Motijheel | 136 | 18:30 | 129 | 11:00
| Barapukuria | 140 | 01:00 | 130 | 23:00 | Munshiganj | 139 | 18:30 | 127 | 11:00
| Barguna | 138 | 06:00 | 128 | 21:00 | Mymensingh | 136 | 03:00 | 124 | 11:00
| Barishal | 137 | 05:00 | 127 | 16:00 | Naogaon | 140 | 02:00 | 126 | 23:00
| Barishal | 139 | 23:00 | 133 | 13:00 | Narail | 135 | 06:00 | 122 | 14:00
| Baroaulia | 138 | 08:00 | 123 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 129 | 12:00 | 123 | 05:00 | Narshingdi | 133 | 18:30 | 125 | 07:00
| Bashundhara | 138 | 19:30 | 130 | 11:00 | Natore | 135 | 02:00 | 128 | 13:00
| BashundharaCement | 138 | 18:30 | 129 | 10:00 | Nawabganj | 134 | 18:30 | 126 | 11:00
| Beanibazar | 138 | 01:00 | 129 | 22:00 | Netrakona | 136 | 00:00 | 123 | 11:00
| Benapole | 136 | 22:00 | 124 | 14:00 | New | 138 | 18:30 | 132 | 10:00
| Bhaluka | 135 | 00:00 | 121 | 11:00 | Niamatpur | 142 | 02:00 | 123 | 23:00
| Bhandaria | 141 | 23:00 | 126 | 19:30 | Noapara | 137 | 23:00 | 130 | 13:00
| Bhangura | 139 | 02:00 | 132 | 20:00 | Pabna | 137 | 06:00 | 130 | 17:00
| Bheramara | 137 | 06:00 | 132 | 13:00 | Palashbari | 140 | 02:00 | 126 | 23:00
| Bheramara(GK) | 137 | 04:00 | 132 | 21:00 | Panchagarh | 144 | 03:00 | 124 | 23:00
| Bhulta | 129 | 19:00 | 121 | 10:00 | Patuakhali | 138 | 07:00 | 131 | 20:00
| Bog-Sherpur | 140 | 00:00 | 130 | 23:00 | PHP | 129 | 13:00 | 122 | 05:00
| Bogura | 142 | 02:00 | 131 | 22:00 | Purbachal | 137 | 18:30 | 131 | 10:00
| Bogura | 142 | 02:00 | 131 | 23:00 | Purbasadipur | 144 | 01:00 | 126 | 22:00
| Brahmanbaria | 133 | 08:00 | 127 | 22:00 | Rahim | 136 | 19:00 | 130 | 10:00
| Cantonment | 134 | 18:30 | 128 | 11:00 | Rajbari | 136 | 06:00 | 129 | 14:00
| Chandpur | 130 | 07:00 | 125 | 17:00 | Rajendrapur | 138 | 19:00 | 128 | 03:00
| Chandraghona | 132 | 14:00 | 125 | 11:00 | Rajshahi | 132 | 02:00 | 124 | 13:00
| Chapai | 132 | 18:30 | 123 | 13:00 | Rajshahi | 131 | 02:00 | 123 | 14:00
| Charsaidpur | 139 | 19:00 | 129 | 11:00 | Ramganj | 127 | 09:00 | 122 | 00:00
| Chauddagram | 130 | 08:00 | 124 | 13:00 | Rampur | 134 | 00:00 | 121 | 11:00
| Chhatak | 135 | 07:00 | 130 | 16:00 | Rampura | 135 | 18:30 | 129 | 13:00
| Chowmuhani | 127 | 08:00 | 120 | 00:00 | Rangamati | 132 | 16:00 | 124 | 11:00
| Chuadanga | 133 | 06:00 | 119 | 14:00 | Rangpur | 141 | 02:00 | 126 | 23:00
| Coxsbazar | 114 | 12:00 | 101 | 23:00 | Ruppur | 136 | 04:00 | 131 | 20:00
| Cumilla(N) | 133 | 18:30 | 128 | 11:00 | Saidpur | 140 | 01:00 | 126 | 23:00
| Cumilla(S) | 133 | 05:00 | 127 | 14:00 | Satkhira | 138 | 22:00 | 126 | 20:00
| Daudkandi | 133 | 19:30 | 125 | 11:00 | Satmasjid | 134 | 18:30 | 128 | 11:00
| Dhaka | 136 | 18:30 | 130 | 10:00 | Savar | 138 | 19:30 | 126 | 11:00
| Dhamrai | 138 | 18:30 | 131 | 11:00 | Shahjadpur | 142 | 00:00 | 135 | 16:00
| Dhanmondi | 136 | 18:30 | 128 | 11:00 | Shahjibazar | 135 | 04:00 | 132 | 00:00
| Dohazari | 126 | 18:00 | 116 | 11:00 | Shahmirpur | 131 | 14:00 | 121 | 11:00
| Faridpur | 136 | 05:00 | 130 | 13:00 | Shariatpur | 138 | 05:00 | 129 | 01:00
| Fatullah | 136 | 18:30 | 129 | 10:00 | Sherpur | 138 | 14:00 | 123 | 11:00
| Fenchuganj | 138 | 06:00 | 134 | 00:00 | Shikalbaha | 133 | 18:30 | 123 | 10:00
| Feni | 130 | 18:30 | 124 | 13:00 | Shikalbaha | 130 | 03:00 | 123 | 11:00
| Ghorashal | 139 | 18:00 | 135 | 10:00 | Shitalakhya | 138 | 18:30 | 128.3 | 11:00
| Goalpara | 139 | 05:00 | 133 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 139 | 06:00 | 132 | 14:00 | Shyampur | 134 | 18:00 | 128 | 12:00
| Gopalganj | 139 | 23:00 | 131 | 15:00 | Shyampur | 134 | 19:00 | 127 | 11:00
| Gopalganj_I | 139 | 05:00 | 134 | 00:00 | Siddhirganj | 136 | 18:30 | 129 | 11:00
| Gulshan | 135 | 19:30 | 129 | 11:00 | Sirajganj | 141 | 03:00 | 130 | 00:00
| Halishahar | 133 | 03:00 | 122 | 11:00 | Sonargaon | 134 | 00:00 | 129 | 08:00
| Haripur | 136 | 19:00 | 130 | 09:00 | Sreemongol | 136 | 03:00 | 132 | 11:00
| HaripurSBU | 137 | 18:30 | 129 | 11:00 | Srinagar | 134 | 18:30 | 127 | 11:00
| Hasnabad | 135 | 00:00 | 130 | 10:00 | SSM | 133 | 00:00 | 122 | 11:00
| Hathazari | 134 | 14:00 | 127 | 11:00 | Sunamganj | 136 | 01:00 | 128 | 21:00
| Ishurdi | 137 | 06:00 | 132 | 14:00 | Sylhet | 136 | 01:00 | 132 | 11:00
| Jaldhaka | 143 | 01:00 | 124 | 23:00 | Tangail | 136 | 00:00 | 129 | 11:00
| Jamalpur | 140 | 14:00 | 125 | 10:00 | Thakurgaon | 144 | 01:00 | 125 | 22:00
| Jashore | 137 | 22:00 | 125 | 14:00 | TK | 130 | 03:00 | 123 | 11:00
| Jhenaidah | 137 | 22:00 | 126 | 13:00 | Tongi | 138 | 13:00 | 134 | 16:00
| Jhenaidah | 136 | 18:30 | 127 | 14:00 | Ullon | 136 | 18:30 | 128 | 11:00
| Joydebpur | 141 | 18:30 | 133 | 05:00 | Uttara | 135 | 22:00 | 126 | 11:00
| Joypurhat | 142 | 01:00 | 126 | 00:00 | UttaraNew | 135 | 18:00 | 126 | 11:00
| Juldah | 133 | 18:30 | 122 | 10:00 | Zigatola | 133 | 18:30 | 128 | 11:00
| Kabirpur | 135 | 01:00 | 130 | 01:00
| Kachua | 130 | 08:00 | 125 | 17:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 137 | 18:30 | 129 | 11:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 135 | 18:30 | 128 | 11:00
| Kaptai | 137 | 23:00 | 126 | 16:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-04-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 486 | 7123 | 3226 | 10349 |  |  |  | QF-LDC-11
0:30 | 433 | 6886.5 | 2952.5 | 9839 | Date: | 2022-04-30
1:00 | 380 | 6650 | 2679 | 9329
1:30 | 515 | 6525 | 2638 | 9163
2:00 | 650 | 6400 | 2597 | 8997
2:30 | 544 | 6376.5 | 2600.5 | 8977 | [5 empty] | Gen. at Eve. Peak | 11464 | 11464 MW (21:00 )
3:00 | 438 | 6353 | 2604 | 8957 | [6 empty] | 21:00
3:30 | 519 | 6226 | 2615.5 | 8841.5 | [5 empty] | Gen. at Day Peak | 9186 | 9186 MW (12:00 )
4:00 | 600 | 6099 | 2627 | 8726 | [6 empty] | 12:00
4:30 | 687 | 5753.5 | 2645.5 | 8399 | [5 empty] | Highest Generation | 11464
5:00 | 774 | 5408 | 2664 | 8072 | [6 empty] | 21:00
5:30 | 767 | 5316.5 | 2595.5 | 7912
6:00 | 760 | 5225 | 2527 | 7752
6:30 | 690 | 5210.5 | 2507 | 7717.5
7:00 | 620 | 5196 | 2487 | 7683
7:30 | 614 | 5227 | 2495.5 | 7722.5
8:00 | 608 | 5258 | 2504 | 7762
8:30 | 590 | 5371 | 2495.5 | 7866.5
9:00 | 572 | 5484 | 2487 | 7971
9:30 | 594 | 5587.5 | 2602 | 8189.5
10:00 | 616 | 5691 | 2717 | 8408
10:30 | 635 | 5780 | 2755.5 | 8535.5
11:00 | 654 | 5869 | 2794 | 8663
11:30 | 612 | 6032.5 | 2892 | 8924.5
12:00 | 570 | 6196 | 2990 | 9186
12:30 | 548 | 6407.5 | 3038.5 | 9446
13:00 | 526 | 6619 | 3087 | 9706
13:30 | 439 | 6719 | 3210.5 | 9929.5
14:00 | 352 | 6819 | 3334 | 10153
14:30 | 348 | 6861 | 3325 | 10186
15:00 | 344 | 6903 | 3316 | 10219
15:30 | 356 | 6822.5 | 3304 | 10126.5
16:00 | 368 | 6742 | 3292 | 10034
16:30 | 413 | 6619.5 | 3342.5 | 9962
17:00 | 458 | 6497 | 3393 | 9890
17:30 | 458 | 6523.5 | 3435.5 | 9959
18:00 | 458 | 6550 | 3478 | 10028
18:30 | 275 | 6894.5 | 3631 | 10525.5
19:00 | 92 | 7239 | 3784 | 11023
19:30 | 104 | 7370 | 3791 | 11161
20:00 | 158 | 7301 | 3735 | 11036 |  |  |  | Executive Engineer
20:30 | 220 | 7377 | 3873 | 11250 |  |  |  | Network Operation Division
21:00 | 282 | 7453 | 4011 | 11464
21:30 | 376 | 7398.5 | 3961 | 11359.5
22:00 | 470 | 7344 | 3911 | 11255 |  |  |  |  | Page 6 of 7
22:30 | 469 | 7335 | 3697.5 | 11032.5
23:00 | 468 | 7326 | 3484 | 10810
23:30 | 477 | 7224.5 | 3355 | 10579.5
24:00 | 486 | 7123 | 3226 | 10349
11464 MW (21:00 )
9186 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-04-30 |  | Energy |  | 230740426
[13 empty] | 2022-04-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4300 | 924 | 2231 | 0 | 1679 | 800 | 35 | 250 | 146 | 114 | 0 | 0
0:30 | 3886.5 | 924.5 | 2113 | 0 | 1826.5 | 675.5 | 35 | 250 | 138 | 120 | 0 | 0 | Date: | 2022-04-30
1:00 | 3473 | 925 | 1995 | 0 | 1974 | 551 | 35 | 250 | 130 | 126 | 0 | 0
1:30 | 3513.5 | 924.5 | 1931 | 0 | 1844 | 541 | 35 | 250 | 130 | 124 | 0 | 0 | [8 empty] | Total Energy | 230.7404 | Total Energy Gen 230.740 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.740 MKWHr
2:00 | 3554 | 924 | 1867 | 0 | 1714 | 531 | 35 | 250 | 130 | 122 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3588.5 | 924 | 1871 | 0 | 1660 | 526.5 | 35 | 250 | 130 | 122 | 0 | 0 | [8 empty] | Energy Requirement | 230.7404
3:00 | 3623 | 924 | 1875 | 0 | 1606 | 522 | 35 | 250 | 130 | 122 | 0 | 0
3:30 | 3602.5 | 924 | 1866 | 0 | 1518.5 | 522.5 | 35 | 250 | 130 | 123 | 0 | 0 | [6 empty] | Shortage
4:00 | 3582 | 924 | 1857 | 0 | 1431 | 523 | 35 | 250 | 130 | 124 | 0 | 0
4:30 | 3578.5 | 924 | 1786 | 0 | 1205.5 | 514 | 35 | 250 | 130 | 106 | 0 | 0
5:00 | 3575 | 924 | 1715 | 0 | 980 | 505 | 35 | 250 | 130 | 88 | 0 | 0
5:30 | 3537 | 924.5 | 1681.5 | 0 | 896 | 496 | 35 | 250 | 131 | 87 | 4 | 0
6:00 | 3499 | 925 | 1648 | 0 | 812 | 487 | 35 | 250 | 132 | 86 | 8 | 0
6:30 | 3439 | 924.5 | 1648 | 0 | 810.5 | 487 | 35 | 250 | 147 | 87 | 19.5 | 0 |  |  |  |  | Coal
7:00 | 3379 | 924 | 1648 | 0 | 809 | 487 | 35 | 250 | 162 | 88 | 31 | 0
7:30 | 3391.5 | 924.5 | 1633.5 | 0 | 844.5 | 474 | 35 | 250 | 154 | 89 | 56.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3404 | 925 | 1619 | 0 | 880 | 461 | 35 | 250 | 146 | 90 | 82 | 0
8:30 | 3470 | 925 | 1628.5 | 0 | 899 | 440.5 | 35 | 250 | 146 | 93 | 109.5 | 0
9:00 | 3536 | 925 | 1638 | 0 | 918 | 420 | 35 | 250 | 146 | 96 | 137 | 0
9:30 | 3604 | 925 | 1772 | 0 | 920.5 | 420 | 35 | 250 | 146 | 92 | 155 | 0
10:00 | 3672 | 925 | 1906 | 0 | 923 | 420 | 35 | 250 | 146 | 88 | 173 | 0
10:30 | 3744.5 | 925 | 1975.5 | 0 | 918.5 | 422 | 35 | 250 | 146 | 93 | 156 | 0
11:00 | 3817 | 925 | 2045 | 0 | 914 | 424 | 35 | 250 | 146 | 98 | 139 | 0
11:30 | 3869 | 925 | 1980.5 | 0 | 1087 | 497 | 35 | 254.5 | 150.5 | 103 | 157.5 | 0
12:00 | 3921 | 925 | 1916 | 0 | 1260 | 570 | 35 | 259 | 155 | 108 | 176 | 0
12:30 | 3896 | 924 | 1935.5 | 0 | 1485 | 615 | 35 | 254.5 | 150.5 | 108 | 177 | 0
13:00 | 3871 | 923 | 1955 | 0 | 1710 | 660 | 35 | 250 | 146 | 108 | 178 | 0
13:30 | 3871 | 923 | 1955 | 0 | 1710 | 660 | 35 | 250 | 146 | 108 | 178 | 0
14:00 | 3871 | 923 | 1955 | 0 | 1710 | 660 | 35 | 250 | 146 | 108 | 178 | 0
14:30 | 3897.5 | 923 | 1933 | 0 | 1927.5 | 729.5 | 34 | 250 | 146 | 109 | 143 | 0
15:00 | 3924 | 923 | 1911 | 0 | 2145 | 799 | 33 | 250 | 146 | 110 | 108 | 0
15:30 | 3904 | 924 | 1908.5 | 0 | 2066.5 | 829 | 33 | 250 | 146 | 104 | 91.5 | 0
16:00 | 3884 | 925 | 1906 | 0 | 1988 | 859 | 33 | 250 | 146 | 98 | 75 | 0
16:30 | 3933 | 924.5 | 1983 | 0 | 1823 | 874 | 33.5 | 250 | 146 | 100 | 49.5 | 0
17:00 | 3933 | 924 | 2060 | 0 | 1658 | 889 | 34 | 250 | 146 | 102 | 24 | 0
17:30 | 3918.5 | 924 | 2072 | 0 | 1698.5 | 924 | 34.5 | 250 | 151 | 103 | 13.5 | 0
18:00 | 3904 | 924 | 2084 | 0 | 1739 | 959 | 35 | 250 | 156 | 104 | 3 | 0
18:30 | 3790 | 924.5 | 2061.5 | 0 | 2242 | 974 | 35 | 250 | 270 | 107 | 1.5 | 0
19:00 | 3676 | 925 | 2039 | 0 | 2745 | 989 | 35 | 250 | 384 | 110 | 0 | 0
19:30 | 3829 | 924 | 2177 | 0 | 2711 | 999 | 35 | 250 | 256 | 110 | 0 | 0
20:00 | 3953 | 925 | 2235 | 0 | 2380 | 1059 | 35 | 250 | 219 | 110 | 0 | 0
20:30 | 4038 | 925 | 2304.5 | 0 | 2378.5 | 1114 | 35 | 250 | 219 | 116 | 0 | 0
21:00 | 4123 | 925 | 2374 | 0 | 2377 | 1169 | 35 | 250 | 219 | 122 | 0 | 0
21:30 | 4140 | 925 | 2323.5 | 0 | 2312 | 1164 | 35 | 250 | 219 | 121 | 0 | 0
22:00 | 4157 | 925 | 2273 | 0 | 2247 | 1159 | 35 | 250 | 219 | 120 | 0 | 0
22:30 | 4256.5 | 924.5 | 2248.5 | 0 | 2054.5 | 1064.5 | 35 | 250 | 208 | 121 | 0 | 0
23:00 | 4356 | 924 | 2224 | 0 | 1862 | 970 | 35 | 250 | 197 | 122 | 0 | 0
23:30 | 4328 | 924 | 2227.5 | 0 | 1770.5 | 885 | 35 | 250 | 171.5 | 118 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35° C
24:00 | 4300 | 924 | 2231 | 0 | 1679 | 800 | 35 | 250 | 146 | 114 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 230.740 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.740 MKWHr
Note on W13: Author:

## Generation
g | 2022-04-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 33 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 106632
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 9 | 12 | 16 | 8 | 18 | 17 | 15 | 11 | 7 | 2 | 0 | [8 empty] | 123390
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 202 | 203 | 204 | 203 | 203 | 217 | 203 | 224 | 210 | 203 | 203 | 203 | 203 | 218 | 212 |  | 203 | 203 | 209 | 215 | 203 | 203 | 203 | 4889433
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 273319
12 | Hathazari 100 MW peaking PP | [19 empty] | 10 | 0 | [5 empty] | 10032
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 17 | 0 |  |  |  |  | 0 | 17 | 34 | 30 | 68 | 68 | 34 | 34 |  | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 1110686
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [15 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 92 | 300 | 300 | 543637
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 30 | 15 | 0 | [7 empty] | 0 | 11 | 15 | 72 | 110 | 110 | 110 |  | 160 | 145 | 95 | 95 | 15 | 15 | 0 | 1159199
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 267636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 180 | 180 | 180 | 180 | 150 | 149 | 150 | 150 | 230 | 230 | 231 | 230 | 230 | 230 | 231 | 231 |  | 180 | 200 | 233 | 233 | 234 | 234 | 235 | 4821000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 250 | 260 | 270 | 270 | 270 | 270 | 270 |  | 210 | 260 | 270 | 270 | 270 | 270 | 270 | 5791500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 24 | 25 | 25 | 28 | 28 | 27 | 27 | 24 | 21 | 27 |  | 27 | 27 | 28 | 31 | 31 | 31 | 31 | 613368
33 | Ashuganj 225 MW CCPP | 182 | 186 | 181 | 181 | 182 | 181 | 181 | 182 | 208 | 187 | 213 | 182 | 181 | 183 | 184 | 183 | 204 | 198 |  | 188 | 182 | 190 | 199 | 183 | 182 | 182 | 4537000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 295 | 280 | 280 | 280 | 280 | 280 | 280 | 325 | 350 | 280 | 280 | 280 | 310 | 310 | 310 | 340 | 325 |  | 280 | 270 | 310 | 335 | 310 | 310 | 310 | 7525900
35 | Ashuganj 55 MW PP (Precision) | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 53 | 52 | 52 | 52 | 51 | 51 | 52 |  | 52 | 52 | 52 | 53 | 54 | 55 | 55 | 1285920
36 | Chandpur 150 MW CCPP | 137 | 137 | 135 | 137 | 137 | 136 | 137 | 137 | 135 | 137 | 137 | 137 | 137 | 137 | 137 | 136 | 135 | 135 |  | 136 | 136 | 136 | 134 | 136 | 137 | 136 | 3256470
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 385 | 377 | 370 | 339 | 334 | 310 | 305 | 309 | 320 | 335 | 380 | 398 | 352 | 386 | 396 | 377 | 377 | 377 |  | 348 | 385 | 367 | 399 | 398 | 397 | 373 | 8837120
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7557850
41 | Haripur 360MW CCPP(HPL) | 325 | 300 | 300 | 300 | 300 | 251 | 251 | 254 | 257 | 286 | 322 | 271 | 271 | 321 | 171 | 193 | 213 | 272 |  | 242 | 275 | 334 | 343 | 342 | 332 | 332 | 6828000
42 | RPCL 210MW CCPP | 161 | 162 | 163 | 163 | 162 | 165 | 164 | 163 | 157 | 157 | 156 | 157 | 162 | 177 | 187 | 188 | 187 | 185 |  | 198 | 210 | 204 | 209 | 213 | 211 | 211 | 4147200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 5 | 20 | 39 | 48 | 37 | 47 | 50 | 30 | 36 | 21 | 4 | 1 |  | 0 | [6 empty] | 321250
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 671064
46 | Shajibazar 330 MW CCPP | 159 | 160 | 159 | 158 | 159 | 160 | 160 | 158 | 157 | 156 | 150 | 155 | 153 | 152 | 153 | 156 | 153 | 156 |  | 158 | 160 | 157 | 158 | 156 | 157 | 157 | 3723000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 40 | 40 | 40 | 40 | 40 | 50 | 60 |  | 40 | 40 | 45 | 56 | 57 | 57 | 55 | 1141920
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 70 | 84 | 84 | 84 | 84 | 84 | 1073280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 158 | 158 | 158 | 159 | 159 | 160 | 159 | 159 | 160 | 220 | 218 | 218 | 219 | 219 | 219 | 219 | 192 | 192 |  | 192 | 219 | 219 | 219 | 219 | 219 | 219 | 4577500
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [17 empty] | 10 |  | 16 | 16 | 16 | 16 | 16 | 17 | 20 | 105980
53 | Sylhet 10MW PP (Desh) | [11 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 131040
54 | Hobiganj 11MW PP Cofidence-E |  |  | 11 | [16 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 87800
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 0 | [15 empty] | 16 | 16 | 17 | 17 | 17 | 28 | 48 | 165600
56 | Shahjahanulla 25 MW PP | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 111984
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 285 | 280 | 275 | 280 | 280 | 280 | 275 | 305 | 300 | 280 | 270 | 280 | 280 | 270 | 300 | 295 |  | 265 | 285 | 290 | 310 | 270 | 265 | 275 | 7050500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 385 | 396 | 393 | 396 | 398 | 400 | 360 | 360 | 360 | 360 |  | 400 | 400 | 400 | 400 | 401 | 400 | 400 | 8870800
58 | Nababganj 55 MW PP (Southern power ) | 17 | [10 empty] | 35 | 35 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 603616
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | [6 empty] | 0 | 0 | 12 | 17 | 19 | 19 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 366960
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 474768
61 | Narshingdi 22 MW PP (Doreen) |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 |  | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 403272
62 | Tangail 22 MW PP (Doreen) | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 192852
63 | Impoprt (Tripura) | 126 | 122 | 122 | 124 | 88 | 86 | 88 | 90 | 96 | 88 | 98 | 108 | 108 | 116 | 110 | 98 | 102 | 104 |  | 110 | 110 | 110 | 122 | 120 | 122 | 114 | 2601600
64 | Malancha, Ctg. EPZ (United) | 42 | 37 | 40 | 42 | 42 | 42 | 42 | 32 | 32 | 32 | 24 | 32 | 38 | 38 | 38 | 40 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 920160
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 443736
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 |  | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 207360
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 32 | 32 | 32 | 32 | 32 | 0 |  | 31 | 31 | 33 | 33 | 33 | 21 | 14 | 702900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 20 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 430440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 27 | 27 | 27 | 27 | 25 | 25 | 21 | 23 | 23 | 23 | 23 | 25 | 25 | 23 | 23 | 25 | 25 |  | 18 | 24 | 27 | 27 | 27 | 27 | 27 | 556200
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 731400
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 101 | 14 | 14 | 13 | 13 | 12 | 12 | 29 | 77 | 95 | 96 | 99 | 100 | 100 | 101 |  | 101 | 101 | 101 | 101 | 98 | 98 | 100 | 1738590
| Feni Lanka Power | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 51 | 51 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1867320
| Chowmuhani 113 MW | 61 | 62 | 59 | 57 | 57 | 57 | 57 | 57 | 57 | 61 | 57 | 57 | 58 | 57 | 57 | 57 | 107 | 114 |  | 114 | 114 | 114 | 114 | 114 | 113 | 100 | 1830360
| Manikgonj 162MW PP(MPGL) | 72 | 17 | 17 | 17 | [7 empty] | 17 | 54 | 66 | 108 | 108 | 54 | 54 |  | 134 | 162 | 162 | 162 | 162 | 126 | 90 | 1575360
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 0 | 7 |  | 30 | 7 | 0 |  |  |  | 0 | 47040
78 | Gazipur 52 MW PP | 7 | 16 |  |  |  |  | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 |  | 24 | 8 | 8 | 12 | 24 | 24 | 25 | 409440
79 | Kodda 150MW PP | [5 empty] | 2 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 350400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 26 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 25 | 25 |  | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 905611
| Gazipur 100 MW PP | 70 | 70 | 70 | 17 | 17 | 17 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 50 | 50 | 50 | 50 | 35 | 1502400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 4 | 4 | 4 | 2 | 2 | 0 | [9 empty] | 32039
| Jodiac Power | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 48 | 54 | 54 | 50 | 50 | 48 | 48 | 961696
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 42 | 68 | 54 | 68 | 68 | 51 | 51 |  | 65 | 68 | 68 | 68 | 68 | 68 | 68 | 1527193
82 | Madanganj 102 PP(Summit) | 70 | 70 | 94 | 94 | 94 | 80 | 80 | 78 | 78 | 78 | 78 | 90 | 90 | 90 | 92 | 92 | 92 | 92 |  | 94 | 91 | 96 | 96 | 96 | 96 | 90 | 1575360
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 140 | 130 | 120 | 125 | 130 | 130 | 135 | 120 | 140 | 138 | 132 | 125 | 130 | 130 | 122 | 126 | 130 | 140 |  | 135 | 120 | 140 | 140 | 125 | 135 | 140 | 3180858
87 | Meghnaghat 100 MW(IEL) | 49 | 20 | 7 | 7 | [7 empty] | 1 | 38 | 23 | 31 | 31 | 31 | 31 |  | 59 | 80 | 78 | 80 | 88 | 97 | 59 | 745920
| Meghnaghat 104 MW PP (OPCL) | 17 | [10 empty] | 17 | 17 | 24 | 35 | 17 | 17 | 17 |  | 76 | 89 | 34 | 17 | 17 | 17 | 17 | 408000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 20 | 0 |  |  |  |  | 0 | 25080
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | [16 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 135504
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 913832
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 | [9 empty] | 3 | 32 | 32 | 32 | 7 | 7 | 24 |  | 70 | 93 | 16 | 16 | 16 | 16 | 16 | 340416
95 | Patenga 50MW PP (Baraka) | 37 | 30 | 18 | 6 | [13 empty] | 5 |  | 21 | 36 | 34 | 37 | 30 | 12 | 12 | 261600
96 | Chattogram 108 MW PP (ECPV) | 83 | 93 | 91 | 88 | 49 | 24 | 11 | 11 | 11 | 11 | 11 | 14 | 54 | 50 | 56 | 57 | 50 | 52 |  | 74 | 80 | 95 | 95 | 94 | 15 | 6 | 1210560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [11 empty] | 25 | 41 | 15 | 15 | 15 |  | 25 | 15 | 15 | 15 | 15 | 15 | 15 | 258060
100 | Manikganj 55 MW PP (Northern) | 17 | [10 empty] | 6 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 585769
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 163 | 130 | 130 | 130 | 3129463
102 | Sarishabari 3 MW Solar Plant | [8 empty] | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 13300
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 17 | 17 | 17 |  |  | 0 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 801360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 2 | 40 | 58 | 70 | 45 | 45 | 50 |  | 100 | 100 | 45 | 45 | 45 | 45 | 45 | 705600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 16 | 0 |  |  |  | 23 | 101 | 114 | 115 | 115 | 114 | 115 | 114 | 115 | 115 | 115 | 115 |  | 127 | 80 | 92 | 55 | 49 | 14 | 0 | 1658450
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 70 | 70 | 50 | 50 | 50 | 50 | 50 | 76 | 76 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1908480
116 | Chandpur 200MW (Desh energy) | 85 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 41 | 34 | 34 | 34 | 34 | 34 | 34 | 683040
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 11 |  | 50 | 50 | 10 | 10 | 0 |  | 0 | 138836
118 | Bibiyana-III 400 MW CCPP | 304 | 328 | 399 | 401 | 401 | 400 | 352 | 352 | 352 | 401 | 404 | 378 | 378 | 378 | 365 | 367 | 370 | 383 |  | 366 | 365 | 413 | 400 | 367 | 367 | 367 | 8832000
| Jamalpur 115 MW PP (United) | [11 empty] | 13 | 40 | 64 | 97 | 97 | 55 | 55 |  | 108 | 108 | 115 | 115 | 115 | 115 | 115 | 1108800
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 260 | 260 | 230 | 230 | 230 | 230 | 230 | 282 | 300 | 300 | 300 | 300 | 245 | 180 |  | 180 | 190 | 192 | 190 | 190 | 190 | 240 | 6029345
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 66 | 0 | [6 empty] | 6 | 20 | 32 | 60 | 60 | 20 | 20 |  | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 780480
| Anlima Energy Ltd. | 112 | 113 | 113 | 111 | 60 | 17 | 17 | 17 | 17 | 17 | 17 | 57 | 80 | 51 | 68 | 68 | 34 | 34 |  | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 1333582
| Bhairob 54.5 MW | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 417600
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 10 | 23 | 27 | 32 | 30 | 30 | 20 | 18 | 8 | 2 | 0 | [8 empty] | 200718
| Chandpur 115(Doreen) | 77 | 80 | 77 | 80 | 80 | 78 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 17 | 17 | 17 |  | 28 | 35 | 45 | 50 | 50 | 50 | 50 | 1355520
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | [7 empty] | 13 | 55 | 55 | 55 | 28 | 0 | 4 |  | 0 |  |  | 19 | 55 | 35 | 35 | 642600
120 | Eastern Zone Total | 6650 | 6400 | 6353 | 6099 | 5408 | 5225 | 5196 | 5258 | 5484 | 5691 | 5869 | 6196 | 6619 | 6819 | 6903 | 6742 | 6497 | 6550 |  | 7239 | 7370 | 7301 | 7453 | 7344 | 7326 | 7123 | 154721556
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 20 |  | 66 | 16 | [5 empty] | 79680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2992320
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 10 | 17 |  | 91 | 91 | 53 | 53 | 17 |  |  | 286560
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 16 | 40 | 56 | 73 | 50 | 70 | 72 | 46 | 36 | 35 | 16 | 2 |  | 0 | [6 empty] | 560880
131
132 | United Payra Power Ltd. | 35 | 17 | 17 | 17 | 17 | 17 | [19 empty] | 0 | 140400
133 | Bhola Nutan Biddut BD LTD (GAS) | 165 | 135 | 134 | 156 | 155 | 135 | 135 | 130 | 130 | 180 | 210 | 195 | 180 | 196 | 208 | 188 | 213 | 211 |  | 211 | 205 | 218 | 219 | 210 | 182 | 152 | 4235973
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 16 | 16 | 16 | 16 | [12 empty] | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 309216
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 66 | 65 | 66 | 67 | 66 | 30 | 30 | 30 | 30 | 30 | 62 | 64 | 60 | 57 | 60 | 45 | 60 | 60 |  | 57 | 51 | 60 | 60 | 51 | 53 | 58 | 1277000
140 | Bhola 33 MW PP (Venture) | 36 | 39 | 38 | 38 | 37 | 33 | 30 | 28 | 26 | 25 | 27 | 27 | 31 | 31 | 32 | 30 | 28 | 31 |  | 38 | 38 | 38 | 39 | 38 | 38 | 38 | 797899
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 29625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 20 | 38 |  | 67 | 67 | 78 | 89 | 89 |  | 0 | 393984
146 | Bheramara HVDC | 925 | 924 | 924 | 924 | 924 | 925 | 924 | 925 | 925 | 925 | 925 | 925 | 923 | 925 | 923 | 925 | 924 | 924 |  | 925 | 924 | 925 | 925 | 925 | 924 | 924 | 22360000
147 | Bheramara 410 MW CCPP | 225 | 240 | 245 | 245 | 290 | 250 | 220 | 220 | 220 | 220 | 220 | 320 | 320 | 315 | 305 | 300 | 290 | 285 |  | 230 | 230 | 230 | 305 | 310 | 315 | 280 | 6075936
148 | Payra 1320 MW | 280 | 280 | 280 | 280 | 270 | 250 | 250 | 250 | 250 | 250 | 250 | 370 | 460 | 600 | 600 | 660 | 690 | 760 |  | 790 | 800 | 860 | 970 | 960 | 770 | 600 | 13354300
149
150 | Barapukuria TPP Unit-1 | 72 | 71 | 72 | 73 | 65 | 67 | 67 | 41 | 0 | [16 empty] | 0 | 602181
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 174 | 200 | 200 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 4589700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 2 | 4 | 5 | 5 | 3 | 4 | 3 | 1 | 0 | 0 | [8 empty] | 32940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 140 | 150 | 150 | 150 | 140 | 140 | 165 | 170 | 170 | 180 | 196 | 170 | 183 | 188 | 183 | 177 | 171 |  | 140 | 162 | 168 | 179 | 185 | 185 | 191 | 4379482
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 139 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3347036
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 264 | 240 | 242 | 241 | 254 | 255 | 254 | 254 | 258 | 420 | 419 | 321 | 320 | 388 | 340 | 340 | 414 | 360 |  | 328 | 414 | 360 | 414 | 414 | 385 | 382 | 7939600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [10 empty] | 22 | 16 | 20 | 20 | 21 | 20 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 260160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [12 empty] | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 119178
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 30 | 0 | [5 empty] | 19192
168 | Santahar 50 MW Peaking PP | [19 empty] | 37 | 37 | 0 |  |  |  |  | 47258
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 25 | 25 | 34 | 34 | 34 | 8 | 0 | 140640
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 10 |  | 46 | 22 | 22 | 22 | 22 | 0 |  | 130664
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 6 | 35 | 42 | 70 | 70 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 553056
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 16 | 35 | 70 | 70 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 517152
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 5 |  | 95 | 100 | 97 | 110 | 72 | 39 | 0 | 416572
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | [10 empty] | 0 | [8 empty] | 526
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 16 | 17 | 0 |  |  |  | 0 | 29760
178