## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-03 | Tuesday
|  |  | Date (day): | 2022-05-03 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14049.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15361 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-02 | 2022-05-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 212 | 230 | 230
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 230 | 252 | 230 | 280 | 85 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 104 | 70 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 366 | 397 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 202 | 327 | 340 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 400 | 340 | 400 | 50 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 77 | 90 | 90
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 280 | 220 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 10 | 78 | 78 | 78 |  | 24 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 10 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 96 | 96
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 335 | 300 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 84 | 84 |  | 18 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 32 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 26 | 25 | 25
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 280 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 35 | 35
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 1898 | 2559 | 4445 | 4615 | 586 | 588
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 90 | 100 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 37 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 35 | 35 | 35 |  | 195 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 203 | 200 | 200
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 42 | 42
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 91 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 100 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 34 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 23 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 34 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2282 | 592 | 1063 | 1546 | 1531 | 231 | 607
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 216 | 225 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 280 | 330 | 350 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 30 | 31 | 31 | 14 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 136 | 138 | 138 |  | 25 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 129 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 26 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 51 | 80 | 80 |  | 34 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 105 | 113 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 51 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 809 | 1254 | 1971 | 2064 | 824 | 119
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 200 | 210 | 200 | 200
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 16 | 140 | 190 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 115 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 27 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 24 | 24
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 261 | 506 | 597.6 | 546 | 0 | 18
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 20 | 20 | 20 |  | 50 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 40 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 | 220 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 53 | 53
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 50 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 60 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 81 | 81 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 178 | 218 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 25 | 25 | 25 | 25 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 17 | 17 | 17
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 270 | 310 | 310 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 327 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 374 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1382 | 1904 | 1972 | 1972 | 265 | 198
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 862 | 919 | 500 | 938
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 37 | 37 |  | 17 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 120 | 120 |  |  | Low demand
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 370 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1161 | 1357 | 1115 | 1513 | 509 | 74
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 26 | 39 | 33 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 76 | 80 | 75 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 480 | 800 | 500 | 900
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 164 | 200 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 746 | 1119 | 878 | 1499 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 8 | 36 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  | 50 | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 141 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 67 | 0 | 0 | 220 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 414 | 400 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 30 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 43 | 43
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 90 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 200 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 486 | 799 | 1177 | 1196 | 821 | 143
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Reserve
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 |  | 74 | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 37 | 110 | 110
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 30 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 205 | 237 | 348 | 425 | 0 | 179
|  | Total |  |  |  |  | 22348 | 21484 | 7540 | 10798 | 14049.6 | 15361 | 3344 | 1926
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7224.7626 | 10346.55 | 13462.2049 | 14718.777
| A. |  | 2022-05-02 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 10882 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 6408 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10798 | MW
| 3 | Day peak Generation : |  |  | 7540 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10346.55 | MW
| 4 | Evening peak Generation : |  |  | 10798 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 212.7579 | MKWHr | By Solar | 1.485 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 140.8785 | MKWHr |  | By Oil: | 25.9537 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.5626 | MKWHr |  | By Hydro: | 0.83924 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3344 | MW | Dhaka | 3018.75 | 3018.75 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1926 | MW | Chittagong | 1033.6 | 1033.6 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5270 | MW | Khulna | 1469 | 1469 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1129.65 | MMCFD |  |  | Rajshahi | 1176.2 | 1176.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 142304775.612 | ii) Oil : | Taka | 208375004.2 | Comilla | 1253 | 1253 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 95121423 | Total | Taka | 445801202.812 | Mymensingh | 959 | 959 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.577 | MKWHr. | Sylhet | 429 | 429 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -204 | MW (E to W) at | 21:00 | hrs | Barisal | 402 | 402 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -382 | MW at | 20:00 | hrs | Rangpur | 606 | 606 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 10346.55 | 10346.55 |  | 0
| B. |  | 2022-05-03 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15361 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 4700 | MW
| 4 | Reserve(Generation end) |  |  |  | 6161 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 179.8725 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6953 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.7455 | MKWHr. | ii) HVDC Flow at Peak Time |  | 919 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2934 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.56 |  | (b) Today: | 75.48 |  | (c) Rule Curve: |  | 81.62
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 220 | 0 | 270 | 101 | 0 | 350 | 302 |  | 0 | 340 | 270 | 0 | 64 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 20 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 203 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 18 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 214 | 8 | 136 | 31 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 32 | 20 | 120 | 192 | 0 | 17 | 0 | 0 | 42 | 25 | 5 | 130 | 110 | 55 | 40 | 0 | 218 | 0 | 6 | 10 | 260 | 17 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 25 | 0 | 90 | 68 | 0 | 402 | 108 | 90 | 0 | 0 | 300 | 54 | 107 | 80 | 60 | 10 | 400 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 59 | 17 |  | 924 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 37 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 720 | 216 | 0 | 0 | 0 | 0 | 34 |  | 6828 | 3448 | 10276 | 4276 | 924 | 2271 | 0 | 1481 | 919 | 35 | 250 | 130 | 120 | 0 | 0 | 75.58
2:00 | 0 | 0 | 170 | 0 | 230 | 12 | 0 | 360 | 302 |  | 0 | 340 | 255 | 0 | 48 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 181 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 18 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 212 | 8 | 137 | 31 | 50 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 118 | 211 | 0 | 17 | 0 | 0 | 42 | 11 | 5 | 130 | 110 | 55 | 40 | 0 | 204 | 0 | 6 | 10 | 270 | 17 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 0 | 90 | 68 | 0 | 402 | 108 | 90 | 0 | 0 | 300 | 54 | 106 | 80 | 60 | 10 | 340 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 59 | 17 |  | 923 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 38 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 560 | 150 | 0 | 0 | 0 | 0 | 34 |  | 6533 | 3002 | 9535 | 4047 | 923 | 1998 | 0 | 1405 | 759 | 35 | 250 | 130 | 118 | 0 | 0 | 75.57
3:00 | 0 | 0 | 170 | 0 | 230 | 12 | 0 | 354 | 303 |  | 0 | 340 | 260 | 0 | 48 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 137 | 31 | 52 | 0 | 10 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 120 | 192 | 0 | 17 | 0 | 0 | 42 | 11 | 5 | 130 | 110 | 55 | 40 | 0 | 178 | 0 | 6 | 10 | 260 | 11 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 0 | 90 | 68 | 0 | 240 | 108 | 90 | 0 | 0 | 260 | 54 | 110 | 80 | 58 | 10 | 330 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 59 | 0 |  | 923 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 38 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 520 | 152 | 0 | 0 | 0 | 0 | 34 |  | 6151 | 2955 | 9106 | 3784 | 923 | 1953 | 0 | 1322 | 719 | 35 | 250 | 130 | 120 | 0 | 0 | 75.57
4:00 | 0 | 0 | 171 | 0 | 230 | 12 | 0 | 313 | 232 |  | 0 | 300 | 220 | 0 | 35 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 15 | 25 | 25 | 0 | 0 | 0 | 33 | 0 | 0 | 16 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 42 | 0 | 0 | 0 | 270 | 0 | 182 | 8 | 135 | 31 | 52 | 0 | 10 | 0 | 0 | 25 | 19 | 11 | 30 | 20 | 120 | 160 | 0 | 17 | 0 | 0 | 42 | 11 | 5 | 110 | 110 | 55 | 20 | 0 | 138 | 0 | 6 | 10 | 255 | 11 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 90 | 17 | 0 | 240 | 108 | 90 | 0 | 0 | 170 | 54 | 110 | 80 | 58 | 10 | 292 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 50 | 0 |  | 834 | 0 | 200 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 75 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 44 | 0 | 0 | 0 | 0 | 0 |  | 5438 | 2570 | 8008 | 3501 | 834 | 1600 | 0 | 966 | 719 | 33 | 235 | 130 | 120 | 0 | 0 | 75.57
5:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 284 | 233 |  | 0 | 300 | 265 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 25 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 285 | 0 | 188 | 8 | 122 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 159 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 85 | 40 | 10 | 0 | 138 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 0 | 0 | 240 | 45 | 17 | 0 | 0 | 135 | 54 | 68 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 638 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 75 | 28 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 105 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 53 | 0 | 0 | 0 | 0 | 0 |  | 4218 | 2222 | 6440 | 3187 | 638 | 1344 | 0 | 337 | 620 | 34 | 190 | 100 | 90 | 0 | 0 | 75.56
6:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 284 | 234 |  | 0 | 300 | 230 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 16 | 20 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 178 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 154 | 8 | 121 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 158 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 85 | 40 | 10 | 0 | 138 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 240 | 8 | 0 | 0 | 0 | 100 | 54 | 68 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 831 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 75 | 28 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 84 | 0 | 0 | 0 | 0 | 0 |  | 4061 | 2347 | 6408 | 3145 | 831 | 1364 | 0 | 241 | 610 | 35 | 90 | 0 | 92 | 0 | 0 | 75.56
7:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 283 | 202 |  | 0 | 300 | 275 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 155 | 8 | 124 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 156 | 0 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 85 | 40 | 10 | 0 | 138 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 0 | 0 | 238 | 8 | 0 | 0 | 0 | 100 | 54 | 68 | 0 | 0 | 0 | 330 | 0 | 7 | 0 | 0 | 0 | 17 | 4 | 0 | 0 |  | 733 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 75 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 131 | 0 | 0 | 0 | 11 | 0 |  | 4143 | 2266 | 6409 | 3149 | 733 | 1426 | 0 | 257 | 610 | 35 | 90 | 0 | 82 | 27 | 0 | 75.56
8:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 283 | 203 |  | 0 | 300 | 240 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 176 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 155 | 8 | 123 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 160 | 0 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 85 | 40 | 10 | 0 | 139 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 0 | 240 | 8 | 0 | 0 | 2 | 100 | 54 | 68 | 0 | 0 | 0 | 330 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 0 |  | 732 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 75 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 480 | 132 | 0 | 0 | 2 | 29 | 0 |  | 4115 | 2328 | 6443 | 3176 | 732 | 1384 | 0 | 240 | 650 | 35 | 90 | 0 | 80 | 56 | 0 | 75.55
9:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 283 | 201 |  | 0 | 300 | 275 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 290 | 0 | 155 | 0 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 160 | 0 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 86 | 40 | 0 | 0 | 139 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 10 | 0 | 0 | 314 | 0 | 0 | 0 | 4 | 100 | 34 | 51 | 0 | 0 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 5 | 0 | 0 |  | 727 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 76 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 480 | 164 | 0 | 0 | 2 | 68 | 0 |  | 4254 | 2360 | 6614 | 3272 | 727 | 1416 | 0 | 195 | 650 | 35 | 90 | 0 | 86 | 143 | 0 | 75.55
10:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 326 | 202 |  | 0 | 300 | 275 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 290 | 0 | 159 | 0 | 137 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | 90 | 204 | 0 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 86 | 40 | 0 | 0 | 139 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 240 | 0 | 0 | 0 | 4 | 100 | 34 | 51 | 0 | 0 | 0 | 340 | 0 | 34 | 0 | 0 | 0 | 10 | 33 | 0 | 0 |  | 726 | 0 | 200 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 76 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 480 | 164 | 0 | 0 | 2 | 108 | 0 |  | 4408 | 2473 | 6881 | 3344 | 726 | 1512 | 0 | 205 | 680 | 35 | 90 | 0 | 90 | 199 | 0 | 75.55
11:00 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 364 | 201 |  | 0 | 300 | 275 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 305 | 0 | 184 | 0 | 137 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 12 | 88 | 200 | 0 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 109 | 40 | 0 | 0 | 139 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 15 | 60 | 0 | 0 | 298 | 3 | 0 | 0 | 5 | 100 | 34 | 51 | 0 | 0 | 0 | 340 | 0 | 51 | 0 | 0 | 0 | 17 | 22 | 0 | 0 |  | 726 | 0 | 200 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 76 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 480 | 164 | 0 | 0 | 5 | 100 | 0 |  | 4661 | 2498 | 7159 | 3571 | 726 | 1553 | 0 | 267 | 680 | 35 | 37 | 0 | 88 | 202 | 0 | 75.54
12:00 | 0 | 0 | 160 | 0 | 230 | 0 | 0 | 366 | 202 |  | 0 | 300 | 280 | 0 | 10 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 295 | 0 | 190 | 0 | 137 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 96 | 200 | 0 | 0 | 2 | 0 | 42 | 0 | 0 | 40 | 110 | 40 | 0 | 0 | 178 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 90 | 0 | 0 | 327 | 16 | 0 | 0 | 5 | 100 | 34 | 51 | 0 | 0 | 0 | 340 | 0 | 27 | 0 | 0 | 0 | 17 | 30 | 0 | 0 |  | 862 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 480 | 164 | 0 | 0 | 5 | 99 | 0 |  | 4942 | 2598 | 7540 | 3674 | 862 | 1659 | 0 | 351 | 680 | 30 | 0 | 0 | 96 | 188 | 0 | 75.54
13:00 | 0 | 0 | 180 | 0 | 230 | 0 | 0 | 367 | 252 |  | 0 | 300 | 275 | 0 | 15 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 315 | 0 | 209 | 0 | 137 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 20 | 92 | 200 | 0 | 0 | 3 | 0 | 42 | 0 | 0 | 40 | 107 | 40 | 40 | 0 | 219 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 90 | 0 | 0 | 401 | 16 | 0 | 0 | 5 | 110 | 34 | 51 | 15 | 0 | 4 | 350 | 0 | 51 | 0 | 0 | 0 | 17 | 31 | 1 | 0 |  | 917 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 510 | 164 | 0 | 0 | 5 | 94 | 0 |  | 5324 | 2770 | 8094 | 3948 | 917 | 1798 | 0 | 386 | 710 | 35 | 0 | 0 | 92 | 208 | 0 | 75.54
14:00 | 0 | 0 | 180 | 0 | 270 | 32 | 0 | 390 | 302 |  | 0 | 340 | 225 | 0 | 15 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 216 | 8 | 137 | 31 | 25 | 0 | 3 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 98 | 200 | 0 | 17 | 2 | 0 | 42 | 53 | 10 | 40 | 109 | 60 | 81 | 0 | 219 | 0 | 10 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 90 | 0 | 0 | 402 | 16 | 0 | 0 | 3 | 220 | 34 | 51 | 34 | 20 | 20 | 401 | 0 | 49 | 0 | 0 | 0 | 17 | 27 | 17 | 0 |  | 918 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 14 | 0 | 0 | 0 | 2 | 0 | 540 | 202 | 0 | 0 | 4 | 78 | 0 |  | 5836 | 2981 | 8817 | 4120 | 918 | 2139 | 0 | 586 | 740 | 35 | 0 | 0 | 98 | 181 | 0 | 75.54
15:00 | 0 | 0 | 229 | 0 | 270 | 92 | 0 | 379 | 272 |  | 0 | 340 | 260 | 18 | 19 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 42 | 0 | 0 | 0 | 285 | 0 | 210 | 8 | 136 | 28 | 52 | 0 | 10 | 0 | 0 | 2 | 19 | 11 | 33 | 20 | 98 | 202 | 0 | 17 | 2 | 0 | 42 | 53 | 10 | 110 | 106 | 60 | 81 | 0 | 219 | 0 | 10 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 76 | 0 | 0 | 403 | 16 | 0 | 0 | 3 | 230 | 34 | 51 | 51 | 84 | 18 | 365 | 0 | 37 | 0 | 0 | 0 | 17 | 21 | 17 | 0 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 540 | 212 | 0 | 0 | 3 | 67 | 0 |  | 6103 | 2893 | 8996 | 4124 | 923 | 2196 | 0 | 733 | 740 | 35 | 0 | 0 | 98 | 147 | 0 | 75.53
16:00 | 0 | 0 | 228 | 0 | 270 | 53 | 0 | 303 | 272 |  | 0 | 340 | 260 | 30 | 40 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 211 | 8 | 137 | 28 | 54 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 90 | 201 | 0 | 17 | 1 | 20 | 42 | 53 | 10 | 110 | 107 | 60 | 50 | 0 | 219 | 0 | 11 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 7 | 76 | 0 | 0 | 367 | 54 | 0 | 0 | 2 | 240 | 34 | 51 | 51 | 96 | 10 | 360 | 0 | 23 | 0 | 0 | 0 | 17 | 14 | 17 | 0 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 540 | 212 | 0 | 0 | 2 | 43 | 0 |  | 6027 | 2867 | 8894 | 4023 | 923 | 2148 | 0 | 841 | 740 | 35 | 0 | 0 | 90 | 94 | 0 | 75.53
17:00 | 0 | 0 | 228 | 0 | 270 | 24 | 0 | 303 | 271 |  | 0 | 310 | 280 | 31 | 48 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 42 | 0 | 0 | 0 | 295 | 0 | 211 | 8 | 137 | 28 | 54 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 88 | 201 | 0 | 17 | 0 | 20 | 42 | 53 | 10 | 110 | 107 | 60 | 50 | 0 | 219 | 0 | 11 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 3 | 90 | 0 | 0 | 365 | 54 | 0 | 0 | 1 | 240 | 34 | 51 | 51 | 106 | 10 | 361 | 0 | 10 | 0 | 0 | 0 | 17 | 6 | 17 | 0 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 510 | 185 | 0 | 0 | 1 | 20 | 0 |  | 6009 | 2735 | 8744 | 4051 | 923 | 2019 | 0 | 875 | 710 | 35 | 0 | 0 | 88 | 43 | 0 | 75.52
18:00 | 0 | 0 | 228 | 0 | 270 | 24 | 0 | 303 | 252 |  | 0 | 310 | 300 | 31 | 48 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 42 | 0 | 0 | 0 | 335 | 0 | 210 | 8 | 136 | 30 | 54 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 92 | 200 | 0 | 17 | 0 | 20 | 42 | 53 | 12 | 110 | 109 | 40 | 50 | 0 | 180 | 0 | 11 | 10 | 300 | 16 | 8 | 0 | 10 | 0 | 0 | 37 | 0 | 0 | 0 | 90 | 0 | 0 | 386 | 58 | 0 | 0 | 0 | 240 | 34 | 51 | 51 | 105 | 10 | 330 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 17 | 6 |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 304 | 10 | 0 | 35 | 0 | 6 | 0 | 0 | 0 | 490 | 163 | 0 | 0 | 0 | 3 | 0 |  | 6061 | 2709 | 8770 | 4047 | 922 | 2065 | 0 | 914 | 690 | 35 | 0 | 0 | 92 | 5 | 0 | 75.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 232 | 0 | 270 | 22 | 0 | 314 | 252 |  | 0 | 310 | 215 | 39 | 62 | 0 | 250 | 0 | 0 | 5 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 25 | 7 | 20 | 25 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 15 | 0 | 51 | 4 | 37 | 7 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 216 | 8 | 136 | 30 | 54 | 0 | 27 | 0 | 50 | 23 | 19 | 11 | 33 | 20 | 98 | 208 | 0 | 17 | 0 | 20 | 42 | 53 | 42 | 130 | 109 | 40 | 81 | 0 | 215 | 0 | 26 | 10 | 280 | 16 | 11 | 0 | 42 | 0 | 0 | 163 | 0 | 3 | 0 | 90 | 21 | 6 | 402 | 107 | 52 | 10 | 0 | 300 | 49 | 70 | 51 | 105 | 17 | 340 | 17 | 0 | 13 | 20 | 0 | 17 | 0 | 30 | 46 |  | 923 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 39 | 16 | 0 | 0 | 0 | 34 | 0 | 51 | 0 | 8 | 34 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 417 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 620 | 205 | 0 | 0 | 0 | 0 | 34 |  | 6877 | 3368 | 10245 | 4069 | 923 | 2235 | 0 | 1792 | 820 | 35 | 0 | 273 | 98 | 0 | 0 | 75.51
19:30 | 0 | 0 | 180 | 0 | 220 | 22 | 0 | 396 | 252 |  | 0 | 310 | 230 | 60 | 78 | 15 | 250 | 0 | 0 | 7 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 10 | 25 | 7 | 20 | 25 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 15 | 0 | 51 | 10 | 50 | 12 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 214 | 8 | 137 | 30 | 54 | 0 | 51 | 0 | 50 | 34 | 19 | 11 | 30 | 20 | 96 | 208 | 0 | 17 | 0 | 20 | 42 | 53 | 47 | 110 | 111 | 40 | 81 | 0 | 218 | 0 | 26 | 10 | 270 | 16 | 11 | 0 | 90 | 0 | 0 | 185 | 0 | 16 | 0 | 90 | 34 | 10 | 353 | 115 | 52 | 17 | 0 | 300 | 54 | 110 | 51 | 105 | 50 | 370 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 51 | 55 |  | 922 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 38 | 16 | 0 | 0 | 0 | 34 | 0 | 51 | 0 | 0 | 40 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 35 | 0 | 35 | 15 | 39 | 0 | 0 | 35 | 790 | 213 | 0 | 0 | 0 | 0 | 0 |  | 7234 | 3403 | 10637 | 3999 | 922 | 2179 | 0 | 2137 | 990 | 35 | 0 | 279 | 96 | 0 | 0 | 0
20:00 | 0 | 0 | 180 | 0 | 220 | 40 | 0 | 395 | 322 |  | 0 | 380 | 270 | 59 | 78 | 0 | 335 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 10 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 18 | 0 | 51 | 10 | 74 | 12 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 215 | 8 | 136 | 30 | 54 | 0 | 51 | 0 | 50 | 34 | 19 | 11 | 30 | 20 | 98 | 209 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 110 | 110 | 60 | 81 | 0 | 218 | 0 | 26 | 10 | 265 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 16 | 0 | 90 | 34 | 0 | 353 | 115 | 52 | 17 | 0 | 300 | 54 | 110 | 51 | 105 | 50 | 400 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 51 | 35 |  | 923 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 88 | 38 | 0 | 0 | 0 | 0 | 34 | 0 | 51 | 0 | 0 | 40 | 8 | 37 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 340 | 53 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 780 | 205 | 0 | 0 | 0 | 0 | 0 |  | 7350 | 3375 | 10725 | 4141 | 923 | 2366 | 0 | 1919 | 980 | 35 | 0 | 263 | 98 | 0 | 0 | 75.51
21:00 | 0 | 0 | 212 | 0 | 252 | 104 | 0 | 397 | 327 |  | 0 | 400 | 220 | 77 | 78 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 10 | 25 | 7 | 20 | 26 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 91 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 216 | 8 | 136 | 30 | 54 | 0 | 51 | 0 | 0 | 26 | 19 | 11 | 33 | 20 | 129 | 210 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 110 | 60 | 81 | 0 | 218 | 0 | 25 | 10 | 270 | 17 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 90 | 17 | 0 | 400 | 115 | 17 | 0 | 0 | 300 | 54 | 110 | 51 | 105 | 23 | 374 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 51 | 0 |  | 919 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 39 | 0 | 0 | 0 | 0 | 8 | 0 | 51 | 0 | 0 | 40 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 800 | 200 | 0 | 0 | 0 | 0 | 0 |  | 7286 | 3512 | 10798 | 4402 | 919 | 2533 | 0 | 1593 | 1000 | 35 | 0 | 187 | 129 | 0 | 0 | 75.51
22:00 | 0 | 0 | 234 | 0 | 280 | 104 | 0 | 396 | 332 |  | 0 | 400 | 240 | 24 | 78 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 7 | 20 | 26 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 46 | 0 | 95 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 137 | 30 | 55 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 102 | 210 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 109 | 60 | 81 | 0 | 218 | 0 | 26 | 10 | 270 | 17 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 90 | 17 | 0 | 401 | 115 | 17 | 0 | 0 | 300 | 54 | 68 | 80 | 105 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 51 | 0 |  | 920 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 430 | 53 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 840 | 215 | 0 | 0 | 0 | 0 | 0 |  | 7234 | 3648 | 10882 | 4643 | 920 | 2590 | 0 | 1418 | 1040 | 35 | 0 | 134 | 102 | 0 | 0 | 75.51
23:00 | 0 | 0 | 233 | 0 | 280 | 104 | 0 | 396 | 336 |  | 0 | 400 | 275 | 0 | 78 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 20 | 26 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 83 | 0 | 22 | 42 | 0 | 0 | 0 | 295 | 0 | 214 | 8 | 136 | 31 | 56 | 0 | 51 | 0 | 0 | 32 | 19 | 11 | 33 | 21 | 106 | 208 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 110 | 60 | 81 | 0 | 219 | 0 | 26 | 10 | 280 | 17 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 90 | 0 | 0 | 402 | 95 | 17 | 0 | 0 | 300 | 54 | 68 | 80 | 105 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 45 | 0 |  | 921 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 420 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 219 | 0 | 0 | 0 | 0 | 0 |  | 7139 | 3616 | 10755 | 4667 | 921 | 2634 | 0 | 1254 | 1000 | 35 | 0 | 138 | 106 | 0 | 0 | 75.5
24:00 | 0 | 0 | 233 | 0 | 280 | 104 | 0 | 397 | 332 |  | 0 | 400 | 245 | 0 | 48 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 20 | 26 | 0 | 0 | 35 | 0 | 30 | 0 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 83 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 135 | 31 | 57 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 33 | 20 | 104 | 210 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 110 | 55 | 81 | 0 | 219 | 0 | 26 | 10 | 290 | 17 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 90 | 0 | 0 | 402 | 95 | 17 | 0 | 0 | 300 | 54 | 68 | 80 | 105 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 0 |  | 922 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 424 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 217 | 0 | 0 | 0 | 0 | 0 |  | 7070 | 3620 | 10690 | 4683 | 922 | 2613 | 0 | 1195 | 1000 | 35 | 0 | 138 | 104 | 0 | 0 | 75.5
KWH | 0 | 0 | 4413000 | 0 | 5979382 | 857272 | 0 | 8349690 | 6346000 |  | 0 | 7907250 | 6260015 | 330240 | 870144 | 13337 | 6359503 | 0 | 0 | 12480 | 15840 | 17760 | 0 | 0 | 0 | 0 | 308160 | 32627 | 75010 | 173880 | 600000 | 235260 | 603400 | 557900 | 13440 | 0 | 447240 | 392000 | 100000 | 0 | 164167 | 4668264 | 0 | 0 | 0 |  | 184560 | 0 | 274424 | 16920 | 586560 | 92160 | 530352 | 1038240 | 0 | 0 | 0 | 7219400 | 0 | 4753000 | 150545 | 3156050 | 577800 | 834720 | 0 | 519991 | 0 | 69280 | 383981 | 301032 | 145620 | 588300 | 400150 | 2293440 | 4521600 | 0 | 206604 | 12600 | 177000 | 980160 | 645600 | 384120 | 2096345 | 2449000 | 119568 | 1023360 | 0 | 4470550 | 0 | 251200 | 159840 | 6239500 | 194304 | 117024 | 0 | 125454 | 0 | 0 | 1821600 | 0 | 97920 | 126630 | 1623360 | 402720 | 18400 | 8087000 | 1448400 | 631200 | 43490 | 34920 | 5121055 | 1172326 | 1853373 | 967860 | 1332240 | 212160 | 8503000 | 48960 | 342310 | 50400 | 276000 | 0 | 380160 | 190381 | 625920 | 185760 |  | 20745454 | 0 | 6643296 | 0 | 47040 | 1140480 | 0 | 0 | 0 | 0 | 14250 | 1935399 | 742420 | 64128 | 0 | 427000 | 0 | 90112 | 0 | 291792 | 0 | 7157 | 84170 | 50880 | 217612 | 337440 | 0 | 194976 | 0 | 0 | 4710300 | 0 | 0 | 4139273 | 0 | 553446 | 723818 | 0 | 0 | 0 | 0 | 7587491 | 337440 | 0 | 358752 | 84240 | 251068 | 0 | 26018 | 107136 | 15852300 | 4065982 | 0 | 0 | 32880 | 719280 | 183744 |  | 139991160 | 72766774 | 212757934 | 93431183 | 20745454 | 47447331 | 0 | 23044219 | 20562600 | 839240 | 1864298 | 1045150 | 2293440 | 1485019 | 0
Fuel Cost | 0 | 0 | 6442980 | 0 | 6637114.02 | 1131599.04 | 0 | 8433186.9 | 6536380 |  | 0 | 8618902.5 | 6948616.65 | 2506521.6 | 5995292.16 | 112831.02 | 6613883.12 | 0 | 0 | 93974.4 | 144460.8 | 174758.4 | 0 | 0 | 0 | 0 | 2249568 | 252206.71 | 739598.6 | 130410 | 450000 | 0 | 0 | 0 | 129964.8 | 0 | 120754.8 | 105840 | 181000 | 0 | 1525111.43 | 5088407.76 | 0 | 0 | 0 |  | 0 | 0 | 2661912.8 | 161586 | 5103072 | 729907.2 | 668243.52 | 3083572.8 | 0 | 0 | 0 | 5342356 | 0 | 4372760 | 194203.05 | 3629457.5 | 652914 | 1168608 | 0 | 889184.61 | 0 | 699728 | 3667018.55 | 382310.64 | 109215 | 1029525 | 300112.5 | 17200800 | 4792896 | 0 | 262387.08 | 200844 | 290280 | 1568256 | 1149168 | 599227.2 | 2389833.3 | 2546960 | 235548.96 | 1954617.6 | 0 | 7734051.5 | 0 | 293904 | 326073.6 | 6301895 | 145728 | 88938.24 | 0 | 948432.24 | 0 | 0 | 9472320 | 0 | 963532.8 | 1480304.7 | 13230384 | 4369512 | 129720 | 7520910 | 13209408 | 5964840 | 378797.9 | 0 | 38715175.8 | 10210959.46 | 16291148.67 | 9659242.8 | 11417296.8 | 1412985.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 119493815.04 | 0 | 6975460.8 | 0 | 369734.4 | 15807052.8 | 0 | 0 | 0 | 0 | 148485 | 2187000.87 | 1150751 | 625889.28 | 0 | 875350 | 0 | 886702.08 | 0 | 2582359.2 | 0 | 96762.64 | 815607.3 | 493027.2 | 2110836.4 | 647884.8 | 0 | 147596.832 | 0 | 0 | 25529826 | 0 | 0 | 4842949.41 | 0 | 730548.72 | 10654600.96 | 0 | 0 | 0 | 0 | 7511616.09 | 3522873.6 | 0 | 3404556.48 | 795225.6 | 1948287.68 | 0 | 287498.9 | 791735.04 | 69591597 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299665429.13 | 285025631.122 | 584691060.252 | 91408738.372 | 119493815.04 | 50896037.24 | 0 | 171981446.26 | 95121423 | 226594.8 | 26461653.76 | 9931904.18 | 17200800 | 1968647.6 | 0
Yesterday Day Peak | 0 | 0 | 160 | 0 | 230 | 0 | 0 | 366 | 202 |  | 0 | 300 | 280 | 0 | 10 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 295 | 0 | 190 | 0 | 137 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 96 | 200 | 0 | 0 | 2 | 0 | 42 | 0 | 0 | 40 | 110 | 40 | 0 | 0 | 178 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 90 | 0 | 0 | 327 | 16 | 0 | 0 | 5 | 100 | 34 | 51 | 0 | 0 | 0 | 340 | 0 | 27 | 0 | 0 | 0 | 17 | 30 | 0 | 0 |  | 862 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 480 | 164 | 0 | 0 | 5 | 99 | 0 |  | 7540 | DayPeak
Yesterday Evening Peak | 0 | 0 | 212 | 0 | 252 | 104 | 0 | 397 | 327 | 0 | 0 | 400 | 220 | 77 | 78 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 10 | 25 | 7 | 20 | 26 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 0 | 91 | 0 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 216 | 8 | 136 | 30 | 54 | 0 | 51 | 0 | 0 | 26 | 19 | 11 | 33 | 20 | 129 | 210 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 110 | 60 | 81 | 0 | 218 | 0 | 25 | 10 | 270 | 17 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 90 | 17 | 0 | 400 | 115 | 17 | 0 | 0 | 300 | 54 | 110 | 51 | 105 | 23 | 374 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 51 | 0 |  | 919 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 39 | 0 | 0 | 0 | 0 | 8 | 0 | 51 | 0 | 0 | 40 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 800 | 200 | 0 | 0 | 0 | 0 | 0 |  | 10798 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 280 | 100 | 0 | 400 | 350 | 0 | 0 | 400 | 305 | 90 | 78 | 55 | 330 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 20 | 25 | 52 | 0 | 35 | 0 | 100 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 0 | 96 | 37 | 22 | 42 | 0 | 0 | 0 | 350 | 0 | 225 | 8 | 138 | 31 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 166 | 200 | 0 | 17 | 0 | 20 | 42 | 53 | 50 | 163 | 110 | 60 | 81 | 0 | 220 | 0 | 25 | 10 | 310 | 17 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 17 |  | 101 | 35 |  | 938 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 37 | 60 | 32 | 86 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 90 | 0 | 43 | 40 | 43 | 38 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 900 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 230 | 0 | 230 | 70 | 0 | 400 | 340 | 0 | 0 | 340 | 305 | 90 | 78 | 55 | 300 | 0 | 0 | 96 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 20 | 25 | 52 | 0 | 35 | 0 | 90 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 0 | 96 | 37 | 22 | 42 | 0 | 0 | 0 | 330 | 0 | 225 | 8 | 138 | 31 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 143 | 200 | 0 | 17 | 1.6 | 20 | 42 | 53 | 50 | 163 | 110 | 60 | 81 | 0 | 220 | 0 | 25 | 10 | 310 | 17 | 11 | 200 | 280 | 300 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 80 | 113 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 17 | 30 | 51 | 35 |  | 500 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 37 | 0 | 32 | 75 | 33 | 50 | 0 | 0 | 0 | 36 | 30 | 90 | 0 | 43 | 40 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 500 | 220 |  | 0 | 6 | 100 | 30
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 230 | 12 | 0 | 282 | 181 | 0 | 0 | 250 | 292 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 25 | 0 | 0 | 35 | 0 | 90 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 22 | 42 | 0 | 0 | 0 | 310 | 0 | 152 | 8 | 137 | 25 | 10 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 94 | 161 | 0 | 0 | 0 | 20 | 42 | 11 | 10 | 110 | 40 | 40 | 10 | 0 | 140 | 0 | 5 | 10 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 0 | 240 | 0 | 0 | 0 | 2 | 15 | 17 | 0 | 0 | 57 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 718 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 141 | 0 | 0 | 0 | 39 | 0 | 0 |  |  |  |  | 25953667 |  | 0
25953667
| Minimum Generation |  | 6408 | 6:00
| Highest Generation |  | 10882 | 22:00
| Day Peak Generation |  | 7540 | 12:00
| Evening Peak Generation |  | 10798 | 21:00
| HVDC Max Flow |  | 924 | 1:00
| HVDC EvPeak Flow |  | 919 | 21:00
| Load factor L.F |  | 81.46%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-03
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7540 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 6953 | MW
Evening Peak Generation : |  | 10798 | MW Hour : | 21:00 | Available Max Generation : |  | 15361 | MW
E.P. Demand (at gen end) : |  | 10798 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 10882 | MW Hour : | 22:00 | Reserve(Generation end) |  | 6161 | MW
Total Gen. (MKWH) : |  | 212.7579 | System Load Factor : | 81.46% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -382 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-03
Actual : | 75.48 | Ft.(MSL) , | Rule curve : | 81.62 | Ft.( MSL )
Gas Consumed : | Total = | 1129.65 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142304775.612
: |  | Coal : | 95121423 | Oil : | 208375004.2 | Total : | 445801202.812
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3250.7535 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1014.2737 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1034.5033 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 921.0269 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 844.4112 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 699.189 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 333.5991 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 226.3708 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 500.8274 |  |  | 0 | 0%
Total | 0 |  | 8824.9548 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 1,2
6) Siddhirganj 210 MW .
7) Sikalbaha-150 MW
8) Ashuganj South
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Khulna 225 MW was shutdown at 11:18 due to low demand.
b) Sirajganj Unit-2 GT was synchronized on gas at 16:44 and ST at 20:06.
c) Ghorashal 132/33 kV T-1 transformer was at 13:23 from 132 kV side.
d) Raozan Unit-1 was synchronized at 22:41 and tripped at 05:37(03/05/2022) due to Burner problem
and again synchronized at 06:45(03/05/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 212 | 4413000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 252 | 5979382 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 857272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 8349690 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 6346000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 7907250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 77 | 330240 | Low Demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 220 | 6260015 | FGMO & gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 78 | 870144 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 13337 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 173880
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 12480 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6359503
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 15840 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 308160 | Low Demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 17760 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 32627 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 75010 | Low Demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 32 | 835260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 603400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 557900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 13440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 125454 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 97920 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 631200 | Low Demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 48960 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 50400 | Reserve.
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 190381
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 185760 | Reserve.
| Dhaka area Total |  |  |  | 5898 | 2559 | 51661665
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 100000 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 164167 | Low Demand
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126630
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 92160 | Reserve.
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 839240 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4668264
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 43490 | Reserve.
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 274424 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 0 | 0 | 16920
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1623360 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 530352
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1038240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 586560 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34920
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 5121055
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1172326
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1853373
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 23 | 212160 | Reserve.
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 276000 | Low Demand
| Chattogram area Total |  |  |  | 2282 | 1063 | 18773641
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4753000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7219400 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 577800 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 834720
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 150545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 519991
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 18400 | Reserve.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 69280 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3156050 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 402720 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 301032
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 145620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 129 | 2293440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 588300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 26 | 383981 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 400150 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 51 | 967860 | Low Demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1332240 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 380160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 625920 | Low Demand
| Cumilla Area Total |  |  |  | 3014 | 1254 | 25120609
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 210 | 4521600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 206604
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 140 | 1821600 | Low Demand
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1448400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 342310
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 184560
| Mymensingh Area Total |  |  |  | 622 | 506 | 8537674
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 20 | 177000 | Gas shortage
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 980160 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2096345
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2449000 | GT-2 Under S/D
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 645600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 50 | 384120
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 117024
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 119568 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1023360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4470550
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 25 | 251200 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 194304
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6239500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 8087000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 159840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 374 | 8503000
| Sylhet Area Total |  |  |  | 2477 | 1904 | 35897571
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 919 | 20745454
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 47040 | Reserve.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 1140480 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 6643296 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 14250 | Reserve.
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 337440 | Low Demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 84240 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 719280
| Khulna Area Total |  |  |  | 2384 | 1357 | 29731480
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 64128 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 39 | 742420
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 1935399 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 15852300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 200 | 4065982
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1958 | 1119 | 22660229
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 427000 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 8 | 90112 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 7157 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 84170 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 141 | 4139273 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 67 | 1277264
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7587491
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 217612 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 337440
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 194976
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 50880 | Low Demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 291792 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 358752 | Reserve.
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 107136 | Reserve.
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32880
| Rajshahi Area Total |  |  |  | 2129 | 799 | 15203935
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Reserve.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4710300
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 37 | 251068 | Low Demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26018
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 183744 | Reserve.
| Rangpur Area Total |  |  |  | 720 | 237 | 5171130
| Total |  |  |  | 21484 | 10798 | 212757934
| Eastern Grid Total |  |  |  | 14293 | 7286 | 139991160
| Western Grid Total |  |  |  | 7191 | 3512 | 72766774
| National Grid Total |  |  |  | 21484 | 10798 | 212757934
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-02
(a) ENTIRE EASTERN GRID : |  | 6693.35 | MW | (b) ENTIRE WESTERN GRID : |  | 3653.2 | MW
i) Dhaka area |  | 3018.75 | MW | i) Khulna area |  | 1469 | MW
ii) Chittagong area |  | 1033.6 | MW | ii) Rajshahi area |  | 1176.2 | MW
iii) Comilla area |  | 1253 | MW | iii) Barisal area |  | 402 | MW
iv) Mymensingh area |  | 959 | MW | iv) Rangpur area |  | 606 | MW
v) Sylhet area |  | 429 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10346.55 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 26 | 00:00 | Hasnabad | 55 | 00:00 | Palashbari | 102 | 00:00
Agargaon | 66 | 00:00 | Hathazari | 93 | 00:00 | Panchagarh | 41 | 19:00
Agrabad | 70 | 00:00 | Ishurdi | 65 | 00:00 | Patuakhali | 139 | 00:00
AKS | 5 | 00:00 | Jaldhaka | 46 | 19:00 | PHP | 3 | 16:00
AKSML | 2 | 00:00 | Jamalpur | 134 | 02:00 | Purbachal | 15 | 00:00
Amnura | 53 | 20:00 | Jashore | 120 | 00:00 | Purbasadipur | 87 | 14:00
Ashuganj | 53 | 03:00 | Jhenaidah | 114 | 22:00 | Rahim | 0 | 00:00
Bagerhat | 104 | 22:00 | Joydebpur | 110 | 00:00 | Rajbari | 72 | 00:00
Bakulia | 107 | 00:00 | Joypurhat | 47 | 00:00 | Rajendrapur | 79 | 00:00
Banani | 30 | 01:00 | Juldah | 15 | 00:00 | Rajshahi | 140 | 19:00
Bangabhaban | 4 | 00:00 | Kabirpur | 117 | 00:00 | Rajshahi | 24 | 22:00
Barapukuria | 42 | 01:00 | Kachua | 82 | 00:00 | Ramganj | 116 | 22:00
Barguna | 20 | 00:00 | Kallyanpur | 87 | 00:00 | Rampur | 15 | 00:00
Barishal | 110 | 23:00 | Kalurghat | N/A | N/A | Rangamati | 12 | 19:00
Barishal | 62 | 00:00 | Kamrangirchar | 38 | 00:00 | Rangpur | 99 | 00:00
Baroaulia | 52 | 22:00 | Kaptai | 4 | 19:00 | Ruppur | 3.2 | 11:00
Baroirhat | 46 | 00:00 | Kazla | 55 | 00:00 | Saidpur | 63 | 19:00
Bashundhara | 129 | 00:00 | Keranigonj | 54 | 00:00 | Satkhira | 125 | 00:00
BashundharaCement | 0 | 00:00 | Khagrachori | 26 | 19:30 | Satmasjid | 83 | 00:00
Beanibazar | 62 | 19:00 | Khulna | 81 | 00:00 | Savar | 110 | 00:00
Benapole | 52 | 22:00 | Khulshi | 109 | 19:30 | Shahjadpur | 111 | 00:00
Bhaluka | 96 | 00:00 | Kishoreganj | 150 | 00:00 | Shahjibazar | 92 | 00:00
Bhandaria | 61 | 00:00 | Kodda | 174 | 18:30 | Shahmirpur | 30.5 | 19:00
Bhangura | 43 | 00:00 | KSRM | 0.45 | 10:00 | Shariatpur | 80 | 00:00
Bheramara(GK) | 56 | 22:00 | Kulaura | 40 | 19:00 | Sherpur | 134 | 18:30
Bhulta | 138 | 00:00 | Kurigram | 48 | 19:00 | Shikalbaha | 27 | 01:00
Bog-Sherpur | 44 | 00:00 | Kushtia | 104 | 00:00 | Shitalakhya | 77 | 00:00
Bogura | 138 | 00:00 | Lalbag | 24 | 00:00 | Sholosohor | N/A | N/A
Borhanuddin | 46 | 20:00 | Lalmonirhat | 33 | 19:30 | Shyampur | 60 | 00:00
Brahmanbaria | 186 | 00:00 | Madanganj | 122 | 00:00 | Siddhirganj | 66 | 00:00
BSRM | 162 | 06:00 | Madaripur | 117 | 00:00 | Sirajganj | 92 | 19:00
Cantonment | 110 | 00:00 | Madartek | 73 | 00:00 | Sonargaon | 50 | 00:00
Chandpur | 74 | 00:00 | Madunaghat | 58 | 22:00 | Sreemongol | 52 | 00:00
Chandraghona | 32 | 00:00 | Magura | 62 | 00:00 | Srinagar | 44.58 | 00:00
Chapai | 57 | 22:00 | Mahasthangarh | 64 | 00:00 | SSM | 0 | 00:00
Charsaidpur | 6 | 01:00 | Manikganj | 82 | 00:00 | Sunamganj | 41 | 20:00
Chauddagram | 61 | 22:00 | Maniknagar | 56 | 00:00 | Sylhet | 114 | 00:00
Chhatak | 25 | 00:00 | Matarbari | 43 | 20:00 | Tangail | 215 | 00:00
Chowmuhani | 222 | 00:00 | Matuail | 32 | 00:00 | Thakurgaon | 65 | 19:30
Chuadanga | 105 | 22:00 | Millgate | 26 | 00:00 | TK | 19.4 | 23:00
Coxsbazar | 118 | 00:00 | Mirpur | 103 | 00:00 | Tongi | 81 | 00:00
Cumilla(N) | 153 | 03:00 | Mirsorai | 3.15 | 23:00 | Ullon | 30 | 01:00
Cumilla(S) | 158 | 00:00 | Mithapukur | 36 | 00:00 | Uttara | 70 | 00:00
Daudkandi | 140 | 20:00 | Modern | 0 | 00:00 | UttaraNew | 13 | 00:00
Dhaka | 16 | 13:00 | Mogbazar | 82 | 00:00 | Zigatola | 35 | 00:00
Dhamrai | 92 | 00:00 | Mongla | 16 | 00:00
Dhanmondi | 111 | 00:00 | Motijheel | 24 | 00:00
Dohazari | 112 | 22:00 | Munshiganj | 95 | 00:00
Faridpur | 144 | 00:00 | Mymensingh | 206 | 00:00
Fatullah | 38 | 00:00 | Naogaon | 108 | 00:00
Fenchuganj | 44 | 00:00 | Narail | 56 | 00:00
Feni | 141 | 00:00 | Narinda | 44 | 00:00
Ghorashal | 39 | 23:00 | Narshingdi | 162 | 00:00
Goalpara | 28 | 00:00 | Natore | 138 | 00:00
Gollamari | 48 | 00:00 | Nawabganj | 55.4 | 00:00
Gopalganj | 98.2 | 22:00 | Netrakona | 114 | 19:30
GPH | 3 | 09:00 | New | 38.8 | 00:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 19:30 | 397 | 21:00 | Kaliakoir | 394 | 0.16667 | 384 | 0.041667
| Bheramara | 406 | 4:00 | 394 | 13:00 | Bhulta | 399 | 0.16667 | 389 | 0.95833
| Ashuganj(N) | 403 | 4:00 | 393 | 13:00 | Gopalganj | 425 | 0.625 | 399 | 0.95833
| Payra | 425 | 4:00 | 410 | 24:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 234 | 20:00 | 219 | 8:00
| Ishurdi | 238 | 5:00 | 224 | 21:00 | Megnaghat | 234 | 18:30 | 229 | 13:00
| Ashuganj | 240 | 4:00 | 232 | 13:00 | Fenchuganj | 243 | 4:00 | 236 | 13:00
| Serajganj | 235 | 5:00 | 228 | 13:00 | Siddhirganj | 230 | 4:00 | 226 | 1:00
| Baghabari | 233 | 2:00 | 226 | 20:00 | Maniknagar | 230 | 4:00 | 224 | 1:00
| Barapukuria | 227 | 3:00 | 215 | 21:00 | Agargaon | 229 | 4:00 | 221 | 1:00
| Bogra | 229 | 6:00 | 220 | 21:00 | Barisal | 246 | 4:00 | 230 | 22:00
| Rajshahi | 235 | 1:00 | 222 | 13:00 | Bhola 225 MW | 248 | 4:00 | 230 | 22:00
| Khulna South | 239 | 2:00 | 218 | 23:00 | AKSML | 233 | 20:00 | 219 | 9:00
| Rampura | 229 | 4:00 | 224 | 1:00 | BSRM | 232 | 20:00 | 218 | 10:00
| Haripur | 228 | 9:00 | 223 | 13:00 | Bibiyana | 240 | 18:30 | 232 | 12:00
| Hasnabad | 230 | 4:00 | 222 | 22:00 | Bhulta | 231 | 4:00 | 225 | 23:00
| Shyampur | 229 | 4:00 | 222 | 1:00 | Ashuganj (S) | 236 | 4:00 | 230 | 13:00
| Aminbazar | 231 | 1:00 | 223 | 2:00 | Kaliakoir | 228 | 4:00 | 222 | 1:00
| Tongi | 227 | 10:00 | 222 | 3:00 | GPH | 235 | 5:00 | 219 | 10:00
| Comilla (N) | 230 | 4:00 | 223 | 13:00 | Jhenaidah | 235 | 2:00 | 215 | 23:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 04:00 | 131 | 01:00 | Manikganj | 134 | 05:00 | 129 | 00:00
| Agargaon | 137 | 04:00 | 132 | 01:00 | Maniknagar | 137 | 04:00 | 129 | 23:00
| Agrabad | 135 | 19:00 | 124 | 10:00 | Matarbari | 119 | 17:00 | 107 | 13:00
| AKS | 134 | 19:30 | 124 | 09:00 | Matuail | 138 | 04:00 | 133 | 00:00
| Aminbazar | 139 | 04:00 | 134 | 15:00 | Millgate | 139 | 19:30 | 133 | 00:00
| Amnura | 131 | 00:00 | 120 | 13:00 | Mirpur | 137 | 01:00 | 132 | 13:00
| Ashuganj | 139 | 08:00 | 133 | 00:00 | Mithapukur | 131 | 05:00 | 124 | 11:00
| Bagerhat | 141 | 02:00 | 123 | 13:00 | Modern | 132 | 18:00 | 124 | 10:00
| Bakulia | 133 | 19:30 | 123 | 10:00 | Mogbazar | 136 | 04:00 | 132 | 00:00
| Banani | 140 | 05:00 | 134 | 02:00 | Mongla | 140 | 02:00 | 124 | 21:00
| Bangabhaban | 137 | 05:00 | 130 | 22:00 | Motijheel | 137 | 05:00 | 130 | 22:00
| Barapukuria | 133 | 05:00 | 125 | 21:00 | Munshiganj | 139 | 00:00 | 132 | 01:00
| Barguna | 138 | 03:00 | 128 | 00:00 | Mymensingh | 133 | 08:00 | 121 | 12:00
| Barishal | 144 | 04:00 | 126 | 11:00 | Naogaon | 129 | 06:00 | 119 | 22:00
| Barishal | 144 | 03:00 | 130 | 22:00 | Narail | 139 | 01:00 | 122 | 21:00
| Baroaulia | 136 | 20:00 | 126 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 130 | 04:00 | 119 | 12:00 | Narshingdi | 135 | 05:00 | 127 | 00:00
| Bashundhara | 140 | 04:00 | 135 | 00:00 | Natore | 132 | 05:00 | 124 | 13:00
| BashundharaCement | 138 | 04:00 | 132 | 01:00 | Nawabganj | 139 | 04:00 | 129 | 01:00
| Beanibazar | 136 | 08:00 | 129 | 23:00 | Netrakona | 136 | 10:00 | 120 | 12:00
| Benapole | 137 | 01:00 | 124 | 13:00 | New | 139 | 07:00 | 135 | 00:00
| Bhaluka | 134 | 08:00 | 122 | 01:00 | Niamatpur | 127 | 08:00 | 116 | 22:00
| Bhandaria | 145 | 03:00 | 121 | 23:00 | Noapara | 139 | 02:00 | 127 | 13:00
| Bhangura | 138 | 02:00 | 132 | 00:00 | Pabna | 138 | 05:00 | 129 | 13:00
| Bheramara | 137 | 04:00 | 131 | 13:00 | Palashbari | 130 | 06:00 | 120 | 22:00
| Bheramara(GK) | 141 | 05:00 | 134 | 21:00 | Panchagarh | 133 | 08:00 | 124 | 13:00
| Bhulta | 135 | 05:00 | 126 | 23:00 | Patuakhali | 136 | 12:00 | 130 | 00:00
| Bog-Sherpur | 134 | 05:00 | 125 | 21:00 | PHP | 129 | 04:00 | 120 | 10:00
| Bogura | 133 | 06:00 | 125 | 21:00 | Purbachal | 139 | 05:00 | 133 | 00:00
| Bogura | 134 | 06:00 | 127 | 21:00 | Purbasadipur | 133 | 07:00 | 120 | 13:00
| Brahmanbaria | 134 | 05:00 | 127 | 00:00 | Rahim | 137 | 04:00 | 133 | 00:00
| Cantonment | 136 | 04:00 | 131 | 00:00 | Rajbari | 138 | 04:00 | 127 | 23:00
| Chandpur | 132 | 04:00 | 120 | 13:00 | Rajendrapur | 135 | 22:00 | 129 | 01:00
| Chandraghona | 135 | 19:30 | 126 | 10:00 | Rajshahi | 130 | 06:00 | 122 | 13:00
| Chapai | 133 | 00:00 | 122 | 13:00 | Rajshahi | 130 | 01:00 | 121 | 13:00
| Charsaidpur | 139 | 04:00 | 133 | 01:00 | Ramganj | 128 | 04:00 | 117 | 12:00
| Chauddagram | 130 | 19:00 | 121 | 12:00 | Rampur | 133 | 20:00 | 124 | 13:00
| Chhatak | 135 | 07:00 | 129 | 00:00 | Rampura | 135 | 04:00 | 131 | 00:00
| Chowmuhani | 128 | 04:00 | 116 | 12:00 | Rangamati | 134 | 19:30 | 125 | 12:00
| Chuadanga | 135 | 00:00 | 118 | 21:00 | Rangpur | 132 | 07:00 | 118 | 22:00
| Coxsbazar | 114 | 11:00 | 104 | 13:00 | Ruppur | 136 | 03:00 | 131 | 23:00
| Cumilla(N) | 134 | 04:00 | 127 | 13:00 | Saidpur | 131 | 07:00 | 120 | 22:00
| Cumilla(S) | 132 | 19:00 | 125 | 12:00 | Satkhira | 140 | 02:00 | 122 | 23:00
| Daudkandi | 135 | 04:00 | 125 | 23:00 | Satmasjid | 137 | 04:00 | 126 | 08:00
| Dhaka | 136 | 04:00 | 131 | 23:00 | Savar | 137 | 04:00 | 130 | 17:00
| Dhamrai | 139 | 04:00 | 129 | 23:00 | Shahjadpur | 142 | 02:00 | 134 | 00:00
| Dhanmondi | 138 | 04:00 | 133 | 00:00 | Shahjibazar | 136 | 05:00 | 132 | 13:00
| Dohazari | 127 | 19:00 | 118 | 00:00 | Shahmirpur | 133 | 19:30 | 123 | 10:00
| Faridpur | 138 | 03:00 | 128 | 22:00 | Shariatpur | 142 | 06:00 | 126 | 23:00
| Fatullah | 138 | 05:00 | 131 | 01:00 | Sherpur | 137 | 18:30 | 115 | 15:00
| Fenchuganj | 137 | 18:30 | 133 | 01:00 | Shikalbaha | 134 | 19:30 | 124 | 10:00
| Feni | 130 | 04:00 | 120 | 10:00 | Shikalbaha | 134 | 19:30 | 124 | 13:00
| Ghorashal | 140 | 04:00 | 135 | 14:00 | Shitalakhya | 138 | 04:00 | 132 | 01:00
| Goalpara | 141 | 02:00 | 129 | 13:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 141 | 02:00 | 129 | 13:00 | Shyampur | 138 | 04:00 | 132 | 00:00
| Gopalganj | 142 | 04:00 | 128 | 23:00 | Shyampur | 137 | 04:00 | 126 | 18:30
| Gopalganj_I | 142 | 04:00 | 131 | 22:00 | Siddhirganj | 137 | 04:00 | 133 | 01:00
| Gulshan | 135 | 04:00 | 131 | 00:00 | Sirajganj | 134 | 06:00 | 127 | 22:00
| Halishahar | 137 | 18:30 | 123 | 10:00 | Sonargaon | 135 | 00:00 | 133 | 07:00
| Haripur | 137 | 04:00 | 133 | 00:00 | Sreemongol | 138 | 07:00 | 134 | 00:00
| HaripurSBU | 138 | 05:00 | 134 | 00:00 | Srinagar | 139 | 04:00 | 132 | 00:00
| Hasnabad | 140 | 04:00 | 134 | 00:00 | SSM | 140 | 19:30 | 126 | 07:00
| Hathazari | 136 | 20:00 | 127 | 08:00 | Sunamganj | 135 | 08:00 | 128 | 23:00
| Ishurdi | 138 | 05:00 | 130 | 21:00 | Sylhet | 135 | 07:00 | 132 | 00:00
| Jaldhaka | 133 | 06:00 | 119 | 19:30 | Tangail | 133 | 05:00 | 128 | 12:00
| Jamalpur | 139 | 18:30 | 117 | 13:00 | Thakurgaon | 132 | 07:00 | 121 | 22:00
| Jashore | 136 | 03:00 | 124 | 13:00 | TK | 135 | 19:00 | 125 | 09:00
| Jhenaidah | 140 | 01:00 | 125 | 21:00 | Tongi | 140 | 18:30 | 134 | 01:00
| Jhenaidah | 140 | 01:00 | 126 | 20:00 | Ullon | 136 | 05:00 | 131 | 00:00
| Joydebpur | 140 | 05:00 | 132 | 13:00 | Uttara | 138 | 04:00 | 131 | 23:00
| Joypurhat | 130 | 06:00 | 119 | 22:00 | UttaraNew | 137 | 04:00 | 132 | 13:00
| Juldah | 134 | 20:00 | 125 | 09:00 | Zigatola | 139 | 05:00 | 132 | 00:00
| Kabirpur | 137 | 01:00 | 131 | 13:00
| Kachua | 133 | 04:00 | 122 | 10:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 139 | 04:00 | 133 | 13:00
| Kalurghat | N/A | N/A | N/A | N/A
| Kamrangirchar | 138 | 04:00 | 132 | 00:00
| Kaptai | 132 | 00:00 | 130 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 166 | 7070 | 3620 | 10690 |  |  |  | QF-LDC-11
0:30 | 296 | 6949 | 3534 | 10483 | Date: | 2022-05-02
1:00 | 426 | 6828 | 3448 | 10276
1:30 | 493 | 6680.5 | 3225 | 9905.5
2:00 | 560 | 6533 | 3002 | 9535
2:30 | 575 | 6342 | 2978.5 | 9320.5 | [5 empty] | Gen. at Eve. Peak | 10798 | 10798 MW (21:00 )
3:00 | 590 | 6151 | 2955 | 9106 | [6 empty] | 21:00
3:30 | 496 | 5794.5 | 2762.5 | 8557 | [5 empty] | Gen. at Day Peak | 7540 | 7540 MW (12:00 )
4:00 | 402 | 5438 | 2570 | 8008 | [6 empty] | 12:00
4:30 | 412 | 4828 | 2396 | 7224 | [5 empty] | Highest Generation | 10882
5:00 | 422 | 4218 | 2222 | 6440 | [6 empty] | 22:00
5:30 | 458 | 4139.5 | 2284.5 | 6424
6:00 | 494 | 4061 | 2347 | 6408
6:30 | 438 | 4102 | 2306.5 | 6408.5
7:00 | 382 | 4143 | 2266 | 6409
7:30 | 323 | 4129 | 2297 | 6426
8:00 | 264 | 4115 | 2328 | 6443
8:30 | 227 | 4184.5 | 2344 | 6528.5
9:00 | 190 | 4254 | 2360 | 6614
9:30 | 227 | 4331 | 2416.5 | 6747.5
10:00 | 264 | 4408 | 2473 | 6881
10:30 | 209 | 4534.5 | 2485.5 | 7020
11:00 | 154 | 4661 | 2498 | 7159
11:30 | 157 | 4801.5 | 2548 | 7349.5
12:00 | 160 | 4942 | 2598 | 7540
12:30 | 110 | 5133 | 2684 | 7817
13:00 | 60 | 5324 | 2770 | 8094
13:30 | 36 | 5580 | 2875.5 | 8455.5
14:00 | 12 | 5836 | 2981 | 8817
14:30 | 72 | 5969.5 | 2937 | 8906.5
15:00 | 132 | 6103 | 2893 | 8996
15:30 | 115 | 6065 | 2880 | 8945
16:00 | 98 | 6027 | 2867 | 8894
16:30 | 122 | 6018 | 2801 | 8819
17:00 | 146 | 6009 | 2735 | 8744
17:30 | 179 | 6035 | 2722 | 8757
18:00 | 212 | 6061 | 2709 | 8770
18:30 | 233 | 6469 | 3038.5 | 9507.5
19:00 | 254 | 6877 | 3368 | 10245
19:30 | 342 | 7234 | 3403 | 10637
20:00 | 382 | 7350 | 3375 | 10725 |  |  |  | Executive Engineer
20:30 | 293 | 7318 | 3443.5 | 10761.5 |  |  |  | Network Operation Division
21:00 | 204 | 7286 | 3512 | 10798
21:30 | 200 | 7260 | 3580 | 10840
22:00 | 196 | 7234 | 3648 | 10882 |  |  |  |  | Page 6 of 7
22:30 | 198 | 7186.5 | 3632 | 10818.5
23:00 | 200 | 7139 | 3616 | 10755
23:30 | 183 | 7104.5 | 3618 | 10722.5
24:00 | 166 | 7070 | 3620 | 10690
10798 MW (21:00 )
7540 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-02 |  | Energy |  | 212757934
[13 empty] | 2022-05-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4683 | 922 | 2613 | 0 | 1195 | 1000 | 35 | 0 | 138 | 104 | 0 | 0
0:30 | 4479.5 | 923 | 2442 | 0 | 1338 | 959.5 | 35 | 125 | 134 | 112 | 0 | 0 | Date: | 2022-05-02
1:00 | 4276 | 924 | 2271 | 0 | 1481 | 919 | 35 | 250 | 130 | 120 | 0 | 0
1:30 | 4161.5 | 923.5 | 2134.5 | 0 | 1443 | 839 | 35 | 250 | 130 | 119 | 0 | 0 | [8 empty] | Total Energy | 212.7579 | Total Energy Gen 212.758 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.758 MKWHr
2:00 | 4047 | 923 | 1998 | 0 | 1405 | 759 | 35 | 250 | 130 | 118 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3915.5 | 923 | 1975.5 | 0 | 1363.5 | 739 | 35 | 250 | 130 | 119 | 0 | 0 | [8 empty] | Energy Requirement | 212.7579
3:00 | 3784 | 923 | 1953 | 0 | 1322 | 719 | 35 | 250 | 130 | 120 | 0 | 0
3:30 | 3642.5 | 878.5 | 1776.5 | 0 | 1144 | 719 | 34 | 242.5 | 130 | 120 | 0 | 0 | [6 empty] | Shortage
4:00 | 3501 | 834 | 1600 | 0 | 966 | 719 | 33 | 235 | 130 | 120 | 0 | 0
4:30 | 3344 | 736 | 1472 | 0 | 651.5 | 669.5 | 33.5 | 212.5 | 115 | 105 | 0 | 0
5:00 | 3187 | 638 | 1344 | 0 | 337 | 620 | 34 | 190 | 100 | 90 | 0 | 0
5:30 | 3166 | 734.5 | 1354 | 0 | 289 | 615 | 34.5 | 140 | 50 | 91 | 0 | 0
6:00 | 3145 | 831 | 1364 | 0 | 241 | 610 | 35 | 90 | 0 | 92 | 0 | 0
6:30 | 3147 | 782 | 1395 | 0 | 249 | 610 | 35 | 90 | 0 | 87 | 13.5 | 0 |  |  |  |  | Coal
7:00 | 3149 | 733 | 1426 | 0 | 257 | 610 | 35 | 90 | 0 | 82 | 27 | 0
7:30 | 3162.5 | 732.5 | 1405 | 0 | 248.5 | 630 | 35 | 90 | 0 | 81 | 41.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3176 | 732 | 1384 | 0 | 240 | 650 | 35 | 90 | 0 | 80 | 56 | 0
8:30 | 3224 | 729.5 | 1400 | 0 | 217.5 | 650 | 35 | 90 | 0 | 83 | 99.5 | 0
9:00 | 3272 | 727 | 1416 | 0 | 195 | 650 | 35 | 90 | 0 | 86 | 143 | 0
9:30 | 3308 | 726.5 | 1464 | 0 | 200 | 665 | 35 | 90 | 0 | 88 | 171 | 0
10:00 | 3344 | 726 | 1512 | 0 | 205 | 680 | 35 | 90 | 0 | 90 | 199 | 0
10:30 | 3457.5 | 726 | 1532.5 | 0 | 236 | 680 | 35 | 63.5 | 0 | 89 | 200.5 | 0
11:00 | 3571 | 726 | 1553 | 0 | 267 | 680 | 35 | 37 | 0 | 88 | 202 | 0
11:30 | 3622.5 | 794 | 1606 | 0 | 309 | 680 | 32.5 | 18.5 | 0 | 92 | 195 | 0
12:00 | 3674 | 862 | 1659 | 0 | 351 | 680 | 30 | 0 | 0 | 96 | 188 | 0
12:30 | 3811 | 889.5 | 1728.5 | 0 | 368.5 | 695 | 32.5 | 0 | 0 | 94 | 198 | 0
13:00 | 3948 | 917 | 1798 | 0 | 386 | 710 | 35 | 0 | 0 | 92 | 208 | 0
13:30 | 3948 | 917 | 1798 | 0 | 386 | 710 | 35 | 0 | 0 | 92 | 208 | 0
14:00 | 3948 | 917 | 1798 | 0 | 386 | 710 | 35 | 0 | 0 | 92 | 208 | 0
14:30 | 4036 | 920 | 1997 | 0 | 559.5 | 725 | 35 | 0 | 0 | 95 | 177.5 | 0
15:00 | 4124 | 923 | 2196 | 0 | 733 | 740 | 35 | 0 | 0 | 98 | 147 | 0
15:30 | 4073.5 | 923 | 2172 | 0 | 787 | 740 | 35 | 0 | 0 | 94 | 120.5 | 0
16:00 | 4023 | 923 | 2148 | 0 | 841 | 740 | 35 | 0 | 0 | 90 | 94 | 0
16:30 | 4051 | 923 | 2083.5 | 0 | 858 | 725 | 35 | 0 | 0 | 89 | 68.5 | 0
17:00 | 4051 | 923 | 2019 | 0 | 875 | 710 | 35 | 0 | 0 | 88 | 43 | 0
17:30 | 4049 | 922.5 | 2042 | 0 | 894.5 | 700 | 35 | 0 | 0 | 90 | 24 | 0
18:00 | 4047 | 922 | 2065 | 0 | 914 | 690 | 35 | 0 | 0 | 92 | 5 | 0
18:30 | 4058 | 922.5 | 2150 | 0 | 1353 | 755 | 35 | 0 | 136.5 | 95 | 2.5 | 0
19:00 | 4069 | 923 | 2235 | 0 | 1792 | 820 | 35 | 0 | 273 | 98 | 0 | 0
19:30 | 3999 | 922 | 2179 | 0 | 2137 | 990 | 35 | 0 | 279 | 96 | 0 | 0
20:00 | 4141 | 923 | 2366 | 0 | 1919 | 980 | 35 | 0 | 263 | 98 | 0 | 0
20:30 | 4271.5 | 921 | 2449.5 | 0 | 1756 | 990 | 35 | 0 | 225 | 113.5 | 0 | 0
21:00 | 4402 | 919 | 2533 | 0 | 1593 | 1000 | 35 | 0 | 187 | 129 | 0 | 0
21:30 | 4522.5 | 919.5 | 2561.5 | 0 | 1505.5 | 1020 | 35 | 0 | 160.5 | 115.5 | 0 | 0
22:00 | 4643 | 920 | 2590 | 0 | 1418 | 1040 | 35 | 0 | 134 | 102 | 0 | 0
22:30 | 4655 | 920.5 | 2612 | 0 | 1336 | 1020 | 35 | 0 | 136 | 104 | 0 | 0
23:00 | 4667 | 921 | 2634 | 0 | 1254 | 1000 | 35 | 0 | 138 | 106 | 0 | 0
23:30 | 4675 | 921.5 | 2623.5 | 0 | 1224.5 | 1000 | 35 | 0 | 138 | 105 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.4° C
24:00 | 4683 | 922 | 2613 | 0 | 1195 | 1000 | 35 | 0 | 138 | 104 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 212.758 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.758 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [11 empty] | 30 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 447240
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 33 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | [14 empty] | 392000
3 | Chattogram TPP-1 | [24 empty] | 0 | 30 | 100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 16 | 16 | 16 | 16 | [9 empty] | 3 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 164167
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 9 | 13 | 15 | 15 | 15 | 16 | 16 | 12 | 7 | 3 | 0 | [8 empty] | 126630
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 181 | 177 | 177 | 177 | 178 | 177 | 176 | 187 | 203 | 218 | 203 | 212 | 203 | 204 | 204 | 207 | 221 |  | 203 | 204 | 203 | 203 | 203 | 204 | 203 | 4668264
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 46 | 51 | 51 | 274424
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 10 | 17 | 17 | 0 |  |  |  | 43490
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 0 |  |  |  | 69280
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 |  | 250 | 250 | 335 | 335 | 336 | 335 | 336 | 6359503
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 10 |  | 42 | 90 | 15 | 0 |  |  |  | 125454
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 150545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 170 | 170 | 171 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 160 | 180 | 180 | 229 | 228 | 228 | 228 |  | 232 | 180 | 180 | 212 | 234 | 233 | 233 | 4413000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 270 | 270 | 270 | 270 |  | 270 | 220 | 220 | 252 | 280 | 280 | 280 | 5979382
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 31 | 31 | 31 | 31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 31 | 31 | 28 | 28 | 28 | 30 |  | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 577800
33 | Ashuganj 225 MW CCPP | 214 | 212 | 182 | 182 | 188 | 154 | 155 | 155 | 155 | 159 | 184 | 190 | 209 | 216 | 210 | 211 | 211 | 210 |  | 216 | 214 | 215 | 216 | 217 | 214 | 217 | 4753000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 270 | 285 | 280 | 280 | 280 | 290 | 290 | 305 | 295 | 315 | 280 | 285 | 280 | 295 | 335 |  | 280 | 280 | 280 | 280 | 280 | 295 | 280 | 7219400
35 | Ashuganj 55 MW PP (Precision) | 52 | 50 | 52 | 52 | 5 | 5 | 5 | 5 |  |  |  |  | 0 | 25 | 52 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 55 | 56 | 57 | 834720
36 | Chandpur 150 MW CCPP | 136 | 137 | 137 | 135 | 122 | 121 | 124 | 123 | 124 | 137 | 137 | 137 | 137 | 137 | 136 | 137 | 137 | 136 |  | 136 | 137 | 136 | 136 | 137 | 136 | 135 | 3156050
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 360 | 354 | 313 | 284 | 284 | 283 | 283 | 283 | 326 | 364 | 366 | 367 | 390 | 379 | 303 | 303 | 303 |  | 314 | 396 | 395 | 397 | 396 | 396 | 397 | 8349690
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 340 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 340 | 340 | 340 | 310 | 310 |  | 310 | 310 | 380 | 400 | 400 | 400 | 400 | 7907250
41 | Haripur 360MW CCPP(HPL) | 302 | 302 | 303 | 232 | 233 | 234 | 202 | 203 | 201 | 202 | 201 | 202 | 252 | 302 | 272 | 272 | 271 | 252 |  | 252 | 252 | 322 | 327 | 332 | 336 | 332 | 6346000
42 | RPCL 210MW CCPP | 192 | 211 | 192 | 160 | 159 | 158 | 156 | 160 | 160 | 204 | 200 | 200 | 200 | 200 | 202 | 201 | 201 | 200 |  | 208 | 208 | 209 | 210 | 210 | 208 | 210 | 4521600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 2 | 49 | 34 | 51 | 27 | 51 | 49 | 37 | 23 | 10 | 2 | [8 empty] | 342310
44 | Fenchugonj CCPP Phase-1 | [15 empty] | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 177000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 980160
46 | Shajibazar 330 MW CCPP | 110 | 110 | 110 | 110 | 85 | 85 | 85 | 85 | 86 | 86 | 109 | 110 | 107 | 109 | 106 | 107 | 107 | 109 |  | 109 | 111 | 110 | 110 | 109 | 110 | 110 | 2449000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 40 |  | 40 | 40 | 60 | 60 | 60 | 60 | 55 | 119568
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 40 | 40 | 20 | 10 | 10 | 10 | 10 | 0 |  |  |  | 40 | 81 | 81 | 50 | 50 | 50 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1023360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 204 | 178 | 138 | 138 | 138 | 138 | 139 | 139 | 139 | 139 | 178 | 219 | 219 | 219 | 219 | 219 | 180 |  | 215 | 218 | 218 | 218 | 218 | 219 | 219 | 4470550
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 11 | 11 | 11 |  | 26 | 26 | 26 | 25 | 26 | 26 | 26 | 251200
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 159840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | [13 empty] | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 117024
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 11 | 11 | 11 | [9 empty] | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 645600
56 | Shahjahanulla 25 MW PP | 17 | 17 | 11 | 11 | [13 empty] | 16 |  | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 194304
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 270 | 260 | 255 | 165 | 165 | 165 | 165 | 190 | 245 | 245 | 305 | 315 | 290 | 280 | 300 | 290 | 300 |  | 280 | 270 | 265 | 270 | 270 | 280 | 290 | 6239500
| Bibiyana South 400 MW | 400 | 340 | 330 | 292 | 300 | 296 | 330 | 330 | 330 | 340 | 340 | 340 | 350 | 401 | 365 | 360 | 361 | 330 |  | 340 | 370 | 400 | 374 | 401 | 400 | 401 | 8503000
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 35 | 17 | 17 | 0 |  |  | 75010
59 | Tangail Palli Power Gen 22 MW | 22 | 23 | [17 empty] | 15 | 15 | 18 | 24 | 24 | 24 | 24 | 184560
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530352
61 | Narshingdi 22 MW PP (Doreen) | 22 | 19 | 19 | 19 | [12 empty] | 10 | 10 |  | 10 | 10 | 10 | 10 | 22 | 22 | 22 | 173880
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 0 | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 206604
63 | Impoprt (Tripura) | 120 | 118 | 120 | 120 | 90 | 92 | 82 | 80 | 86 | 90 | 88 | 96 | 92 | 98 | 98 | 90 | 88 | 92 |  | 98 | 96 | 98 | 129 | 102 | 106 | 104 | 2293440
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 14 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1038240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | [6 empty] | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 301032
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | [6 empty] | 0 |  |  | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 145620
67 | Jangalia 33MW PP (Summit) | 32 | 33 | 33 | 30 | [5 empty] | 13 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 30 | 30 | 33 | 33 | 33 | 33 | 588300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 |  |  |  | 12 | 12 | 12 | 12 | 12 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 400150
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 22 | 22 | 15 | 0 | 0 | 10 | 10 | 8 | 8 | 3 | 3 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 235260
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 603400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 557900
73 | Ghorashal 108MW PP (Regent) | 101 | 12 | 12 | 12 | [9 empty] | 32 | 92 | 53 | 24 | 24 |  | 22 | 22 | 40 | 104 | 104 | 104 | 104 | 857272
| Feni Lanka Power | 80 | 80 | 80 | 80 | [8 empty] | 15 | 34 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 80 | 80 | 80 | 967860
| Chowmuhani 113 MW | 60 | 60 | 58 | 58 | [9 empty] | 20 | 84 | 96 | 106 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1332240
| Manikgonj 162MW PP(MPGL) | [19 empty] | 13 | 17 | 17 | 0 |  |  | 0 | 50400
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 5 | 7 | 7 | 0 |  |  |  | 12480
78 | Gazipur 52 MW PP | [19 empty] | 8 | 8 |  | 0 |  |  |  | 13440
79 | Kodda 150MW PP | [19 empty] | 16 | 16 | 0 |  |  |  |  | 17760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 25 | [10 empty] | 2 | 8 | 8 | 8 |  | 23 | 34 | 34 | 26 | 25 | 32 | 34 | 383981
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 17 | [14 empty] | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 631200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 4 | 4 | 5 | 5 | 5 | 3 | 3 | 2 | 1 | [9 empty] | 34920
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 49 | 54 | 54 | 54 | 54 | 54 | 54 | 1172326
| Karnaphuli Power Ltd. | 107 | 106 | 110 | 110 | 68 | 68 | 68 | 68 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 70 | 110 | 110 | 110 | 68 | 68 | 68 | 1853373
82 | Madanganj 102 PP(Summit) | 64 | 48 | 48 | 35 | [7 empty] | 10 | 15 | 15 | 19 | 40 | 48 | 48 |  | 62 | 78 | 78 | 78 | 78 | 78 | 48 | 870144
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 270 | 255 | 260 | 220 | 265 | 230 | 275 | 240 | 275 | 275 | 275 | 280 | 275 | 225 | 260 | 260 | 280 | 300 |  | 215 | 230 | 270 | 220 | 240 | 275 | 245 | 6260015
87 | Meghnaghat 100 MW(IEL) | [14 empty] | 18 | 30 | 31 | 31 |  | 39 | 60 | 59 | 77 | 24 | 0 |  | 330240
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 17 | 17 | 17 | 0 |  |  |  | 48960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 4 | 10 | 10 | 0 |  |  |  | 16920
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | [9 empty] | 10 | 10 | 10 | 10 | 12 |  | 42 | 47 | 50 | 50 | 50 | 50 | 50 | 384120
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | [9 empty] | 3 | 10 | 10 | 10 | 10 |  | 27 | 51 | 51 | 51 | 51 | 51 | 51 | 519991
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 7 | 7 | 7 | 0 |  |  |  | 15840
95 | Patenga 50MW PP (Baraka) | 18 | 18 | 18 | [16 empty] | 7 | 12 | 12 | 0 |  |  |  | 92160
96 | Chattogram 108 MW PP (ECPV) |  |  |  | 4 | [9 empty] | 2 | 24 | 25 | 26 | 25 |  | 37 | 50 | 74 | 91 | 95 | 83 | 83 | 586560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 0 | 15 | 0 |  |  |  |  | 13337
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 | 0 |  |  |  |  | 32627
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 110 | [7 empty] | 40 | 40 | 40 | 110 | 110 | 110 | 110 |  | 130 | 110 | 110 | 163 | 163 | 163 | 163 | 2096345
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 12600
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 35 | 17 | 0 |  | 308160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 80 | 80 | 80 | 32 | 8 | [5 empty] | 2 | 16 | 16 | 16 | 16 | 32 | 32 | 37 |  | 163 | 185 | 140 | 140 | 140 | 80 | 60 | 1821600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 25 | 16 | 16 | [16 empty] | 3 | 16 | 16 | 0 |  |  |  | 97920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 10 | 10 | 10 | 10 | 10 | 10 | 60 | 90 | 90 | 90 | 76 | 76 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1623360
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 17 | [15 empty] | 21 | 34 | 34 | 17 | 17 | 0 |  | 402720
117 | Ashuganj 150MW PP (Midland) | [19 empty] | 6 | 10 | 0 |  |  |  |  | 18400
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 240 | 240 | 240 | 240 | 238 | 240 | 314 | 240 | 298 | 327 | 401 | 402 | 403 | 367 | 365 | 386 |  | 402 | 353 | 353 | 400 | 401 | 402 | 402 | 8087000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 108 | 45 | 8 | 8 | 8 |  |  | 3 | 16 | 16 | 16 | 16 | 54 | 54 | 58 |  | 107 | 115 | 115 | 115 | 115 | 95 | 95 | 1448400
| Anwara 300 MW PP (United) | 300 | 300 | 260 | 170 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 220 | 230 | 240 | 240 | 240 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5121055
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | [8 empty] | 4 | 20 | 18 | 10 | 10 | 10 |  | 17 | 50 | 50 | 23 | 0 |  |  | 212160
| Anlima Energy Ltd. | 34 | 34 | 34 | [16 empty] | 20 | 68 | 51 | 34 | 17 |  |  | 276000
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 |  | 1 | 17 |  |  | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 380160
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 10 | 5 | 33 | 22 | 30 | 31 | 27 | 21 | 14 | 6 | 0 | [8 empty] | 190381
| Chandpur 115(Doreen) | 59 | 59 | 59 | 50 | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 |  | 30 | 51 | 51 | 51 | 51 | 45 | 34 | 625920
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | [15 empty] | 6 |  | 46 | 55 | 35 | 0 |  |  |  | 185760
120 | Eastern Zone Total | 6828 | 6533 | 6151 | 5438 | 4218 | 4061 | 4143 | 4115 | 4254 | 4408 | 4661 | 4942 | 5324 | 5836 | 6103 | 6027 | 6009 | 6061 |  | 6877 | 7234 | 7350 | 7286 | 7234 | 7139 | 7070 | 139991160
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 32 | 32 | 16 |  |  |  |  | 47040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 37 | [15 empty] | 1140480
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 10 |  | 35 | 35 | 53 | 53 | 53 | 70 | 70 | 337440
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 11 | 29 | 68 | 108 | 100 | 99 | 94 | 78 | 67 | 43 | 20 | 3 | [8 empty] | 719280
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 216 | 150 | 152 | 44 | 53 | 84 | 131 | 132 | 164 | 164 | 164 | 164 | 164 | 202 | 212 | 212 | 185 | 163 |  | 205 | 213 | 205 | 200 | 215 | 219 | 217 | 4065982
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | [18 empty] | 16 | 16 | [5 empty] | 64128
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 86 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 83 |  | 87 | 87 | 88 | 80 | 88 | 86 | 87 | 1935399
140 | Bhola 33 MW PP (Venture) | 37 | 38 | 38 | 27 | 28 | 28 | 25 | 24 | 24 | 24 | 26 | 26 | 30 | 32 | 34 | 33 | 30 | 31 |  | 39 | 38 | 38 | 39 | 38 | 38 | 38 | 742420
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 8 | 8 |  |  |  |  | 14250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 | 15 | 15 |  |  | 84240
146 | Bheramara HVDC | 924 | 923 | 923 | 834 | 638 | 831 | 733 | 732 | 727 | 726 | 726 | 862 | 917 | 918 | 923 | 923 | 923 | 922 |  | 923 | 922 | 923 | 919 | 920 | 921 | 922 | 20745454
147 | Bheramara 410 MW CCPP | 300 | 250 | 250 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 300 | 300 | 300 | 300 | 250 |  | 250 | 250 | 250 | 370 | 390 | 390 | 390 | 6643296
148 | Payra 1320 MW | 720 | 560 | 520 | 520 | 440 | 440 | 440 | 480 | 480 | 480 | 480 | 480 | 510 | 540 | 540 | 540 | 510 | 490 |  | 620 | 790 | 780 | 800 | 840 | 800 | 800 | 15852300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 199 | 180 | 170 | 170 | 170 | 170 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4710300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 50 | 50 | [20 empty] | 427000
| Baghabari 50 MW Peaking PP | [19 empty] | 34 | 34 | 34 | 8 | 0 |  |  | 90112
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 2 | 2 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 32880
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 130 | 130 | 130 | 105 | 113 | 120 | 130 | 130 | 130 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 130 | 130 | 141 | 200 | 214 | 214 | 4139273
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [16 empty] | 1 | 10 |  | 8 | 15 | 23 | 67 | 130 | 130 | 130 | 553446
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 130 | 130 | 130 | 130 | 100 | [11 empty] | 0 | [9 empty] | 723818
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 354 | 256 | 252 | 214 | 258 | 258 | 258 | 250 | 220 | 260 | 300 | 300 | 340 | 414 | 300 | 300 | 250 | 304 |  | 417 | 340 | 340 | 414 | 430 | 420 | 424 | 7587491
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 5 |  | 5 | 5 | 0 |  |  |  |  | 20 | 20 | 20 | 21 | 21 |  | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 337440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 |  |  |  |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 194976
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 0 | [5 empty] | 7157
167 | Katakhali 50 MW Peaking PP | [19 empty] | 34 | 40 | 40 | 40 | 0 |  |  | 84170
168 | Santahar 50 MW Peaking PP | [19 empty] | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 217612
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 50880
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 291792
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [12 empty] | 14 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 0 |  |  |  | 358752
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 35 | 35 | 0 |  |  |  | 107136
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 29 | [14 empty] | 6 |  | 34 | 39 | 34 | 37 | 0 |  |  | 251068
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 2 | 3 | 5 | 3 | 2 | 2 | 2 | 2 | 0 | [8 empty] | 26018
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | [16 empty] | 34 | 0 | [5 empty] | 183744
178