## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-15 | Sunday
|  |  | Date (day): | 2022-05-15 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14813.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15420 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-14 | 2022-05-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 |  | 95 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 96 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 395 | 360 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 282 | 334 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 82 | 90 | 95 | 95
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 125 | 125 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 43 | 95 | 96 | 96 |  | 6 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 94 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 334 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 84 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 133 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 54 | 54 |  | 26 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 240 | 290 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 53 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 78 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 88 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 100 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 60 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 109 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 2958 | 3892 | 4194 | 4274 | 701 | 841
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 49 | 49 | 49 | 49
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 |  | 200 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 223 | 203 | 205 | 205
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 40 | 80 | 80 | 80 |  | 20 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 76 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 13 | 15 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 93 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 245 | 281 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 110 | 106 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 99 | 77 | 110 | 110 |  | 6 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1102 | 1420 | 1514 | 1503 | 411 | 445
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 196 | 210 | 225
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 | 80 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 30 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Line Tripped
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 132 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 41 | 41 |  | 11 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 134 | 135 | 135 |  | 28 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 190 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 120 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 42 | 34 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 100 | 100 | 100 |  | 14 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 32 | 105 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 82 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1045 | 1617 | 1931 | 1969 | 945 | 106
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 96 | 120 | 150 | 52 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 40 | 181 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 106 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 12 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 316 | 427 | 528.6 | 507 | 52 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 253 | 269 | 270 | 270 | 60 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 48 | 50 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 30 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 36 | 39 | 38 | 41 | 9 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 285 | 300 | 341
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Engine problem
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 381 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1661 | 1697 | 1746 | 1790 | 69 | 575
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 915 | 927 | 927
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 28 | 99 | 16 | 99 | 16 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 205 | 200 | 250 | 300 | 110 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 35 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1209 | 1527 | 1870 | 1963 | 126 | 76
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 21 | 30 | 30 | 30
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 86 | 87 | 87 | 107 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 680 | 850 | 800 | 1000
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 170 | 216 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 951 | 1215 | 1204 | 1597 | 107 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 36 | 40 |  | 12 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 139 | 147 | 225 | 225 |  |  | DCT
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 393 | 416 | 400 | 400
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 8 | 37 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 52 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 200 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 710 | 1104 | 1420 | 1419 | 601 | 94
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 |  | 99 | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 52 | 108 | 108 | 108 |  | 5 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 232 | 398 | 406 | 398 | 0 | 274
|  | Total |  |  |  |  | 22348 | 21584 | 10184 | 13297 | 14813.6 | 15420 | 3012 | 2419
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9899.3964 | 12925.4 | 14399.6169 | 14989.0703
| A. |  | 2022-05-14 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13297 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8841 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13297 | MW
| 3 | Day peak Generation : |  |  | 10184 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12925.4 | MW
| 4 | Evening peak Generation : |  |  | 13297 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 260.8376 | MKWHr | By Solar | 0.89501 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 143.0034 | MKWHr |  | By Oil: | 66.4984 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 25.0257 | MKWHr |  | By Hydro: | 0.728 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3012 | MW | Dhaka | 4713.1 | 4713.1 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2419 | MW | Chittagong | 1431.5 | 1431.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5431 | MW | Khulna | 1587.4 | 1587.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1049.3 | MMCFD |  |  | Rajshahi | 1330.4 | 1330.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145699306.532 | ii) Oil : | Taka | 490448568.44 | Comilla | 1224 | 1224 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 114267927 | Total | Taka | 750415801.972 | Mymensingh | 1012 | 1012 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.043 | MKWHr. | Sylhet | 452 | 452 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -52 | MW (E to W) at | 19:30 | hrs | Barisal | 392 | 392 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -52 | MW at | 19:30 | hrs | Rangpur | 783 | 783 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.9° C |  |  | Total | 12925.4 | 12925.4 |  | 0
| B. |  | 2022-05-15 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 38.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15420 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
| 4 | Reserve(Generation end) |  |  |  | 1920 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 264.8197 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9536 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1796 | MKWHr. | ii) HVDC Flow at Peak Time |  | 915 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5075 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.17 |  | (b) Today: | 74.12 |  | (c) Rule Curve: |  | 79.34
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 130 | 92 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 54 | 48 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 193 | 8 | 134 | 32 | 0 | 0 | 51 | 0 | 0 | 34 | 19 | 5 | 33 | 20 | 106 | 107 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 163 | 267 | 60 | 75 | 0 | 219 | 0 | 38 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 64 | 17 | 0 | 0 | 115 | 34 | 85 | 0 | 300 | 54 | 110 | 100 | 40 | 50 | 400 | 35 | 0 | 35 | 99 | 0 | 17 | 0 | 0 | 17 |  | 912 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 145 | 0 | 423 | 0 | 0 | 113 | 0 | 40 | 0 | 0 | 113 | 930 | 218 | 0 | 17 | 0 | 0 | 0 |  | 6724 | 3524 | 10248 | 3936 | 912 | 2251 | 0 | 1908 | 1105 | 30 | 0 | 0 | 106 | 0 | 0 | 74.17
2:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 120 | 92 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 44 | 49 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 184 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 0 | 38 | 19 | 5 | 33 | 20 | 104 | 115 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 163 | 269 | 60 | 75 | 0 | 219 | 0 | 36 | 10 | 280 | 22 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 85 | 0 | 51 | 0 | 245 | 54 | 110 | 90 | 38 | 50 | 400 | 17 | 0 | 17 | 99 | 0 | 17 | 0 | 0 | 0 |  | 912 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 145 | 0 | 419 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 890 | 218 | 0 | 17 | 0 | 0 | 0 |  | 6404 | 3322 | 9726 | 3936 | 912 | 2233 | 0 | 1446 | 1065 | 30 | 0 | 0 | 104 | 0 | 0 | 74.17
3:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 120 | 87 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 11 | 49 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 192 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 33 | 20 | 100 | 162 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 163 | 268 | 60 | 72 | 0 | 219 | 0 | 36 | 10 | 285 | 22 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 150 | 54 | 110 | 90 | 38 | 50 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 0 |  | 910 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 145 | 0 | 425 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 850 | 218 | 0 | 17 | 0 | 0 | 0 |  | 6221 | 3302 | 9523 | 4006 | 910 | 2241 | 0 | 1211 | 1025 | 30 | 0 | 0 | 100 | 0 | 0 | 74.17
4:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 120 | 83 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 11 | 49 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 202 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 19 | 20 | 98 | 152 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 130 | 266 | 50 | 72 | 0 | 179 | 0 | 36 | 10 | 280 | 21 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 65 | 0 | 25 | 0 | 150 | 54 | 110 | 99 | 38 | 38 | 370 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 0 |  | 911 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 143 | 0 | 380 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 800 | 218 | 0 | 17 | 0 | 0 | 0 |  | 6020 | 3252 | 9272 | 3887 | 911 | 2158 | 0 | 1213 | 975 | 30 | 0 | 0 | 98 | 0 | 0 | 74.17
5:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 115 | 84 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 11 | 49 | 22 | 42 | 0 | 0 | 0 | 280 | 0 | 202 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 0 | 41 | 19 | 5 | 24 | 20 | 94 | 152 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 130 | 266 | 50 | 72 | 0 | 179 | 0 | 37 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 65 | 0 | 51 | 0 | 150 | 54 | 110 | 99 | 38 | 38 | 370 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 0 |  | 914 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 134 | 0 | 360 | 0 | 0 | 35 | 0 | 15 | 0 | 0 | 35 | 760 | 218 | 0 | 17 | 0 | 0 | 0 |  | 6005 | 3237 | 9242 | 3939 | 914 | 2133 | 0 | 1197 | 935 | 30 | 0 | 0 | 94 | 0 | 0 | 74.17
6:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 363 | 297 |  | 0 | 225 | 130 | 82 | 0 | 30 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 11 | 49 | 22 | 30 | 0 | 0 | 0 | 280 | 0 | 193 | 8 | 136 | 32 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 24 | 20 | 92 | 147 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 110 | 268 | 40 | 72 | 0 | 179 | 0 | 36 | 10 | 270 | 8 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 40 | 0 | 51 | 0 | 150 | 54 | 106 | 88 | 38 | 38 | 350 | 17 | 1 | 17 | 68 | 0 | 17 | 0 | 0 | 0 |  | 917 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 130 | 0 | 333 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 730 | 218 | 0 | 17 | 0 | 4 | 0 |  | 5816 | 3109 | 8925 | 3845 | 917 | 2040 | 0 | 1090 | 905 | 30 | 0 | 0 | 92 | 6 | 0 | 74.17
7:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 352 | 281 |  | 0 | 225 | 125 | 83 | 0 | 30 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 49 | 0 | 26 | 0 | 0 | 0 | 280 | 0 | 194 | 8 | 134 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 90 | 148 | 0 | 20 | 0 | 43 | 42 | 53 | 50 | 110 | 268 | 40 | 72 | 0 | 179 | 0 | 36 | 10 | 280 | 20 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 40 | 0 | 17 | 2 | 150 | 54 | 92 | 88 | 39 | 38 | 350 | 17 | 2 | 17 | 68 | 0 | 17 | 0 | 0 | 0 |  | 919 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 130 | 0 | 330 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 700 | 218 | 0 | 17 | 0 | 14 | 0 |  | 5749 | 3092 | 8841 | 3840 | 919 | 2019 | 0 | 1044 | 875 | 30 | 0 | 0 | 90 | 24 | 0 | 74.16
8:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 352 | 281 |  | 0 | 225 | 140 | 83 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 11 | 0 | 0 | 30 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 11 | 49 | 20 | 10 | 0 | 0 | 0 | 280 | 0 | 169 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 98 | 136 | 0 | 20 | 0 | 43 | 43 | 53 | 50 | 130 | 266 | 40 | 72 | 0 | 179 | 0 | 36 | 10 | 300 | 20 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 75 | 0 | 17 | 2 | 150 | 54 | 93 | 70 | 38 | 38 | 388 | 17 | 1 | 17 | 68 | 0 | 17 | 0 | 0 | 1 |  | 922 | 0 | 235 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 132 | 0 | 335 | 3 | 0 | 35 | 0 | 1 | 0 | 2 | 0 | 690 | 192 | 0 | 17 | 0 | 36 | 0 |  | 5884 | 3081 | 8965 | 3897 | 922 | 2032 | 0 | 1078 | 865 | 30 | 0 | 0 | 98 | 43 | 0 | 74.16
9:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 353 | 282 |  | 0 | 225 | 120 | 83 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 3 | 19 | 25 | 28 | 25 | 30 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 14 | 49 | 20 | 3 | 0 | 0 | 0 | 280 | 0 | 171 | 8 | 136 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 0 | 20 | 92 | 120 | 0 | 20 | 0 | 44 | 42 | 53 | 50 | 163 | 267 | 60 | 72 | 0 | 211 | 0 | 36 | 0 | 290 | 0 | 11 | 0 | 5 | 0 | 0 | 8 | 0 | 19 | 5 | 38 | 0 | 3 | 0 | 108 | 27 | 22 | 1 | 200 | 54 | 93 | 70 | 38 | 38 | 400 | 17 | 9 | 17 | 85 | 0 | 17 | 0 | 0 | 17 |  | 923 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 132 | 0 | 374 | 17 | 0 | 35 | 0 | 29 | 0 | 3 | 0 | 680 | 192 | 0 | 0 | 0 | 43 | 0 |  | 6156 | 3124 | 9280 | 3914 | 923 | 2059 | 0 | 1298 | 855 | 30 | 0 | 48 | 92 | 61 | 0 | 74.16
10:00 | 0 | 0 | 0 | 170 | 270 | 94 | 0 | 353 | 282 |  | 0 | 225 | 130 | 83 | 1 | 37 | 332 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 27 | 25 | 33 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 63 | 50 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 136 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 0 | 21 | 92 | 108 | 0 | 20 | 0 | 44 | 41 | 50 | 50 | 163 | 268 | 60 | 72 | 0 | 219 | 0 | 38 | 10 | 280 | 0 | 11 | 0 | 75 | 0 | 0 | 8 | 0 | 45 | 15 | 38 | 0 | 20 | 0 | 115 | 52 | 68 | 3 | 245 | 54 | 78 | 70 | 37 | 38 | 400 | 17 | 4 | 17 | 99 | 0 | 17 | 0 | 0 | 17 |  | 923 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 121 | 0 | 374 | 17 | 0 | 35 | 0 | 36 | 0 | 4 | 20 | 670 | 192 | 0 | 0 | 1 | 58 | 0 |  | 6508 | 3117 | 9625 | 3882 | 923 | 2059 | 0 | 1661 | 845 | 30 | 0 | 48 | 92 | 85 | 0 | 74.16
11:00 | 0 | 0 | 0 | 170 | 270 | 96 | 0 | 358 | 282 |  | 0 | 225 | 130 | 82 | 45 | 40 | 331 | 0 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 0 | 54 | 15 | 35 | 19 | 25 | 24 | 0 | 33 | 40 | 0 | 0 | 30 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 74 | 49 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 187 | 8 | 136 | 32 | 0 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 0 | 21 | 96 | 107 | 0 | 20 | 1 | 44 | 41 | 45 | 50 | 163 | 265 | 60 | 75 | 0 | 219 | 0 | 37 | 10 | 295 | 0 | 11 | 0 | 150 | 0 | 0 | 17 | 0 | 49 | 15 | 38 | 5 | 20 | 0 | 108 | 52 | 81 | 4 | 245 | 54 | 73 | 70 | 32 | 38 | 400 | 17 | 26 | 17 | 99 | 0 | 17 | 0 | 0 | 20 |  | 923 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 375 | 17 | 0 | 35 | 0 | 34 | 0 | 4 | 50 | 680 | 192 | 0 | 0 | 0 | 94 | 0 |  | 6749 | 3069 | 9818 | 3750 | 923 | 2075 | 0 | 1897 | 855 | 30 | 0 | 48 | 96 | 144 | 0 | 74.15
12:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 352 | 282 |  | 0 | 225 | 145 | 82 | 43 | 40 | 324 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 27 | 25 | 32 | 42 | 0 | 0 | 30 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 82 | 49 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 136 | 32 | 0 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 0 | 15 | 116 | 104 | 0 | 20 | 1 | 44 | 41 | 50 | 48 | 163 | 253 | 58 | 72 | 0 | 219 | 0 | 36 | 10 | 275 | 0 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 88 | 0 | 38 | 17 | 20 | 0 | 115 | 52 | 105 | 1 | 245 | 54 | 73 | 70 | 32 | 38 | 381 | 60 | 12 | 109 | 99 | 0 | 17 | 0 | 0 | 55 |  | 924 | 0 | 205 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 393 | 17 | 0 | 70 | 0 | 52 | 0 | 5 | 70 | 680 | 170 | 0 | 0 | 2 | 35 | 0 |  | 7082 | 3102 | 10184 | 3716 | 924 | 2072 | 0 | 2367 | 855 | 30 | 0 | 48 | 116 | 56 | 0 | 74.15
13:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 390 | 322 |  | 0 | 225 | 125 | 82 | 64 | 47 | 312 | 0 | 0 | 4 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 18 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 92 | 48 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 138 | 33 | 0 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 0 | 15 | 118 | 104 | 0 | 20 | 1 | 44 | 41 | 50 | 47 | 110 | 264 | 40 | 75 | 0 | 219 | 0 | 38 | 10 | 290 | 0 | 11 | 0 | 195 | 0 | 0 | 67 | 0 | 114 | 19 | 38 | 23 | 28 | 0 | 115 | 52 | 105 | 1 | 283 | 54 | 74 | 70 | 27 | 38 | 304 | 78 | 15 | 155 | 99 | 0 | 17 | 0 | 0 | 55 |  | 922 | 0 | 200 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 40 | 84 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 415 | 30 | 0 | 90 | 32 | 77 | 0 | 5 | 90 | 720 | 174 | 0 | 0 | 5 | 83 | 0 |  | 7242 | 3409 | 10651 | 3641 | 922 | 2081 | 0 | 2787 | 895 | 30 | 0 | 48 | 118 | 129 | 0 | 74.15
14:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 363 | 318 |  | 0 | 225 | 140 | 88 | 70 | 55 | 280 | 0 | 0 | 16 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 25 | 32 | 49 | 0 | 0 | 30 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 92 | 49 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 42 | 18 | 5 | 33 | 18 | 106 | 69 | 0 | 20 | 1 | 44 | 41 | 50 | 47 | 110 | 257 | 40 | 75 | 0 | 219 | 0 | 37 | 10 | 285 | 0 | 11 | 0 | 195 | 0 | 0 | 90 | 0 | 149 | 12 | 38 | 34 | 40 | 0 | 115 | 52 | 105 | 5 | 283 | 54 | 85 | 70 | 28 | 38 | 360 | 104 | 21 | 162 | 99 | 0 | 17 | 0 | 0 | 55 |  | 922 | 0 | 200 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 365 | 70 | 0 | 94 | 32 | 103 | 0 | 5 | 90 | 690 | 210 | 0 | 0 | 1 | 46 | 0 |  | 7400 | 3429 | 10829 | 3644 | 922 | 2076 | 0 | 3047 | 865 | 30 | 0 | 48 | 106 | 91 | 0 | 74.15
15:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 383 | 312 |  | 0 | 225 | 140 | 86 | 79 | 55 | 320 | 0 | 0 | 16 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 25 | 32 | 40 | 0 | 0 | 30 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 92 | 48 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 42 | 18 | 5 | 33 | 20 | 110 | 69 | 0 | 17 | 1 | 44 | 41 | 50 | 50 | 163 | 253 | 42 | 75 | 0 | 219 | 0 | 37 | 10 | 310 | 0 | 11 | 0 | 195 | 0 | 0 | 110 | 0 | 149 | 12 | 38 | 44 | 46 | 0 | 115 | 65 | 105 | 4 | 266 | 54 | 92 | 70 | 28 | 38 | 394 | 104 | 37 | 162 | 99 | 0 | 17 | 0 | 0 | 55 |  | 917 | 0 | 200 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 32 | 102 | 0 | 3 | 100 | 740 | 210 | 0 | 0 | 3 | 29 | 0 |  | 7628 | 3535 | 11163 | 3732 | 917 | 2203 | 0 | 3119 | 915 | 30 | 0 | 48 | 110 | 89 | 0 | 74.14
16:00 | 0 | 0 | 0 | 170 | 270 | 97 | 0 | 390 | 302 |  | 0 | 225 | 125 | 84 | 79 | 55 | 328 | 0 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 0 | 22 | 42 | 0 | 0 | 30 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 70 | 91 | 49 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 178 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 42 | 18 | 5 | 31 | 20 | 108 | 85 | 0 | 17 | 0 | 44 | 41 | 50 | 50 | 163 | 266 | 25 | 72 | 0 | 219 | 0 | 37 | 10 | 270 | 0 | 11 | 0 | 195 | 0 | 0 | 139 | 0 | 149 | 8 | 38 | 106 | 90 | 0 | 88 | 90 | 105 | 2 | 266 | 54 | 93 | 85 | 34 | 52 | 365 | 104 | 13 | 162 | 97 | 0 | 17 | 0 | 13 | 55 |  | 916 | 0 | 200 | 0 | 86 | 0 | 0 | 0 | 0 | 12 | 24 | 85 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 414 | 85 | 0 | 113 | 32 | 102 | 0 | 2 | 113 | 750 | 210 | 0 | 0 | 2 | 26 | 17 |  | 7736 | 3582 | 11318 | 3684 | 916 | 2134 | 0 | 3408 | 925 | 30 | 0 | 60 | 108 | 53 | 0 | 74.14
17:00 | 0 | 0 | 0 | 170 | 270 | 99 | 0 | 362 | 303 |  | 0 | 225 | 130 | 91 | 83 | 55 | 331 | 0 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 25 | 32 | 49 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 70 | 93 | 49 | 22 | 8 | 0 | 0 | 0 | 280 | 0 | 190 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 5 | 33 | 20 | 110 | 85 | 0 | 17 | 0 | 44 | 41 | 53 | 50 | 110 | 264 | 25 | 72 | 0 | 219 | 0 | 37 | 10 | 265 | 0 | 11 | 0 | 145 | 0 | 0 | 179 | 0 | 115 | 4 | 63 | 85 | 115 | 0 | 106 | 98 | 105 | 1 | 281 | 54 | 93 | 70 | 104 | 50 | 350 | 75 | 8 | 126 | 79 | 0 | 17 | 0 | 17 | 0 |  | 916 | 0 | 200 | 0 | 78 | 0 | 0 | 0 | 0 | 30 | 8 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 15 | 72 | 0 | 2 | 113 | 720 | 200 | 0 | 0 | 1 | 11 | 17 |  | 7600 | 3492 | 11092 | 3671 | 916 | 2080 | 0 | 3285 | 895 | 30 | 0 | 78 | 110 | 27 | 0 | 74.14
18:00 | 0 | 0 | 0 | 170 | 270 | 42 | 0 | 316 | 284 |  | 0 | 225 | 135 | 92 | 95 | 55 | 283 | 0 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 25 | 32 | 49 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 17 | 70 | 93 | 49 | 22 | 4 | 0 | 0 | 0 | 280 | 0 | 196 | 8 | 134 | 26 | 0 | 0 | 51 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 108 | 85 | 0 | 17 | 0 | 44 | 41 | 23 | 50 | 110 | 264 | 25 | 72 | 0 | 219 | 0 | 38 | 10 | 270 | 0 | 11 | 0 | 145 | 0 | 0 | 181 | 0 | 105 | 0 | 76 | 85 | 118 | 0 | 106 | 105 | 51 | 0 | 281 | 54 | 93 | 70 | 104 | 52 | 350 | 52 | 0 | 126 | 77 | 0 | 17 | 0 | 17 | 0 |  | 916 | 0 | 200 | 0 | 78 | 0 | 0 | 0 | 0 | 40 | 8 | 84 | 25 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 6 | 24 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 70 | 15 | 72 | 0 | 0 | 70 | 690 | 216 | 0 | 0 | 0 | 4 | 17 |  | 7359 | 3369 | 10728 | 3578 | 916 | 1997 | 0 | 3115 | 865 | 30 | 0 | 115 | 108 | 4 | 0 | 74.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 270 | 95 | 0 | 335 | 332 |  | 0 | 225 | 145 | 91 | 95 | 55 | 326 | 0 | 0 | 27 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 17 | 25 | 32 | 49 | 0 | 0 | 30 | 0 | 0 | 11 | 216 | 0 | 0 | 0 |  | 24 | 26 | 51 | 80 | 94 | 49 | 22 | 15 | 0 | 0 | 0 | 280 | 0 | 196 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 41 | 27 | 19 | 5 | 33 | 20 | 116 | 96 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 262 | 25 | 74 | 0 | 219 | 0 | 39 | 10 | 310 | 8 | 11 | 20 | 210 | 155 | 15 | 181 | 49 | 121 | 0 | 76 | 100 | 123 | 0 | 106 | 105 | 94 | 0 | 281 | 54 | 96 | 100 | 105 | 100 | 400 | 67 | 0 | 135 | 77 | 0 | 17 | 0 | 26 | 24 |  | 912 | 0 | 200 | 0 | 84 | 0 | 0 | 0 | 18 | 46 | 24 | 83 | 29 | 16 | 0 | 0 | 0 | 43 | 5 | 85 | 0 | 34 | 40 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 414 | 85 | 0 | 85 | 60 | 103 | 0 | 0 | 100 | 720 | 216 | 0 | 12 | 0 | 0 | 95 |  | 8539 | 3900 | 12439 | 3720 | 912 | 2250 | 239 | 3789 | 895 | 30 | 0 | 488 | 116 | 0 | 0 | 74.13
19:30 | 0 | 0 | 0 | 170 | 270 | 96 | 0 | 395 | 334 |  | 0 | 225 | 125 | 90 | 95 | 55 | 334 | 0 | 0 | 94 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 80 | 93 | 49 | 22 | 13 | 0 | 0 | 0 | 280 | 0 | 196 | 8 | 134 | 30 | 0 | 0 | 51 | 0 | 41 | 34 | 19 | 5 | 33 | 20 | 120 | 96 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 269 | 30 | 75 | 0 | 219 | 0 | 39 | 10 | 285 | 8 | 11 | 20 | 240 | 53 | 78 | 181 | 100 | 149 | 0 | 76 | 190 | 132 | 0 | 106 | 105 | 105 | 0 | 281 | 54 | 110 | 100 | 105 | 100 | 400 | 104 | 0 | 162 | 77 | 0 | 17 | 0 | 82 | 55 |  | 915 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 21 | 50 | 32 | 86 | 30 | 16 | 0 | 0 | 0 | 43 | 5 | 85 | 0 | 50 | 40 | 52 | 8 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 416 | 105 | 0 | 113 | 105 | 108 | 0 | 0 | 113 | 850 | 216 | 0 | 17 | 0 | 0 | 115 |  | 9053 | 4244 | 13297 | 3826 | 915 | 2210 | 251 | 4392 | 1025 | 30 | 0 | 528 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 332 |  | 0 | 225 | 125 | 91 | 96 | 55 | 333 | 0 | 0 | 99 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 24 | 202 | 0 | 0 | 0 |  | 24 | 51 | 50 | 80 | 94 | 49 | 22 | 22 | 0 | 0 | 0 | 280 | 0 | 192 | 8 | 135 | 31 | 0 | 0 | 51 | 0 | 41 | 31 | 19 | 5 | 33 | 20 | 118 | 96 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 266 | 28 | 72 | 0 | 219 | 0 | 39 | 10 | 270 | 8 | 11 | 0 | 287 | 0 | 25 | 182 | 26 | 149 | 0 | 76 | 185 | 128 | 0 | 106 | 105 | 105 | 0 | 266 | 54 | 110 | 100 | 105 | 100 | 400 | 104 | 0 | 162 | 76 | 0 | 17 | 0 | 76 | 55 |  | 915 | 0 | 205 | 0 | 99 | 0 | 0 | 0 | 37 | 60 | 32 | 87 | 30 | 16 | 0 | 0 | 0 | 43 | 12 | 85 | 0 | 50 | 40 | 52 | 27 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 418 | 105 | 0 | 113 | 105 | 109 | 0 | 0 | 113 | 890 | 206 | 0 | 17 | 0 | 0 | 115 |  | 8856 | 4336 | 13192 | 3825 | 915 | 2195 | 51 | 4414 | 1065 | 30 | 0 | 579 | 118 | 0 | 0 | 74.13
21:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 312 |  | 0 | 225 | 125 | 89 | 96 | 55 | 333 | 0 | 0 | 99 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 49 | 80 | 95 | 49 | 22 | 28 | 0 | 0 | 0 | 280 | 0 | 192 | 8 | 134 | 31 | 0 | 0 | 51 | 0 | 0 | 34 | 19 | 0 | 33 | 15 | 112 | 103 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 267 | 25 | 72 | 0 | 219 | 0 | 39 | 10 | 290 | 8 | 11 | 0 | 292 | 45 | 0 | 182 | 0 | 149 | 0 | 76 | 200 | 128 | 0 | 106 | 105 | 105 | 0 | 266 | 54 | 110 | 100 | 105 | 86 | 400 | 104 | 0 | 162 | 65 | 0 | 17 | 0 | 82 | 55 |  | 915 | 0 | 215 | 0 | 66 | 0 | 0 | 0 | 32 | 60 | 32 | 86 | 31 | 16 | 0 | 0 | 0 | 43 | 6 | 85 | 0 | 50 | 40 | 52 | 39 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 105 | 109 | 0 | 0 | 113 | 1000 | 216 | 0 | 17 | 0 | 0 | 115 |  | 8807 | 4430 | 13237 | 3830 | 915 | 2208 | 45 | 4385 | 1174 | 30 | 0 | 538 | 112 | 0 | 0 | 74.13
22:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 396 | 316 |  | 0 | 225 | 130 | 90 | 96 | 55 | 331 | 0 | 0 | 100 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 212 | 0 | 0 | 0 |  | 24 | 0 | 49 | 80 | 95 | 49 | 22 | 35 | 0 | 0 | 0 | 280 | 0 | 192 | 8 | 134 | 31 | 0 | 0 | 51 | 0 | 0 | 34 | 19 | 5 | 33 | 20 | 114 | 102 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 265 | 30 | 72 | 0 | 219 | 0 | 40 | 10 | 295 | 8 | 11 | 0 | 295 | 0 | 0 | 182 | 0 | 149 | 0 | 76 | 200 | 137 | 0 | 106 | 105 | 99 | 0 | 266 | 54 | 110 | 100 | 105 | 50 | 397 | 104 | 0 | 162 | 71 | 0 | 31 | 0 | 82 | 55 |  | 916 | 0 | 215 | 0 | 66 | 0 | 0 | 0 | 10 | 56 | 32 | 85 | 34 | 16 | 0 | 0 | 0 | 43 | 2 | 85 | 0 | 50 | 40 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 384 | 105 | 0 | 113 | 105 | 109 | 0 | 0 | 113 | 980 | 212 | 0 | 0 | 0 | 0 | 115 |  | 8743 | 4327 | 13070 | 3843 | 916 | 2199 | 0 | 4360 | 1154 | 30 | 0 | 454 | 114 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 395 | 320 |  | 0 | 225 | 125 | 91 | 96 | 55 | 332 | 0 | 0 | 100 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 48 | 40 | 97 | 49 | 22 | 38 | 0 | 0 | 0 | 280 | 0 | 192 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 0 | 33 | 19 | 5 | 33 | 20 | 116 | 103 | 0 | 20 | 0 | 44 | 41 | 22 | 50 | 163 | 268 | 30 | 72 | 0 | 219 | 0 | 40 | 10 | 280 | 8 | 11 | 0 | 295 | 0 | 0 | 182 | 0 | 149 | 0 | 76 | 200 | 135 | 0 | 106 | 105 | 105 | 0 | 266 | 54 | 110 | 100 | 106 | 50 | 400 | 104 | 0 | 162 | 77 | 0 | 35 | 0 | 82 | 55 |  | 916 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 56 | 0 | 86 | 35 | 16 | 0 | 0 | 0 | 43 | 0 | 81 | 0 | 50 | 40 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 380 | 105 | 0 | 113 | 95 | 109 | 0 | 0 | 113 | 1000 | 218 | 0 | 0 | 0 | 0 | 115 |  | 8677 | 4258 | 12935 | 3859 | 916 | 2158 | 0 | 4245 | 1174 | 30 | 0 | 437 | 116 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 395 | 320 |  | 0 | 225 | 120 | 91 | 96 | 55 | 335 | 0 | 0 | 100 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 96 | 49 | 22 | 31 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 135 | 33 | 0 | 0 | 51 | 0 | 0 | 34 | 19 | 6 | 33 | 20 | 114 | 104 | 0 | 20 | 0 | 44 | 41 | 5 | 20 | 163 | 269 | 28 | 72 | 0 | 218 | 0 | 40 | 10 | 265 | 8 | 11 | 0 | 293 | 0 | 0 | 183 | 0 | 149 | 0 | 64 | 200 | 137 | 0 | 106 | 105 | 105 | 0 | 267 | 54 | 110 | 100 | 34 | 50 | 400 | 104 | 0 | 162 | 77 | 0 | 35 | 0 | 82 | 55 |  | 917 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 8 | 15 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 422 | 105 | 0 | 113 | 105 | 109 | 0 | 0 | 113 | 980 | 172 | 0 | 0 | 0 | 0 | 115 |  | 8467 | 4080 | 12547 | 3856 | 917 | 2080 | 0 | 4131 | 1155 | 30 | 0 | 264 | 114 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 4095000 | 6490673 | 2266545 | 0 | 9125880 | 7396000 |  | 0 | 5072250 | 3087855 | 2088000 | 1193808 | 1082424 | 7555294 | 0 | 0 | 614467 | 784800 | 1185600 | 0 | 0 | 0 | 0 | 1307160 | 658580 | 713150 | 405936 | 600000 | 607140 | 590100 | 761300 | 729600 | 0 | 0 | 728000 | 0 | 0 | 139966 | 4787249 | 0 | 0 | 0 |  | 589440 | 112674 | 270129 | 817560 | 1534080 | 1182240 | 505008 | 509280 | 0 | 0 | 0 | 7182500 | 0 | 4575000 | 217454 | 3247270 | 741168 | 0 | 0 | 1176735 | 0 | 68312 | 931656 | 432900 | 143640 | 597600 | 455250 | 2507520 | 2577600 | 0 | 429624 | 6850 | 1034000 | 948936 | 1152000 | 1197216 | 3571691 | 6079000 | 1022784 | 1739520 | 0 | 5021450 | 0 | 886440 | 244260 | 6986000 | 180168 | 237100 | 18432 | 3249272 | 167452 | 64497 | 2222400 | 93075 | 1883660 | 106650 | 1190400 | 1536960 | 1318109 | 0 | 2328000 | 1369920 | 1905228 | 28801 | 5813313 | 1359354 | 2366898 | 2024640 | 1344000 | 1190400 | 9144200 | 1441920 | 143230 | 2276640 | 2032364 | 0 | 493200 | 0 | 484800 | 721800 |  | 22179636 | 0 | 5528160 | 0 | 953280 | 0 | 0 | 0 | 84000 | 339712 | 265875 | 2058199 | 630160 | 178848 | 0 | 0 | 0 | 231872 | 31180 | 458464 | 0 | 245312 | 188634 | 518880 | 143105 | 483360 | 0 | 206496 | 0 | 0 | 4276800 | 0 | 0 | 0 | 0 | 3185355 | 0 | 0 | 0 | 1530118 | 0 | 9452581 | 1201440 | 0 | 1899936 | 703440 | 1567593 | 0 | 24535 | 1725600 | 20748900 | 4851955 | 0 | 199200 | 23340 | 561600 | 661632 |  | 173498447 | 87339198 | 260837645 | 92082098 | 22179636 | 50921302 | 343456 | 63041245 | 25025700 | 728000 | 0 | 3113682 | 2507520 | 895006 | 0
Fuel Cost | 0 | 0 | 0 | 6019650 | 7204647.03 | 2991839.4 | 0 | 9217138.8 | 7617880 |  | 0 | 5528752.5 | 3427519.05 | 15847920 | 8225337.12 | 9157307.04 | 7857505.76 | 0 | 0 | 4626936.51 | 7157376 | 11666304 | 0 | 0 | 0 | 0 | 9542268 | 5090823.4 | 7031659 | 304452 | 450000 | 0 | 0 | 0 | 7055232 | 0 | 0 | 196560 | 0 | 0 | 1300284.14 | 5218101.41 | 0 | 0 | 0 |  | 0 | 1089557.58 | 2620251.3 | 7807698 | 13346496 | 9363340.8 | 636310.08 | 1512561.6 | 0 | 0 | 0 | 5315050 | 0 | 4209000 | 280515.66 | 3734360.5 | 837519.84 | 0 | 0 | 2012216.85 | 0 | 689951.2 | 8897314.8 | 549783 | 107730 | 1045800 | 341437.5 | 18806400 | 2732256 | 0 | 545622.48 | 109189 | 1695760 | 1518297.6 | 2050560 | 1867656.96 | 4071727.74 | 6322160 | 2014884.48 | 3322483.2 | 0 | 8687108.5 | 0 | 1037134.8 | 498290.4 | 7055860 | 135126 | 180196 | 313528.32 | 24564496.32 | 2843334.96 | 1078389.84 | 11556480 | 1556214 | 18535214.4 | 1246738.5 | 9701760 | 16676016 | 9292668.45 | 0 | 21231360 | 12945744 | 16594535.88 | 0 | 43948646.28 | 11839973.34 | 20805033.42 | 20205907.2 | 11518080 | 7928064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127754703.36 | 0 | 5804568 | 0 | 7492780.8 | 0 | 0 | 0 | 881160 | 3560181.76 | 2770417.5 | 2325764.87 | 976748 | 1745556.48 | 0 | 0 | 0 | 2281620.48 | 316788.8 | 4057406.4 | 0 | 3316618.24 | 1827863.46 | 5027947.2 | 1388118.5 | 928051.2 | 0 | 156317.472 | 0 | 0 | 23180256 | 0 | 0 | 0 | 0 | 4204668.6 | 0 | 0 | 0 | 1790238.06 | 0 | 9358055.19 | 12543033.6 | 0 | 18030392.64 | 6640473.6 | 12164521.68 | 0 | 271111.75 | 12752184 | 91087671 | 0 | 0 | 0 | 0 | 0 | 0 |  | 534165285.94 | 364635218.642 | 898800504.582 | 91161453.982 | 127754703.36 | 54537852.55 | 5791467.12 | 454277897.84 | 114267927 | 196560 | 0 | 30379203.48 | 18806400 | 1627039.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 352 | 282 |  | 0 | 225 | 145 | 82 | 43 | 40 | 324 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 27 | 25 | 32 | 42 | 0 | 0 | 30 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 82 | 49 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 136 | 32 | 0 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 0 | 15 | 116 | 104 | 0 | 20 | 1 | 44 | 41 | 50 | 48 | 163 | 253 | 58 | 72 | 0 | 219 | 0 | 36 | 10 | 275 | 0 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 88 | 0 | 38 | 17 | 20 | 0 | 115 | 52 | 105 | 1 | 245 | 54 | 73 | 70 | 32 | 38 | 381 | 60 | 12 | 109 | 99 | 0 | 17 | 0 | 0 | 55 |  | 924 | 0 | 205 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 393 | 17 | 0 | 70 | 0 | 52 | 0 | 5 | 70 | 680 | 170 | 0 | 0 | 2 | 35 | 0 |  | 10184 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 270 | 96 | 0 | 395 | 334 | 0 | 0 | 225 | 125 | 90 | 95 | 55 | 334 | 0 | 0 | 94 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 80 | 93 | 49 | 22 | 13 | 0 | 0 | 0 | 280 | 0 | 196 | 8 | 134 | 30 | 0 | 0 | 51 | 0 | 41 | 34 | 19 | 5 | 33 | 20 | 120 | 96 | 0 | 20 | 0 | 44 | 41 | 53 | 50 | 163 | 269 | 30 | 75 | 0 | 219 | 0 | 39 | 10 | 285 | 8 | 11 | 20 | 240 | 53 | 78 | 181 | 100 | 149 | 0 | 76 | 190 | 132 | 0 | 106 | 105 | 105 | 0 | 281 | 54 | 110 | 100 | 105 | 100 | 400 | 104 | 0 | 162 | 77 | 0 | 17 | 0 | 82 | 55 |  | 915 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 21 | 50 | 32 | 86 | 30 | 16 | 0 | 0 | 0 | 43 | 5 | 85 | 0 | 50 | 40 | 52 | 8 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 416 | 105 | 0 | 113 | 105 | 108 | 0 | 0 | 113 | 850 | 216 | 0 | 17 | 0 | 0 | 115 |  | 13297 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 400 | 330 | 0 | 0 | 225 | 150 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 0 | 30 | 0 | 0 | 25 | 205 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 49 | 22 | 25 | 0 | 0 | 0 | 280 | 0 | 225 | 8 | 135 | 35 | 0 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 21 | 166 | 150 | 0 | 20 | 0 | 44 | 41 | 51 | 50 | 163 | 270 | 60 | 80 | 0 | 220 | 0 | 41 | 10 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 100 | 55 |  | 927 | 0 | 300 | 0 | 99 | 200 | 0 | 0 | 35 | 60 | 32 | 87 | 30 | 110 | 0 | 0 | 0 | 40 | 30 | 85 | 0 | 50 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 108 | 0 | 0 | 113 | 1000 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 170 | 270 | 100 | 0 | 360 | 300 | 0 | 0 | 225 | 125 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 0 | 30 | 0 | 0 | 25 | 205 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 49 | 22 | 15 | 0 | 0 | 0 | 280 | 0 | 210 | 8 | 135 | 35 | 0 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 21 | 143 | 120 | 0 | 20 | 1.6 | 44 | 41 | 51 | 50 | 163 | 270 | 60 | 80 | 0 | 220 | 0 | 38 | 10 | 300 | 8 | 11 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 100 | 105 | 5 | 300 | 54 | 106 | 100 | 113 | 100 | 400 | 104 | 50 | 162 | 110 | 0 | 35 | 30 | 100 | 55 |  | 927 | 0 | 250 | 0 | 16 | 200 | 0 | 0 | 35 | 0 | 32 | 87 | 30 | 50 | 0 | 0 | 0 | 36 | 30 | 85 | 0 | 50 | 40 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 105 | 108 | 0 | 8 | 113 | 800 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 270 | 95 | 0 | 395 | 320 | 0 | 0 | 225 | 110 | 84 | 15 | 55 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 28 | 17 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 76 | 49 | 22 | 9 | 0 | 0 | 0 | 270 | 0 | 197 | 8 | 135 | 28 | 0 | 0 | 51 | 0 | 0 | 34 | 16 | 6 | 33 | 20 | 100 | 104 | 0 | 20 | 1 | 43 | 41 | 22 | 36 | 163 | 259 | 30 | 66 | 0 | 219 | 0 | 37 | 10 | 290 | 8 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 50 | 11 | 38 | 17 | 3 | 0 | 106 | 70 | 91 | 2 | 266 | 54 | 93 | 98 | 28 | 40 | 400 | 55 | 9 | 86 | 78 | 0 | 20 | 0 | 0 | 55 | 0 | 919 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 207 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 780 | 184 | 0 | 0 | 1 | 23 | 0 | 0 |  |  |  |  | 66498383 |  | 0
66498383
| Minimum Generation |  | 8841 | 7:00
| Highest Generation |  | 13297 | 19:30
| Day Peak Generation |  | 10184 | 12:00
| Evening Peak Generation |  | 13297 | 19:30
| HVDC Max Flow |  | 924 | 12:00
| HVDC EvPeak Flow |  | 915 | 19:30
| Load factor L.F |  | 81.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-15
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10184 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9536 | MW
Evening Peak Generation : |  | 13297 | MW Hour : | 19:30 | Available Max Generation : |  | 15420 | MW
E.P. Demand (at gen end) : |  | 13297 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13297 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1920 | MW
Total Gen. (MKWH) : |  | 260.8376 | System Load Factor : | 81.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -52 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-15
Actual : | 74.12 | Ft.(MSL) , | Rule curve : | 79.34 | Ft.( MSL )
Gas Consumed : | Total = | 1049.3 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145699306.532
: |  | Coal : | 114267927 | Oil : | 490448568.44 | Total : | 750415801.972
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4832.0067 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1563.4514 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1528.5911 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1368.2022 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1248.1171 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1024.9943 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 501.0209 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 309.8664 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 752.1753 |  |  | 0 | 0%
Total | 0 |  | 13128.4255 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1,3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Niamatpur 132/33 kV T-3(A+B) transformer was shutdown at 08:43 for D/W and T-3(B) was switched on
at 17:50.
b) Manikganj-Kabirpur 132 kV Ckt-1 & Manikganj GT-4 transformer was under shut down from 09:22 to
13:50 for C/M.
c) Maniknagar-Siddhirganj 230 kV Ckt-1 was shut down at 10:05 for Project work.
d) Shyampur 132/33 kV GT-2 transformer was under shut down from 09:55 to 17:30 for C/M.
e) Gopalganj(Old) 132/33 kV T-1 transformer was under shut down from 07:51 to 09:02 for C/M.
f) Payra 132/33 kV T-3 & T-4 transformers were shut down at 08:52 for D/W.
g) Faridpur 132/33 kV T-3 transformer was under shut down from 08:59 to 12:11 for C/M.
h) Faridpur 132 kV Bus-B was under shut down from 08:56 to 12:17 for C/M.
i) Kachua 132/33 kV T-3 transformer was under shut down from 11:20 to 12:42 for C/M.
j) Hathazari 230 kV Bus-1 was under shut down from 09:00 to 11:56 for C/M.
k) Gopalganj-Faridpur 132 kV Ckt-1 was under shut down from 07:14 to 12:08 for C/M.
l) Shariatpur 132 kV Bus coupler was under shut down from 03:05 to 12:17 for C/M.
m) GPH 230/33/11 kV T-1 transformer was shut down at 12:56 for C/M.
n) Cumilla(S) 132/33 kV T-1, T-2, T--3, T-4 transformer were under shut down(one by one) from 11:21 to
12:59 for C/M.
o) Sirajganj Unit-3 was shutdown at 10:54 due to gas shortage.
p) Mymensingh RPCL Unit-1 was shutdown at 13:14 due to gas shortage.
q) After maintenance Anwara-Sikalbaha 230 kV Ckt-1 was switched on at 15:25.
r) Barishal 132/33 kV T-1 & T-2 transformers tripped at 21:10 due to 33 kV feeder fault | [5 empty] | About 119 MW power interruption occurred under
and were switched on at 21:24. | [5 empty] | Barishal S/S area from 21:10 to 21:24.
s) Bhulta 132/33 kV T-1 & T-2 transformers tripped at 00:48(15/05/2022) showing O/C, E/F due to 33 kV | [5 empty] | About 80 MW power interruption occurred under
PBS feeder fault and T-2 was switched on at 02:06(15/05/2022). | [5 empty] | Bhulta S/S area from 00:48(15/05/2022) to 02:06.
t) Shahjibazar 132/33 kV T-4 transformer was under shut down from 07:00(15/05/2022) to | [5 empty] | About 35 MW power interruption occurred under
07:44(15/05/2022) for C/M by PBS. | [5 empty] | Shahjibazar S/S area from 07:00(15/05/2022) to 07:44.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4095000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6490673 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2266545 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 9125880 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 7396000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5072250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 90 | 2088000 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 3087855 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 95 | 1193808 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1082424
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 405936
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M, Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 94 | 614467 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 334 | 7555294
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 784800 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1307160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1185600 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 658580
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 713150
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1207140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 590100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 761300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 729600 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 240 | 3249272 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 53 | 167452 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 78 | 64497 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 93075
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1883660
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1369920
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1441920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2276640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 721800
| Dhaka area Total |  |  |  | 5898 | 3892 | 69679798
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 139966
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 106650
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 49 | 1182240
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 728000 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4787249
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1905228
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 112674 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 270129 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 817560 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1190400 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505008
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 509280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 1534080 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28801
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 281 | 5813313 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1359354
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2366898
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1190400 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 77 | 2032364 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1420 | 26579594
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4575000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7182500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 741168 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1176735
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 1318109 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 68312 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 134 | 3247270
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 1536960 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 432900
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 143640 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2507520
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 597600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 931656 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 455250 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 18432 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2024640 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1344000
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 493200 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 82 | 484800 | Reserve
| Cumilla Area Total |  |  |  | 3014 | 1617 | 29497146
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 96 | 2577600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 429624
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 181 | 2222400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 2328000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 143230
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 589440
| Mymensingh Area Total |  |  |  | 622 | 427 | 8297144
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1034000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 948936 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3571691
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 269 | 6079000 | Machine problem
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1152000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 50 | 1197216
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 237100
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 1022784 | Machine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1739520 | Machine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5021450
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 886440 | Machine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 180168
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6986000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244260
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9144200
| Sylhet Area Total |  |  |  | 2477 | 1697 | 39444765
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 915 | 22179636
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 953280 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 84000 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 339712 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5528160
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 265875 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1201440
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 703440
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 561600
| Khulna Area Total |  |  |  | 2384 | 1527 | 31817143
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 178848 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 30 | 630160 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2058199 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 850 | 20748900 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 216 | 4851955
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 199200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1215 | 28667262
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 231872 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 31180 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 245312
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 188634 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 147 | 3185355
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 1530118 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 9452581
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 8 | 143105 | Low demand
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 483360
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 206496
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 518880
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 458464 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1899936
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1725600
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23340
| Rajshahi Area Total |  |  |  | 2129 | 1104 | 20324233
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Reserve.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4276800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1567593 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24535
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 661632
| Rangpur Area Total |  |  |  | 720 | 398 | 6530560
| Total |  |  |  | 21584 | 13297 | 260837645
| Eastern Grid Total |  |  |  | 14393 | 9053 | 173498447
| Western Grid Total |  |  |  | 7191 | 4244 | 87339198
| National Grid Total |  |  |  | 21584 | 13297 | 260837645
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-14
(a) ENTIRE EASTERN GRID : |  | 8832.6 | MW | (b) ENTIRE WESTERN GRID : |  | 4092.8 | MW
i) Dhaka area |  | 4713.1 | MW | i) Khulna area |  | 1587.4 | MW
ii) Chittagong area |  | 1431.5 | MW | ii) Rajshahi area |  | 1330.4 | MW
iii) Comilla area |  | 1224 | MW | iii) Barisal area |  | 392 | MW
iv) Mymensingh area |  | 1012 | MW | iv) Rangpur area |  | 783 | MW
v) Sylhet area |  | 452 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12925.4 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 30 | 13:00 | Hasnabad | 74 | 23:00 | Palashbari | 120 | 20:00
Agargaon | 77 | 13:00 | Hathazari | 100 | 19:30 | Panchagarh | 54 | 19:30
Agrabad | 76 | 19:00 | Ishurdi | 73 | 19:30 | Patuakhali | 122 | 23:00
AKS | 14 | 23:00 | Jaldhaka | 58 | 19:30 | PHP | 3 | 02:00
AKSML | 124 | 03:00 | Jamalpur | 144 | 21:00 | Purbachal | 17 | 19:00
Amnura | 50 | 22:00 | Jashore | 121 | 20:00 | Purbasadipur | 106 | 19:30
Ashuganj | 36 | 00:00 | Jhenaidah | 117 | 19:30 | Rahim | 17 | 23:00
Bagerhat | 109 | 20:00 | Joydebpur | 194 | 19:00 | Rajbari | 64 | 21:00
Bakulia | 126 | 19:00 | Joypurhat | 56 | 21:00 | Rajendrapur | 112 | 20:00
Banani | 53 | 11:00 | Juldah | 22 | 00:00 | Rajshahi | 148 | 19:30
Bangabhaban | 8 | 10:00 | Kabirpur | 267 | 18:30 | Rajshahi | 43 | 23:00
Barapukuria | 49 | 21:00 | Kachua | 80 | 22:00 | Ramganj | 112 | 23:00
Barguna | 20 | 00:00 | Kallyanpur | 99 | 19:00 | Rampur | 20.8 | 19:00
Barishal | 121 | 19:30 | Kalurghat | 6 | 10:00 | Rangamati | 14 | 19:00
Barishal | 68 | 23:00 | Kamrangirchar | 63 | 13:00 | Rangpur | 137 | 19:00
Baroaulia | 73 | 11:00 | Kaptai | 45 | 19:30 | Ruppur | 3.2 | 00:00
Baroirhat | 72 | 22:00 | Kazla | 81 | 21:00 | Saidpur | 82 | 19:30
Bashundhara | 164 | 15:00 | Keranigonj | 60 | 14:00 | Satkhira | 120 | 22:00
BashundharaCement | 6 | 11:00 | Khagrachori | 26 | 19:30 | Satmasjid | 91 | 19:00
Beanibazar | 44 | 19:00 | Khulna | 94 | 21:00 | Savar | 184 | 16:00
Benapole | 52 | 21:00 | Khulshi | 209 | 13:00 | Shahjadpur | 90 | 19:30
Bhaluka | 146 | 16:00 | Kishoreganj | 134 | 23:00 | Shahjibazar | 113 | 23:00
Bhandaria | 58 | 19:30 | Kodda | 312 | 11:00 | Shahmirpur | 49 | 16:00
Bhangura | 34 | 21:00 | KSRM | 29 | 17:00 | Shariatpur | 74 | 22:00
Bheramara(GK) | 57 | 22:00 | Kulaura | 42 | 19:30 | Sherpur | 130 | 21:00
Bhulta | 210 | 21:00 | Kurigram | 48 | 21:00 | Shikalbaha | 37 | 19:30
Bog-Sherpur | 62 | 19:30 | Kushtia | 138 | 21:00 | Shitalakhya | 134 | 16:00
Bogura | 157 | 21:00 | Lalbag | 70 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 42 | 23:00 | Lalmonirhat | 39 | 19:00 | Shyampur | 146 | 13:00
Brahmanbaria | 166 | 22:00 | Madanganj | 185 | 19:30 | Siddhirganj | 106 | 11:00
BSRM | 163 | 12:00 | Madaripur | 109 | 23:00 | Sirajganj | 102 | 21:00
Cantonment | 134 | 19:00 | Madartek | 76 | 23:00 | Sonargaon | 80 | 23:00
Chandpur | 74 | 23:00 | Madunaghat | 62 | 19:00 | Sreemongol | 51 | 23:00
Chandraghona | 30 | 19:00 | Magura | 60 | 19:30 | Srinagar | 44.63 | 21:00
Chapai | 65 | 20:00 | Mahasthangarh | 68 | 20:00 | SSM | 4 | 01:00
Charsaidpur | 11 | 23:00 | Manikganj | 90 | 20:00 | Sunamganj | 44 | 22:00
Chauddagram | 54 | 22:00 | Maniknagar | 64 | 19:00 | Sylhet | 118 | 20:00
Chhatak | 21 | 19:00 | Matarbari | 43 | 20:00 | Tangail | 202 | 22:00
Chowmuhani | 228 | 22:00 | Matuail | 60 | 12:00 | Thakurgaon | 77 | 19:30
Chuadanga | 100 | 21:00 | Millgate | 64 | 19:30 | TK | 19.7 | 22:00
Coxsbazar | 123 | 22:00 | Mirpur | 127 | 19:30 | Tongi | 123 | 15:00
Cumilla(N) | 145 | 20:00 | Mirsorai | N/A | N/A | Ullon | 35 | 21:00
Cumilla(S) | 145 | 23:00 | Mithapukur | 30 | 19:30 | Uttara | 85 | 18:30
Daudkandi | 148 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 15 | 19:00
Dhaka | 30 | 13:00 | Mogbazar | 112 | 16:00 | Zigatola | 42 | 19:00
Dhamrai | 126 | 15:00 | Mongla | 38 | 16:00
Dhanmondi | 168 | 16:00 | Motijheel | 33 | 13:00
Dohazari | 106 | 21:00 | Munshiganj | 106 | 23:00
Faridpur | 146 | 21:00 | Mymensingh | 192 | 19:30
Fatullah | 64 | 15:00 | Naogaon | 128 | 21:00
Fenchuganj | 46 | 22:00 | Narail | 52 | 20:00
Feni | 113 | 22:00 | Narinda | 61 | 14:00
Ghorashal | 53 | 22:00 | Narshingdi | 184 | 21:00
Goalpara | 27 | 23:00 | Natore | 150 | 22:00
Gollamari | 51 | 23:00 | Nawabganj | 51.9 | 22:00
Gopalganj | 100 | 21:00 | Netrakona | 113 | 19:00
GPH | 87 | 08:00 | New | 78.2 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 414 | 13:00 | 405 | 6:00 | Kaliakoir | 396 | 0.375 | 385 | 0.41667
| Bheramara | 400 | 6:00 | 395 | 12:00 | Bhulta | 399 | 0.20833 | 388 | 0.375
| Ashuganj(N) | 403 | 19:30 | 392 | 12:00 | Gopalganj | 418 | 0.625 | 400 | 0.041667
| Payra | 421 | 9:00 | 413 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 240 | 16:00 | 228 | 3:00
| Ishurdi | 235 | 6:00 | 228 | 21:00 | Megnaghat | 232 | 9:00 | 225 | 10:00
| Ashuganj | 240 | 16:00 | 235 | 8:00 | Fenchuganj | 244 | 5:00 | 240 | 15:00
| Serajganj | 236 | 5:00 | 233 | 12:00 | Siddhirganj | 230 | 5:00 | 224 | 10:00
| Baghabari | 233 | 6:00 | 230 | 19:30 | Maniknagar | 228 | 5:00 | 221 | 12:00
| Barapukuria | 229 | 13:00 | 222 | 19:30 | Agargaon | 228 | 9:00 | 219 | 10:00
| Bogra | 233 | 4:00 | 226 | 19:30 | Barisal | 240 | 9:00 | 230 | 22:00
| Rajshahi | 236 | 18:30 | 229 | 1:00 | Bhola 225 MW | 243 | 8:00 | 230 | 22:00
| Khulna South | 231 | 9:00 | 218 | 23:00 | AKSML | 237 | 20:00 | 227 | 3:00
| Rampura | 228 | 24:00 | 220 | 10:00 | BSRM | 236 | 18:00 | 227 | 4:00
| Haripur | 227 | 3:00 | 221 | 9:00 | Bibiyana | 242 | 13:00 | 237 | 1:00
| Hasnabad | 228 | 19:30 | 219 | 12:00 | Bhulta | 231 | 24:00 | 224 | 9:00
| Shyampur | 228 | 19:30 | 220 | 10:00 | Ashuganj (S) | 238 | 23:00 | 231 | 11:00
| Aminbazar | 231 | 1:00 | 221 | 2:00 | Kaliakoir | 229 | 19:00 | 221 | 9:00
| Tongi | 230 | 22:00 | 219 | 12:00 | GPH | 238 | 19:30 | 227 | 3:00
| Comilla (N) | 234 | 20:00 | 226 | 2:00 | Jhenaidah | 228 | 9:00 | 218 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 131 | 03:00 | 125 | 12:00 | Manikganj | 133 | 06:00 | 123 | 12:00
| Agargaon | 136 | 05:00 | 130 | 10:00 | Maniknagar | 131 | 03:00 | 125 | 12:00
| Agrabad | 137 | 20:00 | 130 | 03:00 | Matarbari | 124 | 11:00 | 113 | 23:00
| AKS | 136 | 02:00 | 130 | 08:00 | Matuail | 136.7 | 20:00 | 131.4 | 10:00
| Aminbazar | 138 | 03:00 | 129 | 10:00 | Millgate | 134 | 05:00 | 127 | 09:00
| Amnura | 131 | 18:00 | 123 | 12:00 | Mirpur | 137 | 03:00 | 128 | 10:00
| Ashuganj | 139 | 05:00 | 133 | 20:00 | Mithapukur | 133 | 00:00 | 127 | 19:30
| Bagerhat | 135 | 17:00 | 123 | 01:00 | Modern | 136 | 18:00 | 131 | 05:00
| Bakulia | 136 | 16:00 | 127 | 04:00 | Mogbazar | 134 | 03:00 | 126 | 12:00
| Banani | 134 | 23:00 | 127 | 12:00 | Mongla | 135 | 13:00 | 126 | 19:00
| Bangabhaban | 131 | 00:00 | 125 | 12:00 | Motijheel | 131 | 00:00 | 125 | 12:00
| Barapukuria | 134 | 13:00 | 130 | 19:30 | Munshiganj | 140 | 19:30 | 132 | 08:00
| Barguna | 137 | 08:00 | 129 | 22:00 | Mymensingh | 136 | 02:00 | 120 | 19:00
| Barishal | 138 | 18:00 | 129 | 23:00 | Naogaon | 133 | 11:00 | 124 | 19:30
| Barishal | 139 | 09:00 | 130 | 00:00 | Narail | 135 | 09:00 | 125 | 23:00
| Baroaulia | 139 | 20:00 | 130 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 18:30 | 126 | 03:00 | Narshingdi | 133 | 05:00 | 126 | 11:00
| Bashundhara | 134 | 05:00 | 126 | 12:00 | Natore | 133 | 06:00 | 129 | 02:00
| BashundharaCement | 140 | 18:30 | 131 | 09:00 | Nawabganj | 131 | 19:30 | 125 | 10:00
| Beanibazar | 137 | 05:00 | 132 | 19:30 | Netrakona | 130 | 02:00 | 118 | 21:00
| Benapole | 134 | 09:00 | 126 | 19:00 | New | 136 | 23:00 | 126 | 12:00
| Bhaluka | 136 | 02:00 | 116 | 19:00 | Niamatpur | 131 | 05:00 | 118 | 19:30
| Bhandaria | 136 | 10:00 | 122 | 23:00 | Noapara | 137 | 16:00 | 128 | 23:00
| Bhangura | 139 | 05:00 | 134 | 21:00 | Pabna | 136 | 06:00 | 131 | 18:30
| Bheramara | 136 | 06:00 | 133 | 00:00 | Palashbari | 134 | 16:00 | 127 | 19:30
| Bheramara(GK) | 138 | 13:00 | 135 | 03:00 | Panchagarh | 133 | 15:00 | 125 | 18:00
| Bhulta | 131 | 19:00 | 127 | 08:00 | Patuakhali | 136 | 09:00 | 132 | 00:00
| Bog-Sherpur | 136 | 16:00 | 130 | 19:30 | PHP | 135 | 18:00 | 125 | 03:00
| Bogura | 136 | 00:00 | 131 | 20:00 | Purbachal | 134 | 23:00 | 126 | 12:00
| Bogura | 137 | 04:00 | 131 | 19:30 | Purbasadipur | 131 | 23:00 | 126 | 03:00
| Brahmanbaria | 134 | 06:00 | 127 | 21:00 | Rahim | 137 | 19:00 | 132 | 09:00
| Cantonment | 135 | 05:00 | 133 | 04:00 | Rajbari | 135 | 06:00 | 128 | 22:00
| Chandpur | 140 | 19:00 | 123 | 01:00 | Rajendrapur | 133 | 14:00 | 124 | 09:00
| Chandraghona | 138 | 20:00 | 132 | 04:00 | Rajshahi | 129 | 07:00 | 125 | 12:00
| Chapai | 130 | 18:00 | 124 | 14:00 | Rajshahi | 129 | 18:30 | 124 | 01:00
| Charsaidpur | 139 | 19:30 | 132 | 09:00 | Ramganj | 134 | 20:00 | 124 | 01:00
| Chauddagram | 136 | 19:00 | 127 | 00:00 | Rampur | 137 | 19:00 | 129 | 04:00
| Chhatak | 135 | 02:00 | 130 | 21:00 | Rampura | 131 | 03:00 | 124 | 12:00
| Chowmuhani | 133 | 18:30 | 122 | 00:00 | Rangamati | 137 | 20:00 | 130 | 15:00
| Chuadanga | 134 | 09:00 | 122 | 21:00 | Rangpur | 132 | 00:00 | 125 | 19:00
| Coxsbazar | 124 | 11:00 | 110 | 23:00 | Ruppur | 137 | 06:00 | 134 | 01:00
| Cumilla(N) | 136 | 19:00 | 130 | 03:00 | Saidpur | 132 | 03:00 | 127 | 12:00
| Cumilla(S) | 137 | 19:30 | 129 | 13:00 | Satkhira | 137 | 09:00 | 125 | 23:00
| Daudkandi | 134 | 19:00 | 128 | 03:00 | Satmasjid | 136 | 05:00 | 130 | 10:00
| Dhaka | 132 | 06:00 | 125 | 12:00 | Savar | 138 | 20:00 | 126 | 10:00
| Dhamrai | 133 | 05:00 | 125 | 12:00 | Shahjadpur | 147 | 05:00 | 136 | 19:00
| Dhanmondi | 136 | 00:00 | 132 | 10:00 | Shahjibazar | 139 | 03:00 | 132 | 21:00
| Dohazari | 131 | 10:00 | 124 | 23:00 | Shahmirpur | 137 | 20:00 | 130 | 08:00
| Faridpur | 135 | 13:00 | 128 | 23:00 | Shariatpur | 137 | 07:00 | 127 | 00:00
| Fatullah | 137 | 19:30 | 130 | 10:00 | Sherpur | 137 | 17:00 | 123 | 21:00
| Fenchuganj | 139 | 00:00 | 135 | 23:00 | Shikalbaha | 137 | 18:00 | 131 | 06:00
| Feni | 135 | 16:00 | 127 | 00:00 | Shikalbaha | 137 | 19:30 | 129 | 04:00
| Ghorashal | 138 | 00:00 | 135 | 15:00 | Shitalakhya | 139 | 19:00 | 131 | 10:00
| Goalpara | 139 | 16:00 | 130 | 01:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 13:00 | 130 | 01:00 | Shyampur | 136 | 19:00 | 128 | 10:00
| Gopalganj | 139 | 13:00 | 129 | 01:00 | Shyampur | 136 | 19:30 | 130 | 10:00
| Gopalganj_I | 139 | 13:00 | 131 | 01:00 | Siddhirganj | 137 | 19:30 | 131 | 10:00
| Gulshan | 131 | 04:00 | 124 | 12:00 | Sirajganj | 136 | 00:00 | 131 | 19:30
| Halishahar | 136 | 18:00 | 130 | 03:00 | Sonargaon | 137 | 19:00 | 133 | 00:00
| Haripur | 137 | 19:00 | 132 | 09:00 | Sreemongol | 140 | 06:00 | 134 | 19:00
| HaripurSBU | 137 | 19:30 | 132 | 09:00 | Srinagar | 130 | 05:00 | 124 | 12:00
| Hasnabad | 137 | 02:00 | 132 | 10:00 | SSM | 142 | 20:00 | 130 | 07:00
| Hathazari | 139 | 20:00 | 132 | 03:00 | Sunamganj | 134 | 04:00 | 128 | 22:00
| Ishurdi | 137 | 06:00 | 133 | 21:00 | Sylhet | 136 | 04:00 | 133 | 14:00
| Jaldhaka | 132 | 00:00 | 123 | 19:30 | Tangail | 135 | 02:00 | 127 | 19:00
| Jamalpur | 138 | 17:00 | 126 | 21:00 | Thakurgaon | 132 | 22:00 | 124 | 01:00
| Jashore | 133 | 09:00 | 127 | 22:00 | TK | 137 | 19:00 | 133 | 07:00
| Jhenaidah | 137 | 09:00 | 129 | 21:00 | Tongi | 136 | 00:00 | 129 | 11:00
| Jhenaidah | 138 | 09:00 | 129 | 23:00 | Ullon | 131 | 02:00 | 125 | 12:00
| Joydebpur | 140 | 14:00 | 134 | 15:00 | Uttara | 136 | 20:00 | 129 | 10:00
| Joypurhat | 134 | 05:00 | 123 | 20:00 | UttaraNew | 137 | 04:00 | 128 | 10:00
| Juldah | 137 | 18:30 | 130 | 03:00 | Zigatola | 131 | 19:30 | 125 | 10:00
| Kabirpur | 135 | 06:00 | 123 | 12:00
| Kachua | 136 | 19:30 | 124 | 02:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 137 | 00:00 | 131 | 09:00
| Kalurghat | 138 | 19:00 | 130 | 04:00
| Kamrangirchar | 131 | 19:30 | 124 | 12:00
| Kaptai | 136 | 18:00 | 132 | 01:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 214 | 8467 | 4080 | 12547 |  |  |  | QF-LDC-11
0:30 | 282 | 7595.5 | 3802 | 11397.5 | Date: | 2022-05-14
1:00 | 350 | 6724 | 3524 | 10248
1:30 | 310 | 6564 | 3423 | 9987
2:00 | 270 | 6404 | 3322 | 9726
2:30 | 258 | 6312.5 | 3312 | 9624.5 | [5 empty] | Gen. at Eve. Peak | 13297 | 13297 MW (19:30 )
3:00 | 246 | 6221 | 3302 | 9523 | [6 empty] | 19:30
3:30 | 295 | 6120.5 | 3277 | 9397.5 | [5 empty] | Gen. at Day Peak | 10184 | 10184 MW (12:00 )
4:00 | 344 | 6020 | 3252 | 9272 | [6 empty] | 12:00
4:30 | 343 | 6012.5 | 3244.5 | 9257 | [5 empty] | Highest Generation | 13297
5:00 | 342 | 6005 | 3237 | 9242 | [6 empty] | 19:30
5:30 | 366 | 5910.5 | 3173 | 9083.5
6:00 | 390 | 5816 | 3109 | 8925
6:30 | 408 | 5782.5 | 3100.5 | 8883
7:00 | 426 | 5749 | 3092 | 8841
7:30 | 475 | 5816.5 | 3086.5 | 8903
8:00 | 524 | 5884 | 3081 | 8965
8:30 | 593 | 6020 | 3102.5 | 9122.5
9:00 | 662 | 6156 | 3124 | 9280
9:30 | 578 | 6332 | 3120.5 | 9452.5
10:00 | 494 | 6508 | 3117 | 9625
10:30 | 498 | 6628.5 | 3093 | 9721.5
11:00 | 502 | 6749 | 3069 | 9818
11:30 | 448 | 6915.5 | 3085.5 | 10001
12:00 | 394 | 7082 | 3102 | 10184
12:30 | 416 | 7162 | 3255.5 | 10417.5
13:00 | 438 | 7242 | 3409 | 10651
13:30 | 406 | 7321 | 3419 | 10740
14:00 | 374 | 7400 | 3429 | 10829
14:30 | 399 | 7514 | 3482 | 10996
15:00 | 424 | 7628 | 3535 | 11163
15:30 | 397 | 7682 | 3558.5 | 11240.5
16:00 | 370 | 7736 | 3582 | 11318
16:30 | 370 | 7668 | 3537 | 11205
17:00 | 370 | 7600 | 3492 | 11092
17:30 | 365 | 7479.5 | 3430.5 | 10910
18:00 | 360 | 7359 | 3369 | 10728
18:30 | 197 | 7949 | 3634.5 | 11583.5
19:00 | 34 | 8539 | 3900 | 12439
19:30 | 52 | 9053 | 4244 | 13297
20:00 | 4 | 8856 | 4336 | 13192 |  |  |  | Executive Engineer
20:30 | 48 | 8831.5 | 4383 | 13214.5 |  |  |  | Network Operation Division
21:00 | 92 | 8807 | 4430 | 13237
21:30 | 108 | 8775 | 4378.5 | 13153.5
22:00 | 124 | 8743 | 4327 | 13070 |  |  |  |  | Page 6 of 7
22:30 | 121 | 8710 | 4292.5 | 13002.5
23:00 | 118 | 8677 | 4258 | 12935
23:30 | 166 | 8572 | 4169 | 12741
24:00 | 214 | 8467 | 4080 | 12547
13297 MW (19:30 )
10184 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-14 |  | Energy |  | 260837645
[13 empty] | 2022-05-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3856 | 917 | 2080 | 0 | 4131 | 1155 | 30 | 0 | 264 | 114 | 0 | 0
0:30 | 3896 | 914.5 | 2165.5 | 0 | 3019.5 | 1130 | 30 | 0 | 132 | 110 | 0 | 0 | Date: | 2022-05-14
1:00 | 3936 | 912 | 2251 | 0 | 1908 | 1105 | 30 | 0 | 0 | 106 | 0 | 0
1:30 | 3936 | 912 | 2242 | 0 | 1677 | 1085 | 30 | 0 | 0 | 105 | 0 | 0 | [8 empty] | Total Energy | 260.8376 | Total Energy Gen 260.838 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.838 MKWHr
2:00 | 3936 | 912 | 2233 | 0 | 1446 | 1065 | 30 | 0 | 0 | 104 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3971 | 911 | 2237 | 0 | 1328.5 | 1045 | 30 | 0 | 0 | 102 | 0 | 0 | [8 empty] | Energy Requirement | 260.8376
3:00 | 4006 | 910 | 2241 | 0 | 1211 | 1025 | 30 | 0 | 0 | 100 | 0 | 0
3:30 | 3946.5 | 910.5 | 2199.5 | 0 | 1212 | 1000 | 30 | 0 | 0 | 99 | 0 | 0 | [6 empty] | Shortage
4:00 | 3887 | 911 | 2158 | 0 | 1213 | 975 | 30 | 0 | 0 | 98 | 0 | 0
4:30 | 3913 | 912.5 | 2145.5 | 0 | 1205 | 955 | 30 | 0 | 0 | 96 | 0 | 0
5:00 | 3939 | 914 | 2133 | 0 | 1197 | 935 | 30 | 0 | 0 | 94 | 0 | 0
5:30 | 3892 | 915.5 | 2086.5 | 0 | 1143.5 | 920 | 30 | 0 | 0 | 93 | 3 | 0
6:00 | 3845 | 917 | 2040 | 0 | 1090 | 905 | 30 | 0 | 0 | 92 | 6 | 0
6:30 | 3842.5 | 918 | 2029.5 | 0 | 1067 | 890 | 30 | 0 | 0 | 91 | 15 | 0 |  |  |  |  | Coal
7:00 | 3840 | 919 | 2019 | 0 | 1044 | 875 | 30 | 0 | 0 | 90 | 24 | 0
7:30 | 3868.5 | 920.5 | 2025.5 | 0 | 1061 | 870 | 30 | 0 | 0 | 94 | 33.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3897 | 922 | 2032 | 0 | 1078 | 865 | 30 | 0 | 0 | 98 | 43 | 0
8:30 | 3905.5 | 922.5 | 2045.5 | 0 | 1188 | 860 | 30 | 0 | 24 | 95 | 52 | 0
9:00 | 3914 | 923 | 2059 | 0 | 1298 | 855 | 30 | 0 | 48 | 92 | 61 | 0
9:30 | 3898 | 923 | 2059 | 0 | 1479.5 | 850 | 30 | 0 | 48 | 92 | 73 | 0
10:00 | 3882 | 923 | 2059 | 0 | 1661 | 845 | 30 | 0 | 48 | 92 | 85 | 0
10:30 | 3816 | 923 | 2067 | 0 | 1779 | 850 | 30 | 0 | 48 | 94 | 114.5 | 0
11:00 | 3750 | 923 | 2075 | 0 | 1897 | 855 | 30 | 0 | 48 | 96 | 144 | 0
11:30 | 3733 | 923.5 | 2073.5 | 0 | 2132 | 855 | 30 | 0 | 48 | 106 | 100 | 0
12:00 | 3716 | 924 | 2072 | 0 | 2367 | 855 | 30 | 0 | 48 | 116 | 56 | 0
12:30 | 3678.5 | 923 | 2076.5 | 0 | 2577 | 875 | 30 | 0 | 48 | 117 | 92.5 | 0
13:00 | 3641 | 922 | 2081 | 0 | 2787 | 895 | 30 | 0 | 48 | 118 | 129 | 0
13:30 | 3641 | 922 | 2081 | 0 | 2787 | 895 | 30 | 0 | 48 | 118 | 129 | 0
14:00 | 3641 | 922 | 2081 | 0 | 2787 | 895 | 30 | 0 | 48 | 118 | 129 | 0
14:30 | 3686.5 | 919.5 | 2142 | 0 | 2953 | 905 | 30 | 0 | 48 | 114 | 109 | 0
15:00 | 3732 | 917 | 2203 | 0 | 3119 | 915 | 30 | 0 | 48 | 110 | 89 | 0
15:30 | 3708 | 916.5 | 2168.5 | 0 | 3263.5 | 920 | 30 | 0 | 54 | 109 | 71 | 0
16:00 | 3684 | 916 | 2134 | 0 | 3408 | 925 | 30 | 0 | 60 | 108 | 53 | 0
16:30 | 3671 | 916 | 2107 | 0 | 3346.5 | 910 | 30 | 0 | 69 | 109 | 40 | 0
17:00 | 3671 | 916 | 2080 | 0 | 3285 | 895 | 30 | 0 | 78 | 110 | 27 | 0
17:30 | 3624.5 | 916 | 2038.5 | 0 | 3200 | 880 | 30 | 0 | 96.5 | 109 | 15.5 | 0
18:00 | 3578 | 916 | 1997 | 0 | 3115 | 865 | 30 | 0 | 115 | 108 | 4 | 0
18:30 | 3649 | 914 | 2123.5 | 119.5 | 3452 | 880 | 30 | 0 | 301.5 | 112 | 2 | 0
19:00 | 3720 | 912 | 2250 | 239 | 3789 | 895 | 30 | 0 | 488 | 116 | 0 | 0
19:30 | 3826 | 915 | 2210 | 251 | 4392 | 1025 | 30 | 0 | 528 | 120 | 0 | 0
20:00 | 3825 | 915 | 2195 | 51 | 4414 | 1065 | 30 | 0 | 579 | 118 | 0 | 0
20:30 | 3827.5 | 915 | 2201.5 | 48 | 4399.5 | 1119.5 | 30 | 0 | 558.5 | 115 | 0 | 0
21:00 | 3830 | 915 | 2208 | 45 | 4385 | 1174 | 30 | 0 | 538 | 112 | 0 | 0
21:30 | 3836.5 | 915.5 | 2203.5 | 22.5 | 4372.5 | 1164 | 30 | 0 | 496 | 113 | 0 | 0
22:00 | 3843 | 916 | 2199 | 0 | 4360 | 1154 | 30 | 0 | 454 | 114 | 0 | 0
22:30 | 3851 | 916 | 2178.5 | 0 | 4302.5 | 1164 | 30 | 0 | 445.5 | 115 | 0 | 0
23:00 | 3859 | 916 | 2158 | 0 | 4245 | 1174 | 30 | 0 | 437 | 116 | 0 | 0
23:30 | 3857.5 | 916.5 | 2119 | 0 | 4188 | 1164.5 | 30 | 0 | 350.5 | 115 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.9° C
24:00 | 3856 | 917 | 2080 | 0 | 4131 | 1155 | 30 | 0 | 264 | 114 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 260.838 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.838 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 11 | 25 | 24 | 25 | 25 | 25 | 25 | 139966
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 2 | 5 | 15 | 15 | 0 | 19 | 12 | 12 | 8 | 4 | 0 | [8 empty] | 106650
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 205 | 214 | 203 | 203 | 216 | 223 | 204 | 210 | 214 | 202 | 203 | 203 |  | 216 | 203 | 202 | 203 | 212 | 203 | 203 | 4787249
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 51 | 51 | 50 | 49 | 49 | 48 |  | 270129
12 | Hathazari 100 MW peaking PP | [19 empty] | 26 | 51 | 51 | 51 |  |  |  | 112674
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 85 | 51 | 17 | 25 | 51 | 51 | 17 | 17 | 22 | 68 | 81 | 105 | 105 | 105 | 105 | 105 | 105 | 51 |  | 94 | 105 | 105 | 105 | 99 | 105 | 105 | 1905228
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 20 | 20 | 0 |  |  |  |  | 18432
14 | Titas 50 MW Peaking PP | [19 empty] | 41 | 41 | 41 |  |  |  |  | 68312
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 280 | 280 | 250 | 250 | 280 | 335 | 332 | 331 | 324 | 312 | 280 | 320 | 328 | 331 | 283 |  | 326 | 334 | 333 | 333 | 331 | 332 | 335 | 7555294
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 5 | 75 | 150 | 195 | 195 | 195 | 195 | 195 | 145 | 145 |  | 210 | 240 | 287 | 292 | 295 | 295 | 293 | 3249272
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4095000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6490673
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 26 |  | 33 | 30 | 31 | 31 | 31 | 32 | 33 | 741168
33 | Ashuganj 225 MW CCPP | 193 | 184 | 192 | 202 | 202 | 193 | 194 | 169 | 171 | 180 | 187 | 185 | 182 | 185 | 180 | 178 | 190 | 196 |  | 196 | 196 | 192 | 192 | 192 | 192 | 194 | 4575000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 270 | 7182500
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 134 | 135 | 135 | 135 | 135 | 136 | 134 | 135 | 136 | 136 | 136 | 136 | 138 | 135 | 135 | 135 | 135 | 134 |  | 135 | 134 | 135 | 134 | 134 | 135 | 135 | 3247270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 396 | 396 | 396 | 396 | 363 | 352 | 352 | 353 | 353 | 358 | 352 | 390 | 363 | 383 | 390 | 362 | 316 |  | 335 | 395 | 396 | 396 | 396 | 395 | 395 | 9125880
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5072250
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 332 | 332 | 332 | 297 | 281 | 281 | 282 | 282 | 282 | 282 | 322 | 318 | 312 | 302 | 303 | 284 |  | 332 | 334 | 332 | 312 | 316 | 320 | 320 | 7396000
42 | RPCL 210MW CCPP | 107 | 115 | 162 | 152 | 152 | 147 | 148 | 136 | 120 | 108 | 107 | 104 | 104 | 69 | 69 | 85 | 85 | 85 |  | 96 | 96 | 96 | 103 | 102 | 103 | 104 | 2577600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 2 | 1 | 9 | 4 | 26 | 12 | 15 | 21 | 37 | 13 | 8 | 0 | [8 empty] | 143230
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1034000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 948936
46 | Shajibazar 330 MW CCPP | 267 | 269 | 268 | 266 | 266 | 268 | 268 | 266 | 267 | 268 | 265 | 253 | 264 | 257 | 253 | 266 | 264 | 264 |  | 262 | 269 | 266 | 267 | 265 | 268 | 269 | 6079000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 50 | 50 | 40 | 40 | 40 | 60 | 60 | 60 | 58 | 40 | 40 | 42 | 25 | 25 | 25 |  | 25 | 30 | 28 | 25 | 30 | 30 | 28 | 1022784
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 75 | 72 | 75 | 75 | 75 | 72 | 72 | 72 |  | 74 | 75 | 72 | 72 | 72 | 72 | 72 | 1739520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 179 | 179 | 179 | 179 | 179 | 211 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 |  | 219 | 219 | 219 | 219 | 219 | 219 | 218 | 5021450
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 38 | 36 | 36 | 36 | 37 | 36 | 36 | 36 | 36 | 38 | 37 | 36 | 38 | 37 | 37 | 37 | 37 | 38 |  | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 886440
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244260
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237100
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | 53 | 23 |  | 53 | 53 | 53 | 53 | 53 | 22 | 5 | 1152000
56 | Shahjahanulla 25 MW PP | 24 | 22 | 22 | 21 | 0 | 8 | 20 | 20 | 0 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 180168
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 285 | 280 | 280 | 270 | 280 | 300 | 290 | 280 | 295 | 275 | 290 | 285 | 310 | 270 | 265 | 270 |  | 310 | 285 | 270 | 290 | 295 | 280 | 265 | 6986000
| Bibiyana South 400 MW | 400 | 400 | 400 | 370 | 370 | 350 | 350 | 388 | 400 | 400 | 400 | 381 | 304 | 360 | 394 | 365 | 350 | 350 |  | 400 | 400 | 400 | 400 | 397 | 400 | 400 | 9144200
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 3 | 35 | 35 | 35 | 17 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 713150
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 589440
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505008
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 0 |  |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 405936
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 429624
63 | Impoprt (Tripura) | 106 | 104 | 100 | 98 | 94 | 92 | 90 | 98 | 92 | 92 | 96 | 116 | 118 | 106 | 110 | 108 | 110 | 108 |  | 116 | 120 | 118 | 112 | 114 | 116 | 114 | 2507520
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 30 | 26 | 10 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 8 | 4 |  | 15 | 13 | 22 | 28 | 35 | 38 | 31 | 509280
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 432900
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 0 | 5 | 5 | 6 | 143640
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 19 | 24 | 24 | 33 | 33 | 0 |  |  |  |  | 33 | 33 | 31 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 597600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 15 | 15 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 15 | 20 | 20 | 20 | 455250
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 28 | 28 | 27 | 24 | 27 | 18 | 28 | 28 | 28 | 28 | 28 |  | 17 | 28 | 28 | 28 | 28 | 28 | 28 | 607140
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 |  | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 32 | 33 | 32 | 32 | 22 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 761300
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 94 | 96 | 100 | 100 | 100 | 100 | 97 | 99 | 42 |  | 95 | 96 | 100 | 100 | 100 | 100 | 100 | 2266545
| Feni Lanka Power | 100 | 90 | 90 | 99 | 99 | 88 | 88 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 85 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2024640
| Chowmuhani 113 MW | 40 | 38 | 38 | 38 | 38 | 38 | 39 | 38 | 38 | 37 | 32 | 32 | 27 | 28 | 28 | 34 | 104 | 104 |  | 105 | 105 | 105 | 105 | 105 | 106 | 34 | 1344000
| Manikgonj 162MW PP(MPGL) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 109 | 155 | 162 | 162 | 162 | 126 | 126 |  | 135 | 162 | 162 | 162 | 162 | 162 | 162 | 2276640
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 4 | 16 | 16 | 16 | 16 | 16 |  | 27 | 94 | 99 | 99 | 100 | 100 | 100 | 614467
78 | Gazipur 52 MW PP | [7 empty] | 11 | 25 | 37 | 40 | 42 | 49 | 49 | 40 | 42 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 729600
79 | Kodda 150MW PP | [8 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 1185600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 38 | 42 | 43 | 41 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 25 | 25 |  | 27 | 34 | 31 | 34 | 34 | 33 | 34 | 931656
| Gazipur 100 MW PP | 34 | [7 empty] | 27 | 52 | 52 | 52 | 52 | 52 | 65 | 90 | 98 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1369920
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 1 | 3 | 4 | 1 | 1 | 5 | 4 | 2 | 1 | [9 empty] | 28801
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1359354
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 106 | 92 | 93 | 93 | 78 | 73 | 73 | 74 | 85 | 92 | 93 | 93 | 93 |  | 96 | 110 | 110 | 110 | 110 | 110 | 110 | 2366898
82 | Madanganj 102 PP(Summit) | [9 empty] | 1 | 45 | 43 | 64 | 70 | 79 | 79 | 83 | 95 |  | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 1193808
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 130 | 120 | 120 | 120 | 115 | 130 | 125 | 140 | 120 | 130 | 130 | 145 | 125 | 140 | 140 | 125 | 130 | 135 |  | 145 | 125 | 125 | 125 | 130 | 125 | 120 | 3087855
87 | Meghnaghat 100 MW(IEL) | 92 | 92 | 87 | 83 | 84 | 82 | 83 | 83 | 83 | 83 | 82 | 82 | 82 | 88 | 86 | 84 | 91 | 92 |  | 91 | 90 | 91 | 89 | 90 | 91 | 91 | 2088000
| Meghnaghat 104 MW PP (OPCL) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 60 | 78 | 104 | 104 | 104 | 75 | 52 |  | 67 | 104 | 104 | 104 | 104 | 104 | 104 | 1441920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 40 | 40 | 80 | 40 | 40 | 70 | 70 | 70 |  | 80 | 80 | 80 | 80 | 80 | 40 | 40 | 817560
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 47 | 47 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 1197216
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1176735
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 3 | 24 | 24 | 24 | 32 | 64 | 64 | 64 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 784800
95 | Patenga 50MW PP (Baraka) | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 49 | 49 | 48 | 49 | 48 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1182240
96 | Chattogram 108 MW PP (ECPV) | 54 | 44 | 11 | 11 | 11 | 11 | 12 | 11 | 14 | 63 | 74 | 82 | 92 | 92 | 92 | 91 | 93 | 93 |  | 94 | 93 | 94 | 95 | 95 | 97 | 96 | 1534080
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 37 | 40 | 40 | 47 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1082424
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 15 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 658580
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 110 | 110 | 130 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3571691
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 |  |  |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 6850
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1307160
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 155 | 53 | 0 | 45 |  |  |  | 167452
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 15 | 78 | 25 |  |  |  |  | 64497
106 | Mymensingh 200 MW PP (United) | 85 | 45 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 40 | 67 | 90 | 110 | 139 | 179 | 181 |  | 181 | 181 | 182 | 182 | 182 | 182 | 183 | 2222400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 49 | 100 | 26 |  |  |  |  | 93075
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 19 | 45 | 49 | 88 | 114 | 149 | 149 | 149 | 115 | 105 |  | 121 | 149 | 149 | 149 | 149 | 149 | 149 | 1883660
115 | Juldah 100 MW PP Unit-3 (Acorn) | 64 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 63 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 64 | 1190400
116 | Chandpur 200MW (Desh energy) | 17 | 0 | [8 empty] | 5 | 17 | 23 | 34 | 44 | 106 | 85 | 85 |  | 100 | 190 | 185 | 200 | 200 | 200 | 200 | 1536960
117 | Ashuganj 150MW PP (Midland) | [8 empty] | 3 | 20 | 20 | 20 | 28 | 40 | 46 | 90 | 115 | 118 |  | 123 | 132 | 128 | 128 | 137 | 135 | 137 | 1318109
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 85 | 65 | 65 | 65 | 40 | 40 | 75 | 108 | 115 | 108 | 115 | 115 | 115 | 115 | 88 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2328000
| Anwara 300 MW PP (United) | 300 | 245 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 245 | 245 | 245 | 283 | 283 | 266 | 266 | 281 | 281 |  | 281 | 281 | 266 | 266 | 266 | 266 | 267 | 5813313
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 52 | 50 | 52 |  | 100 | 100 | 100 | 86 | 50 | 50 | 50 | 1190400
| Anlima Energy Ltd. | 99 | 99 | 68 | 68 | 68 | 68 | 68 | 68 | 85 | 99 | 99 | 99 | 99 | 99 | 99 | 97 | 79 | 77 |  | 77 | 77 | 76 | 65 | 71 | 77 | 77 | 2032364
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 31 | 35 | 35 | 493200
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | [15 empty] | 13 | 17 | 17 |  | 26 | 82 | 76 | 82 | 82 | 82 | 82 | 484800
| Kanchan Purbachal Power Generation Ltd. | 17 | [6 empty] | 1 | 17 | 17 | 20 | 55 | 55 | 55 | 55 | 55 |  |  |  | 24 | 55 | 55 | 55 | 55 | 55 | 55 | 721800
120 | Eastern Zone Total | 6724 | 6404 | 6221 | 6020 | 6005 | 5816 | 5749 | 5884 | 6156 | 6508 | 6749 | 7082 | 7242 | 7400 | 7628 | 7736 | 7600 | 7359 |  | 8539 | 9053 | 8856 | 8807 | 8743 | 8677 | 8467 | 173498447
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 28 | 45 | 60 | 60 | 86 | 78 | 78 |  | 84 | 99 | 99 | 66 | 66 | 16 | 16 | 953280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 18 | 21 | 37 | 32 | 10 |  |  | 84000
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 3 | 17 | 17 | 17 | 17 | 30 | 70 | 70 | 85 | 105 | 70 |  | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 1201440
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 14 | 36 | 43 | 58 | 94 | 35 | 83 | 46 | 29 | 26 | 11 | 4 | [8 empty] | 561600
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [10 empty] | 12 | 17 | 17 | 17 |  |  |  | 199200
133 | Bhola Nutan Biddut BD LTD (GAS) | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 192 | 192 | 192 | 192 | 170 | 174 | 210 | 210 | 210 | 200 | 216 |  | 216 | 216 | 206 | 216 | 212 | 218 | 172 | 4851955
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | [14 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 178848
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 86 | 87 | 87 | 86 | 86 | 86 | 84 | 85 | 83 | 85 | 80 | 84 | 82 | 82 | 85 | 85 | 84 |  | 83 | 86 | 87 | 86 | 85 | 86 | 87 | 2058199
140 | Bhola 33 MW PP (Venture) | 31 | 29 | 29 | 29 | 28 | 25 | 22 | 17 | 18 | 17 | 18 | 21 | 19 | 23 | 26 | 27 | 25 | 25 |  | 29 | 30 | 30 | 31 | 34 | 35 | 35 | 630160
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 40 | 40 | 40 | 24 | 8 | 8 |  | 24 | 32 | 32 | 32 | 32 |  |  | 265875
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 12 | 30 | 40 |  | 46 | 50 | 60 | 60 | 56 | 56 |  | 339712
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [12 empty] | 32 | 32 | 32 | 32 | 15 | 15 |  | 60 | 105 | 105 | 105 | 105 | 95 | 105 | 703440
146 | Bheramara HVDC | 912 | 912 | 910 | 911 | 914 | 917 | 919 | 922 | 923 | 923 | 923 | 924 | 922 | 922 | 917 | 916 | 916 | 916 |  | 912 | 915 | 915 | 915 | 916 | 916 | 917 | 22179636
147 | Bheramara 410 MW CCPP | 255 | 255 | 260 | 260 | 260 | 255 | 250 | 235 | 215 | 205 | 200 | 205 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 205 | 215 | 215 | 230 | 230 | 5528160
148 | Payra 1320 MW | 930 | 890 | 850 | 800 | 760 | 730 | 700 | 690 | 680 | 670 | 680 | 680 | 720 | 690 | 740 | 750 | 720 | 690 |  | 720 | 850 | 890 | 1000 | 980 | 1000 | 980 | 20748900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 174 | 174 | 174 | 175 | 4276800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 231872
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 5 | 1 | 3 | 2 | 1 | 0 | [8 empty] | 23340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 5 | 4 | 14 | 60 | 138 | 138 | 149 | 159 | 157 | 149 | 142 | 139 | 139 | 139 | 137 | 136 | 137 | 140 |  | 141 | 147 | 148 | 149 | 147 | 147 | 147 | 3185355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 145 | 145 | 145 | 143 | 134 | 130 | 130 | 132 | 132 | 121 | 0 | [15 empty] | 1530118
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 423 | 419 | 425 | 380 | 360 | 333 | 330 | 335 | 374 | 374 | 375 | 393 | 415 | 365 | 414 | 414 | 414 | 414 |  | 414 | 416 | 418 | 414 | 384 | 380 | 422 | 9452581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 5 | 5 | 12 | 6 | 2 | 0 |  | 31180
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 19 | 19 | 19 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 0 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 206496
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 34 | 50 | 50 | 50 | 50 | 50 | 8 | 245312
167 | Katakhali 50 MW Peaking PP | [17 empty] | 6 |  | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 188634
168 | Santahar 50 MW Peaking PP | [20 empty] | 8 | 27 | 39 | 36 | 36 | 35 | 143105
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 16 | 34 | 52 | 52 | 24 | 24 | 24 |  | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 518880
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 85 | 85 | 85 | 85 | 85 | 81 | 81 | 458464
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 90 | 94 | 113 | 113 | 113 | 70 |  | 85 | 113 | 113 | 113 | 113 | 113 | 113 | 1899936
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 35 | 35 | 35 | 35 | 0 |  |  |  | 20 | 50 | 70 | 90 | 90 | 100 | 113 | 113 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1725600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 40 | 40 | 40 | 40 | 15 | 0 |  | 1 | 29 | 36 | 34 | 52 | 77 | 103 | 102 | 102 | 72 | 72 |  | 103 | 108 | 109 | 109 | 109 | 109 | 109 | 1567593
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 5 | 5 | 3 | 2 | 2 | 0 | [8 empty] | 24535
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 17 | 17 |  | 95 | 115 | 115 | 115 | 115 | 115 | 115 | 661632
178