## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-06-12 | Wednesday
|  | Date (day): | 2019-06-12 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12878 | MW |  |  | (b) At Evening Peak Hour : |  | 14402 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-11 | 2019-06-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | ST-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 159 | 160 | 180 | 180
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 0 | 0 | 190 |  | Gas shoetage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 364 | 300 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 68 | 50 | 50 | 50 | 48 |  | Gas Shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 107 | 108 | 108 | 108 | 58 |  | Gas Shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | Gas Shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 338 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 352 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | Megnaghat 450 MW GT-1 |  | 16/06/2019
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 294 | 265 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 158 | 195 | 180 | 180 | 30
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 220 | 180 | 180
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 32 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 49 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 25 | 54 | 35 | 35 |  | 19 | Engine problem
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 132 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 63 | 71 | 73 | 73 |  | 35 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 47 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 48 | 50 | 50
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 70 | 149 | 149
37 | Gazipur 100 MW |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 90 | 100 | 100
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 2527 | 3142 | 4373 | 4773 | 566 | 296
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 24 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15.6 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 47 | 46 | 46
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 39 | 40 | 40 |  | 190 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 212 | 211 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 198 | 130 | 130
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 24 | 24 | 24 |  | 27 | Engine problem
47 | Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 105 | 105 | 106 | 106 | 105 | 105
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 60 | 60
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 50 | 100 | 100
51 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
52 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 17 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 21 | 40 | 15 | 30
53 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 102 | 90 | 90 |  | 18 | Engine problem
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 6.1 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 0 | 46 | 110 | 110
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 948.7 | 1205 | 1380 | 1372 | 160 | 275
54 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 50 | 60 | 110 | 110 | 25 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 215 | 221 | 221
56 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 320 | 360 | 360
57 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 224 | 242 | 0 | 250
58 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 55 | 55 | 55
60 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 | 53 |  | Gas Shortage
61 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 63 | 150 | 150 | 45 |  | Gas shortage
62 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
63 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 150 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 99 | 100 | 100
67 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 70 | 200 | 200 | 200
68 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
69 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 146 | 178 | 138 | 186
70 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
71 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
72 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
73 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1480 | 1744 | 1657 | 2205 | 386 | 61
74 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 145 | 150 | 150 | 52 |  | Gas shortage
75 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 0 | 20 | 20
76 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 70 | 92 | 95 | 95
77 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 2 | 0
78 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 43 | 192 | 100 | 200
79 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 95 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 375.2 | 524 | 467 | 565 | 52 | 0
80 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 56 | 60 | 60
81 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 57 | 58 | 58
82 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
83 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 250 | 252 | 330 | 330 |  |  | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
85 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 49 | 44 | 44
86 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 63 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 67 | 81 | 86 | 86
89 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 42 | 46 | 46 | 46
90 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 125 | 110 | 130 | 130
91 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
92 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 47 | 45 | 45
93 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 24 | 25 | 25
94 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  |  | Under Maint |  | 14/06/2019
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 287 | 250 | 285 | 285 |  |  | On test
95 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1292 | 1269 | 1429 | 1429 | 0 | 0
96 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 660 | 905 | 701 | 947
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
97 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 46 | 99 | 115 | 115
98 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 31 | 31
99 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve.
100 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 50 | 80
101 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 15/06/2019
102 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
104 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 89 | 105 | 105 | 105
105 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 52 | 97 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 879 | 1473 | 1147 | 1555 | 0 | 410
106 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
107 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
108 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 38 | 33 | 33
109 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 146 | 147 | 150 | 150
110 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 263 | 392 | 388 | 414 | 0 | 0
111 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
112 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
113 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 35 | 35
114 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 24 | 50 | 50 | 50
115 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
116 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 40 | 40
117 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 197 | 190 | 200 | 200 |  |  | FGMO
118 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 187 | 200 | 200 |  |  | FGMO
119 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 197 | 220 | 220
120 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 408 | 300 | 414 | 414
121 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 45 | 45
122 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
123 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 15 | 16 | 17 | 17
124 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
125 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 0 | 50 | 43 | 45 |  | 9 | Engine problem
126 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 24 | 90 | 95 | 95
127 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
128 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1084 | 1501 | 1802 | 1854 | 0 | 109
129 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0
130 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74
131 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 17 | 17
132 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 6 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 206 | 232 | 235 | 235 | 74 | 85
| Total |  |  |  |  | 18539 | 17996 | 9054.9 | 11482 | 12878 | 14402 | 1238 | 1236
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8456.3397 | 10723 | 12026.7196 | 13449.9779
A. |  | 2019-06-11 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11482 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7564 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11482 | MW
3 | Day peak Generation : |  |  | 9054.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10723 | MW
4 | Evening peak Generation : |  |  | 11482 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 230.4901 | MKWHr | By Solar | 0.19061 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 152.9063 | MKWHr |  | By Oil: | 51.5421 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.8665 | MKWHr |  | By Hydro: | 0.84792 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1238 | MW | Dhaka | 3449 | 3449 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1236 | MW | Chittagong | 1160 | 1160 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2474 | MW | Khulna | 1450 | 1450 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1389.43 | MMCFD |  |  | Rajshahi | 1199 | 1199 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 106270970.138 | ii) Oil : | Taka | 368415357.65 | Comilla | 1075 | 1075 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18784690 | Total | Taka | 493471017.788 | Mymensingh | 904 | 904 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7.323 | MKWHr. | Sylhet | 466 | 466 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -410 | MW (E to W) at | 21:00 | hrs | Barisal | 351 | 351 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -740 | MW at | 4:00 | hrs | Rangpur | 669 | 669 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.50° C |  |  | Total | 10723 | 10723 |  | 0
B. |  | 2019-06-12 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14402 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 2202 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 244.9032 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8732.5 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.3542 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7824 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.15 |  | (b) Today: | 73.02 |  | (c) Rule Curve: |  | 78.87
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-06-11
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 160 | 110 | 300 | 108 | 73 | 330 | 323 | 0 | 20 | 225 | 285 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 98 | 0 | 64 | 0 | 26 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 30 | 48 | 0 | 39 | 0 | 100 | 100 | 25 | 207 | 0 | 130 | 0 | 0 | 16 | 0 | 34 | 50 | 0 | 47 | 19 | 42 | 0 | 0 | 0 | 360 | 231 | 193 | 63 | 100 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 166 | 146 | 92 | 20 | 0 | 58 | 58 | 53 | 50 | 130 | 254 | 63 | 74 | 46 | 116 | 19 | 45 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 185 | 0 | 70 | 0 | 100 | 200 | 50 | 260 | 93 | 90 | 105 | 0 | 0 |  | 793 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 58 | 32 | 149 | 37 | 110 | 0 | 0 | 60 | 50 | 32 | 85 | 50 | 24 | 0 | 50 | 41 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 17 | 187 | 0 | 185 | 0 | 96 | 100 | 208 | 0 | 360 | 105 | 0 | 108 | 99 | 0 |  | 7204 | 3400 | 10604 | 4591 | 793 | 1864 | 2520 | 199 | 39 | 432 | 166 | 0 | 0 | 73.2
2:00 | 35 | 0 | 160 | 110 | 320 | 111 | 73 | 348 | 323 | 0 | 20 | 225 | 270 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 98 | 0 | 64 | 0 | 6 | 35 | 55 | 55 | 22 | 25 | 14 | 25 | 30 | 0 | 0 | 38 | 0 | 100 | 100 | 25 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 34 | 50 | 0 | 47 | 19 | 42 | 0 | 0 | 0 | 360 | 239 | 181 | 63 | 100 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 164 | 145 | 92 | 20 | 0 | 58 | 58 | 53 | 50 | 130 | 252 | 63 | 74 | 46 | 116 | 19 | 45 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 185 | 0 | 70 | 0 | 100 | 200 | 50 | 260 | 93 | 90 | 105 | 0 | 0 |  | 531 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 58 | 32 | 149 | 36 | 110 | 0 | 0 | 60 | 50 | 32 | 85 | 50 | 24 | 0 | 50 | 41 | 22 | 16 | 8 | 0 | 0 | 199 | 17 | 0 | 195 | 0 | 193 | 0 | 96 | 20 | 208 | 0 | 415 | 105 | 0 | 108 | 99 | 0 |  | 7142 | 3108 | 10250 | 4625 | 531 | 1921 | 2357 | 199 | 38 | 415 | 164 | 0 | 0 | 73.19
3:00 | 35 | 0 | 160 | 110 | 320 | 108 | 73 | 330 | 323 | 0 | 20 | 225 | 287 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 90 | 0 | 72 | 0 | 6 | 35 | 55 | 17 | 22 | 25 | 14 | 25 | 30 | 0 | 0 | 38 | 0 | 100 | 100 | 25 | 211 | 0 | 131 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 47 | 19 | 42 | 0 | 0 | 0 | 360 | 235 | 196 | 63 | 100 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 162 | 146 | 92 | 20 | 0 | 60 | 58 | 53 | 50 | 130 | 250 | 63 | 74 | 46 | 112 | 19 | 45 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 185 | 0 | 35 | 0 | 100 | 200 | 50 | 260 | 94 | 89 | 105 | 0 | 0 |  | 531 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 52 | 32 | 148 | 37 | 110 | 0 | 0 | 60 | 50 | 32 | 85 | 0 | 0 | 0 | 42 | 41 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 186 | 0 | 184 | 0 | 96 | 0 | 208 | 0 | 415 | 105 | 0 | 108 | 99 | 0 |  | 6994 | 2965 | 9959 | 4603 | 531 | 1919 | 2157 | 199 | 38 | 350 | 162 | 0 | 0 | 73.18
4:00 | 35 | 0 | 160 | 110 | 320 | 108 | 73 | 330 | 323 | 0 | 20 | 225 | 270 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 55 | 0 | 71 | 0 | 6 | 35 | 18 | 0 | 22 | 25 | 14 | 0 | 30 | 0 | 0 | 39 | 0 | 100 | 100 | 0 | 205 | 0 | 132 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 47 | 19 | 42 | 0 | 0 | 0 | 360 | 239 | 181 | 63 | 100 | 0 | 55 | 0 | 25 | 0 | 0 | 40 | 22 | 11 | 25 | 20 | 160 | 147 | 92 | 20 | 0 | 60 | 58 | 50 | 50 | 100 | 250 | 63 | 74 | 46 | 112 | 19 | 45 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 100 | 200 | 50 | 261 | 94 | 90 | 72 | 0 | 0 |  | 532 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 46 | 32 | 148 | 37 | 80 | 0 | 0 | 60 | 50 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 185 | 0 | 183 | 0 | 96 | 0 | 208 | 0 | 420 | 105 | 0 | 108 | 99 | 0 |  | 6645 | 2818 | 9463 | 4563 | 532 | 1880 | 1854 | 199 | 39 | 236 | 160 | 0 | 0 | 73.17
5:00 | 35 | 0 | 160 | 110 | 320 | 108 | 73 | 349 | 324 | 0 | 20 | 225 | 270 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 14 | 25 | 30 | 0 | 0 | 40 | 0 | 100 | 100 | 0 | 209 | 0 | 127 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 45 | 19 | 42 | 0 | 0 | 0 | 360 | 235 | 197 | 63 | 100 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 150 | 147 | 92 | 20 | 0 | 56 | 58 | 50 | 50 | 100 | 249 | 63 | 75 | 46 | 110 | 19 | 0 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 140 | 5 | 260 | 94 | 51 | 18 | 0 | 0 |  | 531 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 149 | 36 | 64 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 8 | 0 | 0 | 198 | 0 | 0 | 195 | 0 | 193 | 0 | 95 | 0 | 208 | 0 | 380 | 105 | 0 | 17 | 99 | 0 |  | 6281 | 2520 | 8801 | 4631 | 531 | 1791 | 1410 | 198 | 40 | 50 | 150 | 0 | 0 | 73.16
6:00 | 35 | 0 | 160 | 110 | 320 | 108 | 73 | 329 | 323 | 0 | 20 | 225 | 250 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 35 | 0 | 0 | 22 | 25 | 14 | 25 | 30 | 0 | 0 | 40 | 0 | 100 | 100 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 19 | 42 | 0 | 0 | 0 | 300 | 242 | 182 | 63 | 100 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 128 | 147 | 16 | 20 | 0.1 | 58 | 58 | 50 | 50 | 100 | 252 | 64 | 75 | 46 | 118 | 19 | 45 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 10 | 17 | 0 | 260 | 94 | 51 | 18 | 0 | 0 |  | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 181 | 0 | 96 | 0 | 208 | 0 | 330 | 35 | 0 | 17 | 99 | 0 |  | 5714.4 | 2178 | 7892.4 | 4483 | 531 | 1777 | 708 | 199 | 40 | 24 | 128 | 2.4 | 0 | 73.15
7:00 | 35 | 0 | 160 | 110 | 320 | 108 | 73 | 328 | 304 | 0 | 20 | 225 | 285 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 14 | 25 | 30 | 0 | 0 | 38 | 0 | 100 | 100 | 1 | 206 | 0 | 132 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 18 | 18 | 39 | 0 | 0 | 0 | 300 | 235 | 194 | 63 | 100 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 108 | 145 | 0 | 20 | 0.1 | 57 | 58 | 50 | 50 | 100 | 251 | 62 | 40 | 45 | 115 | 19 | 45 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 10 | 17 | 0 | 221 | 94 | 36 | 18 | 1.8 | 0 |  | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 177 | 0 | 96 | 0 | 199 | 0 | 300 | 35 | 0 | 0 | 52 | 0 |  | 5570.4 | 2065 | 7635.4 | 4434 | 531 | 1683 | 613 | 199 | 38 | 24 | 108 | 5.4 | 0 | 73.14
8:00 | 35 | 0 | 160 | 110 | 320 | 108 | 71 | 334 | 303 | 0 | 20 | 225 | 290 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 14 | 0 | 30 | 0 | 0 | 37 | 0 | 100 | 100 | 19 | 214 | 0 | 134 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 18 | 4 | 50 | 0 | 0 | 300 | 230 | 204 | 63 | 98 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 132 | 145 | 0 | 20 | 0.1 | 58 | 58 | 50 | 50 | 100 | 249 | 61 | 40 | 45 | 124 | 0 | 45 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6 | 10 | 0 | 0 | 219 | 65 | 34 | 18 | 3.3 | 0 |  | 524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 5 | 0 | 0 | 200 | 0 | 0 | 191 | 0 | 156 | 0 | 95 | 0 | 175 | 0 | 300 | 35 | 0 | 0 | 52 | 0 |  | 5569 | 1995 | 7564 | 4423 | 524 | 1643 | 590 | 200 | 37 | 0 | 132 | 15 | 0 | 0
9:00 | 35 | 0 | 160 | 110 | 320 | 108 | 71 | 360 | 303 | 0 | 20 | 225 | 282 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 14 | 0 | 30 | 0 | 0 | 36 | 0 | 100 | 100 | 25 | 210 | 0 | 135 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 18 | 4 | 50 | 0 | 0 | 330 | 231 | 202 | 63 | 98 | 0 | 57 | 0 | 25 | 0 | 0 | 0 | 22 | 8 | 25 | 20 | 138 | 149 | 0 | 20 | 0.8 | 58 | 58 | 50 | 50 | 100 | 250 | 61 | 40 | 45 | 116 | 0 | 45 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 70 | 0 | 0 | 270 | 60 | 34 | 18 | 4.6 | 0 |  | 524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 5 | 0 | 0 | 199 | 0 | 0 | 200 | 0 | 165 | 0 | 94 | 0 | 183 | 0 | 350 | 35 | 0 | 0 | 52 | 0 |  | 5772.5 | 2071 | 7843.5 | 4582 | 524 | 1697 | 645 | 199 | 36 | 0 | 138 | 22.5 | 0 | 0
10:00 | 35 | 0 | 161 | 110 | 370 | 108 | 70 | 354 | 332 | 0 | 20 | 225 | 270 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 6 | 17 | 18 | 0 | 22 | 25 | 14 | 0 | 30 | 0 | 0 | 35 | 0 | 100 | 100 | 25 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 18 | 2 | 50 | 0 | 0 | 330 | 228 | 185 | 63 | 98 | 0 | 56 | 0 | 26 | 0 | 0 | 4 | 22 | 8 | 25 | 20 | 140 | 150 | 2 | 20 | 2.1 | 58 | 58 | 50 | 50 | 130 | 247 | 61 | 72 | 45 | 114 | 0 | 42 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7 | 70 | 0 | 0 | 297 | 75 | 60 | 19 | 5.8 | 0 |  | 661 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 24 | 148 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 5 | 0 | 0 | 199 | 0 | 0 | 197 | 0 | 161 | 0 | 96 | 0 | 191 | 0 | 350 | 70 | 0 | 0 | 53 | 3 |  | 6011.6 | 2304 | 8315.6 | 4620 | 661 | 1781 | 855 | 199 | 35 | 0 | 140 | 24.6 | 0 | 0
11:00 | 35 | 0 | 161 | 110 | 370 | 108 | 70 | 330 | 334 | 0 | 20 | 225 | 260 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 6 | 17 | 18 | 0 | 19 | 25 | 14 | 20 | 30 | 0 | 0 | 36 | 0 | 100 | 100 | 25 | 203 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 47 | 18 | 2 | 50 | 0 | 0 | 330 | 231 | 183 | 63 | 100 | 0 | 54 | 0 | 35 | 0 | 0 | 38 | 22 | 8 | 25 | 20 | 142 | 148 | 36 | 17 | 2.1 | 58 | 58 | 50 | 50 | 163 | 250 | 61 | 68 | 45 | 111 | 0 | 42 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 20.2 | 100 | 17 | 7 | 295 | 96 | 70 | 67 | 5.6 | 0 |  | 661 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 148 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 18 | 15 | 5 | 0 | 0 | 199 | 0 | 0 | 194 | 0 | 168 | 0 | 95 | 0 | 185 | 0 | 350 | 70 | 0 | 0 | 52 | 6 |  | 6268.9 | 2353 | 8621.9 | 4592 | 661 | 1817 | 1123 | 199 | 36 | 24 | 142 | 27.9 | 0 | 0
12:00 | 35 | 0 | 159 | 110 | 364 | 107 | 68 | 350 | 343 | 0 | 20 | 225 | 294 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 6 | 25 | 18 | 0 | 19 | 25 | 14 | 25 | 29 | 0 | 0 | 36 | 0 | 100 | 100 | 24 | 212 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 47 | 15 | 21 | 50 | 0 | 0 | 355 | 224 | 206 | 63 | 100 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 146 | 144 | 70 | 20 | 2.2 | 57 | 58 | 47 | 50 | 163 | 250 | 58 | 67 | 42 | 125 | 0 | 44 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 15.6 | 100 | 70 | 50 | 287 | 96 | 70 | 106 | 6.1 | 0 |  | 660 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 18 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 197 | 0 | 167 | 0 | 95 | 0 | 171 | 0 | 408 | 89 | 0 | 0 | 52 | 6 |  | 6622.9 | 2432 | 9054.9 | 4659 | 660 | 1897 | 1409 | 200 | 36 | 24 | 146 | 23.9 | 0 | 0
13:00 | 35 | 0 | 161 | 110 | 364 | 106 | 67 | 365 | 343 | 0 | 20 | 225 | 270 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 32 | 0 | 70 | 0 | 6 | 45 | 55 | 0 | 22 | 25 | 14 | 25 | 33 | 15 | 0 | 37 | 0 | 100 | 100 | 24 | 208 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 47 | 15 | 5 | 50 | 0 | 0 | 355 | 228 | 197 | 63 | 95 | 0 | 53 | 0 | 35 | 0 | 0 | 52 | 18 | 8 | 25 | 20 | 158 | 131 | 87 | 17 | 2.1 | 56 | 58 | 53 | 50 | 163 | 250 | 59 | 69 | 42 | 108 | 0 | 44 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 15.5 | 100 | 120 | 100 | 289 | 95 | 70 | 106 | 6 | 0 |  | 660 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 24 | 0 | 0 | 8 | 0 | 18 | 15 | 5 | 0 | 0 | 199 | 0 | 0 | 203 | 0 | 174 | 0 | 95 | 0 | 189 | 0 | 407 | 89 | 0 | 43 | 87 | 7 |  | 6766.6 | 2593 | 9359.6 | 4665 | 660 | 1886 | 1675 | 199 | 37 | 56 | 158 | 23.6 | 0 | 0
14:00 | 37 | 0 | 161 | 110 | 340 | 106 | 67 | 343 | 343 | 0 | 20 | 225 | 255 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 48 | 0 | 48 | 0 | 6 | 35 | 55 | 0 | 19 | 25 | 12 | 25 | 33 | 17 | 0 | 37 | 0 | 100 | 100 | 24 | 205 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 46 | 15 | 3 | 50 | 0 | 0 | 360 | 231 | 182 | 63 | 94 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 162 | 144 | 94 | 17 | 2.1 | 56 | 57 | 53 | 50 | 163 | 250 | 60 | 69 | 42 | 112 | 0 | 44 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 10.58 | 100 | 140 | 112 | 289 | 95 | 70 | 106 | 4.02 | 0 |  | 659 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 34 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 199 | 0 | 0 | 194 | 0 | 164 | 0 | 97 | 0 | 185 | 0 | 414 | 89 | 0 | 87 | 86 | 6 |  | 6874.7 | 2648 | 9522.7 | 4601 | 659 | 1903 | 1863 | 199 | 37 | 82 | 162 | 16.7 | 0 | 0
15:00 | 35 | 0 | 160 | 110 | 340 | 105 | 66 | 337 | 336 | 0 | 20 | 225 | 274 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 82 | 0 | 68 | 0 | 6 | 35 | 55 | 0 | 19 | 25 | 12 | 25 | 33 | 35 | 0 | 38 | 0 | 100 | 100 | 25 | 205 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 24 | 47 | 15 | 3 | 50 | 0 | 0 | 360 | 220 | 193 | 63 | 94 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 166 | 143 | 94 | 17 | 1.2 | 56 | 57 | 50 | 49 | 163 | 253 | 60 | 66 | 42 | 112 | 0 | 44 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 14.94 | 100 | 165 | 145 | 286 | 94 | 70 | 106 | 4.24 | 0 |  | 660 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 34 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 191 | 0 | 184 | 0 | 94 | 0 | 202 | 0 | 407 | 86 | 0 | 108 | 86 | 6 |  | 7063.38 | 2694 | 9757.38 | 4629 | 660 | 1877 | 2052 | 199 | 38 | 116 | 166 | 20.38 | 0 | 0
16:00 | 35 | 0 | 160 | 110 | 340 | 100 | 66 | 339 | 337 | 0 | 20 | 225 | 280 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 82 | 0 | 68 | 0 | 6 | 54 | 55 | 0 | 19 | 25 | 12 | 33 | 33 | 48 | 0 | 38 | 0 | 100 | 100 | 25 | 205 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 68 | 46 | 15 | 2 | 50 | 0 | 0 | 360 | 220 | 200 | 63 | 96 | 0 | 53 | 0 | 35 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 166 | 140 | 94 | 17 | 0.5 | 56 | 57 | 53 | 49 | 163 | 247 | 59 | 69 | 43 | 110 | 0 | 42 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 11.55 | 100 | 200 | 149 | 285 | 94 | 70 | 106 | 2.53 | 0 |  | 660 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 70 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 193 | 0 | 190 | 0 | 94 | 0 | 199 | 0 | 405 | 90 | 0 | 108 | 85 | 6 |  | 7192.58 | 2736 | 9928.58 | 4645 | 660 | 1874 | 2180 | 199 | 38 | 152 | 166 | 14.58 | 0 | 0
17:00 | 35 | 0 | 160 | 110 | 340 | 104 | 66 | 329 | 339 | 0 | 20 | 225 | 228 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 82 | 0 | 68 | 0 | 6 | 54 | 55 | 0 | 0 | 25 | 14 | 33 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 25 | 205 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 64 | 46 | 0 | 5 | 50 | 0 | 0 | 360 | 239 | 182 | 63 | 95 | 0 | 50 | 0 | 35 | 0 | 0 | 34 | 20 | 8 | 25 | 20 | 160 | 143 | 86 | 17 | 0.4 | 56 | 57 | 11 | 49 | 163 | 250 | 49 | 10 | 44 | 109 | 0 | 12 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 4.53 | 100 | 200 | 70 | 289 | 94 | 70 | 105 | 1.48 | 0 |  | 660 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 24 | 32 | 139 | 25 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 180 | 0 | 97 | 0 | 193 | 0 | 426 | 60 | 0 | 108 | 97 | 8 |  | 6837.41 | 2678 | 9515.41 | 4551 | 660 | 1772 | 1952 | 199 | 39 | 176 | 160 | 6.41 | 0 | 0
18:00 | 35 | 0 | 160 | 110 | 300 | 32 | 50 | 328 | 256 | 0 | 20 | 225 | 240 | 0 | 0 | 0 | 32 | 0 | 70 | 0 | 0 | 0 | 82 | 0 | 69 | 0 | 6 | 54 | 55 | 0 | 0 | 25 | 14 | 33 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 24 | 205 | 0 | 100 | 0 | 0 | 16 | 16 | 0 | 10 | 64 | 46 | 17 | 14 | 50 | 0 | 0 | 270 | 242 | 182 | 63 | 96 | 0 | 50 | 0 | 35 | 0 | 0 | 16 | 22 | 8 | 25 | 20 | 146 | 143 | 93 | 17 | 0.1 | 56 | 57 | 11 | 10 | 100 | 250 | 49 | 10 | 10 | 108 | 0 | 12 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0.37 | 100 | 200 | 70 | 201 | 94 | 70 | 105 | 0.47 | 0 |  | 661 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 9 | 40 | 32 | 141 | 26 | 4 | 0 | 0 | 50 | 0 | 10 | 70 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 181 | 0 | 178 | 0 | 52 | 0 | 183 | 0 | 263 | 70 | 0 | 108 | 86 | 17 |  | 6254.94 | 2507 | 8761.94 | 4254 | 661 | 1267 | 1968 | 199 | 39 | 227 | 146 | 0.94 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 160 | 110 | 300 | 32 | 50 | 329 | 302 | 26 | 20 | 225 | 300 | 14 | 9 | 6 | 45 | 0 | 75 | 0 | 2 | 16 | 90 | 7 | 69 | 0 | 6 | 54 | 55 | 40 | 19 | 25 | 14 | 33 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 24 | 214 | 0 | 110 | 0 | 0 | 24 | 39 | 0 | 30 | 69 | 47 | 17 | 27 | 50 | 0 | 0 | 270 | 206 | 200 | 63 | 96 | 0 | 54 | 0 | 35 | 0 | 0 | 18 | 22 | 8 | 25 | 20 | 180 | 143 | 93 | 0 | 0 | 56 | 57 | 11 | 20 | 100 | 250 | 61 | 45 | 10 | 118 | 0 | 42 | 10 | 0 | 24 | 11 | 0 | 20 | 0 | 0 | 195 | 0 | 6 | 0 | 100 | 200 | 95 | 250 | 94 | 90 | 106 | 0 | 0 |  | 904 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 20 | 75 | 32 | 147 | 32 | 110 | 0 | 0 | 50 | 42 | 31 | 81 | 24 | 24 | 42 | 42 | 21 | 22 | 16 | 8 | 0 | 0 | 199 | 17 | 17 | 182 | 0 | 181 | 0 | 12 | 1 | 189 | 0 | 350 | 70 | 0 | 108 | 94 | 35 |  | 6843 | 3251 | 10094 | 4363 | 904 | 1458 | 2476 | 199 | 39 | 475 | 180 | 0 | 0 | 73.21
19:30 | 35 | 0 | 160 | 110 | 300 | 32 | 50 | 330 | 326 | 55 | 20 | 225 | 243 | 25 | 30 | 20 | 120 | 0 | 120 | 0 | 10 | 64 | 110 | 50 | 69 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 14 | 33 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 24 | 204 | 0 | 130 | 0 | 0 | 24 | 65 | 56 | 50 | 85 | 47 | 17 | 36 | 50 | 0 | 0 | 320 | 246 | 181 | 63 | 96 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 176 | 146 | 93 | 0 | 0 | 56 | 57 | 50 | 50 | 100 | 250 | 52 | 81 | 38 | 108 | 0 | 42 | 10 | 0 | 24 | 11 | 0 | 75 | 0 | 0 | 195 | 0 | 70 | 0 | 100 | 200 | 150 | 200 | 94 | 90 | 105 | 0 | 0 |  | 905 | 10 | 0 | 0 | 99 | 0 | 0 | 0 | 17 | 70 | 40 | 133 | 37 | 110 | 0 | 0 | 60 | 50 | 32 | 90 | 50 | 43 | 45 | 52 | 37 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 18 | 191 | 0 | 182 | 0 | 91 | 75 | 191 | 0 | 300 | 105 | 0 | 108 | 97 | 35 |  | 7660 | 3538 | 11198 | 4510 | 905 | 1658 | 3094 | 199 | 39 | 617 | 176 | 0 | 0 | 0
20:00 | 35 | 0 | 162 | 110 | 300 | 85 | 50 | 329 | 326 | 55 | 20 | 225 | 245 | 38 | 34 | 27 | 120 | 0 | 110 | 0 | 16 | 50 | 112 | 50 | 69 | 0 | 26 | 54 | 55 | 55 | 19 | 25 | 14 | 33 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 25 | 205 | 0 | 132 | 0 | 0 | 24 | 65 | 68 | 50 | 96 | 47 | 17 | 36 | 50 | 0 | 0 | 320 | 246 | 182 | 55 | 97 | 0 | 55 | 0 | 35 | 0 | 0 | 50 | 22 | 8 | 25 | 20 | 180 | 145 | 93 | 0 | 0 | 56 | 57 | 50 | 49 | 100 | 250 | 42 | 81 | 46 | 106 | 0 | 47 | 10 | 0 | 24 | 11 | 0 | 81 | 0 | 0 | 195 | 0 | 70 | 0 | 100 | 200 | 150 | 200 | 94 | 90 | 106 | 0 | 2 |  | 905 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 26 | 62 | 40 | 132 | 38 | 110 | 0 | 0 | 60 | 50 | 39 | 90 | 50 | 43 | 47 | 52 | 44 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 18 | 185 | 0 | 180 | 0 | 96 | 85 | 185 | 0 | 300 | 105 | 0 | 108 | 97 | 27 |  | 7734 | 3570 | 11304 | 4478 | 905 | 1722 | 3111 | 199 | 39 | 670 | 180 | 0 | 0 | 73.21
21:00 | 35 | 0 | 160 | 110 | 300 | 108 | 50 | 338 | 352 | 0 | 20 | 225 | 265 | 0 | 0 | 0 | 220 | 0 | 195 | 0 | 0 | 32 | 132 | 0 | 71 | 0 | 49 | 54 | 55 | 36 | 19 | 25 | 22 | 28 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 25 | 211 | 0 | 130 | 0 | 0 | 24 | 0 | 68 | 50 | 102 | 47 | 17 | 40 | 60 | 0 | 0 | 320 | 242 | 215 | 63 | 99 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 178 | 145 | 92 | 0 | 0 | 56 | 57 | 50 | 49 | 163 | 252 | 63 | 81 | 46 | 110 | 0 | 47 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 70 | 0 | 100 | 200 | 150 | 250 | 95 | 90 | 106 | 0 | 46 |  | 905 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 55 | 40 | 147 | 38 | 110 | 0 | 0 | 60 | 50 | 38 | 90 | 50 | 43 | 45 | 50 | 44 | 22 | 16 | 11 | 0 | 0 | 199 | 16 | 17 | 190 | 0 | 187 | 0 | 97 | 100 | 197 | 0 | 300 | 105 | 0 | 108 | 97 | 0 |  | 7884 | 3598 | 11482 | 4834 | 905 | 1847 | 2853 | 199 | 39 | 627 | 178 | 0 | 0 | 73.21
22:00 | 35 | 0 | 160 | 110 | 300 | 108 | 50 | 332 | 350 | 0 | 20 | 225 | 293 | 0 | 0 | 0 | 220 | 0 | 190 | 0 | 0 | 32 | 132 | 0 | 73 | 0 | 48 | 54 | 55 | 17 | 19 | 25 | 12 | 28 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 24 | 206 | 0 | 132 | 0 | 0 | 25 | 0 | 68 | 50 | 102 | 47 | 17 | 42 | 100 | 0 | 0 | 320 | 235 | 214 | 63 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 182 | 144 | 92 | 20 | 0 | 50 | 57 | 50 | 49 | 163 | 151 | 61 | 81 | 46 | 128 | 0 | 47 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 70 | 0 | 100 | 200 | 123 | 299 | 94 | 90 | 105 | 0 | 50 |  | 905 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 35 | 56 | 0 | 148 | 39 | 110 | 0 | 0 | 60 | 50 | 39 | 90 | 50 | 43 | 44 | 52 | 41 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 17 | 189 | 0 | 186 | 0 | 97 | 100 | 198 | 0 | 300 | 105 | 0 | 108 | 97 | 0 |  | 7851 | 3555 | 11406 | 4820 | 905 | 1848 | 2792 | 199 | 39 | 621 | 182 | 0 | 0 | 73.06
23:00 | 35 | 0 | 160 | 110 | 300 | 0 | 0 | 355 | 350 | 0 | 20 | 225 | 300 | 0 | 0 | 0 | 218 | 0 | 189 | 0 | 0 | 32 | 130 | 0 | 73 | 0 | 48 | 54 | 55 | 17 | 19 | 25 | 22 | 28 | 33 | 40 | 0 | 37 | 0 | 100 | 100 | 24 | 220 | 0 | 130 | 0 | 0 | 25 | 0 | 66 | 50 | 103 | 47 | 18 | 42 | 90 | 0 | 0 | 270 | 224 | 204 | 8 | 98 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 184 | 140 | 92 | 20 | 0 | 59 | 57 | 50 | 50 | 163 | 150 | 59 | 73 | 46 | 132 | 0 | 47 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 185 | 0 | 70 | 0 | 100 | 200 | 123 | 284 | 95 | 90 | 105 | 0 | 50 |  | 905 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 32 | 56 | 40 | 147 | 39 | 110 | 0 | 0 | 60 | 50 | 39 | 85 | 50 | 43 | 44 | 50 | 42 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 17 | 199 | 0 | 197 | 0 | 96 | 100 | 201 | 0 | 394 | 105 | 0 | 108 | 97 | 0 |  | 7574 | 3702 | 11276 | 4788 | 905 | 1721 | 2832 | 199 | 37 | 610 | 184 | 0 | 0 | 73.05
24:00 | 35 | 0 | 180 | 0 | 350 | 0 | 0 | 407 | 304 | 0 | 20 | 225 | 295 | 0 | 0 | 0 | 224 | 0 | 128 | 0 | 0 | 64 | 130 | 0 | 74 | 0 | 18 | 54 | 55 | 55 | 19 | 25 | 22 | 28 | 33 | 40 | 0 | 37 | 0 | 100 | 100 | 25 | 231 | 0 | 132 | 0 | 0 | 25 | 0 | 66 | 90 | 103 | 47 | 19 | 42 | 80 | 0 | 0 | 300 | 235 | 214 | 8 | 98 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 180 | 144 | 92 | 20 | 0 | 57 | 57 | 50 | 50 | 130 | 150 | 61 | 73 | 46 | 131 | 0 | 47 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 100 | 200 | 148 | 240 | 95 | 90 | 105 | 0 | 0 |  | 906 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 32 | 56 | 40 | 148 | 39 | 110 | 0 | 0 | 60 | 50 | 39 | 85 | 50 | 43 | 44 | 50 | 42 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 17 | 210 | 0 | 214 | 0 | 97 | 100 | 215 | 0 | 414 | 105 | 0 | 108 | 97 | 0 |  | 7543 | 3767 | 11310 | 4808 | 906 | 1663 | 2907 | 199 | 37 | 610 | 180 | 0 | 0 | 73.05
KWH | 804000 | 0 | 3842000 | 2677500 | 8023099 | 2146318 | 1453536 | 8333310 | 7736000 | 67700 | 478900 | 5115875 | 6700945 | 61440 | 65760 | 45180 | 1029982 | 0 | 3802000 | 0 | 24960 | 281376 | 1412160 | 67772 | 1299840 | 0 | 341856 | 947160 | 891715 | 377440 | 440316 | 600000 | 372060 | 539400 | 775900 | 577896 | 0 | 847920 | 0 | 2400000 | 2400000 | 483759 | 4973713 | 0 | 2394044 | 0 | 0 | 447360 | 107496 | 410443 | 485160 | 811200 | 996960 | 392590 | 577440 | 909512 | 0 | 0 | 8260500 | 5587500 | 4719000 | 1455272 | 2302510 | 0 | 1308480 | 0 | 735056 | 0 | 0 | 838008 | 494424 | 212760 | 620800 | 475760 | 3782400 | 3392160 | 1748160 | 353564 | 14000 | 1353000 | 1378680 | 1127400 | 1130472 | 3329877 | 5355000 | 1422048 | 1535040 | 986040 | 2848950 | 131000 | 961000 | 238140 | 0 | 564840 | 247056 | 0 | 117930 | 0 | 0 | 2940000 | 0 | 560160 | 139050 | 2074560 | 3380160 | 1706181 | 6217000 | 2161200 | 1778400 | 1983000 | 37560 | 160582 |  | 16354181 | 144300 | 0 | 0 | 1608000 | 0 | 0 | 0 | 193440 | 553728 | 628500 | 3547923 | 705894 | 1156800 | 0 | 0 | 1375000 | 474176 | 320772 | 1278716 | 607230 | 265285 | 222945 | 476640 | 367268 | 474960 | 369432 | 195174 | 0 | 0 | 4866500 | 127000 | 129000 | 4877636 | 0 | 4536064 | 0 | 2188505 | 680640 | 4920291 | 0 | 8754636 | 2033760 | 0 | 1752480 | 2038896 | 128640 |  | 162135673 | 68354412 | 230490085 | 110576966 | 16354181 | 42329373 | 45800691 | 4866500 | 847920 | 5741444 | 3782400 | 190610 | 0
Fuel Cost | 691440 | 0 | 3304120 | 2302650 | 5134783.36 | 1738517.58 | 1366323.84 | 5083319.1 | 4718960 | 650597 | 656093 | 3427636.25 | 101787354.55 | 385843.2 | 439276.8 | 276049.8 | 669488.3 | 0 | 4220220 | 0 | 156000 | 1854267.84 | 13655587.2 | 431707.64 | 7786041.6 | 0 | 2280179.52 | 6753250.8 | 5573218.75 | 2366548.8 | 330237 | 450000 | 0 | 0 | 0 | 5466896.16 | 0 | 0 | 0 | 2640000 | 2640000 | 4581197.73 | 3282650.58 | 0 | 2753150.6 | 0 | 0 | 3932294.4 | 1157731.92 | 3993610.39 | 3003140.4 | 5240352 | 6520118.4 | 333701.5 | 0 | 827655.92 | 0 | 0 | 5121510 | 3855375 | 3303300 | 1004137.68 | 2210409.6 | 0 | 1125292.8 | 0 | 602745.92 | 0 | 0 | 6218019.36 | 380706.48 | 159570 | 478016 | 356820 | 25871616 | 2544120 | 16065590.4 | 272244.28 | 0 | 1407120 | 1433827.2 | 1082304 | 1017424.8 | 2597304.06 | 3748500 | 1621134.72 | 1642492.8 | 1084644 | 3247803 | 167680 | 893730 | 221470.2 | 0 | 423630 | 187762.56 | 0 | 856171.8 | 0 | 0 | 21021000 | 0 | 0 | 0 | 0 | 31570694.4 | 15935730.54 | 5408790 | 0 | 0 | 0 | 0 | 0 |  | 83406323.1 | 4206345 | 0 | 0 | 13330320 | 0 | 0 | 0 | 2178134.4 | 6522915.84 | 4952580 | 2448066.87 | 698835.06 | 8560320 | 0 | 0 | 1443750 | 5429315.2 | 3438675.84 | 11457295.36 | 5252539.5 | 2361036.5 | 2374364.25 | 4728268.8 | 4322744.36 | 522456 | 347266.08 | 147746.718 | 0 | 0 | 18784690 | 4093210 | 3453330 | 3316792.48 | 0 | 3175244.8 | 0 | 0 | 11795491.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 390000899.53 | 212748057.358 | 602748956.888 | 82179429.068 | 83406323.1 | 24091541.07 | 302132097.89 | 18784690 | 0 | 66283259.76 | 25871616 | 0 | 0
Yesterday Day Peak | 35 | 0 | 159 | 110 | 364 | 107 | 68 | 350 | 343 | 0 | 20 | 225 | 294 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 6 | 25 | 18 | 0 | 19 | 25 | 14 | 25 | 29 | 0 | 0 | 36 | 0 | 100 | 100 | 24 | 212 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 47 | 15 | 21 | 50 | 0 | 0 | 355 | 224 | 206 | 63 | 100 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 146 | 144 | 70 | 20 | 2.2 | 57 | 58 | 47 | 50 | 163 | 250 | 58 | 67 | 42 | 125 | 0 | 44 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 15.6 | 100 | 70 | 50 | 287 | 96 | 70 | 106 | 6.1 | 0 |  | 660 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 32 | 146 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 18 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 197 | 0 | 167 | 0 | 95 | 0 | 171 | 0 | 408 | 89 | 0 | 0 | 52 | 6 |  | 9054.9 | DayPeak
Yesterday Evening Peak | 35 | 0 | 160 | 110 | 300 | 108 | 50 | 338 | 352 | 0 | 20 | 225 | 265 | 0 | 0 | 0 | 220 | 0 | 195 | 0 | 0 | 32 | 132 | 0 | 71 | 0 | 49 | 54 | 55 | 36 | 19 | 25 | 22 | 28 | 33 | 48 | 0 | 39 | 0 | 100 | 100 | 25 | 211 | 0 | 130 | 68 | 0 | 24 | 0 | 0 | 50 | 102 | 47 | 17 | 40 | 60 | 0 | 0 | 320 | 242 | 215 | 63 | 99 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 178 | 145 | 92 | 0 | 0 | 56 | 57 | 50 | 49 | 163 | 252 | 63 | 81 | 46 | 110 | 0 | 47 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 70 | 0 | 100 | 200 | 150 | 250 | 95 | 90 | 106 | 0 | 46 |  | 905 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 55 | 40 | 147 | 38 | 110 | 0 | 0 | 60 | 50 | 38 | 90 | 50 | 43 | 45 | 50 | 44 | 22 | 16 | 11 | 0 | 0 | 199 | 16 | 17 | 190 | 0 | 187 | 0 | 97 | 100 | 197 | 0 | 300 | 105 | 0 | 108 | 97 | 0 |  | 11482 | EvPeak
Forecast for Evening | 35 | 0 | 180 | 0 | 360 | 108 | 50 | 412 | 360 | 110 | 20 | 225 | 335 | 100 | 100 | 55 | 180 | 0 | 180 | 0 | 100 | 102 | 149 | 100 | 73 | 0 | 49 | 35 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 100 | 25 | 225 |  | 130 | 0 | 0 | 24 | 60 | 68 | 100 | 90 | 46 | 19 | 30 | 110 | 0 | 0 | 360 | 250 | 221 | 150 | 100 | 0 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 186 | 150 | 95 | 20 | 0 | 60 | 58 | 51 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 19 | 45 | 10 | 0 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 100 | 105 |  | 110 |  | 947 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 31 | 80 | 40 | 150 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 40 | 45 | 45 | 22 | 17 | 11 | 0 | 0 | 200 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 0
Forecast for Day | 35 | 0 | 180 | 0 | 360 | 108 | 50 | 412 | 360 | 110 | 20 | 225 | 335 | 100 | 100 | 55 | 180 | 0 | 180 | 0 | 100 | 102 | 149 | 100 | 73 | 0 | 49 | 35 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 100 | 25 | 225 | 0 | 130 | 0 | 0 | 24 | 60 | 68 | 100 | 90 | 46 | 19 | 15 | 110 | 0 | 0 | 360 | 0 | 221 | 150 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 150 | 95 | 20 | 2 | 60 | 58 | 51 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 19 | 45 | 10 | 0 | 25 | 11 | 0 | 100 | 100 | 100 | 100 | 100 | 149 | 20 | 100 | 200 | 150 | 285 | 100 | 100 | 105 | 3 | 110 |  | 701 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 31 | 50 | 40 | 150 | 33 | 110 | 0 | 0 | 60 | 0 | 35 | 95 | 50 | 50 | 40 | 43 | 45 | 22 | 17 | 11 | 0 | 0 | 200 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 0
Generation at 08:00(Today) | 35 | 0 | 200 | 0 | 360 | 104 | 50 | 337 | 352 | 0 | 20 | 225 | 285 | 0 | 0 | 0 | 180 | 0 | 180 | 0 | 0 | 0 | 32 | 0 | 73 | 0 | 6 | 35 | 18 | 17 | 0 | 25 | 14 | 25 | 33 | 0 | 0 | 40 | 0 | 100 | 100 | 25 | 231 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 37 | 19 | 6 | 110 | 0 | 0 | 360 | 0 | 193 | 150 | 97 | 0 | 56 | 0 | 35 | 0 | 0 | 8 | 22 | 0 | 25 | 20 | 138 | 144 | 92 | 20 | 1.1 | 57 | 57 | 50 | 50 | 130 | 150 | 61 | 75 | 46 | 114 | 0 | 45 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5.8 | 100 | 62 | 50 | 300 | 95 | 90 | 54 | 2.8 | 0 | 0 | 494 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 145 | 28 | 16 | 0 | 0 | 60 | 8 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 16 | 8 | 0 | 0 | 199 | 0 | 0 | 176 | 0 | 165 | 0 | 95 | 0 | 180 | 0 | 350 | 70 | 0 | 108 | 86 | 0 | 0
199
| Minimum Generation |  | 7564 | 8:00
| Highest Generation |  | 11482 | 21:00
| Day Peak Generation |  | 9054.9 | 12:00
| Evening Peak Generation |  | 11482 | 21:00
| HVDC Max Flow |  | 906 | 24:00
| HVDC EvPeak Flow |  | 905 | 21:00
| Load factor L.F |  | 83.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-06-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9054.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8732.5 | MW
Evening Peak Generation : |  | 11482 | MW Hour : | 21:00 | Available Max Generation : |  | 14402 | MW
E.P. Demand (at gen end) : |  | 11482 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12200 | MW
Maximum Generation : |  | 11482 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2202 | MW
Total Gen. (MKWH) : |  | 230.4901 | System Load Factor : | 83.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -740 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-06-12
Actual : | 73.02 | Ft.(MSL) , | Rule curve : | 78.87 | Ft.( MSL )
Gas Consumed : | Total = | 1389.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106270970.138
|  | Coal : | 18784690 | Oil : | 368415357.65 | Total : | 493471017.788
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4240.2074 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1444.0241 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1294.1753 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1169.5306 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1056.814 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 852.8168 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 474.1265 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.5052 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 657.7477 |  |  | 0 | 0%
Total | 0 |  | 11408.9476 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-1 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal # 3,5
|  |  |  | 4) Bheramara 410 MW. | 10) Meghnaghat 450 MW GT-1
|  |  |  | 5) Siddhirganj ST | 11) Bibiyana-2
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Cumilla(N)-Daudkandi 132 kV Ckt-1 tripped at 11:49 from both ends showing Dist a-phase ,O/C
at Cumilla(N) end & Dist a-phase Z2 at Daudkandi end and was switched on at 12:22.
b) Mymensingh RPCL-Mymensingh S/S 132 kV Ckt-1 was shut under shut down from 11:21 to 15:19 for
breaker maintenance at RPCL end.
c) Shahjibazar ST was shut down at 21:25.
d) Noapara 132/33 kV T1 & T2 transformers tripped at 21:38 from 33 kV sides showing E/F due to 33 kV |  |  |  |  | About 36 MW power interruption occurred under Noapara S/S
REB feeder fault and were switched on at 21:42. |  |  |  |  | area from 21:38 to 21:42.
e) Ghorasal Unit-5 tripped at 23:50 due to bus tripping.
f) Ghorasal-Ashuganj 230 kV Ckt-2 tripped at 00:02(12/06/2019) from Ghorasal end showing C-phase
voltage failure.
g) Ashuganj(S) GT was shut down at 01:41(12/06/2019) for maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 804000 | Gas shortage
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 160 | 3842000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 110 | 2677500 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 8023099
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 50 | 1453536 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 108 | 2146318
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 478900 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8333310 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 67700 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 352 | 7736000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 225 | 5115875 | GT-1 Under maint
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 61440 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 265 | 6700945 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 65760 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 45180 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 67772 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 440316
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 195 | 3802000 | Frequency control
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 24960 | Reserve
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 220 | 1029982
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 32 | 281376 | Low demand
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 341856
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 947160
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1412160 | Engine problem
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 891715
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 377440 | Low demand
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 71 | 1299840 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 972060 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 28 | 539400 | Engine problem
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 775900
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 577896
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 117930 | Reserve
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 70 | 560160 | Low demand
37 | Gazipur 100 MW |  | RPCL | 100 MW | 105 | 90 | 1778400 | Engine problem
| Dhaka area Total |  |  |  | 5803 | 3142 | 63789886
38 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
39 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 483759
40 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 139050
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 47 | 996960
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 39 | 847920 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 211 | 4973713 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 198 | 2394044 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 24 | 447360 | Engine problem
47 | Baraka Sikalbaha PL |  | IPP | 105 MW | 105 | 106 | 1983000
48 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 107496 | Reserve
49 | Dohazari Peaking |  | PDB | 6*17 | 102 | 0 | 410443 | Reserve
50 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 485160 | Low demand
51 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2074560
52 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 392590
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 577440
53 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 102 | 811200 | Engine problem
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 37560
| Anwara United |  | United Group | 300 MW | 0 | 46 | 160582 | on test
| Chattogram area Total |  |  |  | 1786 | 1205 | 22122837
54 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 60 | 909512 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 215 | 4719000 | FGMO
56 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 8260500
57 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 242 | 5587500 | ST under maint
58 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 55 | 1308480
60 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 0 | 0 | machine problem
61 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 63 | 1455272 | Gas shortage
62 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 735056 | Gas shortage
63 | Midland 150MW |  | IPP | 23*7.015 | 150 | 150 | 1706181
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2302510
67 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 3380160
68 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 494424
69 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 212760
** | Tripura |  | Imported power | 0 | 160 | 178 | 3782400
70 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 620800
71 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 838008
72 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 475760
73 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1744 | 36788323
74 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 145 | 3392160 | GT-1 Under maint
75 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 353564 | machine problem
76 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 92 | 1748160
77 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14000
78 | United Mymensingh PPL |  | IPP | 200 | 200 | 192 | 2940000 | Engine problem
79 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 95 | 2161200 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 524 | 10609084
80 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1353000
81 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1378680
82 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3329877
83 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 252 | 5355000 | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 1127400
85 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 49 | 1130472
86 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 247056
87 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 63 | 1422048 | FGMO
88 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 81 | 1535040
89 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 986040 | Engine problem
90 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 110 | 2848950
91 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 131000
92 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 961000
93 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 564840
94 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Gas field shut down
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 250 | 6217000 | On test
95 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 238140
| Sylhet Area Total |  |  |  | 1549 | 1269 | 28825543
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 32 | 144300
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 16354181
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1608000 | Engine problem
98 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 193440
99 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
100 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 55 | 553728
101 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 628500
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 680640
104 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 2033760
105 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 97 | 2038896 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1473 | 24235445
106 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1156800
107 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
108 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 38 | 705894
109 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 147 | 3547923 | FGMO
110 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2188505
| Barisal Area Total |  |  |  | 462 | 392 | 7599122
111 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1375000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 474176
113 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 320772
114 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 607230
115 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 265285 | Engine problem
116 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 222945
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4877636 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4536064 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 197 | 4920291 | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 8754636 | Frequency control
121 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 44 | 367268
122 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 474960
123 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 369432
124 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 195174
125 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 476640
126 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 1278716
127 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
128 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 108 | 1752480
| Rajshahi Area Total |  |  |  | 2070 | 1501 | 31268705
129 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
130 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 199 | 4866500
131 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 127000
132 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 129000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 0 | 128640 | Reserve
| Rangpur Area Total |  |  |  | 484 | 232 | 5251140
| Total |  |  |  | 17996 | 11482 | 230490085
| Eastern Grid Total |  |  |  | 12666 | 7884 | 162135673
| Western Grid Total |  |  |  | 5330 | 3598 | 68354412
| National Grid Total |  |  |  | 17996 | 11482 | 230490085
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-11
| (a) ENTIRE EASTERN GRID : |  | 7054 | MW | (b) ENTIRE WESTERN GRID : |  | 3669 | MW
| i) Dhaka area |  | 3449 | MW | i) Khulna area |  | 1450 | MW
| ii) Chittagong area |  | 1160 | MW | ii) Rajshahi area |  | 1199 | MW
| iii) Comilla area |  | 1075 | MW | iii) Barisal area |  | 351 | MW
| iv) Mymensingh area |  | 904 | MW | iv) Rangpur area |  | 669 | MW
| v) Sylhet area |  | 466 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10723 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 98 | 2000 | Jamalpur | 130 | 2200 | Jessore | 112 | 1930
2 | Munsiganj | 116 | 2000 | Sherpur | 98 | 2300 | Jhenida | 113 | 1930
3 | Sonargaon | 48 | 1930 | Srimongal | 39 | 2400 | Bottail | 130 | 1930
4 | Shyampur | 120 | 2000 | Shahjibazar | 125 | 2100 | G.K Project | 57 | 2000
5 | Bhulta | 122 | 1200 | Fenchuganj | 50 | 2300 | Faridpur | 180 | 2300
6 | Madanganj | 44 | 100 | Kulawara | 49 | 2000 | Madaripur | 123 | 2100
7 | Shitalakhya | 76 | 1200 | Sylhet | 142 | 2000 | Gopalganj | 97 | 2100
8 | Rahim steel | 13 | 1930 | Chatak | 32 | 2100 | Bagerhat | 80 | 1930
9 | Matuail | 58 | 1600 | Sunamganj | 38 | 2000 | Mongla | 36 | 100
10 | Ghorasal | 79 | 2100 | Biani Bazar | 47 | 2000 | Satkhira | 104 | 2000
11 | Narsingdi | 118 | 2100 | Comilla (S) | 184 | 2300 | Gallamari | 50 | 1300
12 | Haripur (SBU) | 65 | 1800 | Comilla(N) | 121 | 2300 | Magura | 54 | 2000
13 | Ullon | 77 | 2300 | Chandpur | 104 | 2300 | Chuadanga | 87 | 100
14 | Hasnabad | 188 | 2100 | Feni | 126 | 1930 | Barisal | 114 | 2200
15 | Magbazar | 123 | 1600 | Chowmuhani | 176 | 2300 | Patuakhali | 107 | 2100
16 | Maniknagar | 100 | 1500 | Ashuganj | 54 | 2300 | Bhandaria | 60 | 2200
17 | Bangabhaban | 34 | 136 | Daudkandi | 128 | 2100 | Barisal (N) | 40 | 2100
18 | Narinda | 72 | 1500 | B.Baria | 149 | 2200 | Sariatpur | 35 | 100
19 | Dhanmondi | 127 | 1400 | Ramganj | 96 | 2300 | Benapol | 43 | 2000
20 | Lalbag | 42 | 1300 | Madunaghat | 68.5 | 2400 | Borhan Uddin | 37 | 200
21 | Madartek | 59 | 2300 | Hathazari | 100 | 1930 | Ishurdi | 64 | 2000
22 | Mirpur | 96 | 1930 | Khulshi | 192 | 2400 | Ruppur Paromanobik | 1 | 100
23 | Kalyanpur | 111 | 2100 | Halishahar | 128 | 2000 | Natore | 134 | 2100
24 | Gulshan | 56 | 1500 | Baraulia | 138 | 1600 | Bogra | 233 | 100
25 | Uttara | 65 | 1930 | Sikalbaha | 35 | 2000 | Noagaon | 118 | 2100
26 | Uttara New | 13 | 1300 | Dohazari | 92 | 2300 | Rajshahi | 158 | 2100
27 | Kamrangirchar | 61 | 2100 | Cox'sbazar | 98 | 2000 | C.Nawabganj | 74 | 2100
28 | Savar | 116 | 1600 | Chandraghona | 28 | 1900 | Amnura | 35 | 2100
29 | Bhasantec | 150 | 1300 | Kaptai | 4.5 | 1900 | Pabna | 114 | 2100
30 | Agargaon | 59 | 1500 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 91 | 2000
31 | Satmosjid | 93 | 2300 | Bakulia | 95 | 2100 | Serajganj | 95 | 2100
32 | Tongi | 128 | 1500 | Julda | 19 | 1100 | Niyamatpur | 61 | 2100
33 | Kabirpur | 161 | 1500 | TK chemical | 0.6 | 100 | Joypurhat | 55 | 100
34 | Basundhara | 132 | 1900 | Modern Steel | 0.2 | 100 | Mohastangor | 15 | 100
35 | Manikganj | 94 | 2100 | Shahmirpur | 29 | 2400 | Rangpur | 131 | 2100
36 | Joydevpur | 208 | 2100 | Khagrachhari | 19 | 2000 | Lalmonirhat | 88 | 2100
37 | New Tongi | 74 | 2100 | Matarbari | 28.5 | 1930 | Saidpur | 96 | 200
38 | Korda | 185 | 2200 | Baroiar Hat | 38 | 2200 | Purbasadipur | 95 | 2000
39 | Dhamrai | 56 | 2100 | Rangamati | 12 | 1900 | Thakurgaon | 65 | 100
40 | Valuka | 94 | 2000 | Abul Khair 230 | 144 | 500 | Palashbari | 133 | 100
41 | Tangail | 169 | 2200 | BSRM | 135 | 500 | Barapukuria | 48 | 2100
42 | Mymensing | 236 | 2100 | Goalpara | 25 | 2300 | Panchagar | 43 | 2000
43 | Kishorganj | 132 | 2200 | Central (S) | 90 | 100 | Joldhaka | 17 | 2100
44 | Netrokona | 104 | 2000 | Noapara | 102 | 2100
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-11
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 394 | 6:00 | 386 | 12:00 | Kaliakoir | 379 | 6:00 | 366
2 | Bheramara | 404 | 6:00 | 383 | 20:00 | Bhulta | 399 | 20:00 | 385
3 | Ashuganj(N) | 403 | 2:00 | 391 | 12:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
1 | Ghorasal | 238 | 1:00 | 234 | 23:00 | Hathazari | 225 | 18:30 | 220
2 | Ishurdi | 237 | 3:00 | 225 | 14:00 | Megnaghat | 230 | 1:00 | 224
3 | Ashuganj | 242 | 1:00 | 235 | 12:00 | Fenchuganj | 239 | 6:00 | 235
4 | Serajganj | 235 | 18:30 | 227 | 21:00 | Siddhirganj | 233 | 2:00 | 220
5 | Baghabari | 232 | 18:00 | 225 | 14:00 | Maniknagar | 230 | 2:00 | 222
6 | Barapukuria | 241 | 7:00 | 223 | 21:00 | Old Airport | 229 | 2:00 | 220
7 | Bogra | 231 | 8:00 | 215 | 1:00 | Barisal | 232 | 2:00 | 222
8 | Khulna South | 231 | 18:00 | 213 | 6:00 | AKSML | 221 | 20:00 | 216
9 | Rampura | 230 | 2:00 | 221 | 15:00 | BSRM | 226 | 18:30 | 218
10 | Haripur | 230 | 1:00 | 221 | 13:00 | Bibiyana | 236 | 7:00 | 231
11 | Hasnabad | 232 | 3:00 | 222 | 12:00 | Bhulta | 233 | 5:00 | 223
12 | Aminbazar | 230 | 2:00 | 221 | 12:00 | Ashuganj (S) | 240 | 1:00 | 234
13 | Tongi | 229 | 4:00 | 219 | 11:00 | Kaliakoir | 232 | 1:00 | 223
14 | Comilla (N) | 236 | 19:30 | 231 | 9:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 135 | 200 | 130 | 1300 | Hathazari | 133 | 2000 | 128
2 | Munsiganj | 137 | 2000 | 129 | 1500 | Khulshi | 130 | 1800 | 126
3 | Megnaghat | 135 | 700 | 130 | 1700 | Halishahar | 133 | 1800 | 128
4 | Shyampur | 134 | 600 | 129 | 1600 | Baraulia | 132 | 1800 | 126
5 | Bhulta | 130 | 100 | 126 | 1200 | Sikalbaha | 133 | 1930 | 128
6 | Madanganj | 135 | 2000 | 127 | 1200 | Dohazari | 130 | 1800 | 125
7 | Shitalakhya | 141 | 2000 | 130 | 1300 | Cox'sbazar | 122 | 1800 | 116
8 | Rahim steal | 136 | 2000 | 131 | 1300 | Chandraghona | 133 | 1830 | 129
9 | Matuail | 135 | 2000 | 129 | 1200 | Kaptai | 132 | 1800 | 126
10 | Ghorasal | 140 | 2000 | 135 | 700 | A. Khaer Stl. | 130 | 300 | 127
11 | Narsinghdi | 131 | 600 | 126 | 1200 | Bakulia | 131 | 1830 | 127
12 | Haripur (SBU) | 136 | 600 | 131 | 1300 | Julda | 133 | 2100 | 128
13 | Ullon | 136 | 300 | 129 | 1500 | TK Chemical | 135 | 1800 | 128
14 | Hasnabad | 137 | 100 | 130 | 1200 | Modern Steel | 132 | 1800 | 127
15 | Magbazar | 137 | 400 | 128 | 1600 | Shahmirpur | 132 | 1800 | 126
16 | Maniknagar | 133 | 400 | 127 | 1200 | Khagrachhari | 132 | 1830 | 127
17 | Bangabhaban | 133 | 400 | 127 | 1200 | Matarbari | 124 | 1800 | 118
18 | Narinda | 133 | 400 | 127 | 1200 | Baroiar Hat | 132 | 1830 | 125
19 | Dhanmondi | 136 | 300 | 129 | 1500 | Rangamati | 132 | 1830 | 128
20 | Lalbag | 138 | 100 | 130 | 1200 | Goalpara | 134 | 500 | 125
21 | Madartek | 136 | 300 | 128 | 1200 | Central s/s | 138 | 1830 | 125
22 | Mirpur | 135 | 400 | 130 | 900 | Noapara | 135 | 1830 | 122
23 | Kalyanpur | 139 | 300 | 132 | 1200 | Jessore | 130 | 1830 | 113
24 | Gulshan | 136 | 600 | 128 | 1200 | Jhenida | 128 | 1830 | 111
25 | Uttara | 135 | 400 | 129 | 1200 | Bottail | 131 | 1700 | 121
26 | Uttara New | 136 | 100 | 126 | 1200 | G.K.Project | 140 | 1800 | 130
27 | Kamrangirchar | 137 | 600 | 129 | 1200 | Faridpur | 134 | 1900 | 120
28 | Savar | 135 | 100 | 129 | 1200 | Madaripur | 135 | 1800 | 123
29 | Bhasantec | 131 | 300 | 123 | 1300 | Gopalganj | 143 | 1830 | 130
30 | Agargaon | 131 | 600 | 124 | 1200 | Bagerhat | 132 | 1830 | 120
31 | Satmosjid | 131 | 600 | 124 | 1200 | Mongla | 134 | 1830 | 124
32 | Tongi | 139 | 400 | 129 | 1200 | Satkhira | 136 | 1830 | 122
33 | Kabirpur | 136 | 700 | 130 | 1300 | Gallamari | 139 | 1830 | 125
34 | Basundhara | 132 | 1930 | 124 | 1200 | Magura | 127 | 1830 | 108
35 | Manikganj | 140 | 1930 | 130 | 1200 | Chuadanga | 124 | 1830 | 103
36 | Joydevpur | 142 | 1600 | 136 | 2000 | Barisal | 135 | 1830 | 130
37 | New Tongi | 136 | 1930 | 127 | 1200 | Patuakhali | 134 | 1830 | 124
38 | Kodda | 138 | 100 | 124 | 1200 | Bhandaria | 135 | 1800 | 125
39 | Dhamrai | 136 | 600 | 130 | 2200 | Barisal (N) | 137 | 200 | 129
40 | Valuka | 129 | 1000 | 119 | 2000 | Sariatpur | 132 | 1800 | 121
41 | Tangail | 135 | 500 | 128 | 2100 | Benapol | 127 | 1000 | 115
42 | Mymensing | 130 | 1000 | 120 | 800 | Ishurdi | 139 | 1830 | 130
43 | Kishorganj | 131 | 1830 | 122 | 2200 | Ruppur Paromanobik | 138 | 600 | 133
44 | Netrokona | 130 | 1000 | 120 | 1900 | Natore | 135 | 1800 | 126
45 | Jamalpur | 138 | 500 | 127 | 700 | Bogra | 138 | 700 | 126
46 | Sherpur | 136 | 1600 | 125 | 1300 | Noagaon | 134 | 700 | 118
47 | Srimongal | 139 | 700 | 134 | 2300 | Rajshahi | 132 | 1800 | 122
48 | Shahjibazar | 137 | 600 | 131 | 2300 | C.Nawabganj | 130 | 1800 | 116
49 | Fenchuganj | 137 | 600 | 134 | 1900 | Amnura | 133 | 1700 | 119
50 | Khulawara | 136 | 600 | 132 | 1930 | Pabna | 137 | 1830 | 128
51 | Sylhet | 136 | 500 | 133 | 1900 | Shahjadpur | 141 | 1800 | 135
52 | Chatak | 135 | 400 | 131 | 2300 | Serajganj | 136 | 800 | 128
53 | Sunamganj | 135 | 700 | 130 | 2100 | Niyamatpur | 133 | 700 | 116
54 | Biani Bazar | 135 | 700 | 130 | 2100 | Joypurhat | 136 | 700 | 116
55 | Comilla(s) | 127 | 700 | 119 | 1930 | Mohastangor | 137 | 800 | 121
56 | Comilla(n) | 137 | 1800 | 136 | 900 | Rangpur | 137 | 600 | 114
57 | Chandpur | 138 | 1800 | 127 | 900 | Lalmonirhat | 137 | 500 | 107
58 | Feni | 130 | 1830 | 125 | 1600 | Saidpur | 138 | 600 | 115
59 | Chowmuhani | 127 | 1800 | 120 | 100 | Purbasadipur | 142 | 600 | 112
60 | Ashuganj | 139 | 700 | 133 | 2300 | Thakurgaon | 137 | 600 | 104
61 | Daudkandi | 133 | 1830 | 126 | 1200 | Palashbari | 135 | 700 | 116
62 | B.Baria | 134 | 700 | 127 | 2200 | Barapukuria | 141 | 700 | 123

## L-Curve
Date | 2019-06-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 290 | 7543 | 3767 | 11310 |  |  |  | QF-LDC-12
0:30 | 475 | 7373.5 | 3583.5 | 10957 | Date: | 2019-06-11
1:00 | 660 | 7204 | 3400 | 10604
1:30 | 690 | 7173 | 3254 | 10427
2:00 | 720 | 7142 | 3108 | 10250
2:30 | 720 | 7068 | 3036.5 | 10104.5 | [5 empty] | Gen. at Eve. Peak | 11482 | 11482 MW (21:00 )
3:00 | 720 | 6994 | 2965 | 9959 | [6 empty] | 21:00
3:30 | 730 | 6819.5 | 2891.5 | 9711 | [5 empty] | Gen. at Day Peak | 9054.9 | 9054.9 MW (12:00 )
4:00 | 740 | 6645 | 2818 | 9463 | [6 empty] | 12:00
4:30 | 730 | 6463 | 2669 | 9132 | [5 empty] | Highest Generation | 11482
5:00 | 720 | 6281 | 2520 | 8801 | [6 empty] | 21:00
5:30 | 700 | 5997.7 | 2349 | 8346.7
6:00 | 680 | 5714.4 | 2178 | 7892.4
6:30 | 620 | 5642.4 | 2121.5 | 7763.9
7:00 | 560 | 5570.4 | 2065 | 7635.4
7:30 | 485 | 5569.7 | 2030 | 7599.7
8:00 | 410 | 5569 | 1995 | 7564
8:30 | 295 | 5670.75 | 2033 | 7703.75
9:00 | 180 | 5772.5 | 2071 | 7843.5
9:30 | 165 | 5892.05 | 2187.5 | 8079.55
10:00 | 150 | 6011.6 | 2304 | 8315.6
10:30 | 175 | 6140.25 | 2328.5 | 8468.75
11:00 | 200 | 6268.9 | 2353 | 8621.9
11:30 | 240 | 6445.9 | 2392.5 | 8838.4
12:00 | 280 | 6622.9 | 2432 | 9054.9
12:30 | 350 | 6694.75 | 2512.5 | 9207.25
13:00 | 420 | 6766.6 | 2593 | 9359.6
13:30 | 415 | 6820.65 | 2620.5 | 9441.15
14:00 | 410 | 6874.7 | 2648 | 9522.7
14:30 | 445 | 6969.04 | 2671 | 9640.04
15:00 | 480 | 7063.38 | 2694 | 9757.38
15:30 | 490 | 7127.98 | 2715 | 9842.98
16:00 | 500 | 7192.58 | 2736 | 9928.58
16:30 | 480 | 7014.995 | 2707 | 9721.995
17:00 | 460 | 6837.41 | 2678 | 9515.41
17:30 | 425 | 6546.175 | 2592.5 | 9138.675
18:00 | 390 | 6254.94 | 2507 | 8761.94
18:30 | 335 | 6548.97 | 2879 | 9427.97
19:00 | 280 | 6843 | 3251 | 10094
19:30 | 440 | 7660 | 3538 | 11198
20:00 | 460 | 7734 | 3570 | 11304 |  |  |  | Executive Engineer
20:30 | 435 | 7809 | 3584 | 11393 |  |  |  | Network Operation Division
21:00 | 410 | 7884 | 3598 | 11482
21:30 | 380 | 7867.5 | 3576.5 | 11444
22:00 | 350 | 7851 | 3555 | 11406 |  |  |  |  | Page 6 of 7
22:30 | 335 | 7712.5 | 3628.5 | 11341
23:00 | 320 | 7574 | 3702 | 11276
23:30 | 305 | 7558.5 | 3734.5 | 11293
24:00 | 290 | 7543 | 3767 | 11310
11482 MW (21:00 )
9054.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-11 |  | Energy | 230490085
[10 empty] | 2019-06-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4808 | 906 | 1663 | 2907 | 199 | 37 | 610 | 0 | 180
0:30 | 4699.5 | 849.5 | 1763.5 | 2713.5 | 199 | 38 | 521 | 0 | 173 | Date: | 2019-06-11
1:00 | 4591 | 793 | 1864 | 2520 | 199 | 39 | 432 | 0 | 166
1:30 | 4608 | 662 | 1892.5 | 2438.5 | 199 | 38.5 | 423.5 | 0 | 165 | [7 empty] | Total Energy | 230.4901 | Total Energy Gen 230.490 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.490 MKWHr
2:00 | 4625 | 531 | 1921 | 2357 | 199 | 38 | 415 | 0 | 164 | [7 empty] | Energy not Served | 0
2:30 | 4614 | 531 | 1920 | 2257 | 199 | 38 | 382.5 | 0 | 163 | [7 empty] | Energy Requirement | 230.4901
3:00 | 4603 | 531 | 1919 | 2157 | 199 | 38 | 350 | 0 | 162
3:30 | 4583 | 531.5 | 1899.5 | 2005.5 | 199 | 38.5 | 293 | 0 | 161 | [6 empty] | Shortage
4:00 | 4563 | 532 | 1880 | 1854 | 199 | 39 | 236 | 0 | 160
4:30 | 4597 | 531.5 | 1835.5 | 1632 | 198.5 | 39.5 | 143 | 0 | 155
5:00 | 4631 | 531 | 1791 | 1410 | 198 | 40 | 50 | 0 | 150
5:30 | 4557 | 531 | 1784 | 1059 | 198.5 | 40 | 37 | 0 | 139
6:00 | 4483 | 531 | 1777 | 708 | 199 | 40 | 24 | 0 | 128
6:30 | 4458.5 | 531 | 1730 | 660.5 | 199 | 39 | 24 | 0 | 118 |  |  |  |  | Coal
7:00 | 4434 | 531 | 1683 | 613 | 199 | 38 | 24 | 0 | 108
7:30 | 4428.5 | 527.5 | 1663 | 601.5 | 199.5 | 37.5 | 12 | 0 | 120 |  |  |  | Oil |  |  |  | ,
8:00 | 4423 | 524 | 1643 | 590 | 200 | 37 | 0 | 0 | 132
8:30 | 4502.5 | 524 | 1670 | 617.5 | 199.5 | 36.5 | 0 | 0 | 135
9:00 | 4582 | 524 | 1697 | 645 | 199 | 36 | 0 | 0 | 138
9:30 | 4601 | 592.5 | 1739 | 750 | 199 | 35.5 | 0 | 0 | 139
10:00 | 4620 | 661 | 1781 | 855 | 199 | 35 | 0 | 0 | 140
10:30 | 4606 | 661 | 1799 | 989 | 199 | 35.5 | 12 | 0 | 141
11:00 | 4592 | 661 | 1817 | 1123 | 199 | 36 | 24 | 0 | 142
11:30 | 4625.5 | 660.5 | 1857 | 1266 | 199.5 | 36 | 24 | 0 | 144
12:00 | 4659 | 660 | 1897 | 1409 | 200 | 36 | 24 | 0 | 146
12:30 | 4662 | 660 | 1891.5 | 1542 | 199.5 | 36.5 | 40 | 0 | 152
13:00 | 4665 | 660 | 1886 | 1675 | 199 | 37 | 56 | 0 | 158
13:30 | 4665 | 660 | 1886 | 1675 | 199 | 37 | 56 | 0 | 158
14:00 | 4665 | 660 | 1886 | 1675 | 199 | 37 | 56 | 0 | 158
14:30 | 4647 | 660 | 1881.5 | 1863.5 | 199 | 37.5 | 86 | 0 | 162
15:00 | 4629 | 660 | 1877 | 2052 | 199 | 38 | 116 | 0 | 166
15:30 | 4637 | 660 | 1875.5 | 2116 | 199 | 38 | 134 | 0 | 166
16:00 | 4645 | 660 | 1874 | 2180 | 199 | 38 | 152 | 0 | 166
16:30 | 4598 | 660 | 1823 | 2066 | 199 | 38.5 | 164 | 0 | 163
17:00 | 4551 | 660 | 1772 | 1952 | 199 | 39 | 176 | 0 | 160
17:30 | 4402.5 | 660.5 | 1519.5 | 1960 | 199 | 39 | 201.5 | 0 | 153
18:00 | 4254 | 661 | 1267 | 1968 | 199 | 39 | 227 | 0 | 146
18:30 | 4308.5 | 782.5 | 1362.5 | 2222 | 199 | 39 | 351 | 0 | 163
19:00 | 4363 | 904 | 1458 | 2476 | 199 | 39 | 475 | 0 | 180
19:30 | 4510 | 905 | 1658 | 3094 | 199 | 39 | 617 | 0 | 176
20:00 | 4478 | 905 | 1722 | 3111 | 199 | 39 | 670 | 0 | 180
20:30 | 4656 | 905 | 1784.5 | 2982 | 199 | 39 | 648.5 | 0 | 179
21:00 | 4834 | 905 | 1847 | 2853 | 199 | 39 | 627 | 0 | 178
21:30 | 4827 | 905 | 1847.5 | 2822.5 | 199 | 39 | 624 | 0 | 180
22:00 | 4820 | 905 | 1848 | 2792 | 199 | 39 | 621 | 0 | 182
22:30 | 4804 | 905 | 1784.5 | 2812 | 199 | 38 | 615.5 | 0 | 183
23:00 | 4788 | 905 | 1721 | 2832 | 199 | 37 | 610 | 0 | 184
23:30 | 4798 | 905.5 | 1692 | 2869.5 | 199 | 37 | 610 | 0 | 182 | Max Temp. in Dhaka |  | 35.50° C
24:00 | 4808 | 906 | 1663 | 2907 | 199 | 37 | 610 | 0 | 180
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 230.490 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.490 MKWHr
Note on W13: Author:

## Generation
2019-06-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 39 | 38 | 38 | 39 | 40 | 40 | 38 | 37 | 36 | 35 | 36 | 36 | 37 | 37 | 38 | 38 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 37 | 37 | 847920
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chittgong ST-2 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 0 | 0 | 0 | 1 | 19 | 25 | 25 | 25 | 24 | 24 | 24 | 25 | 25 | 25 | 24 |  | 24 | 24 | 25 | 25 | 24 | 24 | 25 | 483759
| Teknaf Solartech 20MW | [5 empty] | 2.3 | 3.5 | 11.6 | 17.1 | 16.7 | 20.2 | 15.6 | 15.5 | 10.58 | 14.94 | 11.55 | 4.53 | 0.37 | [8 empty] | 139050
6 | Sikalbaha 225MW (Gas) | 207 | 205 | 211 | 205 | 209 | 204 | 206 | 214 | 210 | 205 | 203 | 212 | 208 | 205 | 205 | 205 | 205 | 205 |  | 214 | 204 | 205 | 211 | 206 | 220 | 231 | 4973713
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 130 | 131 | 132 | 127 | 130 | 132 | 134 | 135 | 130 | 130 | 140 | 140 | 140 | 140 | 145 | 145 | 100 |  | 110 | 130 | 132 | 130 | 132 | 130 | 132 | 2394044
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 34 | 34 | 0 | [16 empty] | 0 | 56 | 68 | 68 | 68 | 66 | 66 | 410443
12 | Hathazari peaking | [17 empty] | 16 |  | 39 | 65 | 65 | 0 |  |  |  | 107496
| Baraka Sikalbaha PL | 105 | 105 | 105 | 72 | 18 | 18 | 18 | 18 | 18 | 19 | 67 | 106 | 106 | 106 | 106 | 106 | 105 | 105 |  | 106 | 105 | 106 | 106 | 105 | 105 | 105 | 1983000
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 165 | 165 | 165 | 165 | 165 | 120 | 125 | 125 | 160 | 158 | 156 | 158 | 158 | 158 | 158 | 158 | 145 | 70 |  | 75 | 120 | 110 | 195 | 190 | 189 | 128 | 3802000
17 | Siddhirganj CCPP-335 MW | [16 empty] | 0 | 32 |  | 45 | 120 | 120 | 220 | 220 | 218 | 224 | 1029982
18 | Summit Gazipur -2 | [19 empty] | 20 | 75 | 81 | 0 |  |  |  | 117930
19 | Ashuganj 195MW Modular | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 55 | 63 | 63 | 8 | 8 | 1455272
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 804000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 161 | 161 | 159 | 161 | 161 | 160 | 160 | 160 | 160 |  | 160 | 160 | 162 | 160 | 160 | 160 | 180 | 3842000
23 | Ghorasal ST: Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 0 | 2677500
24
25 | Ghorasal ST: Unit-7 | 300 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 370 | 370 | 364 | 364 | 340 | 340 | 340 | 340 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 8023099
26
28 | Ashuganj ST: Unit- 3 | [7 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 60 | 100 | 90 | 80 | 909512
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 193 | 181 | 196 | 181 | 197 | 182 | 194 | 204 | 202 | 185 | 183 | 206 | 197 | 182 | 193 | 200 | 182 | 182 |  | 200 | 181 | 182 | 215 | 214 | 204 | 214 | 4719000
34 | Ashuganj CCPP(South) | 231 | 239 | 235 | 239 | 235 | 242 | 235 | 230 | 231 | 228 | 231 | 224 | 228 | 231 | 220 | 220 | 239 | 242 |  | 206 | 246 | 246 | 242 | 235 | 224 | 235 | 5587500
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 300 | 300 | 300 | 330 | 330 | 330 | 355 | 355 | 360 | 360 | 360 | 360 | 270 |  | 270 | 320 | 320 | 320 | 320 | 270 | 300 | 8260500
35 | Ashuganj (Precision) 55MW | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 57 | 56 | 54 | 54 | 53 | 54 | 54 | 53 | 50 | 50 |  | 54 | 54 | 55 | 55 | 55 | 55 | 55 | 1308480
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 98 | 100 | 100 | 95 | 94 | 94 | 96 | 95 | 96 |  | 96 | 96 | 97 | 99 | 100 | 98 | 98 | 2302510
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478900
39 | Haripur 412 MW CCPP | 330 | 348 | 330 | 330 | 349 | 329 | 328 | 334 | 360 | 354 | 330 | 350 | 365 | 343 | 337 | 339 | 329 | 328 |  | 329 | 330 | 329 | 338 | 332 | 355 | 407 | 8333310
40 | Meghnaghat CCPP 450MW | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5115875
41 | Haripur Power CCPP 360MW | 323 | 323 | 323 | 323 | 324 | 323 | 304 | 303 | 303 | 332 | 334 | 343 | 343 | 343 | 336 | 337 | 339 | 256 |  | 302 | 326 | 326 | 352 | 350 | 350 | 304 | 7736000
42 | Mymensingh RPCL 210MW | 146 | 145 | 146 | 147 | 147 | 147 | 145 | 145 | 149 | 150 | 148 | 144 | 131 | 144 | 143 | 140 | 143 | 143 |  | 143 | 146 | 145 | 145 | 144 | 140 | 144 | 3392160
43 | Haripur NEPC 110MW | [19 empty] | 26 | 55 | 55 | 0 |  |  |  | 67700
44 | Fenchugonj CCPP-1 | 58 | 58 | 60 | 60 | 56 | 58 | 57 | 58 | 58 | 58 | 58 | 57 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 50 | 59 | 57 | 1353000
45 | Fenchugonj CCPP-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1378680
46 | Shajibazar 330 MW | 254 | 252 | 250 | 250 | 249 | 252 | 251 | 249 | 250 | 247 | 250 | 250 | 250 | 250 | 253 | 247 | 250 | 250 |  | 250 | 250 | 250 | 252 | 151 | 150 | 150 | 5355000
47 | Shahjibazar GT: Unit- 8, 9 | 63 | 63 | 63 | 63 | 63 | 64 | 62 | 61 | 61 | 61 | 61 | 58 | 59 | 60 | 60 | 59 | 49 | 49 |  | 61 | 52 | 42 | 63 | 61 | 59 | 61 | 1422048
48 | Shahjibazar 86MW | 74 | 74 | 74 | 74 | 75 | 75 | 40 | 40 | 40 | 72 | 68 | 67 | 69 | 69 | 66 | 69 | 10 | 10 |  | 45 | 81 | 81 | 81 | 81 | 73 | 73 | 1535040
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 45 | 45 | 42 | 42 | 42 | 42 | 43 | 44 | 10 |  | 10 | 38 | 46 | 46 | 46 | 46 | 46 | 986040
50 | Sylhet GT 150 MW | 116 | 116 | 112 | 112 | 110 | 118 | 115 | 124 | 116 | 114 | 111 | 125 | 108 | 112 | 112 | 110 | 109 | 108 |  | 118 | 108 | 106 | 110 | 128 | 132 | 131 | 2848950
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | [16 empty] | 131000
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 45 | 0 | 45 | 45 | 45 | 45 | 42 | 42 | 44 | 44 | 44 | 44 | 42 | 12 | 12 |  | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 961000
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238140
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 247056
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 53 | 53 | 50 | 53 | 11 | 11 |  | 11 | 50 | 50 | 50 | 50 | 50 | 50 | 1127400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 22 | 24 | 24 | 24 | 23 | 23 | 23 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 564840
57 | Summit Bibiana- 2
58 | Southern 55MW | 55 | 55 | 17 | 0 | 0 | 0 | [11 empty] | 0 |  | 40 | 55 | 55 | 36 | 17 | 17 | 55 | 377440
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 447360
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 19 | 392590
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 22 | 19 | 19 | 19 | 0 | 0 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440316
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 |  | 0 |  |  | 0 | 20 | 20 | 20 | 353564
63 | Tripura | 166 | 164 | 162 | 160 | 150 | 128 | 108 | 132 | 138 | 140 | 142 | 146 | 158 | 162 | 166 | 166 | 160 | 146 |  | 180 | 176 | 180 | 178 | 182 | 184 | 180 | 3782400
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 4 | 4 | 2 | 2 | 21 | 5 | 3 | 3 | 2 | 5 | 14 |  | 27 | 36 | 36 | 40 | 42 | 42 | 42 | 577440
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 20 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494424
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 212760
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 620800
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475760
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 12 | 12 | 14 | 14 |  | 14 | 14 | 14 | 22 | 12 | 22 | 22 | 372060
71 | Summit Maona | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 20 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 539400
72 | Summit Rupganj | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 775900
73 | Ghorashal (Regent) | 108 | 111 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 106 | 106 | 105 | 100 | 104 | 32 |  | 32 | 32 | 85 | 108 | 108 | 0 |  | 2146318
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [19 empty] | 2 | 10 | 16 | 0 |  |  |  | 24960
78 | Gazipur (RPCL) | 48 | 0 | 0 | [8 empty] | 0 | 15 | 17 | 35 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 40 | 40 | 577896
79 | Kodda 149MW | 98 | 98 | 90 | 55 | [8 empty] | 32 | 48 | 82 | 82 | 82 | 82 |  | 90 | 110 | 112 | 132 | 132 | 130 | 130 | 1412160
80 | Jamalpur 95MW | 92 | 92 | 92 | 92 | 92 | 16 | 0 |  | 0 | 2 | 36 | 70 | 87 | 94 | 94 | 94 | 86 | 93 |  | 93 | 93 | 93 | 92 | 92 | 92 | 92 | 1748160
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 40 | 0 |  |  |  | 0 | 4 | 38 | 52 | 52 | 52 | 52 | 52 | 34 | 16 |  | 18 | 52 | 50 | 52 | 52 | 52 | 52 | 838008
| Gazipur 100 MW | 90 | 90 | 89 | 90 | 51 | 51 | 36 | 34 | 34 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1778400
| Kaptai Solar | [6 empty] | 1.8 | 3.3 | 4.6 | 5.8 | 5.6 | 6.1 | 6 | 4.02 | 4.24 | 2.53 | 1.48 | 0.47 |  | 0 | [6 empty] | 37560
82 | Madanganj 102MW | [19 empty] | 9 | 30 | 34 | 0 |  |  |  | 65760
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [19 empty] | 7 | 50 | 50 | 0 |  |  |  | 67772
86 | Meghnaghat CCPP(Summit) | 285 | 270 | 287 | 270 | 270 | 250 | 285 | 290 | 282 | 270 | 260 | 294 | 270 | 255 | 274 | 280 | 228 | 240 |  | 300 | 243 | 245 | 265 | 293 | 300 | 295 | 6700945
87 | Meghnaghat (IEL) | [17 empty] | 0 |  | 14 | 25 | 38 | 0 |  |  |  | 61440
88 | Ghorashal 78MW (MAX) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 71 | 71 | 70 | 70 | 68 | 67 | 67 | 66 | 66 | 66 | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 |  | 1453536
90 | Ashuganj (United) 53MW
91 | Juldah (Acorn) | 50 | 50 | 0 | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 30 | 50 | 50 | 50 | 50 | 50 | 90 | 485160
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 10 |  | 20 | 50 | 49 | 49 | 49 | 50 | 50 | 1130472
93 | Ashuganj (Midland) 51MW | 35 | 35 | 35 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 735056
94 | Gagnagar (Orion) | [17 empty] | 0 |  | 16 | 64 | 50 | 32 | 32 | 32 | 64 | 281376
95 | Patenga 50MW | 47 | 47 | 47 | 47 | 45 | 20 | 18 | 20 | 22 | 40 | 47 | 47 | 47 | 46 | 47 | 46 | 46 | 46 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 996960
96 | Chattogram ECPV 108 MW |  |  |  | 0 | 5 | 0 | [8 empty] | 24 | 68 | 64 | 64 |  | 69 | 85 | 96 | 102 | 102 | 103 | 103 | 811200
97 | Katpotti 51 MW | 26 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 48 | 26 | 49 | 48 | 48 | 18 | 341856
98 | Bosila 108MW | 64 | 64 | 72 | 71 | 70 | 24 | 8 | 8 | 8 | 51 | 63 | 63 | 70 | 48 | 68 | 68 | 68 | 69 |  | 69 | 69 | 69 | 71 | 73 | 73 | 74 | 1299840
99 | Madanganj-55 MW | [19 empty] | 6 | 20 | 27 | 0 |  |  |  | 45180
100 | Northern 55 MW | 55 | 55 | 55 | 18 |  |  |  |  | 0 | 18 | 18 | 18 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 891715
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 100 |  | 100 | 100 | 100 | 163 | 163 | 163 | 130 | 3329877
102 | Sarishabari (Solar) | [5 empty] | 0.1 | 0.1 | 0.1 | 0.8 | 2.1 | 2.1 | 2.2 | 2.1 | 2.1 | 1.2 | 0.5 | 0.4 | 0.1 |  | 0 | [6 empty] | 14000
103 | Banco Energy 54MW | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 25 | 45 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 947160
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 185 | 185 | 185 | 130 | 80 |  |  |  |  | 0 | 14 | 43 | 7 | 151 | 182 | 187 | 187 | 190 |  | 195 | 195 | 195 | 192 | 184 | 185 | 185 | 2940000
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 70 | 70 | 35 | 0 | [15 empty] | 6 | 70 | 70 | 70 | 70 | 70 | 93 | 560160
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2074560
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 200 | 140 | 17 | 17 | 0 | 0 |  | 17 | 70 | 120 | 140 | 165 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3380160
117 | Midland 150MW | 50 | 50 | 50 | 50 | 5 |  |  |  |  | 0 | 7 | 50 | 100 | 112 | 145 | 149 | 70 | 70 |  | 95 | 150 | 150 | 150 | 123 | 123 | 148 | 1706181
118 | Bibiyana-3 285 MW | 260 | 260 | 260 | 261 | 260 | 260 | 221 | 219 | 270 | 297 | 295 | 287 | 289 | 289 | 286 | 285 | 289 | 201 |  | 250 | 200 | 200 | 250 | 299 | 284 | 240 | 6217000
| United Jamalpur PPL | 93 | 93 | 94 | 94 | 94 | 94 | 94 | 65 | 60 | 75 | 96 | 96 | 95 | 95 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 95 | 94 | 95 | 95 | 2161200
| Anwara United | [20 empty] | 0 | 2 | 46 | 50 | 50 | 0 | 160582
120 | Eastern Zone Total | 7204 | 7142 | 6994 | 6645 | 6281 | 5714.4 | 5570.4 | 5569 | 5772.5 | 6011.6 | 6268.9 | 6622.9 | 6766.6 | 6874.7 | 7063.38 | 7192.58 | 6837.41 | 6254.94 |  | 6843 | 7660 | 7734 | 7884 | 7851 | 7574 | 7543 | 162135673
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 99 | 99 | 99 | 99 | 66 | 0 |  |  |  | 32 | 32 | 46 | 90 | 99 | 99 | 99 | 49 | 49 |  | 73 | 99 | 99 | 99 | 99 | 99 | 99 | 1608000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [17 empty] | 9 |  | 20 | 17 | 26 | 40 | 35 | 32 | 32 | 193440
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 105 | 105 | 105 | 105 | 105 | 35 | 35 | 35 | 35 | 70 | 70 | 89 | 89 | 89 | 86 | 90 | 60 | 70 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 2033760
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 80 | 64 | 0 | [11 empty] | 4 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1156800
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 96 | 95 | 96 | 96 | 95 | 94 | 96 | 95 | 95 | 95 | 97 | 94 | 94 | 97 | 52 |  | 12 | 91 | 96 | 97 | 97 | 96 | 97 | 2188505
| Bhola CCPP 194MW | 149 | 149 | 148 | 148 | 149 | 147 | 147 | 148 | 147 | 148 | 148 | 146 | 146 | 146 | 146 | 146 | 139 | 141 |  | 147 | 133 | 132 | 147 | 148 | 147 | 148 | 3547923
140 | Bhola (Venture) 33MW | 37 | 36 | 37 | 37 | 36 | 26 | 22 | 21 | 20 | 20 | 20 | 22 | 23 | 27 | 27 | 27 | 25 | 26 |  | 32 | 37 | 38 | 38 | 39 | 39 | 39 | 705894
141 | Bangla Trak Noapara | 100 | 20 | 0 | [16 empty] | 1 | 75 | 85 | 100 | 100 | 100 | 100 | 680640
142 | Noapara (KZA) 40MW | 32 | 32 | 32 | 32 | 32 | 0 |  |  |  | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 40 | 40 | 40 | 0 | 40 | 40 | 628500
143 | Gopalganj Peaking | 58 | 58 | 52 | 46 | 0 | [11 empty] | 24 | 40 |  | 75 | 70 | 62 | 55 | 56 | 56 | 56 | 553728
144 | Bheramara GT-1,2,3 | [20 empty] | 10 | 32 | 32 | 32 | 32 | 32 | 144300
145 | Madhumati Power Plant | 99 | 99 | 99 | 99 | 99 | 99 | 52 | 52 | 52 | 53 | 52 | 52 | 87 | 86 | 86 | 85 | 97 | 86 |  | 94 | 97 | 97 | 97 | 97 | 97 | 97 | 2038896
146 | Bheramara HVDC | 793 | 531 | 531 | 532 | 531 | 531 | 531 | 524 | 524 | 661 | 661 | 660 | 660 | 659 | 660 | 660 | 660 | 661 |  | 904 | 905 | 905 | 905 | 905 | 905 | 906 | 16354181
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 199 | 199 | 199 | 199 | 198 | 199 | 199 | 200 | 199 | 199 | 199 | 200 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4866500
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 50 |  | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 1375000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | 50 | [15 empty] | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 474176
157 | Sirajgonj Unit-1 225MW (Gas) | 187 | 195 | 186 | 185 | 195 | 182 | 182 | 191 | 200 | 197 | 194 | 197 | 203 | 194 | 191 | 193 | 183 | 181 |  | 182 | 191 | 185 | 190 | 189 | 199 | 210 | 4877636
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 185 | 193 | 184 | 183 | 193 | 181 | 177 | 156 | 165 | 161 | 168 | 167 | 174 | 164 | 184 | 190 | 180 | 178 |  | 181 | 182 | 180 | 187 | 186 | 197 | 214 | 4536064
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 208 | 208 | 208 | 208 | 208 | 208 | 199 | 175 | 183 | 191 | 185 | 171 | 189 | 185 | 202 | 199 | 193 | 183 |  | 189 | 191 | 185 | 197 | 198 | 201 | 215 | 4920291
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 360 | 415 | 415 | 420 | 380 | 330 | 300 | 300 | 350 | 350 | 350 | 408 | 407 | 414 | 407 | 405 | 426 | 263 |  | 350 | 300 | 300 | 300 | 300 | 394 | 414 | 8754636
161 | Bera Peaking | 32 | 32 | 32 | [14 empty] | 10 |  | 31 | 32 | 39 | 38 | 39 | 39 | 39 | 320772
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 18 | 19 | 17 | 17 | 21 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 474960
163 | Bogra (EPL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 369432
164 | Ullapara (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 195174
165 | Amnura 50MW | 50 | 50 | [7 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 50 | 50 | 50 | 50 | 50 | 50 | 607230
166 | Katakhali (Northern) | 24 | 24 | [15 empty] | 0 |  | 24 | 43 | 43 | 43 | 43 | 43 | 43 | 265285
167 | Katakhali Peaking | [17 empty] | 0 |  | 42 | 45 | 47 | 45 | 44 | 44 | 44 | 222945
168 | Santahar Peaking | 41 | 41 | 41 | [16 empty] | 21 | 37 | 44 | 44 | 41 | 42 | 42 | 367268
169 | Rajlanka 52 MW | 50 | 50 | 42 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 42 | 52 | 52 | 50 | 52 | 50 | 50 | 476640
170 | Chapainawabganj-100 MW | 85 | 85 | 85 | 85 | 50 | 24 | 24 | 0 | 0 | 0 | 24 | 24 | 24 | 34 | 34 | 70 | 70 | 70 |  | 81 | 90 | 90 | 90 | 90 | 85 | 85 | 1278716
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 17 | 17 | [5 empty] | 0 | 43 | 87 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1752480
173 | Rangpur GT | 17 | 17 | [17 empty] | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 127000
175 | Saidpur GT | 17 | [18 empty] | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 129000
176 | Confidence Rangpur | [8 empty] | 0 | 3 | 6 | 6 | 7 | 6 | 6 | 6 | 8 | 17 |  | 35 | 35 | 27 | 0 |  |  |  | 128640
177
178
178 | Western Zone Total | 3400 | 3108 | 2965 | 2818 | 2520 | 2178 | 2065 | 1995 | 2071 | 2304 | 2353 | 2432 | 2593 | 2648 | 2694 | 2736 | 2678 | 2507 | 0 | 3251 | 3538 | 3570 | 3598 | 3555 | 3702 | 3767 | 68354412