## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-17 | Tuesday
|  |  | Date (day): | 2022-05-17 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14492.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15063 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-16 | 2022-05-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 250 | 250 | 250 |  | 115 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 95 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 284 | 280 | 0 | 0 |  | 412 | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 253 | 223 | 340 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 92 | 95 | 95
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 143 | 125 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 79 | 95 | 96 | 96 |  | 6 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 85 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 333 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 84 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 52 | 54 | 54 |  | 26 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 45 | 48 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 277 | 275 | 290 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 302 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 100 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3429 | 3940 | 3879 | 3874 | 671 | 1273
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 49 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 0 | 30 | 30 |  | 200 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 221 | 203 | 205 | 205
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 60 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 33 | 45 | 80 | 80 |  | 20 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 83 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 15 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 93 | 94 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 285 | 282 | 290 | 290 |  | 10 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 94 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 91 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 97 | 110 | 110 |  | 6 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1139 | 1388 | 1509 | 1494 | 411 | 455
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 183 | 200 | 225
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 280 | 280 | 80 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 32 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 5 | 0 | 0 | 55 |  | Engine problem
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 134 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 18 | 41 | 41 |  | 11 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 128 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 32 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 42 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 100 | 110 | 110 | 110 |  | 4 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 9 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 64 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1323 | 1652 | 1886 | 1934 | 945 | 141
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 66 | 98 | 120 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 176 | 166 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 94 | 105 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 401 | 413 | 528.6 | 497 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 0 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 46 | 50 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 50 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 38 | 0 | 38 | 41 | 9 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 11 | 8 | 8
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 305 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 280 | 280 | 280 | 280
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1644 | 1649 | 1745 | 1789 | 339 | 186
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 923 | 931 | 931
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 12 | 80 | 16 | 115 |  |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 0 | 80 |  | 29 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 320 | 320 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 32 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1410 | 1774 | 1944 | 2023 | 90 | 56
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 20 | 33 | 33 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 86 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1030 | 800 | 1050 |  |  | FGNO
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 210 | 212 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1079 | 1410 | 1189 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 35 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 14 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 191 | 200 | 205
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 37 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 84 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 156 | 200 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 910 | 1323 | 1404 | 1403 | 601 | 100
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 |  | 99 | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 72 | 107 | 110 | 110 |  | 3 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 252 | 405 | 408 | 400 | 0 | 272
|  | Total |  |  |  |  | 22348 | 21584 | 11587 | 13954 | 14492.6 | 15063 | 3227 | 2491
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11102.1629 | 13370.12 | 13886.1833 | 14432.7159
| A. |  | 2022-05-16 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13954 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10066 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13954 | MW
| 3 | Day peak Generation : |  |  | 11587 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13370.12 | MW
| 4 | Evening peak Generation : |  |  | 13954 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 291.3479 | MKWHr | By Solar | 1.1082 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 139.7984 | MKWHr |  | By Oil: | 97.8722 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 26.6001 | MKWHr |  | By Hydro: | 0.73964 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3227 | MW | Dhaka | 4884.54 | 4884.54 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2491 | MW | Chittagong | 1439.58 | 1439.58 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5718 | MW | Khulna | 1666.4 | 1666.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1028.77 | MMCFD |  |  | Rajshahi | 1466.6 | 1466.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 140928900.922 | ii) Oil : | Taka | 763599547.62 | Comilla | 1267 | 1267 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 121165535 | Total | Taka | 1025693983.542 | Mymensingh | 1025 | 1025 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 447 | 447 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 364 | MW (E to W) at | 21:00 | hrs | Barisal | 418 | 418 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 206 | MW at | 3:00 | hrs | Rangpur | 756 | 756 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 13370.12 | 13370.12 |  | 0
| B. |  | 2022-05-17 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 37.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15063 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 1063 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 292.3084 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8165 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.312 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9174 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.07 |  | (b) Today: | 74.01 |  | (c) Rule Curve: |  | 78.96
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 333 | 300 |  | 0 | 225 | 125 | 87 | 96 | 55 | 336 | 0 | 0 | 99 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 97 | 49 | 22 | 36 | 0 | 0 | 0 | 270 | 0 | 168 | 8 | 91 | 34 | 0 | 0 | 43 | 0 | 0 | 34 | 19 | 9 | 33 | 20 | 124 | 131 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 78 | 0 | 219 | 0 | 37 | 10 | 275 | 11 | 11 | 0 | 293 | 0 | 0 | 184 | 0 | 134 | 0 | 64 | 200 | 135 | 280 | 105 | 105 | 105 | 0 | 275 | 54 | 101 | 108 | 9 | 50 | 360 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 916 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 86 | 35 | 32 | 0 | 0 | 0 | 43 | 0 | 83 | 0 | 50 | 0 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 384 | 105 | 0 | 113 | 105 | 19 | 0 | 0 | 113 | 980 | 218 | 0 | 0 | 0 | 0 | 17 |  | 8284 | 4087 | 12371 | 3772 | 916 | 2085 | 0 | 3965 | 1155 | 30 | 0 | 324 | 124 | 0 | 0 | 74.07
2:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 343 | 300 |  | 0 | 225 | 135 | 91 | 96 | 55 | 335 | 0 | 0 | 99 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 97 | 50 | 22 | 36 | 0 | 0 | 0 | 270 | 0 | 158 | 8 | 90 | 34 | 0 | 0 | 43 | 0 | 0 | 34 | 19 | 9 | 33 | 20 | 120 | 120 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 78 | 0 | 219 | 0 | 37 | 10 | 280 | 11 | 11 | 0 | 298 | 0 | 0 | 186 | 0 | 135 | 0 | 38 | 200 | 137 | 280 | 96 | 105 | 105 | 0 | 282 | 54 | 103 | 108 | 9 | 50 | 360 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 918 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 381 | 105 | 0 | 113 | 105 | 34 | 0 | 0 | 113 | 940 | 215 | 0 | 0 | 0 | 0 | 17 |  | 8254 | 3880 | 12134 | 3756 | 918 | 2093 | 0 | 3918 | 1115 | 30 | 0 | 184 | 120 | 0 | 0 | 74.07
3:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 348 | 312 |  | 0 | 225 | 130 | 90 | 96 | 55 | 335 | 0 | 0 | 76 | 24 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 97 | 50 | 20 | 38 | 0 | 0 | 0 | 260 | 0 | 163 | 8 | 91 | 34 | 0 | 0 | 43 | 0 | 0 | 38 | 19 | 9 | 33 | 20 | 120 | 134 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 78 | 0 | 219 | 0 | 37 | 10 | 270 | 11 | 11 | 0 | 293 | 0 | 0 | 186 | 0 | 149 | 0 | 38 | 200 | 128 | 280 | 96 | 105 | 105 | 0 | 283 | 54 | 110 | 108 | 9 | 50 | 360 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 17 | 55 |  | 922 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 380 | 105 | 0 | 113 | 40 | 38 | 0 | 0 | 113 | 900 | 213 | 0 | 0 | 0 | 0 | 0 |  | 8109 | 3731 | 11840 | 3788 | 922 | 2085 | 0 | 3666 | 1075 | 30 | 0 | 154 | 120 | 0 | 0 | 74.07
4:00 | 0 | 0 | 0 | 170 | 260 | 82 | 0 | 351 | 306 |  | 0 | 225 | 135 | 90 | 96 | 50 | 335 | 0 | 0 | 32 | 16 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 49 | 0 | 0 | 30 | 0 | 0 | 4 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 55 | 50 | 20 | 38 | 0 | 0 | 0 | 265 | 0 | 180 | 8 | 90 | 34 | 0 | 0 | 43 | 0 | 0 | 43 | 19 | 9 | 33 | 20 | 114 | 130 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 78 | 0 | 219 | 0 | 37 | 10 | 295 | 11 | 11 | 0 | 293 | 0 | 0 | 187 | 0 | 149 | 0 | 38 | 136 | 125 | 280 | 105 | 105 | 51 | 0 | 284 | 54 | 110 | 108 | 9 | 38 | 360 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 0 | 55 |  | 923 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 380 | 105 | 0 | 113 | 15 | 38 | 0 | 0 | 113 | 850 | 215 | 0 | 0 | 0 | 0 | 0 |  | 7892 | 3655 | 11547 | 3825 | 923 | 2096 | 0 | 3402 | 1025 | 30 | 0 | 132 | 114 | 0 | 0 | 74.07
5:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 358 | 306 |  | 0 | 225 | 130 | 90 | 70 | 55 | 337 | 0 | 0 | 8 | 7 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 25 | 25 | 33 | 42 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 51 | 50 | 20 | 38 | 0 | 0 | 0 | 265 | 0 | 192 | 8 | 91 | 34 | 0 | 0 | 43 | 0 | 0 | 43 | 19 | 9 | 33 | 20 | 108 | 136 | 0 | 20 | 0 | 43 | 30 | 31 | 30 | 130 | 0 | 25 | 75 | 0 | 219 | 0 | 37 | 10 | 280 | 11 | 11 | 0 | 95 | 0 | 0 | 179 | 0 | 138 | 0 | 38 | 120 | 100 | 280 | 106 | 105 | 51 | 0 | 283 | 54 | 110 | 108 | 9 | 38 | 380 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 0 | 55 |  | 922 | 0 | 295 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 380 | 70 | 0 | 113 | 15 | 38 | 0 | 0 | 113 | 840 | 213 | 0 | 0 | 0 | 0 | 0 |  | 7558 | 3586 | 11144 | 3879 | 922 | 2086 | 0 | 2972 | 1015 | 30 | 0 | 132 | 108 | 0 | 0 | 74.07
6:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 361 | 314 |  | 0 | 225 | 135 | 90 | 32 | 30 | 280 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 25 | 25 | 33 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 41 | 50 | 20 | 38 | 0 | 0 | 0 | 265 | 0 | 200 | 8 | 91 | 34 | 0 | 0 | 43 | 0 | 0 | 25 | 19 | 9 | 33 | 20 | 104 | 136 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 75 | 0 | 219 | 0 | 37 | 10 | 275 | 11 | 11 | 0 | 45 | 0 | 0 | 140 | 0 | 92 | 1 | 38 | 51 | 50 | 280 | 106 | 90 | 51 | 0 | 190 | 54 | 110 | 70 | 8 | 38 | 380 | 54 | 2 | 126 | 78 | 0 | 34 | 0 | 0 | 34 |  | 924 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 113 | 15 | 38 | 0 | 0 | 95 | 810 | 184 | 0 | 0 | 0 | 2 | 0 |  | 6788 | 3452 | 10240 | 3845 | 924 | 2061 | 0 | 2188 | 985 | 30 | 0 | 98 | 104 | 5 | 0 | 74.07
7:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 370 | 314 |  | 0 | 225 | 125 | 89 | 32 | 30 | 280 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 25 | 25 | 16 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 10 | 0 | 34 | 0 | 26 | 50 | 22 | 36 | 0 | 0 | 0 | 265 | 0 | 197 | 8 | 91 | 34 | 0 | 0 | 43 | 0 | 0 | 25 | 19 | 9 | 22 | 20 | 100 | 109 | 0 | 20 | 0 | 44 | 30 | 31 | 30 | 130 | 0 | 25 | 75 | 0 | 219 | 0 | 36 | 10 | 285 | 11 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 88 | 7 | 38 | 51 | 50 | 280 | 115 | 90 | 51 | 1 | 190 | 54 | 110 | 70 | 9 | 38 | 380 | 54 | 6 | 126 | 97 | 0 | 17 | 0 | 0 | 27 |  | 923 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 113 | 15 | 38 | 0 | 0 | 95 | 810 | 187 | 0 | 0 | 0 | 9 | 0 |  | 6725 | 3451 | 10176 | 3809 | 923 | 2057 | 0 | 2117 | 985 | 30 | 0 | 132 | 100 | 23 | 0 | 74.06
8:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 365 | 312 |  | 0 | 225 | 135 | 88 | 32 | 30 | 280 | 0 | 0 | 8 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 25 | 25 | 16 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 10 | 0 | 34 | 0 | 26 | 50 | 22 | 3 | 0 | 0 | 0 | 265 | 0 | 188 | 8 | 91 | 31 | 0 | 0 | 43 | 0 | 0 | 25 | 19 | 9 | 25 | 20 | 106 | 105 | 0 | 20 | 1 | 44 | 30 | 42 | 30 | 130 | 0 | 30 | 75 | 0 | 219 | 0 | 36 | 10 | 270 | 11 | 5 | 0 | 45 | 0 | 0 | 100 | 0 | 85 | 4 | 38 | 51 | 50 | 280 | 115 | 70 | 51 | 3 | 190 | 54 | 110 | 70 | 9 | 38 | 400 | 54 | 9 | 126 | 97 | 0 | 17 | 0 | 0 | 43 |  | 924 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 352 | 17 | 0 | 113 | 15 | 38 | 0 | 0 | 95 | 760 | 186 | 0 | 0 | 1 | 36 | 0 |  | 6664 | 3402 | 10066 | 3813 | 924 | 1997 | 0 | 2109 | 935 | 30 | 0 | 98 | 106 | 54 | 0 | 74.06
9:00 | 0 | 0 | 0 | 170 | 260 | 98 | 0 | 362 | 292 |  | 0 | 225 | 114 | 85 | 31 | 30 | 333 | 0 | 0 | 16 | 40 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 45 | 22 | 25 | 29 | 25 | 33 | 36 | 0 | 0 | 30 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 13 | 0 | 34 | 30 | 26 | 49 | 0 | 2 | 0 | 0 | 0 | 275 | 0 | 184 | 8 | 89 | 31 | 0 | 0 | 43 | 0 | 0 | 26 | 19 | 7 | 33 | 20 | 112 | 73 | 0 | 20 | 1 | 44 | 30 | 47 | 47 | 163 | 0 | 30 | 69 | 0 | 219 | 0 | 36 | 10 | 295 | 11 | 11 | 0 | 45 | 0 | 0 | 110 | 0 | 85 | 15 | 38 | 70 | 63 | 280 | 106 | 80 | 61 | 3 | 240 | 54 | 110 | 80 | 9 | 50 | 397 | 68 | 17 | 133 | 97 | 0 | 17 | 0 | 2 | 55 |  | 923 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 352 | 17 | 0 | 113 | 15 | 38 | 0 | 1 | 95 | 770 | 186 | 0 | 0 | 2 | 59 | 0 |  | 7047 | 3396 | 10443 | 3820 | 923 | 2029 | 0 | 2354 | 945 | 30 | 0 | 132 | 112 | 98 | 0 | 74.06
10:00 | 0 | 0 | 0 | 170 | 260 | 95 | 0 | 322 | 277 |  | 0 | 225 | 142 | 81 | 37 | 55 | 300 | 0 | 0 | 72 | 74 | 98 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 25 | 25 | 33 | 41 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 17 | 0 | 0 | 30 | 82 | 49 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 182 | 8 | 89 | 31 | 0 | 0 | 43 | 0 | 0 | 34 | 19 | 7 | 33 | 17 | 116 | 69 | 0 | 16 | 1 | 44 | 30 | 45 | 47 | 130 | 0 | 20 | 72 | 0 | 187 | 0 | 37 | 10 | 255 | 11 | 11 | 0 | 212 | 0 | 0 | 130 | 0 | 128 | 19 | 38 | 184 | 113 | 280 | 105 | 105 | 105 | 5 | 282 | 54 | 110 | 108 | 9 | 50 | 393 | 89 | 17 | 162 | 97 | 0 | 17 | 0 | 17 | 55 |  | 924 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 252 | 17 | 0 | 70 | 15 | 34 | 0 | 1 | 50 | 700 | 166 | 0 | 0 | 3 | 48 | 0 |  | 7662 | 3101 | 10763 | 3705 | 924 | 1844 | 0 | 3077 | 875 | 30 | 0 | 98 | 116 | 94 | 0 | 74.06
11:00 | 0 | 0 | 0 | 170 | 260 | 97 | 0 | 306 | 261 |  | 0 | 225 | 140 | 90 | 56 | 55 | 331 | 0 | 0 | 85 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 41 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 93 | 49 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 185 | 8 | 90 | 29 | 0 | 0 | 43 | 0 | 0 | 36 | 19 | 7 | 28 | 20 | 120 | 69 | 0 | 16 | 1 | 44 | 30 | 45 | 47 | 163 | 0 | 30 | 72 | 0 | 212 | 0 | 36 | 9 | 270 | 0 | 11 | 0 | 283 | 0 | 0 | 131 | 0 | 149 | 19 | 38 | 200 | 115 | 280 | 95 | 90 | 105 | 4 | 282 | 0 | 110 | 100 | 11 | 50 | 400 | 104 | 38 | 162 | 97 | 0 | 17 | 0 | 17 | 55 |  | 924 | 0 | 320 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 416 | 35 | 0 | 81 | 32 | 60 | 0 | 3 | 70 | 720 | 198 | 0 | 0 | 2 | 98 | 0 |  | 7922 | 3516 | 11438 | 3765 | 924 | 2070 | 0 | 3303 | 895 | 30 | 0 | 166 | 120 | 165 | 0 | 74.05
12:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 284 | 253 |  | 0 | 225 | 143 | 90 | 79 | 55 | 325 | 0 | 0 | 90 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 45 | 0 | 0 | 30 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 93 | 49 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 180 | 8 | 90 | 29 | 0 | 0 | 43 | 0 | 0 | 43 | 19 | 7 | 25 | 20 | 122 | 66 | 0 | 0 | 1 | 44 | 30 | 47 | 46 | 163 | 0 | 30 | 72 | 0 | 220 | 0 | 38 | 9 | 260 | 0 | 11 | 0 | 277 | 0 | 0 | 176 | 0 | 149 | 19 | 38 | 200 | 118 | 280 | 94 | 90 | 105 | 2 | 285 | 0 | 94 | 100 | 10 | 50 | 394 | 104 | 46 | 162 | 96 | 0 | 17 | 0 | 17 | 55 |  | 924 | 0 | 320 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 20 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 32 | 72 | 0 | 5 | 95 | 750 | 210 | 0 | 0 | 5 | 69 | 0 |  | 7936 | 3651 | 11587 | 3727 | 924 | 2067 | 0 | 3479 | 925 | 30 | 0 | 166 | 122 | 147 | 0 | 74.05
13:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 270 | 247 |  | 0 | 225 | 112 | 89 | 90 | 55 | 325 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 93 | 49 | 22 | 3 | 0 | 0 | 0 | 275 | 0 | 175 | 8 | 88 | 29 | 0 | 0 | 43 | 0 | 0 | 42 | 19 | 7 | 25 | 20 | 120 | 66 | 0 | 0 | 1 | 44 | 30 | 0 | 49 | 163 | 0 | 25 | 72 | 0 | 220 | 0 | 0 | 10 | 300 | 11 | 11 | 0 | 275 | 58 | 50 | 165 | 25 | 149 | 18 | 38 | 200 | 120 | 280 | 104 | 100 | 105 | 5 | 284 | 0 | 93 | 105 | 9 | 50 | 400 | 104 | 19 | 162 | 97 | 0 | 14 | 0 | 53 | 55 |  | 924 | 0 | 310 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 23 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 0 | 45 | 22 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 105 | 108 | 0 | 5 | 95 | 790 | 210 | 0 | 0 | 4 | 89 | 72 |  | 8026 | 4010 | 12036 | 3695 | 924 | 1993 | 133 | 3842 | 965 | 35 | 0 | 188 | 120 | 141 | 0 | 74.05
14:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 267 | 242 |  | 0 | 225 | 120 | 88 | 94 | 55 | 320 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 93 | 49 | 22 | 3 | 0 | 0 | 0 | 275 | 0 | 179 | 8 | 89 | 29 | 0 | 0 | 43 | 0 | 41 | 41 | 18 | 7 | 25 | 20 | 128 | 63 | 0 | 17 | 1 | 44 | 30 | 0 | 49 | 163 | 0 | 30 | 74 | 0 | 220 | 0 | 0 | 10 | 270 | 11 | 11 | 0 | 265 | 53 | 50 | 164 | 25 | 149 | 16 | 38 | 200 | 122 | 280 | 103 | 105 | 105 | 5 | 284 | 0 | 93 | 105 | 9 | 38 | 396 | 104 | 26 | 162 | 97 | 0 | 35 | 0 | 83 | 0 |  | 922 | 0 | 310 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 24 | 16 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 25 | 0 | 52 | 38 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 105 | 108 | 0 | 4 | 95 | 780 | 210 | 0 | 0 | 3 | 74 | 72 |  | 8053 | 4008 | 12061 | 3706 | 922 | 1971 | 128 | 3838 | 955 | 35 | 0 | 249 | 128 | 129 | 0 | 74.05
15:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 265 | 243 |  | 0 | 225 | 134 | 89 | 94 | 55 | 320 | 0 | 0 | 98 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 21 | 0 | 0 | 33 | 90 | 44 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 187 | 8 | 89 | 31 | 0 | 0 | 43 | 0 | 48 | 42 | 18 | 7 | 32 | 20 | 132 | 65 | 0 | 17 | 1 | 44 | 30 | 0 | 49 | 163 | 0 | 30 | 70 | 0 | 220 | 0 | 0 | 10 | 300 | 11 | 11 | 30 | 248 | 202 | 98 | 155 | 96 | 149 | 13 | 38 | 200 | 130 | 280 | 93 | 90 | 105 | 4 | 283 | 0 | 93 | 105 | 8 | 39 | 388 | 104 | 16 | 162 | 97 | 0 | 35 | 0 | 83 | 0 |  | 923 | 0 | 310 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 29 | 16 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 25 | 7 | 52 | 37 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 105 | 108 | 0 | 4 | 95 | 800 | 210 | 0 | 0 | 1 | 72 | 72 |  | 8348 | 4034 | 12382 | 3714 | 923 | 2013 | 426 | 3791 | 975 | 35 | 0 | 262 | 132 | 111 | 0 | 74.04
16:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 262 | 236 |  | 0 | 225 | 123 | 89 | 93 | 55 | 326 | 0 | 0 | 96 | 84 | 120 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 40 | 0 | 35 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 42 | 0 | 33 | 91 | 38 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 187 | 8 | 91 | 30 | 0 | 0 | 43 | 0 | 48 | 42 | 18 | 7 | 32 | 20 | 130 | 63 | 0 | 20 | 1 | 44 | 30 | 0 | 49 | 163 | 0 | 35 | 72 | 0 | 220 | 0 | 0 | 10 | 300 | 11 | 11 | 30 | 260 | 204 | 93 | 163 | 99 | 149 | 8 | 38 | 200 | 122 | 280 | 93 | 90 | 105 | 2 | 283 | 7 | 106 | 105 | 9 | 39 | 392 | 104 | 14 | 162 | 97 | 0 | 35 | 0 | 83 | 36 |  | 922 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 29 | 16 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 25 | 31 | 52 | 37 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 89 | 108 | 0 | 2 | 95 | 800 | 210 | 0 | 0 | 0 | 54 | 72 |  | 8420 | 4021 | 12441 | 3727 | 922 | 1997 | 426 | 3832 | 975 | 35 | 0 | 316 | 130 | 81 | 0 | 74.04
17:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 253 | 232 |  | 0 | 225 | 128 | 89 | 93 | 55 | 328 | 0 | 0 | 84 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 24 | 17 | 0 | 33 | 91 | 36 | 22 | 6 | 0 | 0 | 0 | 275 | 0 | 202 | 8 | 91 | 20 | 0 | 0 | 43 | 0 | 48 | 42 | 18 | 3 | 32 | 20 | 126 | 70 | 0 | 20 | 1 | 44 | 30 | 0 | 50 | 163 | 0 | 50 | 72 | 0 | 220 | 0 | 0 | 10 | 290 | 11 | 11 | 0 | 263 | 0 | 0 | 163 | 0 | 149 | 3 | 38 | 200 | 118 | 280 | 103 | 105 | 105 | 1 | 283 | 54 | 110 | 96 | 9 | 38 | 394 | 104 | 8 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 922 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 27 | 16 | 0 | 0 | 0 | 34 | 14 | 50 | 0 | 25 | 31 | 52 | 37 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 85 | 107 | 0 | 1 | 95 | 800 | 210 | 0 | 0 | 0 | 23 | 72 |  | 8061 | 4041 | 12102 | 3748 | 922 | 1991 | 0 | 3905 | 975 | 35 | 0 | 363 | 126 | 37 | 0 | 74.04
18:00 | 0 | 0 | 0 | 170 | 250 | 97 | 0 | 246 | 226 |  | 0 | 225 | 120 | 84 | 93 | 55 | 330 | 0 | 0 | 80 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 17 | 0 | 33 | 92 | 40 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 189 | 8 | 88 | 26 | 1 | 0 | 43 | 0 | 48 | 41 | 18 | 8 | 32 | 20 | 120 | 75 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 110 | 0 | 50 | 74 | 0 | 220 | 0 | 0 | 10 | 285 | 11 | 11 | 0 | 260 | 0 | 0 | 164 | 0 | 149 | 0 | 79 | 170 | 120 | 280 | 103 | 105 | 105 | 0 | 283 | 54 | 110 | 96 | 9 | 50 | 360 | 104 | 2 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 923 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 14 | 8 | 8 | 85 | 26 | 16 | 0 | 0 | 0 | 34 | 14 | 50 | 0 | 25 | 0 | 16 | 37 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 350 | 105 | 0 | 50 | 50 | 74 | 0 | 0 | 50 | 790 | 210 | 0 | 0 | 0 | 5 | 34 |  | 7954 | 3748 | 11702 | 3709 | 923 | 1858 | 0 | 3731 | 965 | 35 | 0 | 354 | 120 | 7 | 0 | 74.04
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 276 | 221 |  | 0 | 225 | 142 | 87 | 94 | 55 | 325 | 0 | 0 | 80 | 84 | 132 | 0 | 0 | 0 | 0 | 18 | 55 | 55 | 22 | 25 | 23 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 |  | 24 | 60 | 51 | 45 | 93 | 46 | 22 | 12 | 0 | 0 | 0 | 275 | 0 | 186 | 8 | 90 | 29 | 5 | 0 | 43 | 0 | 48 | 42 | 18 | 5 | 32 | 20 | 136 | 105 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 50 | 75 | 0 | 220 | 0 | 0 | 10 | 280 | 11 | 11 | 200 | 265 | 306 | 100 | 165 | 98 | 149 | 0 | 81 | 188 | 122 | 280 | 105 | 105 | 105 | 0 | 265 | 54 | 110 | 110 | 9 | 90 | 387 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 923 | 0 | 310 | 0 | 70 | 0 | 0 | 0 | 34 | 35 | 16 | 85 | 31 | 48 | 0 | 0 | 0 | 34 | 15 | 84 | 0 | 50 | 0 | 46 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 196 | 0 | 0 | 24 | 0 | 0 | 414 | 105 | 46 | 70 | 105 | 102 | 0 | 0 | 95 | 840 | 210 | 0 | 10 | 0 | 0 | 80 |  | 9014 | 4331 | 13345 | 3806 | 923 | 2010 | 774 | 4107 | 1015 | 35 | 8 | 531 | 136 | 0 | 0 | 74.03
19:30 | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 282 | 221 |  | 0 | 225 | 144 | 89 | 94 | 55 | 329 | 0 | 0 | 82 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 60 | 51 | 45 | 93 | 50 | 22 | 16 | 0 | 0 | 0 | 275 | 0 | 186 | 8 | 90 | 32 | 5 | 0 | 43 | 0 | 48 | 42 | 19 | 5 | 32 | 20 | 136 | 105 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 75 | 0 | 220 | 0 | 0 | 10 | 320 | 11 | 11 | 200 | 277 | 305 | 100 | 165 | 99 | 149 | 0 | 81 | 200 | 125 | 280 | 105 | 105 | 105 | 0 | 265 | 54 | 110 | 110 | 9 | 90 | 398 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 64 | 55 |  | 924 | 0 | 310 | 0 | 80 | 0 | 0 | 0 | 44 | 65 | 16 | 84 | 30 | 48 | 0 | 0 | 0 | 34 | 15 | 84 | 0 | 50 | 0 | 52 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 198 | 0 | 0 | 100 | 0 | 0 | 414 | 105 | 151 | 113 | 105 | 102 | 0 | 0 | 95 | 1000 | 212 | 0 | 17 | 0 | 0 | 115 |  | 9128 | 4816 | 13944 | 3842 | 924 | 2057 | 955 | 4241 | 1175 | 35 | 8 | 571 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 276 | 221 |  | 0 | 225 | 135 | 89 | 95 | 55 | 330 | 0 | 0 | 83 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 60 | 51 | 45 | 94 | 48 | 22 | 22 | 0 | 0 | 0 | 275 | 0 | 188 | 8 | 90 | 32 | 5 | 0 | 51 | 0 | 0 | 42 | 19 | 5 | 32 | 20 | 136 | 99 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 50 | 75 | 0 | 220 | 0 | 0 | 10 | 320 | 11 | 11 | 200 | 278 | 300 | 100 | 165 | 100 | 149 | 0 | 82 | 200 | 125 | 280 | 105 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 90 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 67 | 55 |  | 923 | 0 | 320 | 0 | 80 | 0 | 0 | 0 | 44 | 65 | 16 | 85 | 31 | 48 | 0 | 0 | 0 | 34 | 12 | 84 | 0 | 50 | 0 | 52 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 198 | 0 | 0 | 100 | 0 | 0 | 414 | 105 | 152 | 113 | 105 | 110 | 0 | 0 | 95 | 1020 | 212 | 0 | 17 | 0 | 0 | 115 |  | 9074 | 4853 | 13927 | 3823 | 923 | 2063 | 952 | 4272 | 1195 | 35 | 8 | 520 | 136 | 0 | 0 | 74.03
21:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 280 | 223 |  | 0 | 225 | 125 | 92 | 95 | 55 | 333 | 0 | 0 | 85 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 60 | 51 | 45 | 94 | 50 | 22 | 16 | 0 | 0 | 0 | 275 | 0 | 183 | 8 | 90 | 32 | 5 | 0 | 43 | 0 | 18 | 42 | 19 | 5 | 32 | 20 | 128 | 98 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 50 | 75 | 0 | 220 | 0 | 0 | 10 | 305 | 11 | 11 | 200 | 275 | 302 | 100 | 166 | 100 | 149 | 0 | 83 | 200 | 134 | 280 | 105 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 91 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 64 | 55 |  | 923 | 0 | 320 | 0 | 80 | 0 | 0 | 0 | 44 | 65 | 32 | 86 | 33 | 32 | 0 | 0 | 0 | 34 | 14 | 84 | 0 | 50 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 191 | 0 | 0 | 100 | 0 | 0 | 414 | 105 | 156 | 113 | 105 | 107 | 0 | 0 | 113 | 1030 | 212 | 0 | 17 | 0 | 0 | 115 |  | 9042 | 4912 | 13954 | 3818 | 923 | 2024 | 958 | 4319 | 1205 | 0 | 8 | 571 | 128 | 0 | 0 | 74.03
22:00 | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 283 | 222 |  | 0 | 225 | 125 | 90 | 95 | 45 | 334 | 0 | 0 | 91 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 24 | 60 | 51 | 45 | 96 | 48 | 22 | 16 | 0 | 0 | 0 | 280 | 0 | 188 | 8 | 90 | 33 | 5 | 0 | 35 | 0 | 48 | 42 | 19 | 5 | 33 | 20 | 134 | 101 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 75 | 0 | 220 | 0 | 0 | 10 | 275 | 11 | 11 | 80 | 275 | 142 | 99 | 175 | 98 | 149 | 0 | 84 | 200 | 137 | 280 | 105 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 79 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 72 | 55 |  | 922 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 44 | 65 | 32 | 86 | 34 | 32 | 0 | 0 | 0 | 34 | 14 | 81 | 0 | 50 | 32 | 52 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 197 | 0 | 0 | 10 | 0 | 0 | 414 | 105 | 100 | 113 | 105 | 110 | 0 | 0 | 113 | 1020 | 216 | 0 | 17 | 0 | 0 | 115 |  | 8823 | 4801 | 13624 | 3853 | 922 | 1989 | 529 | 4360 | 1195 | 35 | 8 | 599 | 134 | 0 | 0 | 74.03
23:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 283 | 222 |  | 0 | 225 | 120 | 91 | 95 | 55 | 335 | 0 | 0 | 87 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 60 | 0 | 22 | 96 | 50 | 22 | 37 | 0 | 0 | 0 | 280 | 0 | 190 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 48 | 43 | 19 | 5 | 33 | 20 | 132 | 106 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 60 | 75 | 0 | 220 | 0 | 0 | 0 | 270 | 0 | 11 | 10 | 276 | 43 | 98 | 174 | 100 | 149 | 0 | 84 | 200 | 135 | 280 | 105 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 50 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 922 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 44 | 58 | 0 | 87 | 34 | 32 | 0 | 0 | 0 | 34 | 16 | 81 | 0 | 50 | 32 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 419 | 105 | 0 | 113 | 105 | 111 | 0 | 0 | 113 | 1010 | 186 | 0 | 17 | 0 | 0 | 115 |  | 8554 | 4605 | 13159 | 3864 | 922 | 1935 | 251 | 4297 | 1185 | 30 | 0 | 543 | 132 | 0 | 0 | 74.02
24:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 300 | 247 |  | 0 | 225 | 140 | 94 | 95 | 55 | 335 | 0 | 0 | 82 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 12 | 0 | 22 | 96 | 50 | 22 | 30 | 0 | 0 | 0 | 275 | 0 | 193 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 48 | 43 | 19 | 5 | 33 | 20 | 132 | 105 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 55 | 75 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 276 | 0 | 25 | 174 | 25 | 149 | 0 | 62 | 200 | 133 | 280 | 95 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 38 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 923 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 44 | 59 | 0 | 87 | 35 | 32 | 0 | 0 | 0 | 34 | 15 | 81 | 0 | 50 | 40 | 52 | 0 | 10 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 418 | 105 | 0 | 70 | 105 | 111 | 0 | 0 | 70 | 1010 | 216 | 0 | 17 | 0 | 0 | 72 |  | 8325 | 4422 | 12747 | 3876 | 923 | 2033 | 50 | 4054 | 1184 | 30 | 0 | 465 | 132 | 0 | 0 | 74.02
KWH | 0 | 0 | 0 | 4205250 | 6082545 | 2250863 | 0 | 7499780 | 6350000 |  | 0 | 5075100 | 3144727 | 2133120 | 1919808 | 1230869 | 7768567 | 0 | 0 | 1680000 | 1554336 | 2873280 | 0 | 0 | 0 | 0 | 1008360 | 1171123 | 1191184 | 445140 | 600000 | 543420 | 617300 | 639700 | 1070400 | 0 | 347640 | 392000 | 0 | 0 | 349228 | 4881783 | 0 | 0 | 0 |  | 513600 | 425336 | 338339 | 578160 | 1907520 | 1150080 | 531888 | 454560 | 0 | 0 | 0 | 6974900 | 0 | 4489000 | 217454 | 2154840 | 716040 | 36000 | 0 | 969742 | 0 | 442280 | 939427 | 436248 | 171540 | 746300 | 472500 | 2917440 | 2170560 | 0 | 391140 | 9550 | 1035000 | 689856 | 465000 | 1031256 | 3658254 | 0 | 856512 | 1767360 | 0 | 5242790 | 0 | 460420 | 233100 | 7046000 | 231648 | 255800 | 742272 | 5622871 | 1579071 | 810264 | 3804000 | 750864 | 3338208 | 132840 | 1212480 | 4085760 | 2798472 | 6625000 | 2413200 | 2463600 | 2263199 | 32844 | 6488509 | 1078349 | 2596061 | 2384880 | 224280 | 1233600 | 9283400 | 2426880 | 240330 | 3828960 | 2324673 | 0 | 747000 | 0 | 1217280 | 1194480 |  | 22312000 | 0 | 7500096 | 0 | 739200 | 0 | 0 | 0 | 223200 | 385408 | 97125 | 2056217 | 545300 | 611616 | 0 | 0 | 0 | 484832 | 118673 | 728856 | 0 | 490347 | 180100 | 873538 | 415745 | 443760 | 0 | 198396 | 0 | 0 | 4263200 | 0 | 39000 | 0 | 0 | 4921909 | 0 | 0 | 306240 | 0 | 0 | 9322945 | 2068800 | 515367 | 2589696 | 1640304 | 1765094 | 0 | 33483 | 2316096 | 22336900 | 4891473 | 0 | 99600 | 26640 | 632500 | 1077696 |  | 194096590 | 97251352 | 291347942 | 91435065 | 22312000 | 48363314 | 4704078 | 86513069 | 26600100 | 739640 | 39000 | 6616049 | 2917440 | 1108187 | 0
Fuel Cost | 0 | 0 | 0 | 6181717.5 | 6751624.95 | 2971139.16 | 0 | 7574777.8 | 6540500 |  | 0 | 5531859 | 3490646.97 | 16190380.8 | 13227477.12 | 10413151.74 | 8079309.68 | 0 | 0 | 12650400 | 14175544.32 | 28273075.2 | 0 | 0 | 0 | 0 | 7361028 | 9052780.79 | 11745074.24 | 333855 | 450000 | 0 | 0 | 0 | 10350768 | 0 | 93862.8 | 105840 | 0 | 0 | 3244328.12 | 5321143.47 | 0 | 0 | 0 |  | 0 | 4112999.12 | 3281888.3 | 5521428 | 16595424 | 9108633.6 | 670178.88 | 1350043.2 | 0 | 0 | 0 | 5161426 | 0 | 4129880 | 280515.66 | 2478066 | 809125.2 | 50400 | 0 | 1658258.82 | 0 | 4467028 | 8971527.85 | 554034.96 | 128655 | 1306025 | 354375 | 21880800 | 2300793.6 | 0 | 496747.8 | 152227 | 1697400 | 1103769.6 | 827700 | 1608759.36 | 4170409.56 | 0 | 1687328.64 | 3375657.6 | 0 | 9070026.7 | 0 | 538691.4 | 475524 | 7116460 | 173736 | 194408 | 12626046.72 | 42508904.76 | 26812625.58 | 13547614.08 | 19780800 | 12554446.08 | 32847966.72 | 1552899.6 | 9881712 | 44330496 | 19729227.6 | 6161250 | 22008384 | 23281020 | 19712463.29 | 0 | 49053128.04 | 9392419.79 | 22819376.19 | 23801102.4 | 1922079.6 | 8215776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128517120 | 0 | 7875100.8 | 0 | 5810112 | 0 | 0 | 0 | 2341368 | 4039075.84 | 1012042.5 | 2323525.21 | 845215 | 5969372.16 | 0 | 0 | 0 | 4770746.88 | 1205717.68 | 6450375.6 | 0 | 6629491.44 | 1745169 | 8464583.22 | 4032726.5 | 852019.2 | 0 | 150185.772 | 0 | 0 | 23106544 | 0 | 1112670 | 0 | 0 | 6496919.88 | 0 | 0 | 5209142.4 | 0 | 0 | 9229715.55 | 21598272 | 8766392.67 | 24576215.04 | 15484469.76 | 13697129.44 | 0 | 369987.15 | 17115949.44 | 98058991 | 0 | 0 | 0 | 0 | 0 | 0 |  | 740510374.96 | 437856345.132 | 1178366720.092 | 90015386.442 | 128517120 | 50913514.48 | 79516267.53 | 618250439.97 | 121165535 | 199702.8 | 1112670 | 64720170.12 | 21880800 | 2075113.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 284 | 253 |  | 0 | 225 | 143 | 90 | 79 | 55 | 325 | 0 | 0 | 90 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 45 | 0 | 0 | 30 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 93 | 49 | 22 | 2 | 0 | 0 | 0 | 275 | 0 | 180 | 8 | 90 | 29 | 0 | 0 | 43 | 0 | 0 | 43 | 19 | 7 | 25 | 20 | 122 | 66 | 0 | 0 | 1 | 44 | 30 | 47 | 46 | 163 | 0 | 30 | 72 | 0 | 220 | 0 | 38 | 9 | 260 | 0 | 11 | 0 | 277 | 0 | 0 | 176 | 0 | 149 | 19 | 38 | 200 | 118 | 280 | 94 | 90 | 105 | 2 | 285 | 0 | 94 | 100 | 10 | 50 | 394 | 104 | 46 | 162 | 96 | 0 | 17 | 0 | 17 | 55 |  | 924 | 0 | 320 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 20 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 32 | 72 | 0 | 5 | 95 | 750 | 210 | 0 | 0 | 5 | 69 | 0 |  | 11587 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 250 | 95 | 0 | 280 | 223 | 0 | 0 | 225 | 125 | 92 | 95 | 55 | 333 | 0 | 0 | 85 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 60 | 51 | 45 | 94 | 50 | 22 | 16 | 0 | 0 | 0 | 275 | 0 | 183 | 8 | 90 | 32 | 5 | 0 | 43 | 0 | 18 | 42 | 19 | 5 | 32 | 20 | 128 | 98 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 50 | 75 | 0 | 220 | 0 | 0 | 10 | 305 | 11 | 11 | 200 | 275 | 302 | 100 | 166 | 100 | 149 | 0 | 83 | 200 | 134 | 280 | 105 | 105 | 105 | 0 | 282 | 54 | 110 | 110 | 9 | 91 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 64 | 55 |  | 923 | 0 | 320 | 0 | 80 | 0 | 0 | 0 | 44 | 65 | 32 | 86 | 33 | 32 | 0 | 0 | 0 | 34 | 14 | 84 | 0 | 50 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 8 | 0 | 0 | 191 | 0 | 0 | 100 | 0 | 0 | 414 | 105 | 156 | 113 | 105 | 107 | 0 | 0 | 113 | 1030 | 212 | 0 | 17 | 0 | 0 | 115 |  | 13954 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 0 | 350 | 0 | 0 | 225 | 150 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 50 | 22 | 25 | 0 | 0 | 0 | 280 | 0 | 225 | 8 | 90 | 35 | 0 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 21 | 166 | 140 | 0 | 20 | 0 | 44 | 30 | 51 | 50 | 163 | 0 | 60 | 80 | 0 | 220 | 0 | 41 | 10 | 341 | 8 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 280 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 110 | 113 | 100 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 100 | 55 |  | 931 | 0 | 320 | 0 | 115 | 200 | 0 | 0 | 35 | 80 | 32 | 86 | 33 | 110 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 50 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 50 | 22 | 15 | 0 | 0 | 0 | 280 | 0 | 200 | 8 | 90 | 35 | 0 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 21 | 143 | 120 | 0 | 20 | 1.6 | 44 | 30 | 51 | 50 | 163 | 0 | 60 | 80 | 0 | 220 | 0 | 38 | 10 | 300 | 8 | 11 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 280 | 115 | 100 | 105 | 5 | 290 | 54 | 110 | 110 | 113 | 100 | 400 | 104 | 50 | 162 | 110 | 0 | 35 | 30 | 100 | 55 |  | 931 | 0 | 320 | 0 | 16 | 200 | 0 | 0 | 35 | 0 | 32 | 86 | 33 | 50 | 0 | 0 | 0 | 35 | 30 | 85 | 0 | 50 | 40 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 800 | 220 |  | 0 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 0 | 337 | 0 | 0 | 225 | 145 | 91 | 62 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 26 | 0 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 76 | 42 | 22 | 9 | 0 | 0 | 0 | 270 | 0 | 161 | 8 | 91 | 16 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 110 | 80 | 0 | 0 | 0 | 43 | 22 | 0 | 50 | 110 | 0 | 60 | 0 | 0 | 219 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 2 | 38 | 50 | 24 | 80 | 0 | 0 | 51 | 2 | 245 | 35 | 92 | 88 | 9 | 42 | 400 | 35 | 4 | 35 | 97 | 0 | 0 | 0 | 0 | 55 | 0 | 915 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 423 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 162 | 0 | 0 | 1 | 52 | 0 | 0 |  |  |  |  | 97872196 |  | 0
97872196
| Minimum Generation |  | 10066 | 8:00
| Highest Generation |  | 13954 | 21:00
| Day Peak Generation |  | 11587 | 12:00
| Evening Peak Generation |  | 13954 | 21:00
| HVDC Max Flow |  | 924 | 6:00
| HVDC EvPeak Flow |  | 923 | 21:00
| Load factor L.F |  | 87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-17
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11587 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8165 | MW
Evening Peak Generation : |  | 13954 | MW Hour : | 21:00 | Available Max Generation : |  | 15063 | MW
E.P. Demand (at gen end) : |  | 13954 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13954 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1063 | MW
Total Gen. (MKWH) : |  | 291.3479 | System Load Factor : | 87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 206 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-17
Actual : | 74.01 | Ft.(MSL) , | Rule curve : | 78.96 | Ft.( MSL )
Gas Consumed : | Total = | 1028.77 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 140928900.922
: |  | Coal : | 121165535 | Oil : | 763599547.62 | Total : | 1025693983.542
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4940.3686 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1601.0861 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1562.4505 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1398.8468 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1275.7827 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1047.3215 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.4941 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 315.5883 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 769.3999 |  |  | 0 | 0%
Total | 0 |  | 13423.3385 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Haripur 412 MW EGCB
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1,3
9) Shahjibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Dohazari-Sikalbaha 132 kV Ckt-2 was under shut down from 08:26 to 09:48 for C/M.
b) Jhenaidah(New) 230/132 kV T-01 transformer was shut down at 09:06 for D/W.
c) Natore 132/33 kV T-1 transformer was under shut down from 09:10 to 11:45 due to high temperature.
d) Payra 400/132 kV T-01 transformer was shut down at 10:01 for D/W.
e) Ghorashal 230/132 kV AT-02 transformer was under shut down from 11:33 to 14:12 for C/M.
f) Bogura-Naogaon 132 kV both Ckts tripped at 09:08 Ckt-2 from both ends & Ckt-1 from Bogura end | [5 empty] | About 147 MW power interruption occurred under Naogaon,
and were switched on at 09:46(Ckt-2) & 12:56(Ckt-1). | [5 empty] | Joypurhat & Niamatpur S/S area from 09:08 to 09:46.
g) Kachua 132/33 kV T-2 transformer was under shut down from 13:32 to 18:38 due to R/H maintenance
at 33 kV Bus isolator(incomer).
h) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 14:40 to 16:01 for tree trimming.
i) Sonargaon 132/33 kV T-2 transformer was under shut down from 16:21 to 16:58 due to R/H maintenance
at 33 kV Bus DS of 33 kV Headquarter PBS feeder.
j) Haripur 230/132 kV T-02 transformer was switched on at 17:28.
k) Chowddagram 132/33 kV T-1 transformer was under shut down from 15:22 to 17:28 for C/M.
l) Rajshahi(Old)-Rajshahi(New) 132 kV Ckt-1 tripped at 17:45 from Rajshahi(Old) end showing Dist. Z1, C-φ
and was switched on at 17:55.
m) Polashbari-Mohasthangar 132 kV Ckt-1 tripped at 04:22(17/05/2022) from both ends showing Dist. R-φ,
SOTF at Polashbari end Dist. Z1, A-φ, AR block at Mohasthangar end and was switched on at 07:16(17/05/2022).
n) Bogura-Sherpur 132 kV Ckt-1 tripped at 04:48(17/05/2022) showing AR block, Z1, A,C-φ and was
switched on at 05:13(17/05/2022).
o) Bogura-Confidence-1 P.P. 132 kV Ckt tripped at 04:48(17/05/2022) showing Dist. Z1, B-φ and was
switched on at 05:12(17/05/2022).
p) 33 kV side of Mongla 132/33 kV T-1 & T-2 transformer tripped at 04:54(17/05/2022) due to 33 kV WZPDCL | [5 empty] | About 28 MW power interruption occurred under
feeder fault and T-1 was switched on at 06:07(17/05/2022). | [5 empty] | Mongla S/S area from 04:54(17/05/2022) to 06:07.
q) Tongi 230/132 kV T-02 transformer was shut down at 05:26(17/05/2022) for C/M.
r) Rampal 400/230 kV transformer was shut down at 06:23(17/05/2022) for C/M.
s) Haripur 412 MW ST was shut down at 04:47(17/05/2022) & GT at 05:01(17/05/2022) for maintenance.
t) B.Baria-Shahjibazar 132 kV Ckt tripped at 07:50(17/05/2022) from B.Baria end showing Dist. Z1, SOTF.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4205250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6082545
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2250863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 280 | 7499780 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 223 | 6350000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5075100 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 92 | 2133120 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 3144727 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 95 | 1919808 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1230869
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 445140
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 85 | 1680000 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7768567
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1554336 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1008360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2873280 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1171123
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1191184
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1143420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 617300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 639700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1070400 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 5622871
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 302 | 1579071
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 810264
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 750864
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3338208
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2463600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2426880
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3828960
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1194480
| Dhaka area Total |  |  |  | 5898 | 3940 | 83070070
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 349228
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132840
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1150080
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 0 | 739640 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4881783
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2263199
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 425336 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 338339 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 45 | 578160 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 83 | 1212480 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 531888
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 454560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 1907520 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32844
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 282 | 6488509 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1078349
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2596061 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 91 | 1233600
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 2324673 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1388 | 28719089
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4489000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6974900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 32 | 716040 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 36000 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 969742
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 134 | 2798472 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 18 | 442280
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2154840 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4085760
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436248
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 171540 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2917440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 746300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 939427 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 472500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 742272
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 110 | 2384880
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 224280 | lube oil shortage.
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 747000 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 64 | 1217280 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1652 | 33883655
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 98 | 2170560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 391140
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 166 | 3804000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 2413200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 240330
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 513600
| Mymensingh Area Total |  |  |  | 622 | 413 | 9542380
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1035000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 689856 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3658254
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 465000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 50 | 1031256 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 255800
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 856512
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1767360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5242790
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 460420 | gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 11 | 231648
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7046000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 280 | 6625000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 233100
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9283400
| Sylhet Area Total |  |  |  | 2477 | 1649 | 38881396
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22312000
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 80 | 739200 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 44 | 223200 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 385408 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7500096
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 97125 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 306240
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2068800
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1640304
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 632500
| Khulna Area Total |  |  |  | 2384 | 1774 | 35904873
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 611616 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 33 | 545300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2056217 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1030 | 22336900 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 212 | 4891473
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 99600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1410 | 30541106
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 484832 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 14 | 118673 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 490347
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 180100 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4921909
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9322945
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 415745 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 443760
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 198396
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 873538
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 84 | 728856 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 156 | 515367 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2589696
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2316096
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26640
| Rajshahi Area Total |  |  |  | 2129 | 1323 | 23626900
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Reserve.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4263200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 39000 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1765094 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33483
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1077696
| Rangpur Area Total |  |  |  | 720 | 405 | 7178473
| Total |  |  |  | 21584 | 13954 | 291347942
| Eastern Grid Total |  |  |  | 14393 | 9042 | 194096590
| Western Grid Total |  |  |  | 7191 | 4912 | 97251352
| National Grid Total |  |  |  | 21584 | 13954 | 291347942
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-16
(a) ENTIRE EASTERN GRID : |  | 9063.12 | MW | (b) ENTIRE WESTERN GRID : |  | 4307 | MW
i) Dhaka area |  | 4884.54 | MW | i) Khulna area |  | 1666.4 | MW
ii) Chittagong area |  | 1439.58 | MW | ii) Rajshahi area |  | 1466.6 | MW
iii) Comilla area |  | 1267 | MW | iii) Barisal area |  | 418 | MW
iv) Mymensingh area |  | 1025 | MW | iv) Rangpur area |  | 756 | MW
v) Sylhet area |  | 447 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13370.12 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 16:00 | Hasnabad | 69 | 00:00 | Palashbari | 122 | 00:00
Agargaon | 98 | 13:00 | Hathazari | 102 | 21:00 | Panchagarh | 58 | 19:30
Agrabad | 88 | 15:00 | Ishurdi | 80 | 19:30 | Patuakhali | 131 | 22:00
AKS | 17 | 18:00 | Jaldhaka | 56 | 19:00 | PHP | 5 | 10:00
AKSML | 116 | 23:00 | Jamalpur | 150 | 04:00 | Purbachal | 19 | 19:00
Amnura | 53 | 21:00 | Jashore | 131 | 19:30 | Purbasadipur | 101 | 20:00
Ashuganj | 38 | 11:00 | Jhenaidah | 124 | 20:00 | Rahim | 525 | 01:00
Bagerhat | 112 | 23:00 | Joydebpur | 187 | 00:00 | Rajbari | 70 | 23:00
Bakulia | 134 | 15:00 | Joypurhat | 60 | 19:30 | Rajendrapur | 110 | 01:00
Banani | 53 | 15:00 | Juldah | 22 | 14:00 | Rajshahi | 173 | 21:00
Bangabhaban | 24 | 11:00 | Kabirpur | 291 | 18:00 | Rajshahi | 35 | 22:00
Barapukuria | 48 | 20:00 | Kachua | 76 | 22:00 | Ramganj | 124 | 19:00
Barguna | 20 | 00:00 | Kallyanpur | 108 | 19:00 | Rampur | 21 | 00:00
Barishal | 110 | 21:00 | Kalurghat | 6 | 16:00 | Rangamati | 14 | 19:00
Barishal | 70 | 20:00 | Kamrangirchar | 70 | 13:00 | Rangpur | 133 | 19:30
Baroaulia | 81 | 20:00 | Kaptai | 5 | 19:00 | Ruppur | 4.6 | 18:00
Baroirhat | 61 | 20:00 | Kazla | 86 | 16:00 | Saidpur | 86 | 20:00
Bashundhara | 190 | 16:00 | Keranigonj | 90 | 23:00 | Satkhira | 128 | 21:00
BashundharaCement | 2 | 00:00 | Khagrachori | 28 | 21:00 | Satmasjid | 103 | 19:00
Beanibazar | 40 | 19:00 | Khulna | 93 | 19:30 | Savar | 199 | 16:00
Benapole | 54 | 21:00 | Khulshi | 162 | 23:00 | Shahjadpur | 116 | 19:30
Bhaluka | 144 | 05:00 | Kishoreganj | 146 | 04:00 | Shahjibazar | 115 | 22:00
Bhandaria | 59 | 21:00 | Kodda | 342 | 15:00 | Shahmirpur | 45.3 | 20:00
Bhangura | 36 | 19:30 | KSRM | 31.95 | 10:00 | Shariatpur | 78 | 23:00
Bheramara(GK) | 60 | 20:00 | Kulaura | 44 | 19:00 | Sherpur | 132 | 22:00
Bhulta | 200 | 17:00 | Kurigram | 60 | 00:00 | Shikalbaha | 29 | 19:00
Bog-Sherpur | 64 | 20:00 | Kushtia | 140 | 19:30 | Shitalakhya | 128 | 11:00
Bogura | 176 | 21:00 | Lalbag | 77 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 43 | 22:00 | Lalmonirhat | 42 | 19:30 | Shyampur | 162 | 12:00
Brahmanbaria | 160 | 19:00 | Madanganj | 186 | 18:30 | Siddhirganj | 116 | 16:00
BSRM | 153 | 13:00 | Madaripur | 114 | 23:00 | Sirajganj | 110 | 20:00
Cantonment | 154 | 19:00 | Madartek | 88 | 23:00 | Sonargaon | 84 | 23:00
Chandpur | 81 | 21:00 | Madunaghat | 63 | 19:00 | Sreemongol | 58 | 19:30
Chandraghona | 34 | 20:00 | Magura | 62 | 21:00 | Srinagar | 47.2 | 22:00
Chapai | 68 | 21:00 | Mahasthangarh | 72 | 22:00 | SSM | 12 | 06:00
Charsaidpur | 23 | 20:00 | Manikganj | 90 | 00:00 | Sunamganj | 41 | 19:30
Chauddagram | 56 | 22:00 | Maniknagar | 90 | 13:00 | Sylhet | 137 | 19:00
Chhatak | 20 | 20:00 | Matarbari | 43 | 20:00 | Tangail | 206 | 23:00
Chowmuhani | 230 | 23:00 | Matuail | 63 | 16:00 | Thakurgaon | 71 | 20:00
Chuadanga | 107 | 20:00 | Millgate | 60 | 11:00 | TK | 20.8 | 21:00
Coxsbazar | 126 | 19:00 | Mirpur | 139 | 19:00 | Tongi | 140 | 13:00
Cumilla(N) | 163 | 21:00 | Mirsorai | N/A | N/A | Ullon | 41 | 21:00
Cumilla(S) | 168 | 19:30 | Mithapukur | 30 | 00:00 | Uttara | 102 | 16:00
Daudkandi | 151 | 20:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 14:00
Dhaka | 38 | 11:00 | Mogbazar | 139 | 15:00 | Zigatola | 46 | 16:00
Dhamrai | 132 | 19:30 | Mongla | 34 | 00:00
Dhanmondi | 180 | 13:00 | Motijheel | 40 | 13:00
Dohazari | 108 | 21:00 | Munshiganj | 104 | 00:00
Faridpur | 153 | 23:00 | Mymensingh | 235 | 19:30
Fatullah | 69 | 15:00 | Naogaon | 132 | 21:00
Fenchuganj | 46 | 19:30 | Narail | 58 | 19:30
Feni | 128 | 22:00 | Narinda | 76 | 13:00
Ghorashal | 62 | 23:00 | Narshingdi | 188 | 21:00
Goalpara | 29 | 23:00 | Natore | 140 | 22:00
Gollamari | 58 | 13:00 | Nawabganj | 57.8 | 22:00
Gopalganj | 105 | 22:00 | Netrakona | 117 | 00:00
GPH | 93 | 21:00 | New | 83.2 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 8:00 | 403 | 14:00 | Kaliakoir | 398 | 0.77083 | 382 | 0.5
| Bheramara | 399 | 8:00 | 393 | 15:00 | Bhulta | 399 | 0.083333 | 384 | 0.5
| Ashuganj(N) | 404 | 3:00 | 390 | 12:00 | Gopalganj | 415 | 0.625 | 400 | 0.95833
| Payra | 419 | 18:00 | 406 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 7:00 | Hathazari | 240 | 18:00 | 230 | 24:00
| Ishurdi | 235 | 8:00 | 227 | 19:30 | Megnaghat | 231 | 5:00 | 227 | 13:00
| Ashuganj | 240 | 1:00 | 235 | 9:00 | Fenchuganj | 243 | 2:00 | 238 | 19:00
| Serajganj | 236 | 23:00 | 230 | 19:00 | Siddhirganj | 232 | 3:00 | 222 | 11:00
| Baghabari | 233 | 5:00 | 227 | 19:00 | Maniknagar | 229 | 3:00 | 218 | 12:00
| Barapukuria | 232 | 23:00 | 220 | 19:30 | Agargaon | 229 | 18:30 | 218 | 12:00
| Bogra | 235 | 23:00 | 222 | 19:30 | Barisal | 238 | 18:30 | 229 | 22:00
| Rajshahi | 238 | 9:00 | 226 | 20:00 | Bhola 225 MW | 244 | 11:00 | 229 | 22:00
| Khulna South | 232 | 18:00 | 218 | 24:00 | AKSML | 240 | 18:00 | 227 | 24:00
| Rampura | 228 | 1:00 | 219 | 12:00 | BSRM | 236 | 5:00 | 226 | 24:00
| Haripur | 227 | 3:00 | 219 | 12:00 | Bibiyana | 240 | 3:00 | 236 | 12:00
| Hasnabad | 228 | 21:00 | 219 | 17:00 | Bhulta | 231 | 5:00 | 221 | 12:00
| Shyampur | 228 | 2:00 | 219 | 12:00 | Ashuganj (S) | 238 | 2:00 | 230 | 17:00
| Aminbazar | 227 | 1:00 | 221 | 2:00 | Kaliakoir | 231 | 3:00 | 219 | 12:00
| Tongi | 226 | 1:00 | 219 | 11:00 | GPH | 239 | 18:00 | 228 | 24:00
| Comilla (N) | 232 | 21:00 | 225 | 12:00 | Jhenaidah | 227 | 8:00 | 214 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 22:00 | 125 | 09:00 | Manikganj | 131 | 20:00 | 121 | 12:00
| Agargaon | 137 | 03:00 | 128 | 11:00 | Maniknagar | 131 | 05:00 | 123 | 11:00
| Agrabad | 135 | 09:00 | 130 | 15:00 | Matarbari | 124 | 10:00 | 109 | 23:00
| AKS | 136 | 18:00 | 130 | 13:00 | Matuail | 136 | 01:00 | 132 | 12:00
| Aminbazar | 137 | 00:00 | 132 | 08:00 | Millgate | 135 | 02:00 | 125 | 12:00
| Amnura | 130 | 17:00 | 123 | 04:00 | Mirpur | 137 | 03:00 | 130 | 08:00
| Ashuganj | 137 | 06:00 | 133 | 00:00 | Mithapukur | 135 | 23:00 | 126 | 20:00
| Bagerhat | 135 | 18:00 | 126 | 00:00 | Modern | 137 | 18:00 | 130 | 14:00
| Bakulia | 136 | 18:00 | 130 | 00:00 | Mogbazar | 134 | 21:00 | 125 | 09:00
| Banani | 135 | 02:00 | 124 | 12:00 | Mongla | 136 | 18:00 | 126 | 00:00
| Bangabhaban | 131 | 02:00 | 123 | 12:00 | Motijheel | 131 | 02:00 | 123 | 12:00
| Barapukuria | 137 | 23:00 | 128 | 19:30 | Munshiganj | 139 | 02:00 | 133 | 08:00
| Barguna | 137 | 18:30 | 129 | 00:00 | Mymensingh | 132 | 08:00 | 116 | 19:00
| Barishal | 136 | 09:00 | 129 | 23:00 | Naogaon | 138 | 23:00 | 121 | 20:00
| Barishal | 138 | 18:30 | 130 | 22:00 | Narail | 133 | 09:00 | 124 | 19:30
| Baroaulia | 137 | 21:00 | 131 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 10:00 | 128 | 00:00 | Narshingdi | 132 | 13:00 | 128 | 12:00
| Bashundhara | 135 | 02:00 | 124 | 12:00 | Natore | 134 | 23:00 | 127 | 19:30
| BashundharaCement | 138 | 21:00 | 133 | 08:00 | Nawabganj | 138 | 03:00 | 129 | 12:00
| Beanibazar | 136 | 23:00 | 131 | 19:00 | Netrakona | 129 | 18:00 | 115 | 00:00
| Benapole | 133 | 18:00 | 126 | 15:00 | New | 135 | 03:00 | 125 | 12:00
| Bhaluka | 130 | 08:00 | 110 | 19:00 | Niamatpur | 139 | 23:00 | 117 | 20:00
| Bhandaria | 134 | 10:00 | 124 | 00:00 | Noapara | 137 | 18:00 | 130 | 00:00
| Bhangura | 138 | 06:00 | 132 | 20:00 | Pabna | 135 | 06:00 | 129 | 20:00
| Bheramara | 136 | 06:00 | 131 | 20:00 | Palashbari | 133 | 17:00 | 123 | 19:30
| Bheramara(GK) | 137 | 07:00 | 133 | 19:30 | Panchagarh | 136 | 23:00 | 125 | 10:00
| Bhulta | 129 | 21:00 | 126 | 12:00 | Patuakhali | 136 | 18:30 | 130 | 00:00
| Bog-Sherpur | 138 | 23:00 | 128 | 20:00 | PHP | 133 | 09:00 | 127 | 23:00
| Bogura | 137 | 08:00 | 128 | 21:00 | Purbachal | 135 | 02:00 | 123 | 12:00
| Bogura | 139 | 23:00 | 129 | 20:00 | Purbasadipur | 135 | 00:00 | 126 | 10:00
| Brahmanbaria | 133 | 07:00 | 126 | 19:00 | Rahim | 137 | 03:00 | 133 | 15:00
| Cantonment | 136 | 03:00 | 127 | 17:00 | Rajbari | 134 | 08:00 | 127 | 19:30
| Chandpur | 137 | 18:30 | 129 | 06:00 | Rajendrapur | 133 | 04:00 | 124 | 09:00
| Chandraghona | 138 | 18:00 | 131 | 23:00 | Rajshahi | 130 | 17:00 | 124 | 19:30
| Chapai | 131 | 17:00 | 124 | 12:00 | Rajshahi | 129 | 07:00 | 123 | 15:00
| Charsaidpur | 140 | 22:00 | 133 | 12:00 | Ramganj | 132 | 10:00 | 124 | 19:00
| Chauddagram | 134 | 10:00 | 129 | 08:00 | Rampur | 135 | 22:00 | 130 | 15:00
| Chhatak | 135 | 22:00 | 130 | 19:30 | Rampura | 134 | 21:00 | 124 | 09:00
| Chowmuhani | 131 | 13:00 | 120 | 23:00 | Rangamati | 135 | 03:00 | 131 | 15:00
| Chuadanga | 132 | 08:00 | 120 | 19:30 | Rangpur | 135 | 06:00 | 124 | 19:30
| Coxsbazar | 124 | 18:00 | 107 | 23:00 | Ruppur | 136 | 05:00 | 131 | 19:30
| Cumilla(N) | 139 | 17:00 | 132 | 12:00 | Saidpur | 135 | 00:00 | 124 | 20:00
| Cumilla(S) | 136 | 18:00 | 127 | 19:00 | Satkhira | 135 | 18:00 | 126 | 19:30
| Daudkandi | 138 | 21:00 | 130 | 06:00 | Satmasjid | 136 | 02:00 | 128 | 12:00
| Dhaka | 134 | 21:00 | 125 | 09:00 | Savar | 138 | 01:00 | 130 | 12:00
| Dhamrai | 133 | 03:00 | 124 | 12:00 | Shahjadpur | 140 | 06:00 | 135 | 19:30
| Dhanmondi | 137 | 01:00 | 131 | 11:00 | Shahjibazar | 136 | 07:00 | 132 | 00:00
| Dohazari | 132 | 18:00 | 121 | 23:00 | Shahmirpur | 136 | 18:00 | 130 | 23:00
| Faridpur | 138 | 09:00 | 128 | 20:00 | Shariatpur | 135 | 18:00 | 125 | 23:00
| Fatullah | 136 | 20:00 | 130 | 11:00 | Sherpur | 135 | 08:00 | 120 | 19:00
| Fenchuganj | 138 | 07:00 | 134 | 19:00 | Shikalbaha | 136 | 05:00 | 131 | 15:00
| Feni | 134 | 10:00 | 129 | 23:00 | Shikalbaha | 135 | 03:00 | 131 | 15:00
| Ghorashal | 139 | 01:00 | 136 | 23:00 | Shitalakhya | 139 | 02:00 | 132 | 09:00
| Goalpara | 138 | 18:00 | 132 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 137 | 18:00 | 132 | 00:00 | Shyampur | 135 | 04:00 | 128 | 12:00
| Gopalganj | 139 | 18:00 | 134 | 01:00 | Shyampur | 136 | 21:00 | 129 | 11:00
| Gopalganj_I | 138 | 18:30 | 133 | 01:00 | Siddhirganj | 137 | 02:00 | 131 | 12:00
| Gulshan | 133 | 21:00 | 123 | 10:00 | Sirajganj | 136 | 04:00 | 128 | 19:30
| Halishahar | 137 | 18:00 | 130 | 14:00 | Sonargaon | 138 | 21:00 | 132 | 12:00
| Haripur | 137 | 03:00 | 132 | 13:00 | Sreemongol | 139 | 07:00 | 133 | 19:00
| HaripurSBU | 137 | 04:00 | 132 | 12:00 | Srinagar | 138 | 04:00 | 130 | 12:00
| Hasnabad | 137 | 00:00 | 132 | 12:00 | SSM | 138 | 21:00 | 133 | 04:00
| Hathazari | 139 | 21:00 | 134 | 15:00 | Sunamganj | 133 | 08:00 | 128 | 19:00
| Ishurdi | 136 | 07:00 | 131 | 20:00 | Sylhet | 134 | 04:00 | 132 | 12:00
| Jaldhaka | 134 | 00:00 | 123 | 19:00 | Tangail | 134 | 05:00 | 124 | 19:00
| Jamalpur | 138 | 08:00 | 124 | 19:00 | Thakurgaon | 137 | 23:00 | 124 | 08:00
| Jashore | 134 | 18:30 | 126 | 23:00 | TK | 137 | 18:00 | 131 | 14:00
| Jhenaidah | 137 | 09:00 | 128 | 20:00 | Tongi | 135 | 03:00 | 127 | 11:00
| Jhenaidah | 137 | 08:00 | 129 | 20:00 | Ullon | 134 | 22:00 | 124 | 10:00
| Joydebpur | 141 | 13:00 | 135 | 15:00 | Uttara | 138 | 02:00 | 128 | 12:00
| Joypurhat | 138 | 23:00 | 119 | 11:00 | UttaraNew | 138 | 02:00 | 129 | 12:00
| Juldah | 137 | 21:00 | 131 | 15:00 | Zigatola | 137 | 03:00 | 130 | 12:00
| Kabirpur | 134 | 01:00 | 122 | 15:00
| Kachua | 135 | 01:00 | 130 | 07:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 138 | 03:00 | 131 | 12:00
| Kalurghat | 138 | 18:00 | 130 | 13:00
| Kamrangirchar | 138 | 21:00 | 130 | 12:00
| Kaptai | 135 | 01:00 | 132 | 19:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 788 | 8325 | 4422 | 12747 |  |  |  | QF-LDC-11
0:30 | 593 | 8304.5 | 4254.5 | 12559 | Date: | 2022-05-16
1:00 | 398 | 8284 | 4087 | 12371
1:30 | 310 | 8269 | 3983.5 | 12252.5
2:00 | 222 | 8254 | 3880 | 12134
2:30 | 214 | 8181.5 | 3805.5 | 11987 | [5 empty] | Gen. at Eve. Peak | 13954 | 13954 MW (21:00 )
3:00 | 206 | 8109 | 3731 | 11840 | [6 empty] | 21:00
3:30 | 246 | 8000.5 | 3693 | 11693.5 | [5 empty] | Gen. at Day Peak | 11587 | 11587 MW (12:00 )
4:00 | 286 | 7892 | 3655 | 11547 | [6 empty] | 12:00
4:30 | 316 | 7725 | 3620.5 | 11345.5 | [5 empty] | Highest Generation | 13954
5:00 | 346 | 7558 | 3586 | 11144 | [6 empty] | 21:00
5:30 | 441 | 7173 | 3519 | 10692
6:00 | 536 | 6788 | 3452 | 10240
6:30 | 532 | 6756.5 | 3451.5 | 10208
7:00 | 528 | 6725 | 3451 | 10176
7:30 | 599 | 6694.5 | 3426.5 | 10121
8:00 | 670 | 6664 | 3402 | 10066
8:30 | 657 | 6855.5 | 3399 | 10254.5
9:00 | 644 | 7047 | 3396 | 10443
9:30 | 516 | 7354.5 | 3248.5 | 10603
10:00 | 388 | 7662 | 3101 | 10763
10:30 | 539 | 7792 | 3308.5 | 11100.5
11:00 | 690 | 7922 | 3516 | 11438
11:30 | 647 | 7929 | 3583.5 | 11512.5
12:00 | 604 | 7936 | 3651 | 11587
12:30 | 610 | 7981 | 3830.5 | 11811.5
13:00 | 616 | 8026 | 4010 | 12036
13:30 | 628 | 8039.5 | 4009 | 12048.5
14:00 | 640 | 8053 | 4008 | 12061
14:30 | 629 | 8200.5 | 4021 | 12221.5
15:00 | 618 | 8348 | 4034 | 12382
15:30 | 642 | 8384 | 4027.5 | 12411.5
16:00 | 666 | 8420 | 4021 | 12441
16:30 | 731 | 8240.5 | 4031 | 12271.5
17:00 | 796 | 8061 | 4041 | 12102
17:30 | 694 | 8007.5 | 3894.5 | 11902
18:00 | 592 | 7954 | 3748 | 11702
18:30 | 525 | 8484 | 4039.5 | 12523.5
19:00 | 458 | 9014 | 4331 | 13345
19:30 | 432 | 9128 | 4816 | 13944
20:00 | 352 | 9074 | 4853 | 13927 |  |  |  | Executive Engineer
20:30 | 358 | 9058 | 4882.5 | 13940.5 |  |  |  | Network Operation Division
21:00 | 364 | 9042 | 4912 | 13954
21:30 | 442 | 8932.5 | 4856.5 | 13789
22:00 | 520 | 8823 | 4801 | 13624 |  |  |  |  | Page 6 of 7
22:30 | 597 | 8688.5 | 4703 | 13391.5
23:00 | 674 | 8554 | 4605 | 13159
23:30 | 731 | 8439.5 | 4513.5 | 12953
24:00 | 788 | 8325 | 4422 | 12747
13954 MW (21:00 )
11587 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-16 |  | Energy |  | 291347942
[13 empty] | 2022-05-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3876 | 923 | 2033 | 50 | 4054 | 1184 | 30 | 0 | 465 | 132 | 0 | 0
0:30 | 3824 | 919.5 | 2059 | 25 | 4009.5 | 1169.5 | 30 | 0 | 394.5 | 128 | 0 | 0 | Date: | 2022-05-16
1:00 | 3772 | 916 | 2085 | 0 | 3965 | 1155 | 30 | 0 | 324 | 124 | 0 | 0
1:30 | 3764 | 917 | 2089 | 0 | 3941.5 | 1135 | 30 | 0 | 254 | 122 | 0 | 0 | [8 empty] | Total Energy | 291.3479 | Total Energy Gen 291.348 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 291.348 MKWHr
2:00 | 3756 | 918 | 2093 | 0 | 3918 | 1115 | 30 | 0 | 184 | 120 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3772 | 920 | 2089 | 0 | 3792 | 1095 | 30 | 0 | 169 | 120 | 0 | 0 | [8 empty] | Energy Requirement | 291.3479
3:00 | 3788 | 922 | 2085 | 0 | 3666 | 1075 | 30 | 0 | 154 | 120 | 0 | 0
3:30 | 3806.5 | 922.5 | 2090.5 | 0 | 3534 | 1050 | 30 | 0 | 143 | 117 | 0 | 0 | [6 empty] | Shortage
4:00 | 3825 | 923 | 2096 | 0 | 3402 | 1025 | 30 | 0 | 132 | 114 | 0 | 0
4:30 | 3852 | 922.5 | 2091 | 0 | 3187 | 1020 | 30 | 0 | 132 | 111 | 0 | 0
5:00 | 3879 | 922 | 2086 | 0 | 2972 | 1015 | 30 | 0 | 132 | 108 | 0 | 0
5:30 | 3862 | 923 | 2073.5 | 0 | 2580 | 1000 | 30 | 0 | 115 | 106 | 2.5 | 0
6:00 | 3845 | 924 | 2061 | 0 | 2188 | 985 | 30 | 0 | 98 | 104 | 5 | 0
6:30 | 3827 | 923.5 | 2059 | 0 | 2152.5 | 985 | 30 | 0 | 115 | 102 | 14 | 0 |  |  |  |  | Coal
7:00 | 3809 | 923 | 2057 | 0 | 2117 | 985 | 30 | 0 | 132 | 100 | 23 | 0
7:30 | 3811 | 923.5 | 2027 | 0 | 2113 | 960 | 30 | 0 | 115 | 103 | 38.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3813 | 924 | 1997 | 0 | 2109 | 935 | 30 | 0 | 98 | 106 | 54 | 0
8:30 | 3816.5 | 923.5 | 2013 | 0 | 2231.5 | 940 | 30 | 0 | 115 | 109 | 76 | 0
9:00 | 3820 | 923 | 2029 | 0 | 2354 | 945 | 30 | 0 | 132 | 112 | 98 | 0
9:30 | 3762.5 | 923.5 | 1936.5 | 0 | 2715.5 | 910 | 30 | 0 | 115 | 114 | 96 | 0
10:00 | 3705 | 924 | 1844 | 0 | 3077 | 875 | 30 | 0 | 98 | 116 | 94 | 0
10:30 | 3735 | 924 | 1957 | 0 | 3190 | 885 | 30 | 0 | 132 | 118 | 129.5 | 0
11:00 | 3765 | 924 | 2070 | 0 | 3303 | 895 | 30 | 0 | 166 | 120 | 165 | 0
11:30 | 3746 | 924 | 2068.5 | 0 | 3391 | 910 | 30 | 0 | 166 | 121 | 156 | 0
12:00 | 3727 | 924 | 2067 | 0 | 3479 | 925 | 30 | 0 | 166 | 122 | 147 | 0
12:30 | 3711 | 924 | 2030 | 66.5 | 3660.5 | 945 | 32.5 | 0 | 177 | 121 | 144 | 0
13:00 | 3695 | 924 | 1993 | 133 | 3842 | 965 | 35 | 0 | 188 | 120 | 141 | 0
13:30 | 3695 | 924 | 1993 | 133 | 3842 | 965 | 35 | 0 | 188 | 120 | 141 | 0
14:00 | 3695 | 924 | 1993 | 133 | 3842 | 965 | 35 | 0 | 188 | 120 | 141 | 0
14:30 | 3704.5 | 923.5 | 2003 | 279.5 | 3816.5 | 970 | 35 | 0 | 225 | 126 | 126 | 0
15:00 | 3714 | 923 | 2013 | 426 | 3791 | 975 | 35 | 0 | 262 | 132 | 111 | 0
15:30 | 3720.5 | 922.5 | 2005 | 426 | 3811.5 | 975 | 35 | 0 | 289 | 131 | 96 | 0
16:00 | 3727 | 922 | 1997 | 426 | 3832 | 975 | 35 | 0 | 316 | 130 | 81 | 0
16:30 | 3748 | 922 | 1994 | 213 | 3868.5 | 975 | 35 | 0 | 339.5 | 128 | 59 | 0
17:00 | 3748 | 922 | 1991 | 0 | 3905 | 975 | 35 | 0 | 363 | 126 | 37 | 0
17:30 | 3728.5 | 922.5 | 1924.5 | 0 | 3818 | 970 | 35 | 0 | 358.5 | 123 | 22 | 0
18:00 | 3709 | 923 | 1858 | 0 | 3731 | 965 | 35 | 0 | 354 | 120 | 7 | 0
18:30 | 3757.5 | 923 | 1934 | 387 | 3919 | 990 | 35 | 4 | 442.5 | 128 | 3.5 | 0
19:00 | 3806 | 923 | 2010 | 774 | 4107 | 1015 | 35 | 8 | 531 | 136 | 0 | 0
19:30 | 3842 | 924 | 2057 | 955 | 4241 | 1175 | 35 | 8 | 571 | 136 | 0 | 0
20:00 | 3823 | 923 | 2063 | 952 | 4272 | 1195 | 35 | 8 | 520 | 136 | 0 | 0
20:30 | 3820.5 | 923 | 2043.5 | 955 | 4295.5 | 1200 | 17.5 | 8 | 545.5 | 132 | 0 | 0
21:00 | 3818 | 923 | 2024 | 958 | 4319 | 1205 | 0 | 8 | 571 | 128 | 0 | 0
21:30 | 3835.5 | 922.5 | 2006.5 | 743.5 | 4339.5 | 1200 | 17.5 | 8 | 585 | 131 | 0 | 0
22:00 | 3853 | 922 | 1989 | 529 | 4360 | 1195 | 35 | 8 | 599 | 134 | 0 | 0
22:30 | 3858.5 | 922 | 1962 | 390 | 4328.5 | 1190 | 32.5 | 4 | 571 | 133 | 0 | 0
23:00 | 3864 | 922 | 1935 | 251 | 4297 | 1185 | 30 | 0 | 543 | 132 | 0 | 0
23:30 | 3870 | 922.5 | 1984 | 150.5 | 4175.5 | 1184.5 | 30 | 0 | 504 | 132 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.2° C
24:00 | 3876 | 923 | 2033 | 50 | 4054 | 1184 | 30 | 0 | 465 | 132 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 291.348 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 291.348 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [12 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 0 | 35 | 30 | 30 | 347640
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | [12 empty] | 392000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 8 |  | 4 | [8 empty] | 17 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 349228
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 7 | 4 | 15 | 19 | 19 | 19 | 18 | 16 | 13 | 8 | 3 | 0 | [8 empty] | 132840
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 203 | 202 | 203 | 203 | 204 | 203 | 203 | 221 | 204 | 204 | 205 | 204 | 202 | 204 |  | 220 | 216 | 203 | 203 | 202 | 203 | 204 | 4881783
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [5 empty] | 0 | 34 | 34 | 34 | 0 | [7 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 0 |  | 338339
12 | Hathazari 100 MW peaking PP | [14 empty] | 0 | 42 | 17 | 17 |  | 60 | 60 | 60 | 60 | 60 | 60 | 12 | 425336
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 61 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2263199
| Daudkandi 200 MW PP (B.Trac) | [14 empty] | 30 | 30 | 0 |  |  | 200 | 200 | 200 | 200 | 80 | 10 |  | 742272
14 | Titas 50 MW Peaking PP | [12 empty] | 0 | 41 | 48 | 48 | 48 | 48 |  | 48 | 48 | 0 | 18 | 48 | 48 | 48 | 442280
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 336 | 335 | 335 | 335 | 337 | 280 | 280 | 280 | 333 | 300 | 331 | 325 | 325 | 320 | 320 | 326 | 328 | 330 |  | 325 | 329 | 330 | 333 | 334 | 335 | 335 | 7768567
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 298 | 293 | 293 | 95 | 45 | 45 | 45 | 45 | 212 | 283 | 277 | 275 | 265 | 248 | 260 | 263 | 260 |  | 265 | 277 | 278 | 275 | 275 | 276 | 276 | 5622871
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4205250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6082545
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 31 | 31 | 31 | 29 | 29 | 29 | 29 | 31 | 30 | 20 | 26 |  | 29 | 32 | 32 | 32 | 33 | 33 | 33 | 716040
33 | Ashuganj 225 MW CCPP | 168 | 158 | 163 | 180 | 192 | 200 | 197 | 188 | 184 | 182 | 185 | 180 | 175 | 179 | 187 | 187 | 202 | 189 |  | 186 | 186 | 188 | 183 | 188 | 190 | 193 | 4489000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 260 | 265 | 265 | 265 | 265 | 265 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 280 | 280 | 275 | 6974900
35 | Ashuganj 55 MW PP (Precision) | [17 empty] | 1 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 36000
36 | Chandpur 150 MW CCPP | 91 | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 89 | 89 | 90 | 90 | 88 | 89 | 89 | 91 | 91 | 88 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2154840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 333 | 343 | 348 | 351 | 358 | 361 | 370 | 365 | 362 | 322 | 306 | 284 | 270 | 267 | 265 | 262 | 253 | 246 |  | 276 | 282 | 276 | 280 | 283 | 283 | 300 | 7499780
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5075100
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 312 | 306 | 306 | 314 | 314 | 312 | 292 | 277 | 261 | 253 | 247 | 242 | 243 | 236 | 232 | 226 |  | 221 | 221 | 221 | 223 | 222 | 222 | 247 | 6350000
42 | RPCL 210MW CCPP | 131 | 120 | 134 | 130 | 136 | 136 | 109 | 105 | 73 | 69 | 69 | 66 | 66 | 63 | 65 | 63 | 70 | 75 |  | 105 | 105 | 99 | 98 | 101 | 106 | 105 | 2170560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 6 | 9 | 17 | 17 | 38 | 46 | 19 | 26 | 16 | 14 | 8 | 2 |  | 0 | [6 empty] | 240330
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 1035000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 689856
46 | Shajibazar 330 MW CCPP | 0
47 | Shahjibazar GTPP Unit- 8 & 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 20 | 30 | 30 | 25 | 30 | 30 | 35 | 50 | 50 |  | 50 | 60 | 50 | 50 | 60 | 60 | 55 | 856512
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 69 | 72 | 72 | 72 | 72 | 74 | 70 | 72 | 72 | 74 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1767360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 187 | 212 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5242790
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 37 | 36 | 38 | 0 | 0 | [12 empty] | 460420
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 233100
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255800
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 42 | 47 | 45 | 45 | 47 | 0 | [13 empty] | 465000
56 | Shahjahanulla 25 MW PP | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 231648
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 270 | 295 | 280 | 275 | 285 | 270 | 295 | 255 | 270 | 260 | 300 | 270 | 300 | 300 | 290 | 285 |  | 280 | 320 | 320 | 305 | 275 | 270 | 290 | 7046000
| Bibiyana South 400 MW | 360 | 360 | 360 | 360 | 380 | 380 | 380 | 400 | 397 | 393 | 400 | 394 | 400 | 396 | 388 | 392 | 394 | 360 |  | 387 | 398 | 400 | 400 | 400 | 400 | 400 | 9283400
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1191184
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 10 | 10 | 10 | 13 | 17 | 18 | 18 | 18 | 18 | 21 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 513600
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531888
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 445140
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 0 |  | 17 | 17 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 391140
63 | Impoprt (Tripura) | 124 | 120 | 120 | 114 | 108 | 104 | 100 | 106 | 112 | 116 | 120 | 122 | 120 | 128 | 132 | 130 | 126 | 120 |  | 136 | 136 | 136 | 128 | 134 | 132 | 132 | 2917440
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 38 | 38 | 38 | 38 | 36 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 6 | 2 |  | 12 | 16 | 22 | 16 | 16 | 37 | 30 | 454560
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 436248
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 3 | 8 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 171540
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 25 | 33 | 33 | 28 | 25 | 25 | 25 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 746300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 472500
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 25 | 22 | 22 | 22 | 22 | 22 | 22 | 28 | 28 |  | 23 | 27 | 27 | 27 | 28 | 28 | 28 | 543420
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 617300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 639700
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 82 | 98 | 98 | 98 | 98 | 98 | 95 | 97 | 95 | 95 | 98 | 95 | 95 | 95 | 97 |  | 100 | 100 | 100 | 95 | 95 | 98 | 98 | 2250863
| Feni Lanka Power | 108 | 108 | 108 | 108 | 108 | 70 | 70 | 70 | 80 | 108 | 100 | 100 | 105 | 105 | 105 | 105 | 96 | 96 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2384880
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 11 | 10 | 9 | 9 | 8 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 224280
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 126 | 126 | 126 | 133 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3828960
77 | Siddhirganj 100 PP(Dutch Bangla) | 99 | 99 | 76 | 32 | 8 | 8 | 8 | 8 | 16 | 72 | 85 | 90 | 98 | 98 | 98 | 96 | 84 | 80 |  | 80 | 82 | 83 | 85 | 91 | 87 | 82 | 1680000
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 42 | 33 | 33 | 33 | 36 | 41 | 41 | 45 | 48 | 48 | 48 | 40 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 1070400
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 98 | 98 | 64 | 98 | 98 | 132 | 132 | 132 | 132 | 132 | 120 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2873280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 34 | 38 | 43 | 43 | 25 | 25 | 25 | 26 | 34 | 36 | 43 | 42 | 41 | 42 | 42 | 42 | 41 |  | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 939427
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 70 | 80 | 105 | 90 | 90 | 100 | 105 | 90 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2463600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 3 | 5 | 4 | 2 | 5 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 32844
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 0 |  |  |  |  | 7 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1078349
| Karnaphuli Power Ltd. | 101 | 103 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 94 | 93 | 93 | 93 | 106 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2596061
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 70 | 32 | 32 | 32 | 31 | 37 | 56 | 79 | 90 | 94 | 94 | 93 | 93 | 93 |  | 94 | 94 | 95 | 95 | 95 | 95 | 95 | 1919808
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 125 | 135 | 130 | 135 | 130 | 135 | 125 | 135 | 114 | 142 | 140 | 143 | 112 | 120 | 134 | 123 | 128 | 120 |  | 142 | 144 | 135 | 125 | 125 | 120 | 140 | 3144727
87 | Meghnaghat 100 MW(IEL) | 87 | 91 | 90 | 90 | 90 | 90 | 89 | 88 | 85 | 81 | 90 | 90 | 89 | 88 | 89 | 89 | 89 | 84 |  | 87 | 89 | 89 | 92 | 90 | 91 | 94 | 2133120
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 54 | 54 | 54 | 68 | 89 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2426880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 10 | 0 |  |  |  |  | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 45 | 45 | 45 | 45 | 45 | 22 | 22 | 578160
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 47 | 47 | 47 | 46 | 49 | 49 | 49 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 30 | 30 | 1031256
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 51 | 43 | 35 | 43 | 43 | 969742
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 24 | 16 | 7 | 7 | 7 | 7 | 40 | 74 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1554336
95 | Patenga 50MW PP (Baraka) | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 44 | 38 | 36 | 40 |  | 46 | 50 | 48 | 50 | 48 | 50 | 50 | 1150080
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 55 | 51 | 41 | 26 | 26 | 26 | 82 | 93 | 93 | 93 | 93 | 90 | 91 | 91 | 92 |  | 93 | 93 | 94 | 94 | 96 | 96 | 96 | 1907520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 50 | 55 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 1230869
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1171123
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3658254
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 9550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 18 | 35 | 35 | 54 | 54 | 54 | 54 | 1008360
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 58 | 53 | 202 | 204 | 0 | 0 |  | 306 | 305 | 300 | 302 | 142 | 43 |  | 1579071
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 50 | 50 | 98 | 93 | 0 | 0 |  | 100 | 100 | 100 | 100 | 99 | 98 | 25 | 810264
106 | Mymensingh 200 MW PP (United) | 184 | 186 | 186 | 187 | 179 | 140 | 100 | 100 | 110 | 130 | 131 | 176 | 165 | 164 | 155 | 163 | 163 | 164 |  | 165 | 165 | 165 | 166 | 175 | 174 | 174 | 3804000
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 25 | 25 | 96 | 99 | 0 | 0 |  | 98 | 99 | 100 | 100 | 98 | 100 | 25 | 750864
114 | Kodda 149 MW PP Unit-1 (Summit) | 134 | 135 | 149 | 149 | 138 | 92 | 88 | 85 | 85 | 128 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3338208
115 | Juldah 100 MW PP Unit-3 (Acorn) | 64 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 79 |  | 81 | 81 | 82 | 83 | 84 | 84 | 62 | 1212480
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 136 | 120 | 51 | 51 | 51 | 70 | 184 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 170 |  | 188 | 200 | 200 | 200 | 200 | 200 | 200 | 4085760
117 | Ashuganj 150MW PP (Midland) | 135 | 137 | 128 | 125 | 100 | 50 | 50 | 50 | 63 | 113 | 115 | 118 | 120 | 122 | 130 | 122 | 118 | 120 |  | 122 | 125 | 125 | 134 | 137 | 135 | 133 | 2798472
118 | Bibiyana-III 400 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6625000
| Jamalpur 115 MW PP (United) | 105 | 96 | 96 | 105 | 106 | 106 | 115 | 115 | 106 | 105 | 95 | 94 | 104 | 103 | 93 | 93 | 103 | 103 |  | 105 | 105 | 105 | 105 | 105 | 105 | 95 | 2413200
| Anwara 300 MW PP (United) | 275 | 282 | 283 | 284 | 283 | 190 | 190 | 190 | 240 | 282 | 282 | 285 | 284 | 284 | 283 | 283 | 283 | 283 |  | 265 | 265 | 282 | 282 | 282 | 282 | 282 | 6488509
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 38 | 38 | 38 | 38 | 38 | 50 | 50 | 50 | 50 | 50 | 38 | 39 | 39 | 38 | 50 |  | 90 | 90 | 90 | 91 | 79 | 50 | 38 | 1233600
| Anlima Energy Ltd. | 97 | 97 | 97 | 97 | 97 | 78 | 97 | 97 | 97 | 97 | 97 | 96 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2324673
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 747000
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 83 | 83 | 17 | [5 empty] | 2 | 17 | 17 | 17 | 53 | 83 | 83 | 83 | 83 | 83 |  | 83 | 64 | 67 | 64 | 72 | 83 | 83 | 1217280
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 34 | 27 | 43 | 55 | 55 | 55 | 55 | 55 | 0 |  | 36 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1194480
120 | Eastern Zone Total | 8284 | 8254 | 8109 | 7892 | 7558 | 6788 | 6725 | 6664 | 7047 | 7662 | 7922 | 7936 | 8026 | 8053 | 8348 | 8420 | 8061 | 7954 |  | 9014 | 9128 | 9074 | 9042 | 8823 | 8554 | 8325 | 194096590
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 5 | 12 | 15 | 15 | 15 | 16 | 16 | 66 |  | 70 | 80 | 80 | 80 | 115 | 115 | 49 | 739200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 14 |  | 34 | 44 | 44 | 44 | 44 | 44 | 44 | 223200
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 70 | 17 | 17 | 17 | 17 | 17 | 35 | 53 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2068800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 9 | 36 | 59 | 48 | 98 | 69 | 89 | 74 | 72 | 54 | 23 | 5 |  | 0 | [6 empty] | 632500
131
132 | United Payra Power Ltd. | [19 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 99600
133 | Bhola Nutan Biddut BD LTD (GAS) | 218 | 215 | 213 | 215 | 213 | 184 | 187 | 186 | 186 | 166 | 198 | 210 | 210 | 210 | 210 | 210 | 210 | 210 |  | 210 | 212 | 212 | 212 | 216 | 186 | 216 | 4891473
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 48 | 48 | 48 | 32 | 32 | 32 | 32 | 611616
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 86 | 87 | 87 | 86 | 86 | 86 | 85 | 85 | 85 | 83 | 83 | 83 | 84 | 84 | 84 | 85 |  | 85 | 84 | 85 | 86 | 86 | 87 | 87 | 2056217
140 | Bhola 33 MW PP (Venture) | 35 | 34 | 30 | 31 | 30 | 26 | 22 | 20 | 20 | 20 | 20 | 20 | 23 | 24 | 29 | 29 | 27 | 26 |  | 31 | 30 | 31 | 33 | 34 | 34 | 35 | 545300
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [9 empty] | 24 | 100 | 100 | 100 | 10 |  |  | 306240
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 16 | 16 | 16 | 32 | 32 |  |  | 97125
143 | Gopalganj 100 MW Peaking PP | 30 | [16 empty] | 8 |  | 35 | 65 | 65 | 65 | 65 | 58 | 59 | 385408
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 40 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 32 | 105 | 105 | 105 | 89 | 85 | 50 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1640304
146 | Bheramara HVDC | 916 | 918 | 922 | 923 | 922 | 924 | 923 | 924 | 923 | 924 | 924 | 924 | 924 | 922 | 923 | 922 | 922 | 923 |  | 923 | 924 | 923 | 923 | 922 | 922 | 923 | 22312000
147 | Bheramara 410 MW CCPP | 265 | 265 | 280 | 290 | 295 | 305 | 310 | 310 | 290 | 300 | 320 | 320 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 320 | 320 | 320 | 325 | 325 | 7500096
148 | Payra 1320 MW | 980 | 940 | 900 | 850 | 840 | 810 | 810 | 760 | 770 | 700 | 720 | 750 | 790 | 780 | 800 | 800 | 800 | 790 |  | 840 | 1000 | 1020 | 1030 | 1020 | 1010 | 1010 | 22336900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 174 | 4263200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | [9 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 484832
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 3 | 2 | 5 | 4 | 3 | 1 | 0 | 0 | 0 | [8 empty] | 26640
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 181 | 181 | 184 | 190 | 193 | 196 | 201 | 204 | 201 | 191 | 188 | 205 | 201 | 201 | 195 | 195 | 194 | 194 |  | 196 | 198 | 198 | 191 | 197 | 205 | 207 | 4921909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 384 | 381 | 380 | 380 | 380 | 380 | 380 | 352 | 352 | 252 | 416 | 414 | 414 | 414 | 414 | 414 | 414 | 350 |  | 414 | 414 | 414 | 414 | 414 | 419 | 418 | 9322945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 4 | 4 | 4 | 14 | 14 |  | 15 | 15 | 12 | 14 | 14 | 16 | 15 | 118673
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 22 | 21 | 0 | 10 | 443760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 11 | 11 | 11 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198396
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 50 | 16 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 490347
167 | Katakhali 50 MW Peaking PP | [14 empty] | 7 | 31 | 31 | [5 empty] | 32 | 32 | 32 | 40 | 180100
168 | Santahar 50 MW Peaking PP | 36 | [11 empty] | 22 | 38 | 37 | 37 | 37 | 37 |  | 38 | 38 | 38 | 37 | 38 | 38 | 0 | 415745
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 45 | 52 | 52 | 52 | 52 | 16 |  | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 873538
170 | Chapainawabganj 100 MW Peaking PP | 83 | 52 | 22 | [13 empty] | 50 | 50 |  | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 728856
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 46 | 151 | 152 | 156 | 100 | 0 |  | 515367
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 81 | 113 | 113 | 113 | 113 | 113 | 113 | 50 |  | 70 | 113 | 113 | 113 | 113 | 113 | 70 | 2589696
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 95 | 95 | 95 | 95 | 50 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 50 |  | 95 | 95 | 95 | 113 | 113 | 113 | 70 | 2316096
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 8 | 8 | 8 | 8 | 8 | 0 |  | 39000
176 | Rangpur 113 MW PP (Confidence) | 19 | 34 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 34 | 60 | 72 | 108 | 108 | 108 | 108 | 107 | 74 |  | 102 | 102 | 110 | 107 | 110 | 111 | 111 | 1765094
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 1 | 3 | 5 | 5 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 33483
178 | Energypac Power Venture Thakurgaon Ltd. | 17 | 17 | [10 empty] | 72 | 72 | 72 | 72 | 72 | 34 |  | 80 | 115 | 115 | 115 | 115 | 115 | 72 | 1077696
178