## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-18 | Wednesday
|  |  | Date (day): | 2022-05-18 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14331.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15066 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-17 | 2022-05-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 250 | 250 | 250 |  | 115 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 96 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 317 | 320 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 81 | 88 | 95 | 95
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 130 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 79 | 96 | 96 | 96 |  | 6 | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 77 | 91 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 328 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 87 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 53 | 54 | 54 |  | 26 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 246 | 278 | 290 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 72 | 304 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 25 | 98 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 32 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 125 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 92 | 105 | 100 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3271 | 3762 | 3852 | 3847 | 701 | 1290
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 |  | 200 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 22 | 22 | 80 | 80 |  | 20 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 23 | 7 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 92 | 94 | 96 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 266 | 267 | 290 | 290 |  | 10 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 64 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 97 | 108 | 110 | 110 |  | 6 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1187 | 1370 | 1516 | 1509 | 411 | 455
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 194 | 200 | 225
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 270 | 270 | 90 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 35 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 5 | 5 | 5 | 50 |  | Engine problem
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 142 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 41 | 41 |  | 11 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 130 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 30 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 42 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 7 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 95 | 100 | 110 | 110 |  | 4 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 67 | 81 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1394 | 1689 | 1754 | 1928 | 950 | 141
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 67 | 115 | 120 | 150 | 52 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 43 | 190 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 112 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 320 | 461 | 528.6 | 507 | 52 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 50 | 50 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 78 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 219 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 34 | 38 | 41 | 9 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 10 | 11 | 11 | 11
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 330 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 80 | 80 | 80 | 80 |  |  | ST Sync. Process
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 398 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1457 | 1573 | 1548 | 1592 | 339 | 186
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 915 | 913 | 931 | 931
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 19 | 99 | 16 | 100 |  |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 67 | 0 | 80 |  | 29 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 270 | 280 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 104 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1468 | 1744 | 1912 | 2016 | 90 | 48
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 64 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 25 | 33 | 33 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 75 | 70 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 530 | 800 | 1050 |  |  | FGNO
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 204 | 212 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 29 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 836 | 938 | 1189 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 35 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 19 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 168 | 220 | 220 |  |  | Running on HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 200 | 200 | 20 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 420 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 37 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 52 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 151 | 200 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 59 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 760 | 1317 | 1624 | 1618 | 401 | 100
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 174 | 174 | 175 | 175 |  | 99 | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 9 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 81 | 104 | 110 | 110
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 72 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 333 | 402 | 408 | 400 | 0 | 269
|  | Total |  |  |  |  | 22348 | 21584 | 11026 | 13256 | 14331.6 | 15066 | 3052 | 2497
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10797.2953 | 12981.04 | 14034.3296 | 14753.4964
| A. |  | 2022-05-17 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13454 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8165 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13256 | MW
| 3 | Day peak Generation : |  |  | 11026 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12981.04 | MW
| 4 | Evening peak Generation : |  |  | 13256 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 276.8216 | MKWHr | By Solar | 1.1072 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 130.0391 | MKWHr |  | By Oil: | 98.7866 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 21.135 | MKWHr |  | By Hydro: | 0.7161 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3052 | MW | Dhaka | 4929.34 | 4929.34 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2497 | MW | Chittagong | 1408.1 | 1408.1 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5549 | MW | Khulna | 1742 | 1742 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 981.27 | MMCFD |  |  | Rajshahi | 1271.6 | 1271.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 131463837.122 | ii) Oil : | Taka | 802005438.23 | Comilla | 1264 | 1264 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 97173746 | Total | Taka | 1030643021.352 | Mymensingh | 881 | 881 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 356 | 356 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 156 | MW (E to W) at | 21:00 | hrs | Barisal | 431 | 431 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 72 | MW at | 20:00 | hrs | Rangpur | 698 | 698 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 12981.04 | 12981.04 |  | 0
| B. |  | 2022-05-18 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15066 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11100 | MW
| 4 | Reserve(Generation end) |  |  |  | 1066 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 288.0558 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10470 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1164 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9213 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.01 |  | (b) Today: | 73.94 |  | (c) Rule Curve: |  | 78.77
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 316 | 258 |  | 0 | 225 | 120 | 97 | 95 | 43 | 335 | 0 | 0 | 87 | 84 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 23 | 0 | 0 | 11 | 94 | 50 | 22 | 33 | 0 | 0 | 0 | 275 | 0 | 193 | 8 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 126 | 107 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 55 | 75 | 0 | 219 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 275 | 0 | 0 | 174 | 0 | 149 | 0 | 63 | 200 | 135 | 280 | 96 | 105 | 105 | 0 | 282 | 54 | 99 | 110 | 9 | 38 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 83 | 55 |  | 917 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 86 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 50 | 15 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 417 | 105 | 0 | 70 | 105 | 111 | 0 | 0 | 70 | 950 | 217 | 0 | 17 | 0 | 0 | 34 |  | 8185 | 4154 | 12339 | 3889 | 917 | 2027 | 0 | 3957 | 1125 | 30 | 0 | 268 | 126 | 0 | 0 | 74.02
2:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 325 | 263 |  | 0 | 225 | 120 | 98 | 95 | 55 | 335 | 0 | 0 | 40 | 84 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 23 | 0 | 0 | 11 | 94 | 50 | 22 | 33 | 0 | 0 | 0 | 275 | 0 | 193 | 8 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 124 | 132 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 55 | 75 | 0 | 219 | 0 | 0 | 0 | 260 | 11 | 11 | 0 | 280 | 0 | 0 | 140 | 0 | 149 | 0 | 38 | 200 | 133 | 280 | 106 | 105 | 105 | 0 | 283 | 49 | 93 | 110 | 9 | 38 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 55 | 55 |  | 918 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 375 | 105 | 0 | 70 | 67 | 111 | 0 | 0 | 70 | 940 | 187 | 0 | 17 | 0 | 0 | 0 |  | 8022 | 3864 | 11886 | 3934 | 918 | 1939 | 0 | 3726 | 1115 | 30 | 0 | 100 | 124 | 0 | 0 | 74.02
3:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 333 | 262 |  | 0 | 225 | 125 | 97 | 95 | 55 | 336 | 0 | 0 | 16 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 24 | 0 | 30 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 11 | 95 | 50 | 22 | 39 | 0 | 0 | 0 | 275 | 0 | 188 | 8 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 120 | 135 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 55 | 75 | 0 | 219 | 0 | 0 | 0 | 255 | 11 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 149 | 0 | 38 | 200 | 70 | 280 | 108 | 105 | 105 | 0 | 283 | 35 | 93 | 110 | 9 | 38 | 400 | 104 | 0 | 162 | 97 | 0 | 35 | 0 | 55 | 55 |  | 918 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 370 | 105 | 0 | 70 | 32 | 43 | 0 | 0 | 70 | 850 | 217 | 0 | 17 | 0 | 0 | 0 |  | 7719 | 3644 | 11363 | 3939 | 918 | 1968 | 0 | 3299 | 1025 | 30 | 0 | 64 | 120 | 0 | 0 | 74.01
4:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 252 | 277 |  | 0 | 225 | 125 | 97 | 95 | 55 | 336 | 0 | 0 | 16 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 24 | 0 | 30 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 11 | 95 | 50 | 22 | 38 | 0 | 0 | 0 | 275 | 0 | 185 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 120 | 135 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 163 | 0 | 55 | 75 | 0 | 219 | 0 | 0 | 0 | 280 | 11 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 149 | 0 | 38 | 200 | 70 | 280 | 115 | 105 | 105 | 0 | 282 | 35 | 93 | 110 | 9 | 38 | 400 | 104 | 0 | 144 | 97 | 0 | 35 | 0 | 17 | 55 |  | 917 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 370 | 105 | 0 | 70 | 32 | 0 | 0 | 0 | 35 | 850 | 219 | 0 | 17 | 0 | 0 | 0 |  | 7616 | 3568 | 11184 | 3858 | 917 | 2016 | 0 | 3155 | 1024 | 30 | 0 | 64 | 120 | 0 | 0 | 74.01
5:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 147 | 278 |  | 0 | 225 | 140 | 94 | 95 | 55 | 300 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 24 | 0 | 30 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 |  | 24 | 0 | 0 | 11 | 95 | 44 | 22 | 35 | 0 | 0 | 0 | 275 | 0 | 189 | 8 | 91 | 30 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 114 | 135 | 0 | 20 | 0 | 43 | 30 | 0 | 30 | 110 | 0 | 55 | 75 | 0 | 219 | 0 | 0 | 0 | 270 | 11 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 129 | 0 | 38 | 180 | 70 | 200 | 115 | 105 | 105 | 0 | 282 | 35 | 93 | 110 | 9 | 38 | 400 | 104 | 0 | 144 | 97 | 0 | 35 | 0 | 0 | 55 |  | 916 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 370 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 218 | 0 | 17 | 0 | 0 | 0 |  | 7147 | 3372 | 10519 | 3645 | 916 | 1943 | 0 | 2802 | 1005 | 30 | 0 | 64 | 114 | 0 | 0 | 74.01
6:00 | 0 | 0 | 0 | 170 | 250 | 98 | 0 | 0 | 298 |  | 0 | 225 | 130 | 90 | 95 | 55 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 16 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 11 | 95 | 0 | 22 | 30 | 0 | 0 | 0 | 275 | 0 | 189 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 108 | 118 | 0 | 20 | 0 | 43 | 30 | 0 | 48 | 110 | 0 | 60 | 75 | 0 | 219 | 0 | 0 | 10 | 270 | 11 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 124 | 1 | 38 | 180 | 70 | 70 | 8 | 72 | 105 | 0 | 283 | 35 | 93 | 110 | 9 | 38 | 400 | 104 | 0 | 144 | 97 | 0 | 35 | 0 | 0 | 55 |  | 915 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 172 | 0 | 17 | 0 | 6 | 0 |  | 6462 | 2899 | 9361 | 3274 | 915 | 1970 | 0 | 2366 | 675 | 30 | 0 | 16 | 108 | 7 | 0 | 74.01
7:00 | 0 | 0 | 0 | 170 | 250 | 99 | 0 | 0 | 332 |  | 0 | 225 | 125 | 90 | 91 | 55 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 26 | 0 | 33 | 16 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 11 | 95 | 6 | 22 | 26 | 0 | 0 | 0 | 270 | 0 | 188 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 102 | 110 | 0 | 0 | 0 | 43 | 30 | 0 | 50 | 110 | 0 | 60 | 75 | 0 | 219 | 0 | 0 | 10 | 260 | 11 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 124 | 5 | 38 | 136 | 70 | 15 | 0 | 34 | 96 | 2 | 281 | 35 | 93 | 110 | 9 | 38 | 360 | 90 | 0 | 108 | 97 | 0 | 26 | 0 | 0 | 55 |  | 916 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 437 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 162 | 0 | 0 | 0 | 25 | 0 |  | 6120 | 2796 | 8916 | 2996 | 916 | 1998 | 0 | 2151 | 675 | 30 | 0 | 16 | 102 | 32 | 0 | 74
8:00 | 0 | 0 | 0 | 170 | 250 | 100 | 0 | 0 | 337 |  | 0 | 225 | 145 | 91 | 62 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 26 | 0 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 11 | 76 | 42 | 22 | 9 | 0 | 0 | 0 | 270 | 0 | 161 | 8 | 91 | 16 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 110 | 80 | 0 | 0 | 0 | 43 | 22 | 0 | 50 | 110 | 0 | 60 | 0 | 0 | 219 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 54 | 2 | 38 | 50 | 24 | 80 | 0 | 0 | 51 | 2 | 245 | 35 | 92 | 88 | 9 | 42 | 400 | 35 | 4 | 35 | 97 | 0 | 0 | 0 | 0 | 55 |  | 915 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 423 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 162 | 0 | 0 | 1 | 52 | 0 |  | 5376 | 2789 | 8165 | 2999 | 915 | 1916 | 0 | 1457 | 675 | 30 | 0 | 0 | 110 | 63 | 0 | 74
9:00 | 0 | 0 | 0 | 170 | 250 | 97 | 0 | 0 | 332 |  | 0 | 225 | 120 | 82 | 48 | 35 | 337 | 0 | 0 | 6 | 32 | 16 | 0 | 0 | 0 | 0 | 38 | 35 | 50 | 0 | 25 | 22 | 17 | 33 | 7 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 5 | 0 | 0 | 21 | 73 | 44 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 161 | 8 | 90 | 28 | 5 | 0 | 51 | 0 | 0 | 34 | 0 | 5 | 30 | 20 | 116 | 70 | 0 | 20 | 0 | 43 | 30 | 0 | 50 | 163 | 0 | 60 | 10 | 0 | 219 | 0 | 0 | 10 | 315 | 7 | 0 | 0 | 23 | 0 | 0 | 7 | 0 | 30 | 8 | 38 | 54 | 60 | 80 | 12 | 14 | 68 | 4 | 283 | 35 | 102 | 95 | 9 | 50 | 400 | 68 | 11 | 105 | 97 | 0 | 4 | 0 | 0 | 55 |  | 915 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 425 | 38 | 0 | 1 | 0 | 25 | 0 | 3 | 0 | 500 | 164 | 0 | 0 | 3 | 76 | 0 |  | 5904 | 2959 | 8863 | 3192 | 915 | 2000 | 0 | 1815 | 674 | 30 | 0 | 16 | 116 | 105 | 0 | 74
10:00 | 0 | 0 | 0 | 170 | 250 | 97 | 0 | 0 | 345 |  | 0 | 225 | 120 | 82 | 92 | 55 | 300 | 0 | 0 | 48 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 21 | 17 | 33 | 29 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 91 | 43 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 191 | 8 | 91 | 32 | 5 | 0 | 43 | 0 | 0 | 40 | 0 | 0 | 25 | 0 | 116 | 70 | 0 | 20 | 0 | 43 | 30 | 0 | 50 | 163 | 0 | 60 | 50 | 0 | 205 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 145 | 0 | 0 | 24 | 0 | 122 | 18 | 38 | 90 | 150 | 80 | 28 | 38 | 68 | 3 | 283 | 35 | 110 | 95 | 9 | 50 | 360 | 104 | 24 | 144 | 97 | 0 | 17 | 0 | 0 | 55 |  | 916 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 25 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 418 | 70 | 0 | 30 | 0 | 37 | 0 | 5 | 0 | 500 | 166 | 0 | 0 | 3 | 102 | 0 |  | 6637 | 3047 | 9684 | 3058 | 916 | 2039 | 0 | 2632 | 674 | 30 | 0 | 64 | 116 | 155 | 0 | 74
11:00 | 0 | 0 | 0 | 180 | 250 | 95 | 0 | 0 | 332 |  | 0 | 225 | 140 | 80 | 79 | 40 | 333 | 0 | 0 | 73 | 87 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 21 | 17 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 20 | 209 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 92 | 43 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 199 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 43 | 0 | 7 | 25 | 0 | 120 | 70 | 0 | 16 | 2 | 43 | 30 | 0 | 50 | 163 | 0 | 60 | 72 | 0 | 219 | 0 | 0 | 10 | 300 | 7 | 0 | 0 | 188 | 0 | 0 | 24 | 0 | 125 | 18 | 38 | 172 | 127 | 80 | 49 | 90 | 77 | 1 | 282 | 35 | 110 | 95 | 9 | 100 | 400 | 104 | 36 | 144 | 97 | 0 | 17 | 0 | 25 | 55 |  | 916 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 21 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 92 | 0 | 35 | 0 | 70 | 0 | 5 | 30 | 500 | 166 | 0 | 0 | 4 | 56 | 34 |  | 7184 | 3143 | 10327 | 3198 | 916 | 2071 | 0 | 3098 | 674 | 30 | 0 | 98 | 120 | 122 | 0 | 73.99
12:00 | 0 | 0 | 0 | 180 | 250 | 97 | 0 | 0 | 322 |  | 0 | 225 | 140 | 81 | 79 | 55 | 328 | 0 | 0 | 77 | 87 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 92 | 44 | 0 | 4 | 0 | 0 | 0 | 270 | 0 | 210 | 8 | 90 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 0 | 7 | 25 | 7 | 122 | 67 | 0 | 16 | 2 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 72 | 0 | 220 | 0 | 0 | 10 | 320 | 10 | 0 | 0 | 246 | 72 | 25 | 43 | 32 | 125 | 18 | 38 | 200 | 140 | 80 | 115 | 92 | 85 | 3 | 266 | 35 | 110 | 95 | 9 | 100 | 398 | 104 | 53 | 144 | 97 | 0 | 17 | 0 | 67 | 55 |  | 915 | 0 | 320 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 16 | 75 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 59 | 0 | 81 | 0 | 6 | 60 | 500 | 204 | 0 | 0 | 4 | 104 | 72 |  | 7629 | 3397 | 11026 | 3233 | 915 | 2126 | 129 | 3492 | 674 | 30 | 0 | 115 | 122 | 190 | 0 | 73.99
13:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 0 | 322 |  | 0 | 225 | 120 | 80 | 78 | 55 | 322 | 0 | 0 | 90 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 91 | 44 | 0 | 6 | 0 | 0 | 0 | 270 | 0 | 183 | 8 | 90 | 33 | 0 | 0 | 51 | 0 | 42 | 43 | 0 | 7 | 25 | 7 | 120 | 67 | 0 | 16 | 2 | 43 | 30 | 0 | 48 | 163 | 0 | 60 | 75 | 0 | 219 | 0 | 0 | 10 | 300 | 10 | 0 | 30 | 252 | 300 | 96 | 74 | 99 | 125 | 19 | 38 | 200 | 143 | 80 | 115 | 105 | 85 | 2 | 266 | 35 | 103 | 94 | 8 | 65 | 400 | 104 | 34 | 144 | 98 | 0 | 20 | 0 | 81 | 55 |  | 916 | 0 | 315 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 87 | 0 | 95 | 0 | 7 | 100 | 500 | 207 | 0 | 0 | 3 | 76 | 72 |  | 8004 | 3510 | 11514 | 3193 | 916 | 2095 | 525 | 3656 | 674 | 30 | 0 | 162 | 120 | 143 | 0 | 73.99
14:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 0 | 317 |  | 0 | 225 | 140 | 79 | 94 | 55 | 324 | 0 | 0 | 90 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 92 | 43 | 22 | 5 | 0 | 0 | 0 | 270 | 0 | 182 | 8 | 90 | 34 | 5 | 0 | 51 | 0 | 48 | 43 | 0 | 7 | 32 | 0 | 124 | 68 | 0 | 16 | 1 | 43 | 30 | 0 | 48 | 163 | 0 | 60 | 77 | 0 | 219 | 0 | 18 | 10 | 305 | 10 | 0 | 30 | 268 | 243 | 97 | 80 | 96 | 149 | 17 | 38 | 200 | 138 | 80 | 106 | 105 | 88 | 2 | 266 | 35 | 110 | 94 | 9 | 42 | 400 | 104 | 43 | 144 | 102 | 0 | 35 | 0 | 81 | 55 |  | 910 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 113 | 0 | 110 | 0 | 5 | 113 | 500 | 207 | 0 | 0 | 4 | 71 | 72 |  | 8058 | 3571 | 11629 | 3194 | 910 | 2139 | 466 | 3763 | 674 | 30 | 0 | 186 | 124 | 143 | 0 | 73.99
15:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 0 | 317 |  | 0 | 225 | 140 | 79 | 94 | 55 | 318 | 0 | 0 | 90 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 28 | 25 | 33 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 219 | 0 | 0 | 0 |  | 24 | 9 | 0 | 22 | 92 | 47 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 203 | 8 | 90 | 34 | 5 | 0 | 51 | 0 | 48 | 42 | 0 | 7 | 32 | 8 | 132 | 67 | 0 | 17 | 0 | 44 | 30 | 0 | 48 | 163 | 0 | 60 | 78 | 0 | 193 | 0 | 12 | 10 | 270 | 11 | 0 | 195 | 278 | 303 | 97 | 80 | 96 | 149 | 13 | 38 | 200 | 139 | 79 | 106 | 105 | 105 | 2 | 266 | 35 | 110 | 94 | 9 | 39 | 394 | 104 | 4 | 144 | 108 | 0 | 35 | 0 | 74 | 55 |  | 911 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 31 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 26 | 0 | 0 | 414 | 105 | 22 | 113 | 15 | 109 | 0 | 3 | 113 | 500 | 164 | 0 | 0 | 1 | 71 | 92 |  | 8263 | 3591 | 11854 | 3197 | 911 | 2056 | 739 | 3818 | 674 | 30 | 0 | 203 | 132 | 94 | 0 | 73.98
16:00 | 0 | 0 | 0 | 180 | 250 | 97 | 0 | 0 | 313 |  | 0 | 225 | 140 | 79 | 94 | 55 | 326 | 0 | 0 | 90 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 24 | 9 | 0 | 22 | 92 | 46 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 195 | 8 | 90 | 34 | 5 | 0 | 43 | 0 | 47 | 42 | 0 | 7 | 32 | 8 | 130 | 70 | 0 | 20 | 0 | 44 | 30 | 0 | 48 | 163 | 0 | 60 | 78 | 0 | 204 | 0 | 12 | 10 | 320 | 11 | 11 | 196 | 278 | 191 | 97 | 132 | 98 | 134 | 9 | 38 | 200 | 142 | 83 | 106 | 105 | 105 | 3 | 282 | 35 | 110 | 94 | 9 | 39 | 398 | 104 | 11 | 144 | 90 | 0 | 35 | 0 | 71 | 55 |  | 910 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 6 | 70 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 31 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 50 | 0 | 0 | 414 | 105 | 149 | 113 | 15 | 109 | 0 | 1 | 113 | 540 | 165 | 0 | 0 | 1 | 34 | 115 |  | 8250 | 3787 | 12037 | 3216 | 910 | 2090 | 781 | 3905 | 714 | 30 | 0 | 202 | 130 | 59 | 0 | 73.98
17:00 | 0 | 0 | 0 | 180 | 250 | 95 | 0 | 0 | 314 |  | 0 | 225 | 115 | 80 | 94 | 55 | 325 | 0 | 0 | 90 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 9 | 0 | 22 | 92 | 50 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 191 | 8 | 90 | 34 | 5 | 0 | 43 | 0 | 47 | 42 | 0 | 7 | 32 | 8 | 126 | 72 | 0 | 20 | 0 | 43 | 30 | 0 | 48 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 22 | 10 | 280 | 5 | 11 | 150 | 265 | 89 | 97 | 143 | 98 | 134 | 3 | 50 | 200 | 143 | 80 | 106 | 105 | 105 | 1 | 283 | 44 | 110 | 81 | 9 | 39 | 400 | 75 | 5 | 144 | 90 | 0 | 35 | 0 | 81 | 55 |  | 910 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 27 | 48 | 0 | 0 | 0 | 43 | 0 | 80 | 0 | 50 | 31 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 20 | 0 | 0 | 414 | 94 | 152 | 113 | 50 | 109 | 0 | 1 | 113 | 350 | 166 | 0 | 0 | 1 | 21 | 115 |  | 8037 | 3748 | 11785 | 3220 | 910 | 2035 | 606 | 3977 | 524 | 30 | 0 | 325 | 126 | 32 | 0 | 73.98
18:00 | 0 | 0 | 0 | 180 | 250 | 92 | 0 | 0 | 272 |  | 0 | 225 | 130 | 79 | 94 | 55 | 260 | 0 | 0 | 90 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 9 | 0 | 22 | 93 | 12 | 22 | 6 | 0 | 0 | 0 | 270 | 0 | 191 | 8 | 90 | 35 | 5 | 0 | 43 | 0 | 47 | 42 | 0 | 7 | 32 | 20 | 118 | 71 | 0 | 20 | 0 | 43 | 30 | 0 | 50 | 130 | 0 | 60 | 78 | 0 | 219 | 0 | 22 | 10 | 270 | 11 | 11 | 20 | 267 | 21 | 25 | 143 | 25 | 147 | 0 | 90 | 200 | 139 | 80 | 108 | 105 | 105 | 0 | 283 | 54 | 110 | 81 | 9 | 39 | 400 | 104 | 1 | 126 | 108 | 0 | 35 | 0 | 81 | 55 |  | 911 | 0 | 280 | 0 | 30 | 0 | 0 | 0 | 22 | 0 | 32 | 70 | 26 | 48 | 0 | 0 | 0 | 43 | 4 | 80 | 0 | 50 | 31 | 52 | 30 | 21 | 0 | 11 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 10 | 0 | 0 | 300 | 105 | 20 | 113 | 105 | 110 | 0 | 0 | 113 | 450 | 168 | 0 | 0 | 0 | 4 | 115 |  | 7635 | 3677 | 11312 | 3146 | 911 | 1856 | 121 | 4104 | 623 | 30 | 0 | 398 | 118 | 5 | 0 | 73.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 250 | 94 | 0 | 0 | 313 |  | 0 | 225 | 140 | 88 | 94 | 55 | 320 | 0 | 0 | 90 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 24 | 42 | 51 | 22 | 94 | 43 | 22 | 9 | 0 | 0 | 0 | 270 | 0 | 192 | 8 | 90 | 35 | 5 | 0 | 43 | 0 | 47 | 43 | 0 | 7 | 32 | 20 | 136 | 101 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 78 | 0 | 220 | 0 | 35 | 10 | 290 | 11 | 11 | 195 | 278 | 304 | 99 | 190 | 100 | 149 | 0 | 90 | 200 | 140 | 80 | 107 | 105 | 105 | 0 | 283 | 54 | 110 | 81 | 9 | 63 | 398 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 55 |  | 912 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 45 | 42 | 0 | 73 | 30 | 48 | 0 | 0 | 0 | 43 | 4 | 84 | 0 | 50 | 37 | 52 | 37 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 40 | 0 | 0 | 414 | 105 | 56 | 113 | 105 | 109 | 0 | 0 | 113 | 480 | 206 | 0 | 8 | 0 | 0 | 115 |  | 8696 | 4059 | 12755 | 3231 | 912 | 2134 | 794 | 4292 | 654 | 30 | 8 | 564 | 136 | 0 | 0 | 73.97
19:30 | 0 | 0 | 0 | 180 | 250 | 94 | 0 | 0 | 316 |  | 0 | 225 | 140 | 88 | 94 | 55 | 324 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 24 | 43 | 51 | 22 | 94 | 50 | 22 | 17 | 0 | 0 | 0 | 270 | 0 | 196 | 8 | 90 | 35 | 5 | 0 | 43 | 0 | 40 | 43 | 0 | 7 | 32 | 20 | 134 | 102 | 0 | 20 | 0 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 35 | 10 | 320 | 11 | 11 | 200 | 278 | 302 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 140 | 80 | 110 | 105 | 105 | 0 | 283 | 54 | 110 | 81 | 9 | 64 | 396 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 82 | 55 |  | 913 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 40 | 53 | 30 | 70 | 30 | 48 | 0 | 0 | 0 | 43 | 20 | 84 | 0 | 50 | 37 | 52 | 37 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 8 | 0 | 0 | 168 | 0 | 0 | 100 | 0 | 0 | 418 | 105 | 150 | 113 | 105 | 109 | 0 | 0 | 113 | 500 | 211 | 0 | 17 | 0 | 0 | 115 |  | 8748 | 4319 | 13067 | 3248 | 913 | 2184 | 952 | 4344 | 674 | 30 | 8 | 580 | 134 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 0 | 317 |  | 0 | 225 | 137 | 88 | 96 | 55 | 325 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 224 | 0 | 0 | 0 |  | 24 | 51 | 51 | 22 | 94 | 50 | 22 | 22 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 40 | 42 | 0 | 7 | 0 | 20 | 130 | 115 | 0 | 20 | 0 | 44 | 30 | 34 | 50 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 36 | 10 | 330 | 11 | 11 | 200 | 278 | 302 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 140 | 80 | 112 | 105 | 105 | 0 | 283 | 54 | 110 | 90 | 9 | 64 | 395 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 80 | 55 |  | 913 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 45 | 70 | 40 | 70 | 29 | 48 | 0 | 0 | 0 | 43 | 21 | 84 | 0 | 50 | 40 | 43 | 37 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 10 | 0 | 0 | 169 | 0 | 0 | 100 | 0 | 0 | 415 | 105 | 151 | 113 | 105 | 109 | 0 | 0 | 113 | 490 | 209 | 0 | 17 | 0 | 0 | 115 |  | 8810 | 4334 | 13144 | 3238 | 913 | 2236 | 953 | 4356 | 664 | 30 | 10 | 614 | 130 | 0 | 0 | 73.97
21:00 | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 0 | 317 |  | 0 | 225 | 130 | 88 | 96 | 55 | 328 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 51 | 22 | 94 | 50 | 22 | 23 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 40 | 42 | 0 | 7 | 30 | 20 | 130 | 115 | 0 | 20 | 0 | 44 | 30 | 53 | 50 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 34 | 10 | 330 | 11 | 11 | 200 | 278 | 304 | 98 | 190 | 100 | 149 | 0 | 90 | 200 | 142 | 80 | 112 | 105 | 105 | 0 | 267 | 54 | 110 | 100 | 9 | 64 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 55 |  | 913 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 45 | 67 | 40 | 70 | 33 | 64 | 0 | 0 | 0 | 43 | 19 | 81 | 0 | 50 | 38 | 52 | 37 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 9 | 0 | 0 | 168 | 0 | 0 | 100 | 0 | 0 | 420 | 105 | 151 | 113 | 105 | 104 | 0 | 0 | 113 | 530 | 212 | 0 | 29 | 0 | 0 | 115 |  | 8855 | 4401 | 13256 | 3269 | 913 | 2259 | 953 | 4385 | 704 | 30 | 9 | 604 | 130 | 0 | 0 | 73.97
22:00 | 0 | 0 | 0 | 180 | 250 | 98 | 0 | 0 | 317 |  | 0 | 225 | 142 | 88 | 94 | 55 | 330 | 0 | 0 | 86 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 208 | 0 | 0 | 0 |  | 24 | 51 | 51 | 22 | 94 | 50 | 22 | 32 | 0 | 0 | 0 | 270 | 0 | 198 | 8 | 92 | 35 | 5 | 0 | 51 | 0 | 40 | 43 | 19 | 7 | 33 | 20 | 128 | 117 | 0 | 20 | 0 | 44 | 30 | 53 | 50 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 35 | 10 | 300 | 11 | 11 | 200 | 280 | 272 | 97 | 190 | 99 | 149 | 0 | 90 | 200 | 142 | 80 | 115 | 105 | 105 | 0 | 248 | 54 | 110 | 100 | 9 | 64 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 55 |  | 913 | 0 | 265 | 0 | 80 | 0 | 0 | 0 | 45 | 65 | 40 | 70 | 35 | 48 | 0 | 0 | 0 | 43 | 19 | 81 | 0 | 50 | 38 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 9 | 0 | 0 | 194 | 0 | 0 | 70 | 0 | 0 | 418 | 105 | 151 | 113 | 105 | 109 | 0 | 0 | 113 | 790 | 212 | 0 | 35 | 0 | 0 | 115 |  | 8829 | 4625 | 13454 | 3326 | 913 | 2253 | 889 | 4341 | 964 | 30 | 9 | 601 | 128 | 0 | 0 | 73.97
23:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 0 | 328 |  | 0 | 225 | 135 | 85 | 96 | 55 | 330 | 0 | 0 | 89 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 0 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 3 | 22 | 94 | 50 | 22 | 37 | 0 | 0 | 0 | 270 | 0 | 202 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 40 | 43 | 19 | 0 | 33 | 20 | 132 | 125 | 0 | 20 | 0 | 44 | 30 | 53 | 50 | 0 | 0 | 60 | 78 | 0 | 219 | 0 | 34 | 10 | 300 | 11 | 11 | 200 | 275 | 304 | 97 | 190 | 99 | 149 | 0 | 90 | 200 | 150 | 80 | 103 | 105 | 105 | 0 | 248 | 54 | 110 | 96 | 9 | 50 | 401 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 0 |  | 914 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 45 | 65 | 0 | 85 | 36 | 48 | 0 | 0 | 0 | 43 | 20 | 81 | 0 | 50 | 38 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 9 | 0 | 0 | 195 | 0 | 0 | 80 | 0 | 0 | 419 | 105 | 151 | 113 | 105 | 99 | 0 | 0 | 113 | 890 | 212 | 0 | 35 | 0 | 0 | 115 |  | 8550 | 4702 | 13252 | 3304 | 914 | 2102 | 931 | 4211 | 1064 | 30 | 9 | 555 | 132 | 0 | 0 | 73.96
24:00 | 0 | 0 | 0 | 180 | 250 | 102 | 0 | 0 | 337 |  | 0 | 225 | 120 | 83 | 96 | 55 | 332 | 0 | 0 | 90 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 207 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 94 | 50 | 22 | 31 | 0 | 0 | 0 | 270 | 0 | 205 | 8 | 88 | 35 | 5 | 0 | 43 | 0 | 41 | 43 | 19 | 0 | 33 | 20 | 130 | 153 | 0 | 20 | 0 | 44 | 30 | 53 | 50 | 0 | 0 | 60 | 78 | 0 | 219 | 0 | 35 | 10 | 300 | 11 | 11 | 150 | 278 | 201 | 95 | 191 | 99 | 149 | 0 | 38 | 200 | 142 | 80 | 108 | 105 | 105 | 0 | 247 | 54 | 102 | 96 | 9 | 50 | 401 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 9 |  | 914 | 0 | 255 | 0 | 49 | 0 | 0 | 0 | 45 | 65 | 0 | 85 | 35 | 32 | 0 | 0 | 0 | 43 | 19 | 81 | 0 | 50 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 70 | 0 | 0 | 417 | 105 | 151 | 113 | 105 | 102 | 0 | 0 | 113 | 960 | 216 | 0 | 35 | 0 | 0 | 115 |  | 8339 | 4699 | 13038 | 3367 | 914 | 2087 | 766 | 4115 | 1134 | 30 | 0 | 495 | 130 | 0 | 0 | 73.96
KWH | 0 | 0 | 0 | 4221000 | 6013073 | 2306272 | 0 | 1392640 | 7372000 |  | 0 | 5053350 | 3150749 | 2089920 | 2128848 | 1282540 | 7688694 | 0 | 0 | 1466880 | 1572048 | 2226720 | 0 | 0 | 0 | 0 | 1291320 | 1191856 | 1200646 | 325764 | 600000 | 615420 | 461900 | 735300 | 905280 | 0 | 716100 | 0 | 0 | 0 | 401878 | 4982478 | 0 | 0 | 0 |  | 532800 | 298368 | 236521 | 440040 | 2204160 | 1044480 | 50712 | 421920 | 0 | 0 | 0 | 6979000 | 0 | 4665000 | 217454 | 2152770 | 768744 | 132960 | 0 | 1075128 | 0 | 510376 | 1002048 | 191412 | 140400 | 737000 | 368650 | 2921280 | 2253120 | 0 | 363420 | 5550 | 1030000 | 688152 | 216000 | 1123776 | 3552873 | 0 | 1413696 | 1683840 | 0 | 5131510 | 0 | 266780 | 191880 | 7199500 | 219782 | 176000 | 1647168 | 5444725 | 2803984 | 1043657 | 2592000 | 1074111 | 3236544 | 115425 | 1252800 | 4329120 | 2933963 | 2878000 | 2132400 | 2275200 | 2366909 | 29520 | 6508582 | 1075684 | 2522460 | 2329020 | 220080 | 1215360 | 9433000 | 2457600 | 221230 | 3431520 | 2430055 | 0 | 745560 | 0 | 1310400 | 1284120 |  | 22116363 | 0 | 7380288 | 0 | 750720 | 0 | 0 | 0 | 232800 | 368256 | 244125 | 1879109 | 691232 | 834240 | 0 | 0 | 0 | 338544 | 105378 | 702480 | 0 | 584189 | 345632 | 903480 | 224035 | 380160 | 0 | 190026 | 0 | 0 | 4263200 | 0 | 37000 | 0 | 0 | 4507191 | 0 | 0 | 698880 | 0 | 0 | 9749491 | 2403840 | 1199973 | 1832928 | 1059120 | 1751750 | 0 | 30666 | 1727232 | 16871800 | 4620491 | 0 | 290400 | 27240 | 677520 | 1461888 |  | 185339975 | 91481667 | 276821642 | 80633251 | 22116363 | 49405856 | 8467773 | 84692758 | 21135000 | 716100 | 37000 | 5589110 | 2921280 | 1107151 | 0
Fuel Cost | 0 | 0 | 0 | 6204870 | 6674511.03 | 3044279.04 | 0 | 1406566.4 | 7593160 |  | 0 | 5508151.5 | 3497331.39 | 15862492.8 | 14667762.72 | 10850288.4 | 7996241.76 | 0 | 0 | 11045606.4 | 14337077.76 | 21910924.8 | 0 | 0 | 0 | 0 | 9426636 | 9213046.88 | 11838369.56 | 244323 | 450000 | 0 | 0 | 0 | 8754057.6 | 0 | 193347 | 0 | 0 | 0 | 3733446.62 | 5430901.02 | 0 | 0 | 0 |  | 0 | 2885218.56 | 2294253.7 | 4202382 | 19176192 | 8272281.6 | 63897.12 | 1253102.4 | 0 | 0 | 0 | 5164460 | 0 | 4291800 | 280515.66 | 2475685.5 | 868680.72 | 186144 | 0 | 1838468.88 | 0 | 5154797.6 | 9569558.4 | 243093.24 | 105300 | 1289750 | 276487.5 | 21909600 | 2388307.2 | 0 | 461543.4 | 88467 | 1689200 | 1101043.2 | 384480 | 1753090.56 | 4050275.22 | 0 | 2784981.12 | 3216134.4 | 0 | 8877512.3 | 0 | 312132.6 | 391435.2 | 7271495 | 164836.5 | 133760 | 28018327.68 | 41162121 | 47611648.32 | 17449945.04 | 13478400 | 17959135.92 | 31847592.96 | 1349318.25 | 10210320 | 46970952 | 20684439.15 | 2676540 | 19447488 | 21500640 | 20615777.39 | 0 | 49204879.92 | 9369207.64 | 22172423.4 | 23243619.6 | 1886085.6 | 8094297.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127390250.88 | 0 | 7749302.4 | 0 | 5900659.2 | 0 | 0 | 0 | 2442072 | 3859322.88 | 2543782.5 | 2123393.17 | 1071409.6 | 8142182.4 | 0 | 0 | 0 | 3331272.96 | 1070640.48 | 6216948 | 0 | 7898235.28 | 3349174.08 | 8754721.2 | 2173139.5 | 729907.2 | 0 | 143849.682 | 0 | 0 | 23106544 | 0 | 1055610 | 0 | 0 | 5949492.12 | 0 | 0 | 11887948.8 | 0 | 0 | 9651996.09 | 25096089.6 | 20411540.73 | 17394486.72 | 9998092.8 | 13593580 | 0 | 338859.3 | 12764244.48 | 74067202 | 0 | 0 | 0 | 0 | 0 | 0 |  | 761706913.73 | 420205950.052 | 1181912863.782 | 79430328.382 | 127390250.88 | 52033508.74 | 143338546.49 | 602923517.18 | 97173746 | 193347 | 1055610 | 54687764.56 | 21909600 | 1776644.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 250 | 97 | 0 | 0 | 322 |  | 0 | 225 | 140 | 81 | 79 | 55 | 328 | 0 | 0 | 77 | 87 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 22 | 92 | 44 | 0 | 4 | 0 | 0 | 0 | 270 | 0 | 210 | 8 | 90 | 33 | 0 | 0 | 51 | 0 | 0 | 43 | 0 | 7 | 25 | 7 | 122 | 67 | 0 | 16 | 2 | 44 | 30 | 0 | 50 | 163 | 0 | 60 | 72 | 0 | 220 | 0 | 0 | 10 | 320 | 10 | 0 | 0 | 246 | 72 | 25 | 43 | 32 | 125 | 18 | 38 | 200 | 140 | 80 | 115 | 92 | 85 | 3 | 266 | 35 | 110 | 95 | 9 | 100 | 398 | 104 | 53 | 144 | 97 | 0 | 17 | 0 | 67 | 55 |  | 915 | 0 | 320 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 16 | 75 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 59 | 0 | 81 | 0 | 6 | 60 | 500 | 204 | 0 | 0 | 4 | 104 | 72 |  | 11026 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 0 | 317 | 0 | 0 | 225 | 130 | 88 | 96 | 55 | 328 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 22 | 94 | 50 | 22 | 23 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 40 | 42 | 0 | 7 | 30 | 20 | 130 | 115 | 0 | 20 | 0 | 44 | 30 | 53 | 50 | 163 | 0 | 60 | 78 | 0 | 219 | 0 | 34 | 10 | 330 | 11 | 11 | 200 | 278 | 304 | 98 | 190 | 100 | 149 | 0 | 90 | 200 | 142 | 80 | 112 | 105 | 105 | 0 | 267 | 54 | 110 | 100 | 9 | 64 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 55 |  | 913 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 45 | 67 | 40 | 70 | 33 | 64 | 0 | 0 | 0 | 43 | 19 | 81 | 0 | 50 | 38 | 52 | 37 | 21 | 0 | 11 | 0 | 0 | 174 | 0 | 9 | 0 | 0 | 168 | 0 | 0 | 100 | 0 | 0 | 420 | 105 | 151 | 113 | 105 | 104 | 0 | 0 | 113 | 530 | 212 | 0 | 29 | 0 | 0 | 115 |  | 13256 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 250 | 100 | 0 | 0 | 330 | 0 | 0 | 225 | 150 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 50 | 22 | 25 | 0 | 0 | 0 | 270 | 0 | 225 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 166 | 150 | 0 | 20 | 0 | 44 | 30 | 51 | 50 | 163 | 0 | 60 | 80 | 0 | 220 | 0 | 41 | 10 | 341 | 11 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 80 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 110 | 113 | 100 | 400 | 104 | 0 | 144 | 110 | 0 | 35 |  | 100 | 55 |  | 931 | 0 | 320 | 0 | 100 | 200 | 0 | 0 | 35 | 80 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 50 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 200 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 250 | 100 | 0 | 0 | 320 | 0 | 0 | 225 | 150 | 95 | 96 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 25 | 33 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 80 | 96 | 50 | 22 | 7 | 0 | 0 | 0 | 270 | 0 | 200 | 8 | 90 | 35 | 5 | 0 | 51 | 0 | 41 | 43 | 0 | 11 | 33 | 20 | 143 | 120 | 0 | 20 | 1.6 | 44 | 30 | 51 | 50 | 163 | 0 | 60 | 80 | 0 | 220 | 0 | 38 | 10 | 300 | 11 | 11 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 80 | 115 | 100 | 105 | 5 | 290 | 54 | 110 | 110 | 9 | 100 | 400 | 104 | 50 | 144 | 110 | 0 | 35 | 30 | 100 | 55 |  | 931 | 0 | 280 | 0 | 16 | 200 | 0 | 0 | 35 | 0 | 40 | 86 | 33 | 50 | 0 | 0 | 0 | 35 | 30 | 85 | 0 | 50 | 40 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 200 | 0 | 410 | 105 | 200 | 113 | 105 | 110 | 0 | 8 | 113 | 800 | 220 |  | 0 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 250 | 97 | 0 | 0 | 323 | 0 | 0 | 225 | 130 | 74 | 48 | 30 | 329 | 0 | 0 | 7 | 16 | 6 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 49 | 0 | 30 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 22 | 90 | 0 | 22 | 6 | 0 | 0 | 0 | 270 | 0 | 187 | 8 | 90 | 34 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 110 | 155 | 0 | 20 | 1 | 44 | 30 | 53 | 47 | 0 | 0 | 60 | 78 | 0 | 192 | 0 | 33 | 10 | 290 | 11 | 5 | 0 | 97 | 0 | 0 | 100 | 0 | 138 | 3 | 38 | 100 | 40 | 80 | 115 | 105 | 68 | 1 | 264 | 54 | 92 | 78 | 9 | 39 | 382 | 53 | 25 | 144 | 109 | 0 | 35 | 0 | 17 | 55 | 0 | 914 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 41 | 84 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 124 | 0 | 414 | 105 | 0 | 113 | 105 | 75 | 0 | 1 | 95 | 920 | 210 | 0 | 17 | 1 | 15 | 17 | 0 |  |  |  |  | 98786641 |  | 0
98786641
| Minimum Generation |  | 8165 | 8:00
| Highest Generation |  | 13454 | 22:00
| Day Peak Generation |  | 11026 | 12:00
| Evening Peak Generation |  | 13256 | 21:00
| HVDC Max Flow |  | 918 | 2:00
| HVDC EvPeak Flow |  | 913 | 21:00
| Load factor L.F |  | 85.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-18
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11026 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10470 | MW
Evening Peak Generation : |  | 13256 | MW Hour : | 21:00 | Available Max Generation : |  | 15066 | MW
E.P. Demand (at gen end) : |  | 13256 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13454 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1066 | MW
Total Gen. (MKWH) : |  | 276.8216 | System Load Factor : | 85.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 72 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-18
Actual : | 73.94 | Ft.(MSL) , | Rule curve : | 78.77 | Ft.( MSL )
Gas Consumed : | Total = | 981.27 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 131463837.122
: |  | Coal : | 97173746 | Oil : | 802005438.23 | Total : | 1030643021.352
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5046.9651 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1638.1076 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1595.7583 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1428.992 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1302.9976 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1069.2849 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 523.7805 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 321.217 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 786.3439 |  |  | 0 | 0%
Total | 0 |  | 13713.4468 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Haripur 412 MW EGCB
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1
9) Shahjibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Payra-Gopalganj 400 kV Ckt-1 was under shut down from 08:59 to 10:43 for C/M.
b) 33 kV side of B.Baria 132/33 kV T-1 & T-2 transformer(incomer) tripped at 08:37 showing E/F | [5 empty] | About 16 MW power interruption occurred under
and were switched on at 09:17. | [5 empty] | B.Baria S/S area from 08:37 to 09:17.
c) Chattak 132/33 kV T-1 transformer was shut down at 09:19 for C/M.
d) Chandpur-Kachua 132 kV Ckt-1 was under shut down from 10:51 to 13:07 for D/W.
e) Tongi S/S-Tongi P.P. 132 kV Ckt was under shut down from 10:42 to 21:32 for C/M.
f) Barishal(N) 132/33 kV T-4 transformer was under shut down from 09:58 to 14:39 for D/W.
g) Haripur S/S-Haripur EGCB 412 MW P.P. 132 kV Ckt was under shut down from 11:12 to 16:28 for C/M.
h) Rangpur 132/33 kV T-3 transformer was under shut down from 11:43 to 15:35 due to R/H maintenance
at CT.
i) Keraniganj GIS 132/33 kV T-1 transformer was under shut down from 12:09 to 14:06 due to R/H maintenance.
j) Kabirpur 132/33 kV T-2 transformer was under shut down from 08:23 to 11:44 due to 33 kV PBS work. | [5 empty] | About 60 MW power interruption occurred under
Kabirpur S/S area from 08:23 to 11:44.
k) Rampal 400/230 kV transformer was switched on at 13:45 and again tripped by PRD at 15:56 and
was switched on at 18:28.
l) Payra-Gopalganj 400 kV Ckt-1 tripped at 15:58 and was switched on at 19:51.
m) Barishal 132 kV Bus coupler tripped at 15:56 due to O/L and was switched on at 16:04. | [5 empty] | About 195 MW power interruption occurred under
Barishal & Barguna S/S area from 15:56 to 16:04.
n) Madanganj-Charsayedpur 132 kV Ckt-1 & 2(one by one) was under shut down from 15:48 to 17:10 due
to OPGW line problem.
o) Cumilla(N)-Kachua 132 kV Ckt was under shut down from 18:43 to 21:17 for Alarm checking.
p) Payra P.P.-Payra 132 kV S/S 400 kV Ckt was switched on at 16:34.
q) Payra Unit-1 went to house load and again synchronized with grid at 16:24.
r) Keraniganj 132/33 kV T-3(A+B) transformer was under shut down from 15:03 to 16:23 due to R/H maintenance.
s) Barishal 132 kV Bus coupler was opened on at 23:22.
t) Kushiara CCPP was shut down at 22:52 due to problem with DCS system.
u) Bhulta 132/33 kV T-1 transformer was under shut down from 22:35 to 23:34 due to 33 kV Bus | [5 empty] | About 45 MW power interruption occurred under
maintenance by PBS. | [5 empty] | Bhulta S/S area from 22:35 to 23:34.
v) Sirajganj unit-3 GT was synchronize at 00:40(18/05/2022) and ST at 03:44(18/05/2022).
w) Tongi 230/132 kV T-03 transformer was under shut down from 05:10(18/05/2022) to 07:30(18/05/2022) for C/M.
x) Sikalbaha-Dohazari 132 kV Ckt-2 was under shut down from 06:28(18/05/2022) to 07:46(18/05/2022) | [5 empty] | About 35 MW power interruption occurred under
for C/M. | [5 empty] | Dohazari & Cox's Bazar S/S area from 06:28 to 07:46.
y) Dhamrai 132/33 kV T-1 transformer was shut down at 07:04(18/05/2022) for C/M. | [5 empty] | About 5 MW power interruption has been running under
Dhamrai S/S area since 07:04(18/05/2022).
z) Jashore-Noapara 132 kV Ckt-1 was under shut down since 07:19(18-05-22) for C/M.
aa) Payra P.P.-Payra S/S 132 kV Ckt-3 was switched on at 07:36(18/05/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6013073 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2306272 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 1392640 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 317 | 7372000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5053350 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 88 | 2089920 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3150749 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 2128848
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1282540
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 325764
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1466880 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7688694
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1572048
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1291320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2226720 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1191856
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1200646
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1215420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 461900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 735300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 905280 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 5444725 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 2803984
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 98 | 1043657
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1074111
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3236544
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2275200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2457600
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3431520 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1284120
| Dhaka area Total |  |  |  | 5898 | 3762 | 78343681
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 401878
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115425
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1044480
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 716100 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4982478
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2366909
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 298368 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 236521 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 22 | 440040 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1252800 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 50712
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 421920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 2204160 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29520
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 267 | 6508582 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1075684
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2522460
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 64 | 1215360
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2430055
| Chattogram area Total |  |  |  | 2382 | 1370 | 28313452
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 4665000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 6979000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 768744 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 132960 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1075128
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2933963
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 510376 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2152770 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4329120
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 191412 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 140400 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2921280
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 30 | 737000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 1002048 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 368650 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1647168
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2329020 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 220080 | Lube oil shortage.
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 745560 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 81 | 1310400 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1689 | 35377533
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 115 | 2253120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 363420
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 190 | 2592000
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 112 | 2132400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 221230
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 532800
| Mymensingh Area Total |  |  |  | 622 | 461 | 8100520
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1030000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 688152 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3552873
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 216000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 50 | 1123776
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 176000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1413696
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1683840
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5131510
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 34 | 266780 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 11 | 219782 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 7199500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 80 | 2878000 | ST synchronized process.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 191880
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9433000
| Sylhet Area Total |  |  |  | 2477 | 1573 | 35204789
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 22116363
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 750720 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 45 | 232800 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 67 | 368256 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 270 | 7380288 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 244125
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 698880
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2403840
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1059120
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 677520
| Khulna Area Total |  |  |  | 2384 | 1744 | 35931912
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 834240 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 33 | 691232 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 70 | 1879109 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 16871800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 212 | 4620491
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 29 | 290400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 938 | 25187272
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 338544 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 19 | 105378 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 584189
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 345632 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 168 | 4507191
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 9749491
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 224035 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 380160
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 190026
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 903480
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 702480 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 151 | 1199973 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1832928
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1727232
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27240
| Rajshahi Area Total |  |  |  | 2129 | 1317 | 22817979
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Reserve.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 174 | 4263200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 9 | 37000 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1751750
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30666
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1461888
| Rangpur Area Total |  |  |  | 720 | 402 | 7544504
| Total |  |  |  | 21584 | 13256 | 276821642
| Eastern Grid Total |  |  |  | 14393 | 8855 | 185339975
| Western Grid Total |  |  |  | 7191 | 4401 | 91481667
| National Grid Total |  |  |  | 21584 | 13256 | 276821642
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-17
(a) ENTIRE EASTERN GRID : |  | 8838.44 | MW | (b) ENTIRE WESTERN GRID : |  | 4142.6 | MW
i) Dhaka area |  | 4929.34 | MW | i) Khulna area |  | 1742 | MW
ii) Chittagong area |  | 1408.1 | MW | ii) Rajshahi area |  | 1271.6 | MW
iii) Comilla area |  | 1264 | MW | iii) Barisal area |  | 431 | MW
iv) Mymensingh area |  | 881 | MW | iv) Rangpur area |  | 698 | MW
v) Sylhet area |  | 356 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12981.04 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 34 | 20:00 | Hasnabad | 158 | 19:00 | Palashbari | 108 | 01:00
Agargaon | 97 | 13:00 | Hathazari | 103 | 22:00 | Panchagarh | 58 | 19:30
Agrabad | 86 | 17:00 | Ishurdi | 79 | 19:30 | Patuakhali | 133 | 23:00
AKS | 19 | 09:00 | Jaldhaka | 56 | 19:00 | PHP | 5 | 10:00
AKSML | 128 | 18:00 | Jamalpur | 124 | 22:00 | Purbachal | 20 | 21:00
Amnura | 42 | 23:00 | Jashore | 131 | 21:00 | Purbasadipur | 100 | 21:00
Ashuganj | 41 | 12:00 | Jhenaidah | 126 | 19:30 | Rahim | 20 | 23:00
Bagerhat | 117 | 22:00 | Joydebpur | 199 | 18:30 | Rajbari | 72 | 19:30
Bakulia | 132 | 16:00 | Joypurhat | 58 | 19:30 | Rajendrapur | 112 | 01:00
Banani | 52 | 13:00 | Juldah | 24 | 12:00 | Rajshahi | 168 | 21:00
Bangabhaban | 22 | 10:00 | Kabirpur | 277 | 17:00 | Rajshahi | 36 | 23:00
Barapukuria | 49 | 19:30 | Kachua | 84 | 22:00 | Ramganj | 126 | 22:00
Barguna | 22 | 22:00 | Kallyanpur | 111 | 19:00 | Rampur | 21 | 00:00
Barishal | 121 | 13:00 | Kalurghat | 6 | 10:00 | Rangamati | 14 | 19:00
Barishal | 70 | 19:00 | Kamrangirchar | 73 | 13:00 | Rangpur | 124 | 22:00
Baroaulia | 83 | 20:00 | Kaptai | 4.5 | 19:30 | Ruppur | 4.8 | 09:00
Baroirhat | 63 | 20:00 | Kazla | 91 | 19:30 | Saidpur | 74 | 21:00
Bashundhara | 186 | 15:00 | Keranigonj | 82 | 01:00 | Satkhira | 129 | 22:00
BashundharaCement | 6 | 23:00 | Khagrachori | 26 | 20:00 | Satmasjid | 102 | 19:00
Beanibazar | 32 | 22:00 | Khulna | 99 | 21:00 | Savar | 191 | 10:00
Benapole | 56 | 22:00 | Khulshi | 187 | 09:00 | Shahjadpur | 98 | 19:30
Bhaluka | 126 | 23:00 | Kishoreganj | 132 | 00:00 | Shahjibazar | 118 | 01:00
Bhandaria | 62 | 21:00 | Kodda | 331 | 11:00 | Shahmirpur | 46.3 | 00:00
Bhangura | 37 | 21:00 | KSRM | 21.2 | 00:00 | Shariatpur | 78 | 21:00
Bheramara(GK) | 61 | 21:00 | Kulaura | 32 | 19:00 | Sherpur | 142 | 00:00
Bhulta | 208 | 22:00 | Kurigram | 53 | 19:30 | Shikalbaha | 33 | 00:00
Bog-Sherpur | 48 | 21:00 | Kushtia | 144 | 21:00 | Shitalakhya | 135 | 16:00
Bogura | 157 | 22:00 | Lalbag | 78 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 44 | 22:00 | Lalmonirhat | 36 | 19:00 | Shyampur | 164 | 06:00
Brahmanbaria | 170 | 01:00 | Madanganj | 183 | 22:00 | Siddhirganj | 116 | 15:00
BSRM | 164 | 03:00 | Madaripur | 116 | 22:00 | Sirajganj | 94 | 22:00
Cantonment | 154 | 19:00 | Madartek | 86 | 00:00 | Sonargaon | 89 | 00:00
Chandpur | 81 | 00:00 | Madunaghat | 63 | 19:00 | Sreemongol | 42 | 00:00
Chandraghona | 32 | 21:00 | Magura | 64 | 20:00 | Srinagar | 47.34 | 21:00
Chapai | 78 | 21:00 | Mahasthangarh | 66 | 02:00 | SSM | 16 | 02:00
Charsaidpur | 37 | 12:00 | Manikganj | 92 | 22:00 | Sunamganj | 33 | 19:30
Chauddagram | 56 | 20:00 | Maniknagar | 85 | 13:00 | Sylhet | 90 | 19:00
Chhatak | 13 | 19:30 | Matarbari | 46 | 19:30 | Tangail | 187 | 22:00
Chowmuhani | 228 | 00:00 | Matuail | 64 | 12:00 | Thakurgaon | 66 | 22:00
Chuadanga | 110 | 21:00 | Millgate | 58 | 16:00 | TK | 20.8 | 21:00
Coxsbazar | 121 | 22:00 | Mirpur | 138 | 19:30 | Tongi | 134 | 17:00
Cumilla(N) | 151 | 00:00 | Mirsorai | N/A | N/A | Ullon | 43 | 22:00
Cumilla(S) | 169 | 19:30 | Mithapukur | 26 | 00:00 | Uttara | 104 | 14:00
Daudkandi | 160 | 19:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 14:00
Dhaka | 40 | 12:00 | Mogbazar | 127 | 15:00 | Zigatola | 47 | 18:30
Dhamrai | 128 | 20:00 | Mongla | 32 | 12:00
Dhanmondi | 160 | 13:00 | Motijheel | 40 | 13:00
Dohazari | 108 | 21:00 | Munshiganj | 110 | 23:00
Faridpur | 146 | 19:00 | Mymensingh | 234 | 00:00
Fatullah | 68 | 15:00 | Naogaon | 118 | 21:00
Fenchuganj | 38 | 00:00 | Narail | 58 | 19:30
Feni | 132 | 22:00 | Narinda | 74 | 15:00
Ghorashal | 59 | 00:00 | Narshingdi | 186 | 00:00
Goalpara | 30 | 14:00 | Natore | 140 | 22:00
Gollamari | 63 | 20:00 | Nawabganj | 59 | 22:00
Gopalganj | 108 | 22:00 | Netrakona | 104 | 00:00
GPH | 91 | 13:00 | New | 83.8 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 21:00 | 404 | 12:00 | Kaliakoir | 399 | 0.77083 | 385 | 0.33333
| Bheramara | 398 | 8:00 | 392 | 15:00 | Bhulta | 400 | 0.16667 | 380 | 0.5
| Ashuganj(N) | 404 | 2:00 | 384 | 12:00 | Gopalganj | 416 | 0.625 | 402 | 0.58333
| Payra | 420 | 7:00 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 239 | 18:00 | 230 | 14:00
| Ishurdi | 237 | 17:00 | 226 | 12:00 | Megnaghat | 232 | 18:30 | 228 | 10:00
| Ashuganj | 242 | 3:00 | 235 | 8:00 | Fenchuganj | 245 | 2:00 | 238 | 23:00
| Serajganj | 238 | 17:00 | 230 | 9:00 | Siddhirganj | 231 | 6:00 | 222 | 5:00
| Baghabari | 236 | 17:00 | 228 | 7:00 | Maniknagar | 228 | 6:00 | 218 | 12:00
| Barapukuria | 236 | 6:00 | 227 | 8:00 | Agargaon | 228 | 18:00 | 216 | 12:00
| Bogra | 236 | 4:00 | 227 | 10:00 | Barisal | 239 | 18:00 | 231 | 1:00
| Rajshahi | 240 | 17:00 | 226 | 11:00 | Bhola 225 MW | 242 | 7:00 | 231 | 1:00
| Khulna South | 234 | 15:00 | 215 | 7:00 | AKSML | 237 | 21:00 | 229 | 1:00
| Rampura | 229 | 4:00 | 220 | 11:00 | BSRM | 234 | 21:00 | 227 | 12:00
| Haripur | 226 | 20:00 | 218 | 12:00 | Bibiyana | 242 | 9:00 | 236 | 8:00
| Hasnabad | 228 | 22:00 | 220 | 11:00 | Bhulta | 230 | 2:00 | 219 | 12:00
| Shyampur | 228 | 21:00 | 217 | 12:00 | Ashuganj (S) | 238 | 2:00 | 229 | 12:00
| Aminbazar | 229 | 1:00 | 219 | 2:00 | Kaliakoir | 229 | 1:00 | 221 | 13:00
| Tongi | 231 | 6:00 | 218 | 11:00 | GPH | 236 | 19:30 | 228 | 24:00
| Comilla (N) | 232 | 5:00 | 226 | 12:00 | Jhenaidah | 230 | 15:00 | 215 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 01:00 | 127 | 12:00 | Manikganj | 131 | 19:30 | 125 | 12:00
| Agargaon | 136 | 02:00 | 127 | 12:00 | Maniknagar | 131 | 06:00 | 122 | 12:00
| Agrabad | 135 | 18:00 | 129 | 12:00 | Matarbari | 121 | 08:00 | 109 | 00:00
| AKS | 135 | 09:00 | 127 | 13:00 | Matuail | 137 | 21:00 | 129.5 | 12:00
| Aminbazar | 137 | 02:00 | 131 | 10:00 | Millgate | 134 | 01:00 | 127 | 12:00
| Amnura | 135 | 17:00 | 122 | 11:00 | Mirpur | 137 | 06:00 | 130 | 10:00
| Ashuganj | 140 | 08:00 | 134 | 00:00 | Mithapukur | 138 | 04:00 | 130 | 08:00
| Bagerhat | 137 | 18:30 | 124 | 00:00 | Modern | 134 | 18:00 | 129 | 00:00
| Bakulia | 134 | 18:30 | 128 | 00:00 | Mogbazar | 137 | 03:00 | 128 | 12:00
| Banani | 136 | 06:00 | 126 | 12:00 | Mongla | 136 | 15:00 | 126 | 00:00
| Bangabhaban | 130 | 00:00 | 122 | 12:00 | Motijheel | 130 | 00:00 | 122 | 12:00
| Barapukuria | 139 | 06:00 | 132 | 08:00 | Munshiganj | 139 | 19:30 | 132 | 08:00
| Barguna | 137 | 18:00 | 129 | 00:00 | Mymensingh | 140 | 07:00 | 125 | 00:00
| Barishal | 137 | 18:00 | 129 | 07:00 | Naogaon | 134 | 17:00 | 129 | 08:00
| Barishal | 138 | 06:00 | 132 | 00:00 | Narail | 135 | 18:00 | 125 | 01:00
| Baroaulia | 138 | 21:00 | 130 | 00:00 | Narinda
| Baroirhat | 134 | 18:30 | 126 | 01:00 | Narshingdi | 133 | 06:00 | 123 | 12:00
| Bashundhara | 134 | 01:00 | 126 | 15:00 | Natore | 136 | 17:00 | 128 | 08:00
| BashundharaCement | 139 | 21:00 | 132 | 07:00 | Nawabganj | 138 | 21:00 | 129 | 12:00
| Beanibazar | 139 | 09:00 | 134 | 00:00 | Netrakona | 139 | 07:00 | 124 | 00:00
| Benapole | 139 | 18:30 | 124 | 07:00 | New | 135 | 02:00 | 127 | 14:00
| Bhaluka | 139 | 07:00 | 120 | 00:00 | Niamatpur | 137 | 05:00 | 125 | 20:00
| Bhandaria | 135 | 07:00 | 124 | 00:00 | Noapara | 140 | 18:30 | 127 | 00:00
| Bhangura | 140 | 17:00 | 134 | 12:00 | Pabna | 136 | 06:00 | 129 | 12:00
| Bheramara | 137 | 06:00 | 129 | 12:00 | Palashbari | 137 | 05:00 | 129 | 08:00
| Bheramara(GK) | 140 | 17:00 | 131 | 10:00 | Panchagarh | 137 | 03:00 | 125 | 01:00
| Bhulta | 131 | 07:00 | 125 | 11:00 | Patuakhali | 136 | 17:00 | 130 | 00:00
| Bog-Sherpur | 140 | 06:00 | 133 | 10:00 | PHP | 133 | 07:00 | 126 | 00:00
| Bogura | 139 | 04:00 | 132 | 09:00 | Purbachal | 137 | 06:00 | 126 | 12:00
| Bogura | 140 | 04:00 | 132 | 10:00 | Purbasadipur | 137 | 03:00 | 126 | 09:00
| Brahmanbaria | 139 | 08:00 | 130 | 22:00 | Rahim | 137 | 20:00 | 130 | 12:00
| Cantonment | 135 | 02:00 | 126 | 12:00 | Rajbari | 135 | 18:00 | 126 | 12:00
| Chandpur | 137 | 17:00 | 132 | 00:00 | Rajendrapur | 135 | 08:00 | 124 | 09:00
| Chandraghona | 136 | 07:00 | 130 | 00:00 | Rajshahi | 133 | 17:00 | 123 | 11:00
| Chapai | 134 | 17:00 | 123 | 11:00 | Rajshahi | 131 | 17:00 | 122 | 11:00
| Charsaidpur | 140 | 22:00 | 132 | 12:00 | Ramganj | 133 | 18:00 | 125 | 01:00
| Chauddagram | 134 | 06:00 | 129 | 04:00 | Rampur | 135 | 21:00 | 129 | 15:00
| Chhatak | 136 | 07:00 | 132 | 23:00 | Rampura | 136 | 04:00 | 129 | 11:00
| Chowmuhani | 131 | 10:00 | 121 | 00:00 | Rangamati | 135 | 07:00 | 129 | 15:00
| Chuadanga | 133 | 18:30 | 121 | 12:00 | Rangpur | 137 | 03:00 | 128 | 22:00
| Coxsbazar | 121 | 09:00 | 107 | 00:00 | Ruppur | 138 | 17:00 | 130 | 12:00
| Cumilla(N) | 136 | 07:00 | 132 | 00:00 | Saidpur | 137 | 02:00 | 127 | 09:00
| Cumilla(S) | 136 | 07:00 | 128 | 15:00 | Satkhira | 138 | 15:00 | 123 | 07:00
| Daudkandi | 137 | 19:00 | 127 | 12:00 | Satmasjid | 135 | 02:00 | 127 | 12:00
| Dhaka | 137 | 04:00 | 128 | 12:00 | Savar | 137 | 03:00 | 130 | 12:00
| Dhamrai | 132 | 02:00 | 124 | 12:00 | Shahjadpur | 141 | 17:00 | 136 | 10:00
| Dhanmondi | 137 | 01:00 | 129 | 12:00 | Shahjibazar | 139 | 09:00 | 132 | 00:00
| Dohazari | 130 | 18:30 | 123 | 00:00 | Shahmirpur | 135 | 19:30 | 129 | 00:00
| Faridpur | 135 | 18:00 | 127 | 12:00 | Shariatpur | 136 | 18:00 | 127 | 00:00
| Fatullah | 137 | 21:00 | 128 | 12:00 | Sherpur | 140 | 07:00 | 129 | 00:00
| Fenchuganj | 139 | 14:00 | 135 | 00:00 | Shikalbaha | 135 | 10:00 | 130 | 00:00
| Feni | 135 | 07:00 | 128 | 00:00 | Shikalbaha | 135 | 20:00 | 130 | 00:00
| Ghorashal | 137 | 00:00 | 137 | 00:00 | Shitalakhya | 139 | 02:00 | 131 | 12:00
| Goalpara | 140 | 18:30 | 129 | 07:00 | Sholosohor
| Gollamari | 141 | 21:00 | 126 | 13:00 | Shyampur | 136 | 22:00 | 130 | 00:00
| Gopalganj | 141 | 18:30 | 128 | 14:00 | Shyampur | 136 | 21:00 | 129 | 12:00
| Gopalganj_I | 139 | 18:30 | 131 | 14:00 | Siddhirganj | 137 | 02:00 | 131 | 12:00
| Gulshan | 136 | 03:00 | 127 | 12:00 | Sirajganj | 140 | 06:00 | 132 | 11:00
| Halishahar | 136 | 21:00 | 129 | 08:00 | Sonargaon | 137 | 18:30 | 131 | 12:00
| Haripur | 137 | 20:00 | 130 | 12:00 | Sreemongol | 140 | 09:00 | 134 | 00:00
| HaripurSBU | 137 | 05:00 | 131 | 12:00 | Srinagar | 137 | 04:00 | 129 | 12:00
| Hasnabad | 138 | 03:00 | 132 | 11:00 | SSM | 140 | 18:30 | 130 | 00:00
| Hathazari | 139 | 18:00 | 133 | 00:00 | Sunamganj | 136 | 09:00 | 131 | 22:00
| Ishurdi | 137 | 06:00 | 130 | 12:00 | Sylhet | 136 | 09:00 | 134 | 00:00
| Jaldhaka | 137 | 03:00 | 128 | 09:00 | Tangail | 138 | 06:00 | 128 | 11:00
| Jamalpur | 140 | 07:00 | 132 | 15:00 | Thakurgaon | 136 | 03:00 | 124 | 09:00
| Jashore | 137 | 18:00 | 124 | 12:00 | TK | 136 | 18:00 | 131 | 00:00
| Jhenaidah | 137 | 18:00 | 126 | 13:00 | Tongi | 135 | 03:00 | 129 | 11:00
| Jhenaidah | 138 | 18:30 | 126 | 11:00 | Ullon | 136 | 06:00 | 127 | 12:00
| Joydebpur | 140 | 21:00 | 132 | 09:00 | Uttara | 136 | 23:00 | 127 | 12:00
| Joypurhat | 138 | 05:00 | 126 | 21:00 | UttaraNew | 137 | 06:00 | 130 | 10:00
| Juldah | 136 | 18:00 | 129 | 00:00 | Zigatola | 137 | 21:00 | 129 | 12:00
| Kabirpur | 138 | 07:00 | 125 | 15:00
| Kachua | 136 | 17:00 | 130 | 00:00
Kaliakoir
| Kallyanpur | 137 | 03:00 | 131 | 15:00
| Kalurghat | 135 | 07:00 | 130 | 00:00
| Kamrangirchar | 138 | 05:00 | 131 | 12:00
| Kaptai | 135 | 00:00 | 132 | 10:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 582 | 8339 | 4699 | 13038 |  |  |  | QF-LDC-11
0:30 | 546 | 8262 | 4426.5 | 12688.5 | Date: | 2022-05-17
1:00 | 510 | 8185 | 4154 | 12339
1:30 | 446 | 8103.5 | 4009 | 12112.5
2:00 | 382 | 8022 | 3864 | 11886
2:30 | 411 | 7870.5 | 3754 | 11624.5 | [5 empty] | Gen. at Eve. Peak | 13256 | 13256 MW (21:00 )
3:00 | 440 | 7719 | 3644 | 11363 | [6 empty] | 21:00
3:30 | 486 | 7667.5 | 3606 | 11273.5 | [5 empty] | Gen. at Day Peak | 11026 | 11026 MW (12:00 )
4:00 | 532 | 7616 | 3568 | 11184 | [6 empty] | 12:00
4:30 | 598 | 7381.5 | 3470 | 10851.5 | [5 empty] | Highest Generation | 13454
5:00 | 664 | 7147 | 3372 | 10519 | [6 empty] | 22:00
5:30 | 638 | 6804.5 | 3135.5 | 9940
6:00 | 612 | 6462 | 2899 | 9361
6:30 | 523 | 6291 | 2847.5 | 9138.5
7:00 | 434 | 6120 | 2796 | 8916
7:30 | 420 | 5748 | 2792.5 | 8540.5
8:00 | 406 | 5376 | 2789 | 8165
8:30 | 430 | 5640 | 2874 | 8514
9:00 | 454 | 5904 | 2959 | 8863
9:30 | 471 | 6270.5 | 3003 | 9273.5
10:00 | 488 | 6637 | 3047 | 9684
10:30 | 429 | 6910.5 | 3095 | 10005.5
11:00 | 370 | 7184 | 3143 | 10327
11:30 | 416 | 7406.5 | 3270 | 10676.5
12:00 | 462 | 7629 | 3397 | 11026
12:30 | 410 | 7816.5 | 3453.5 | 11270
13:00 | 358 | 8004 | 3510 | 11514
13:30 | 336 | 8031 | 3540.5 | 11571.5
14:00 | 314 | 8058 | 3571 | 11629
14:30 | 392 | 8160.5 | 3581 | 11741.5
15:00 | 470 | 8263 | 3591 | 11854
15:30 | 456 | 8256.5 | 3689 | 11945.5
16:00 | 442 | 8250 | 3787 | 12037
16:30 | 548 | 8143.5 | 3767.5 | 11911
17:00 | 654 | 8037 | 3748 | 11785
17:30 | 608 | 7836 | 3712.5 | 11548.5
18:00 | 562 | 7635 | 3677 | 11312
18:30 | 387 | 8165.5 | 3868 | 12033.5
19:00 | 212 | 8696 | 4059 | 12755
19:30 | 76 | 8748 | 4319 | 13067
20:00 | 72 | 8810 | 4334 | 13144 |  |  |  | Executive Engineer
20:30 | 114 | 8832.5 | 4367.5 | 13200 |  |  |  | Network Operation Division
21:00 | 156 | 8855 | 4401 | 13256
21:30 | 305 | 8842 | 4513 | 13355
22:00 | 454 | 8829 | 4625 | 13454 |  |  |  |  | Page 6 of 7
22:30 | 466 | 8689.5 | 4663.5 | 13353
23:00 | 478 | 8550 | 4702 | 13252
23:30 | 530 | 8444.5 | 4700.5 | 13145
24:00 | 582 | 8339 | 4699 | 13038
13256 MW (21:00 )
11026 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-17 |  | Energy |  | 276821642
[13 empty] | 2022-05-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3367 | 914 | 2087 | 766 | 4115 | 1134 | 30 | 0 | 495 | 130 | 0 | 0
0:30 | 3628 | 915.5 | 2057 | 383 | 4036 | 1129.5 | 30 | 0 | 381.5 | 128 | 0 | 0 | Date: | 2022-05-17
1:00 | 3889 | 917 | 2027 | 0 | 3957 | 1125 | 30 | 0 | 268 | 126 | 0 | 0
1:30 | 3911.5 | 917.5 | 1983 | 0 | 3841.5 | 1120 | 30 | 0 | 184 | 125 | 0 | 0 | [8 empty] | Total Energy | 276.8216 | Total Energy Gen 276.822 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 276.822 MKWHr
2:00 | 3934 | 918 | 1939 | 0 | 3726 | 1115 | 30 | 0 | 100 | 124 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3936.5 | 918 | 1953.5 | 0 | 3512.5 | 1070 | 30 | 0 | 82 | 122 | 0 | 0 | [8 empty] | Energy Requirement | 276.8216
3:00 | 3939 | 918 | 1968 | 0 | 3299 | 1025 | 30 | 0 | 64 | 120 | 0 | 0
3:30 | 3898.5 | 917.5 | 1992 | 0 | 3227 | 1024.5 | 30 | 0 | 64 | 120 | 0 | 0 | [6 empty] | Shortage
4:00 | 3858 | 917 | 2016 | 0 | 3155 | 1024 | 30 | 0 | 64 | 120 | 0 | 0
4:30 | 3751.5 | 916.5 | 1979.5 | 0 | 2978.5 | 1014.5 | 30 | 0 | 64 | 117 | 0 | 0
5:00 | 3645 | 916 | 1943 | 0 | 2802 | 1005 | 30 | 0 | 64 | 114 | 0 | 0
5:30 | 3459.5 | 915.5 | 1956.5 | 0 | 2584 | 840 | 30 | 0 | 40 | 111 | 3.5 | 0
6:00 | 3274 | 915 | 1970 | 0 | 2366 | 675 | 30 | 0 | 16 | 108 | 7 | 0
6:30 | 3135 | 915.5 | 1984 | 0 | 2258.5 | 675 | 30 | 0 | 16 | 105 | 19.5 | 0 |  |  |  |  | Coal
7:00 | 2996 | 916 | 1998 | 0 | 2151 | 675 | 30 | 0 | 16 | 102 | 32 | 0
7:30 | 2997.5 | 915.5 | 1957 | 0 | 1804 | 675 | 30 | 0 | 8 | 106 | 47.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2999 | 915 | 1916 | 0 | 1457 | 675 | 30 | 0 | 0 | 110 | 63 | 0
8:30 | 3095.5 | 915 | 1958 | 0 | 1636 | 674.5 | 30 | 0 | 8 | 113 | 84 | 0
9:00 | 3192 | 915 | 2000 | 0 | 1815 | 674 | 30 | 0 | 16 | 116 | 105 | 0
9:30 | 3125 | 915.5 | 2019.5 | 0 | 2223.5 | 674 | 30 | 0 | 40 | 116 | 130 | 0
10:00 | 3058 | 916 | 2039 | 0 | 2632 | 674 | 30 | 0 | 64 | 116 | 155 | 0
10:30 | 3128 | 916 | 2055 | 0 | 2865 | 674 | 30 | 0 | 81 | 118 | 138.5 | 0
11:00 | 3198 | 916 | 2071 | 0 | 3098 | 674 | 30 | 0 | 98 | 120 | 122 | 0
11:30 | 3215.5 | 915.5 | 2098.5 | 64.5 | 3295 | 674 | 30 | 0 | 106.5 | 121 | 156 | 0
12:00 | 3233 | 915 | 2126 | 129 | 3492 | 674 | 30 | 0 | 115 | 122 | 190 | 0
12:30 | 3213 | 915.5 | 2110.5 | 327 | 3574 | 674 | 30 | 0 | 138.5 | 121 | 166.5 | 0
13:00 | 3193 | 916 | 2095 | 525 | 3656 | 674 | 30 | 0 | 162 | 120 | 143 | 0
13:30 | 3193 | 916 | 2095 | 525 | 3656 | 674 | 30 | 0 | 162 | 120 | 143 | 0
14:00 | 3193 | 916 | 2095 | 525 | 3656 | 674 | 30 | 0 | 162 | 120 | 143 | 0
14:30 | 3195 | 913.5 | 2075.5 | 632 | 3737 | 674 | 30 | 0 | 182.5 | 126 | 118.5 | 0
15:00 | 3197 | 911 | 2056 | 739 | 3818 | 674 | 30 | 0 | 203 | 132 | 94 | 0
15:30 | 3206.5 | 910.5 | 2073 | 760 | 3861.5 | 694 | 30 | 0 | 202.5 | 131 | 76.5 | 0
16:00 | 3216 | 910 | 2090 | 781 | 3905 | 714 | 30 | 0 | 202 | 130 | 59 | 0
16:30 | 3220 | 910 | 2062.5 | 693.5 | 3941 | 619 | 30 | 0 | 263.5 | 128 | 45.5 | 0
17:00 | 3220 | 910 | 2035 | 606 | 3977 | 524 | 30 | 0 | 325 | 126 | 32 | 0
17:30 | 3183 | 910.5 | 1945.5 | 363.5 | 4040.5 | 573.5 | 30 | 0 | 361.5 | 122 | 18.5 | 0
18:00 | 3146 | 911 | 1856 | 121 | 4104 | 623 | 30 | 0 | 398 | 118 | 5 | 0
18:30 | 3188.5 | 911.5 | 1995 | 457.5 | 4198 | 638.5 | 30 | 4 | 481 | 127 | 2.5 | 0
19:00 | 3231 | 912 | 2134 | 794 | 4292 | 654 | 30 | 8 | 564 | 136 | 0 | 0
19:30 | 3248 | 913 | 2184 | 952 | 4344 | 674 | 30 | 8 | 580 | 134 | 0 | 0
20:00 | 3238 | 913 | 2236 | 953 | 4356 | 664 | 30 | 10 | 614 | 130 | 0 | 0
20:30 | 3253.5 | 913 | 2247.5 | 953 | 4370.5 | 684 | 30 | 9.5 | 609 | 130 | 0 | 0
21:00 | 3269 | 913 | 2259 | 953 | 4385 | 704 | 30 | 9 | 604 | 130 | 0 | 0
21:30 | 3297.5 | 913 | 2256 | 921 | 4363 | 834 | 30 | 9 | 602.5 | 129 | 0 | 0
22:00 | 3326 | 913 | 2253 | 889 | 4341 | 964 | 30 | 9 | 601 | 128 | 0 | 0
22:30 | 3315 | 913.5 | 2177.5 | 910 | 4276 | 1014 | 30 | 9 | 578 | 130 | 0 | 0
23:00 | 3304 | 914 | 2102 | 931 | 4211 | 1064 | 30 | 9 | 555 | 132 | 0 | 0
23:30 | 3335.5 | 914 | 2094.5 | 848.5 | 4163 | 1099 | 30 | 4.5 | 525 | 131 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.2° C
24:00 | 3367 | 914 | 2087 | 766 | 4115 | 1134 | 30 | 0 | 495 | 130 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 276.822 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 276.822 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716100
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 8 | 8 | [7 empty] | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 401878
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 2 | 8 | 18 | 18 | 18 | 19 | 17 | 13 | 9 | 3 | 0 | [8 empty] | 115425
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 203 | 204 | 208 | 203 | 203 | 203 | 203 | 203 | 209 | 218 | 204 | 203 | 219 | 221 | 203 | 203 |  | 222 | 218 | 224 | 204 | 208 | 204 | 207 | 4982478
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 3 |  | 236521
12 | Hathazari 100 MW peaking PP | [14 empty] | 9 | 9 | 9 | 9 |  | 42 | 43 | 51 | 51 | 51 | 51 |  | 298368
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 96 | 51 | 68 | 68 | 77 | 85 | 85 | 88 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2366909
| Daudkandi 200 MW PP (B.Trac) | [12 empty] | 30 | 30 | 195 | 196 | 150 | 20 |  | 195 | 200 | 200 | 200 | 200 | 200 | 150 | 1647168
14 | Titas 50 MW Peaking PP | [12 empty] | 42 | 48 | 48 | 47 | 47 | 47 |  | 47 | 40 | 40 | 40 | 40 | 40 | 41 | 510376
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 336 | 336 | 300 | 280 | 280 | 280 | 337 | 300 | 333 | 328 | 322 | 324 | 318 | 326 | 325 | 260 |  | 320 | 324 | 325 | 328 | 330 | 330 | 332 | 7688694
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 280 | 245 | 245 | 145 | 95 | 95 | 15 | 23 | 145 | 188 | 246 | 252 | 268 | 278 | 278 | 265 | 267 |  | 278 | 278 | 278 | 278 | 280 | 275 | 278 | 5444725
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4221000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6013073
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 16 | 28 | 32 | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 768744
33 | Ashuganj 225 MW CCPP | 193 | 193 | 188 | 185 | 189 | 189 | 188 | 161 | 161 | 191 | 199 | 210 | 183 | 182 | 203 | 195 | 191 | 191 |  | 192 | 196 | 194 | 194 | 198 | 202 | 205 | 4665000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 275 | 275 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6979000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 132960
36 | Chandpur 150 MW CCPP | 91 | 91 | 91 | 90 | 91 | 90 | 90 | 91 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 92 | 90 | 88 | 2152770
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 316 | 325 | 333 | 252 | 147 | [21 empty] | 1392640
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5053350
41 | Haripur 360MW CCPP(HPL) | 258 | 263 | 262 | 277 | 278 | 298 | 332 | 337 | 332 | 345 | 332 | 322 | 322 | 317 | 317 | 313 | 314 | 272 |  | 313 | 316 | 317 | 317 | 317 | 328 | 337 | 7372000
42 | RPCL 210MW CCPP | 107 | 132 | 135 | 135 | 135 | 118 | 110 | 80 | 70 | 70 | 70 | 67 | 67 | 68 | 67 | 70 | 72 | 71 |  | 101 | 102 | 115 | 115 | 117 | 125 | 153 | 2253120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 0 | 4 | 11 | 24 | 36 | 53 | 34 | 43 | 4 | 11 | 5 | 1 |  | 0 | [6 empty] | 221230
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 44 | 44 | 43 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1030000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688152
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1413696
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 10 | 50 | 72 | 72 | 75 | 77 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1683840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 205 | 219 | 220 | 219 | 219 | 193 | 204 | 219 | 219 |  | 220 | 219 | 219 | 219 | 219 | 219 | 219 | 5131510
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [13 empty] | 18 | 12 | 12 | 22 | 22 |  | 35 | 35 | 36 | 34 | 35 | 34 | 35 | 266780
53 | Sylhet 10MW PP (Desh) | [5 empty] | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 191880
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [8 empty] | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 176000
55 | Fenchugonj 51 MW PP (Barakatullah) | [21 empty] | 34 | 53 | 53 | 53 | 53 | 216000
56 | Shahjahanulla 25 MW PP |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 7 |  | 7 | 10 | 10 | 10 | 11 | 11 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219782
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 260 | 255 | 280 | 270 | 270 | 260 | 270 | 315 | 290 | 300 | 320 | 300 | 305 | 270 | 320 | 280 | 270 |  | 290 | 320 | 330 | 330 | 300 | 300 | 300 | 7199500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 360 | 400 | 400 | 360 | 400 | 398 | 400 | 400 | 394 | 398 | 400 | 400 |  | 398 | 396 | 395 | 400 | 400 | 401 | 401 | 9433000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 17 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1200646
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 24 |  |  | 5 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 532800
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 50712
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 0 | 16 | 16 | 16 | 0 | 15 | 19 | 19 | 19 |  | 0 | 0 | 0 | 19 | 19 | 19 | 19 | 325764
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 16 | 16 | 16 | 16 | 17 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 363420
63 | Impoprt (Tripura) | 126 | 124 | 120 | 120 | 114 | 108 | 102 | 110 | 116 | 116 | 120 | 122 | 120 | 124 | 132 | 130 | 126 | 118 |  | 136 | 134 | 130 | 130 | 128 | 132 | 130 | 2921280
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 39 | 38 | 35 | 30 | 26 | 9 | 2 | 2 | 2 | 4 | 6 | 5 | 2 | 2 | 2 | 6 |  | 9 | 17 | 22 | 23 | 32 | 37 | 31 | 421920
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [15 empty] | 19 | 19 | 19 | 191412
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 |  |  | 140400
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 25 | 25 | 25 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 0 | 30 | 33 | 33 | 33 | 737000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 0 | 7 | 7 | 0 | 8 | 8 | 8 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 368650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 22 | 21 | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 615420
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 461900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 735300
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 98 | 98 | 98 | 99 | 100 | 97 | 97 | 95 | 97 | 99 | 99 | 99 | 97 | 95 | 92 |  | 94 | 94 | 96 | 96 | 98 | 99 | 102 | 2306272
| Feni Lanka Power | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 88 | 95 | 95 | 95 | 95 | 94 | 94 | 94 | 94 | 81 | 81 |  | 81 | 81 | 90 | 100 | 100 | 96 | 96 | 2329020
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 220080
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 144 | 144 | 144 | 108 | 35 | 105 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 126 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3431520
77 | Siddhirganj 100 PP(Dutch Bangla) | 87 | 40 | 16 | 16 |  |  |  |  | 6 | 48 | 73 | 77 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 91 | 91 | 91 | 86 | 89 | 90 | 1466880
78 | Gazipur 52 MW PP | 49 | 25 | 24 | 24 | 24 | 16 | 16 |  | 7 | 29 | 49 | 49 | 49 | 40 | 40 | 48 | 48 | 48 |  | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 905280
79 | Kodda 150MW PP | 132 | 100 | 64 | 64 | 64 | 16 | 16 |  | 16 | 64 | 98 | 115 | 115 | 115 | 115 | 115 | 115 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2226720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 34 | 40 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 |  | 43 | 43 | 42 | 42 | 43 | 43 | 43 | 1002048
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 72 | 34 |  | 14 | 38 | 90 | 92 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2275200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 4 | 3 | 1 | 3 | 2 | 2 | 2 | 3 | 1 | 0 | [8 empty] | 29520
| Jodiac Power | 54 | 49 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 44 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1075684
| Karnaphuli Power Ltd. | 99 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 102 | 110 | 110 | 110 | 103 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 2522460
82 | Madanganj 102 PP(Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 91 | 62 | 48 | 92 | 79 | 79 | 78 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 96 | 96 | 94 | 96 | 96 | 2128848
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 120 | 120 | 125 | 125 | 140 | 130 | 125 | 145 | 120 | 120 | 140 | 140 | 120 | 140 | 140 | 140 | 115 | 130 |  | 140 | 140 | 137 | 130 | 142 | 135 | 120 | 3150749
87 | Meghnaghat 100 MW(IEL) | 97 | 98 | 97 | 97 | 94 | 90 | 90 | 91 | 82 | 82 | 80 | 81 | 80 | 79 | 79 | 79 | 80 | 79 |  | 88 | 88 | 88 | 88 | 88 | 85 | 83 | 2089920
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 90 | 35 | 68 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 75 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2457600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 440040
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 48 | 48 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1123776
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 43 | 43 | 43 |  | 43 | 43 | 51 | 51 | 51 | 51 | 43 | 1075128
94 | Gagnagar 102 MW PP (Digital Power) | 84 | 84 | 24 | 16 | 0 |  |  |  | 32 | 64 | 87 | 87 | 90 | 90 | 90 | 90 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1572048
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 44 |  | 6 | 42 | 44 | 43 | 43 | 44 | 44 | 43 | 47 | 46 | 50 | 12 |  | 43 | 50 | 50 | 50 | 50 | 50 | 50 | 1044480
96 | Chattogram 108 MW PP (ECPV) | 94 | 94 | 95 | 95 | 95 | 95 | 95 | 76 | 73 | 91 | 92 | 92 | 91 | 92 | 92 | 92 | 92 | 93 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2204160
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 43 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 35 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1282540
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1191856
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 |  | 163 | 163 | 163 | 163 | 163 |  |  | 3552873
102 | Sarishabari 3 MW Solar Plant | [10 empty] | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 5550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1291320
104 | Keranigonj 300 MW PP (APR) | [11 empty] | 72 | 300 | 243 | 303 | 191 | 89 | 21 |  | 304 | 302 | 302 | 304 | 272 | 304 | 201 | 2803984
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 25 | 96 | 97 | 97 | 97 | 97 | 25 |  | 99 | 100 | 100 | 98 | 97 | 97 | 95 | 1043657
106 | Mymensingh 200 MW PP (United) | 174 | 140 | 100 | 100 | 100 | 0 |  |  | 7 | 24 | 24 | 43 | 74 | 80 | 80 | 132 | 143 | 143 |  | 190 | 190 | 190 | 190 | 190 | 190 | 191 | 2592000
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 32 | 99 | 96 | 96 | 98 | 98 | 25 |  | 100 | 100 | 100 | 100 | 99 | 99 | 99 | 1074111
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 129 | 124 | 124 | 54 | 30 | 122 | 125 | 125 | 125 | 149 | 149 | 134 | 134 | 147 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3236544
115 | Juldah 100 MW PP Unit-3 (Acorn) | 63 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 50 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 38 | 1252800
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 180 | 180 | 136 | 50 | 54 | 90 | 172 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4329120
117 | Ashuganj 150MW PP (Midland) | 135 | 133 | 70 | 70 | 70 | 70 | 70 | 24 | 60 | 150 | 127 | 140 | 143 | 138 | 139 | 142 | 143 | 139 |  | 140 | 140 | 140 | 142 | 142 | 150 | 142 | 2933963
118 | Bibiyana-III 400 MW CCPP | 280 | 280 | 280 | 280 | 200 | 70 | 15 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 83 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2878000
| Jamalpur 115 MW PP (United) | 96 | 106 | 108 | 115 | 115 | 8 | 0 |  | 12 | 28 | 49 | 115 | 115 | 106 | 106 | 106 | 106 | 108 |  | 107 | 110 | 112 | 112 | 115 | 103 | 108 | 2132400
| Anwara 300 MW PP (United) | 282 | 283 | 283 | 282 | 282 | 283 | 281 | 245 | 283 | 283 | 282 | 266 | 266 | 266 | 266 | 282 | 283 | 283 |  | 283 | 283 | 283 | 267 | 248 | 248 | 247 | 6508582
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 42 | 50 | 50 | 100 | 100 | 65 | 42 | 39 | 39 | 39 | 39 |  | 63 | 64 | 64 | 64 | 64 | 50 | 50 | 1215360
| Anlima Energy Ltd. | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98 | 102 | 108 | 90 | 90 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2430055
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 26 |  | 4 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 745560
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 83 | 55 | 55 | 17 | [6 empty] | 25 | 67 | 81 | 81 | 74 | 71 | 81 | 81 |  | 81 | 82 | 80 | 81 | 81 | 81 | 81 | 1310400
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 |  | 9 | 1284120
120 | Eastern Zone Total | 8185 | 8022 | 7719 | 7616 | 7147 | 6462 | 6120 | 5376 | 5904 | 6637 | 7184 | 7629 | 8004 | 8058 | 8263 | 8250 | 8037 | 7635 |  | 8696 | 8748 | 8810 | 8855 | 8829 | 8550 | 8339 | 185339975
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 16 | 16 | 16 | 16 | 16 | 30 |  | 99 | 99 | 99 | 99 | 80 | 80 | 49 | 750720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 22 |  | 45 | 40 | 45 | 45 | 45 | 45 | 45 | 232800
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 53 | 53 | 35 | 38 | 70 | 92 | 94 | 105 | 105 | 105 | 105 | 94 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2403840
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 25 | 52 | 76 | 102 | 56 | 104 | 76 | 71 | 71 | 34 | 21 | 4 |  | 0 | [6 empty] | 677520
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | [13 empty] | 8 | 17 | 17 | 29 | 35 | 35 | 35 | 290400
133 | Bhola Nutan Biddut BD LTD (GAS) | 217 | 187 | 217 | 219 | 218 | 172 | 162 | 162 | 164 | 166 | 166 | 204 | 207 | 207 | 164 | 165 | 166 | 168 |  | 206 | 211 | 209 | 212 | 212 | 212 | 216 | 4620491
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 23 | 32 | 32 | 48 | 48 | 32 | 32 | 48 | 48 |  | 48 | 48 | 48 | 64 | 48 | 48 | 32 | 834240
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 87 | 87 | 86 | 84 | 75 | 75 | 75 | 75 | 75 | 75 | 84 | 82 | 70 | 70 | 70 | 70 |  | 73 | 70 | 70 | 70 | 70 | 85 | 85 | 1879109
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 31 | 30 | 26 | 23 | 21 | 23 | 25 | 25 | 25 | 26 | 26 | 29 | 27 | 27 | 26 |  | 30 | 30 | 29 | 33 | 35 | 36 | 35 | 691232
141 | Noapara 100 MW PP (Bangla Trac) | [14 empty] | 26 | 50 | 20 | 10 |  | 40 | 100 | 100 | 100 | 70 | 80 | 70 | 698880
142 | Noapara 40 MW PP (Khanjahan Ali) | [10 empty] | 0 | 16 |  | 8 |  | 6 | 40 | 32 |  | 0 | 30 | 40 | 40 | 40 |  |  | 244125
143 | Gopalganj 100 MW Peaking PP | 40 | [18 empty] | 42 | 53 | 70 | 67 | 65 | 65 | 65 | 368256
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 67 | 32 | 32 | [10 empty] | 15 | 15 | 50 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1059120
146 | Bheramara HVDC | 917 | 918 | 918 | 917 | 916 | 915 | 916 | 915 | 915 | 916 | 916 | 915 | 916 | 910 | 911 | 910 | 910 | 911 |  | 912 | 913 | 913 | 913 | 913 | 914 | 914 | 22116363
147 | Bheramara 410 MW CCPP | 325 | 325 | 325 | 325 | 325 | 280 | 240 | 240 | 340 | 300 | 300 | 320 | 315 | 310 | 300 | 290 | 285 | 280 |  | 275 | 275 | 275 | 270 | 265 | 260 | 255 | 7380288
148 | Payra 1320 MW | 950 | 940 | 850 | 850 | 830 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 540 | 350 | 450 |  | 480 | 500 | 490 | 530 | 790 | 890 | 960 | 16871800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 174 | 175 | 175 | 175 | 175 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 173 |  | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 4263200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 0 | [14 empty] | 0 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 338544
| Sirajgonj 6.55 MW Solar | [7 empty] | 1 | 3 | 3 | 4 | 4 | 3 | 4 | 1 | 1 | 1 | [9 empty] | 27240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 206 | 206 | 204 | 207 | 210 | 209 | 158 | 156 | 160 | 160 | 160 | 160 | 160 | 160 | 162 | 174 | 172 | 150 |  | 150 | 168 | 169 | 168 | 194 | 195 | 196 | 4507191
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 375 | 370 | 370 | 370 | 414 | 437 | 423 | 425 | 418 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 300 |  | 414 | 418 | 415 | 420 | 418 | 419 | 417 | 9749491
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 0 | [16 empty] | 4 |  | 4 | 20 | 21 | 19 | 19 | 20 | 19 | 105378
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 0 |  |  |  |  | 22 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 380160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 190026
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | 0 | [9 empty] | 16 | 16 | 34 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 584189
167 | Katakhali 50 MW Peaking PP | 15 | 0 | [10 empty] | 5 | 23 | 31 | 31 | 31 | 31 |  | 37 | 37 | 40 | 38 | 38 | 38 | 32 | 345632
168 | Santahar 50 MW Peaking PP | [17 empty] | 30 |  | 37 | 37 | 37 | 37 | 36 | 37 | 37 | 224035
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 34 | 0 |  |  |  |  | 10 | 34 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 43 | 52 | 52 | 52 | 52 | 903480
170 | Chapainawabganj 100 MW Peaking PP | 81 | 0 | [14 empty] | 80 | 80 |  | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 702480
171 | Baghabari 200 MW PP (Paramount) | [14 empty] | 22 | 149 | 152 | 20 |  | 56 | 150 | 151 | 151 | 151 | 151 | 151 | 1199973
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 0 |  |  |  | 1 | 30 | 35 | 59 | 87 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1832928
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 70 | 35 | 0 | [5 empty] | 30 | 60 | 100 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1727232
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 8 | 8 | 10 | 9 | 9 | 9 |  | 37000
176 | Rangpur 113 MW PP (Confidence) | 111 | 111 | 43 | 0 |  |  |  |  | 25 | 37 | 70 | 81 | 95 | 110 | 109 | 109 | 109 | 110 |  | 109 | 109 | 109 | 104 | 109 | 99 | 102 | 1751750
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 3 | 5 | 5 | 6 | 7 | 5 | 3 | 1 | 1 | 0 | [8 empty] | 30666
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 0 | [8 empty] | 34 | 72 | 72 | 72 | 92 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1461888
178