## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-23 | Monday
|  |  | Date (day): | 2022-05-23 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14132.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14732 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-22 | 2022-05-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 |  | 95 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 102 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 25 | 350 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 321 | 320 | 340 | 330
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 81 | 71 | 72 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 120 | 138 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 80 | 96 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 64 | 90 | 90 | 90 |  | 10 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 327 | 335 | 0 |  |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 75 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 90 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 53 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 48 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 228 | 242 | 270 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 235 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 98 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 98 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 91 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3088 | 3611 | 3855 | 3823 | 671 | 921
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 1 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 28 | 24 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 35 | 0 | 0 |  | 230 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 207 | 213 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 43 | 43 | 43 |  | 55 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 65 | 85 | 86 | 86 |  | 22 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 235 | 283 | 280 | 280 |  | 20 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 35 | 35 | 35 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 92 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1034 | 1251 | 1214 | 1272 | 601 | 496
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 173 | 127 | 175 | 170 | 71 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 340 | 340
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 29 | 30 | 30 |  | 15 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 33 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 98 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 6 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 128 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 21 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 36 | 42 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 110 | 110
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 113 | 28 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 17 |  | 37 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 100 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1250 | 1582 | 1676 | 1779 | 931 | 301
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 148 | 140 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 74 | 195 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 98 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 397 | 495 | 518.6 | 497 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 113 | 80 | 110 | 110 | 220 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 55 | 55 | 55
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 35 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 12 | 12 | 12
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 391 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1684 | 1706 | 1781 | 1822 | 321 | 229
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 923 | 927 | 927
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 99 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 150 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 61 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 220 | 230 | 230 | 180 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 16 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 90 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 12 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 42 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 106 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1382 | 1658 | 1907 | 1937 | 180 | 68
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 48 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 23 | 32 | 20 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 85 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 1020 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 200 | 218 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1097 | 1420 | 1443 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 27 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 220 |  |  | Running on HSD.
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 168 | 174 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 418 | 415 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 38 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 2 | 52 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 168 | 160 | 160 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 45 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 761 | 1341 | 1337 | 1560 | 421 | 138
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 102 | 103 | 103 |  | 10 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 6 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 258 | 392 | 401 | 393 | 99 | 180
|  | Total |  |  |  |  | 22348 | 21584 | 10951 | 13456 | 14132.6 | 14732 | 3394 | 2341
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10652.4192 | 13089.12 | 13747.2724 | 14330.3297
| A. |  | 2022-05-22 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13456 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8751 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13456 | MW
| 3 | Day peak Generation : |  |  | 10951 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13089.12 | MW
| 4 | Evening peak Generation : |  |  | 13456 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 266.1793 | MKWHr | By Solar | 1.0562 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.6697 | MKWHr |  | By Oil: | 78.0768 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 25.7491 | MKWHr |  | By Hydro: | 0.75228 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3394 | MW | Dhaka | 4758.62 | 4758.62 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2341 | MW | Chittagong | 1411.5 | 1411.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5735 | MW | Khulna | 1613 | 1613 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 997.5 | MMCFD |  |  | Rajshahi | 1275 | 1275 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 150028548.12 | ii) Oil : | Taka | 1047215739.2 | Comilla | 1299 | 1299 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 216012319 | Total | Taka | 1413256606.32 | Mymensingh | 1005 | 1005 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 499 | 499 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 498 | MW (E to W) at | 21:00 | hrs | Barisal | 407 | 407 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 456 | MW at | 20:00 | hrs | Rangpur | 821 | 821 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 13089.12 | 13089.12 |  | 0
| B. |  | 2022-05-23 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14732 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
| 4 | Reserve(Generation end) |  |  |  | 732 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 276.9404 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9232 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.216 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6592 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 13:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.07 |  | (b) Today: | 74.58 |  | (c) Rule Curve: |  | 77.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 105 | 0 | 0 | 331 |  | 0 | 225 | 110 | 83 | 32 | 45 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 81 | 41 | 22 | 35 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 102 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 104 | 160 | 0 | 20 | 0 | 43 | 42 | 51 | 50 | 110 | 70 | 50 | 81 | 0 | 219 | 0 | 39 | 10 | 290 | 12 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 50 | 0 | 38 | 34 | 0 | 400 | 109 | 34 | 105 | 0 | 246 | 54 | 92 | 50 | 54 | 38 | 401 | 90 | 0 | 162 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 424 | 70 | 0 | 113 | 15 | 110 | 0 | 0 | 113 | 760 | 200 | 0 | 17 | 0 | 0 | 0 |  | 6682 | 3623 | 10305 | 3714 | 912 | 2152 | 0 | 2442 | 935 | 30 | 0 | 16 | 104 | 0 | 0 | 74.02
2:00 | 0 | 0 | 0 | 180 | 230 | 105 | 0 | 0 | 331 |  | 0 | 225 | 125 | 82 | 16 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 39 | 45 | 22 | 40 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 100 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 104 | 160 | 0 | 20 | 0 | 43 | 42 | 51 | 50 | 110 | 109 | 50 | 81 | 0 | 219 | 0 | 38 | 10 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 26 | 0 | 38 | 34 | 0 | 400 | 109 | 34 | 68 | 0 | 246 | 54 | 93 | 50 | 36 | 38 | 401 | 55 | 0 | 126 | 108 | 0 | 17 | 0 | 0 | 55 |  | 911 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 429 | 17 | 0 | 113 | 15 | 90 | 0 | 0 | 113 | 740 | 202 | 0 | 17 | 0 | 0 | 0 |  | 6435 | 3535 | 9970 | 3779 | 911 | 2157 | 0 | 2074 | 915 | 30 | 0 | 0 | 104 | 0 | 0 | 74.03
3:00 | 0 | 0 | 0 | 180 | 230 | 104 | 0 | 0 | 338 |  | 0 | 225 | 115 | 82 | 16 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 26 | 45 | 22 | 40 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 102 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 104 | 160 | 0 | 20 | 0 | 43 | 42 | 51 | 50 | 110 | 110 | 50 | 81 | 0 | 219 | 0 | 37 | 10 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 38 | 34 | 0 | 401 | 109 | 34 | 68 | 0 | 246 | 54 | 92 | 50 | 28 | 38 | 401 | 17 | 0 | 90 | 108 | 0 | 17 | 0 | 0 | 55 |  | 911 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 430 | 17 | 0 | 70 | 15 | 75 | 0 | 0 | 70 | 740 | 203 | 0 | 17 | 0 | 0 | 0 |  | 6298 | 3435 | 9733 | 3783 | 911 | 2163 | 0 | 1827 | 915 | 30 | 0 | 0 | 104 | 0 | 0 | 74.04
4:00 | 0 | 0 | 0 | 180 | 230 | 104 | 0 | 0 | 337 |  | 0 | 225 | 110 | 82 | 16 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 23 | 45 | 22 | 40 | 0 | 0 | 0 | 280 | 0 | 183 | 8 | 100 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 100 | 160 | 0 | 20 | 0 | 43 | 42 | 51 | 50 | 110 | 111 | 50 | 81 | 0 | 219 | 0 | 37 | 10 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 38 | 34 | 0 | 400 | 109 | 34 | 34 | 0 | 246 | 54 | 92 | 50 | 29 | 38 | 401 | 17 | 0 | 17 | 108 | 0 | 17 | 0 | 0 | 55 |  | 911 | 0 | 280 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 430 | 17 | 0 | 70 | 15 | 40 | 0 | 0 | 35 | 740 | 201 | 0 | 17 | 0 | 0 | 0 |  | 6150 | 3359 | 9509 | 3781 | 911 | 2144 | 0 | 1628 | 915 | 30 | 0 | 0 | 100 | 0 | 0 | 74.05
5:00 | 0 | 0 | 0 | 180 | 200 | 104 | 0 | 0 | 336 |  | 0 | 225 | 110 | 82 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 24 | 45 | 22 | 40 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 102 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 96 | 161 | 0 | 20 | 0 | 43 | 42 | 51 | 47 | 110 | 110 | 50 | 81 | 0 | 219 | 0 | 37 | 10 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 38 | 23 | 0 | 400 | 75 | 17 | 17 | 0 | 210 | 54 | 92 | 50 | 28 | 26 | 401 | 0 | 0 | 0 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 280 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 433 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 740 | 206 | 0 | 17 | 0 | 0 | 0 |  | 5879 | 3213 | 9092 | 3756 | 912 | 2145 | 0 | 1238 | 915 | 30 | 0 | 0 | 96 | 0 | 0 | 74.06
6:00 | 0 | 0 | 0 | 180 | 200 | 104 | 0 | 0 | 307 |  | 0 | 225 | 135 | 50 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 15 | 45 | 22 | 32 | 0 | 0 | 0 | 290 | 0 | 191 | 8 | 100 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 33 | 20 | 92 | 160 | 0 | 20 | 0 | 43 | 42 | 11 | 47 | 110 | 111 | 50 | 40 | 0 | 219 | 0 | 37 | 10 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 1 | 38 | 17 | 0 | 352 | 35 | 0 | 17 | 0 | 210 | 54 | 92 | 50 | 29 | 26 | 360 | 0 | 4 | 0 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 370 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 740 | 203 | 0 | 17 | 0 | 3 | 0 |  | 5622 | 3129 | 8751 | 3682 | 912 | 1992 | 0 | 1120 | 915 | 30 | 0 | 0 | 92 | 8 | 0 | 74.07
7:00 | 0 | 0 | 0 | 180 | 250 | 104 | 0 | 0 | 308 |  | 0 | 225 | 135 | 40 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 22 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 11 | 45 | 22 | 24 | 0 | 0 | 0 | 300 | 0 | 193 | 8 | 102 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 25 | 20 | 86 | 158 | 0 | 20 | 0 | 43 | 42 | 11 | 47 | 110 | 110 | 50 | 40 | 0 | 219 | 0 | 37 | 10 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 4 | 38 | 17 | 0 | 400 | 35 | 0 | 17 | 1 | 210 | 54 | 92 | 50 | 29 | 26 | 401 | 0 | 14 | 0 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 370 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 700 | 203 | 0 | 17 | 0 | 13 | 0 |  | 5747 | 3098 | 8845 | 3800 | 912 | 2003 | 0 | 1106 | 875 | 30 | 0 | 0 | 86 | 33 | 0 | 74.08
8:00 | 0 | 0 | 0 | 180 | 250 | 105 | 0 | 0 | 320 |  | 0 | 225 | 140 | 40 | 0 | 15 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 25 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 11 | 45 | 22 | 4 | 0 | 0 | 0 | 280 | 0 | 170 | 8 | 100 | 28 | 30 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 25 | 20 | 94 | 157 | 0 | 20 | 1 | 43 | 42 | 20 | 50 | 110 | 112 | 50 | 73 | 0 | 219 | 0 | 37 | 10 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 8 | 38 | 17 | 0 | 402 | 35 | 0 | 17 | 3 | 210 | 54 | 92 | 50 | 28 | 25 | 400 | 0 | 8 | 0 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 270 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 417 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 680 | 203 | 0 | 17 | 1 | 61 | 0 |  | 5754 | 3160 | 8914 | 3745 | 912 | 2089 | 0 | 1104 | 855 | 30 | 0 | 0 | 94 | 85 | 0 | 74.1
9:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 321 |  | 0 | 225 | 120 | 68 | 0 | 15 | 335 | 0 | 0 | 11 | 7 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 24 | 0 | 25 | 25 | 25 | 33 | 24 | 0 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 2 | 0 | 0 | 10 | 29 | 44 | 22 | 2 | 0 | 0 | 0 | 300 | 0 | 146 | 8 | 100 | 28 | 10 | 0 | 0 | 0 | 0 | 43 | 19 | 5 | 25 | 20 | 98 | 159 | 0 | 0 | 1 | 44 | 42 | 50 | 20 | 110 | 110 | 50 | 78 | 0 | 220 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 5 | 0 | 0 | 41 | 0 | 49 | 11 | 38 | 38 | 0 | 402 | 98 | 90 | 77 | 4 | 228 | 54 | 92 | 98 | 29 | 25 | 386 | 18 | 21 | 66 | 108 | 0 | 17 | 0 | 4 | 55 |  | 917 | 0 | 260 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 353 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 0 | 680 | 160 | 0 | 17 | 3 | 78 | 0 |  | 6351 | 3080 | 9431 | 3722 | 917 | 1909 | 0 | 1730 | 855 | 30 | 0 | 48 | 98 | 122 | 0 | 74.12
10:00 | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 322 |  | 0 | 225 | 120 | 81 | 40 | 45 | 328 | 0 | 0 | 24 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 25 | 33 | 24 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 15 | 8 | 0 | 10 | 68 | 44 | 22 | 2 | 0 | 0 | 0 | 270 | 0 | 144 | 8 | 99 | 28 | 5 | 0 | 0 | 0 | 0 | 39 | 16 | 5 | 25 | 20 | 106 | 148 | 0 | 20 | 1 | 44 | 42 | 22 | 20 | 110 | 112 | 60 | 75 | 0 | 220 | 0 | 0 | 10 | 290 | 12 | 0 | 0 | 134 | 0 | 0 | 60 | 0 | 149 | 13 | 38 | 117 | 0 | 404 | 109 | 105 | 105 | 5 | 228 | 54 | 93 | 114 | 29 | 25 | 391 | 87 | 47 | 134 | 108 | 0 | 17 | 0 | 17 | 55 |  | 919 | 0 | 250 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 375 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 15 | 630 | 210 | 0 | 17 | 2 | 62 | 0 |  | 7093 | 3072 | 10165 | 3677 | 919 | 1932 | 0 | 2505 | 805 | 30 | 0 | 56 | 106 | 135 | 0 | 74.15
11:00 | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 321 |  | 0 | 225 | 125 | 81 | 73 | 40 | 328 | 0 | 0 | 54 | 58 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 25 | 33 | 40 | 0 | 30 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 23 | 8 | 0 | 10 | 67 | 43 | 20 | 2 | 0 | 0 | 0 | 270 | 0 | 161 | 8 | 98 | 27 | 5 | 0 | 0 | 0 | 19 | 39 | 16 | 5 | 25 | 20 | 106 | 143 | 0 | 20 | 1 | 44 | 42 | 0 | 0 | 110 | 111 | 60 | 10 | 0 | 220 | 0 | 0 | 10 | 285 | 12 | 3 | 0 | 170 | 0 | 0 | 60 | 0 | 149 | 15 | 38 | 176 | 0 | 402 | 99 | 105 | 105 | 5 | 232 | 54 | 92 | 114 | 29 | 25 | 399 | 90 | 43 | 144 | 108 | 0 | 17 | 0 | 42 | 55 |  | 923 | 0 | 245 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 421 | 0 | 0 | 35 | 0 | 26 | 0 | 6 | 35 | 640 | 217 | 0 | 17 | 3 | 34 | 0 |  | 7259 | 3154 | 10413 | 3688 | 923 | 1878 | 0 | 2791 | 815 | 30 | 0 | 75 | 106 | 107 | 0 | 74.18
12:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 321 |  | 0 | 225 | 120 | 81 | 80 | 40 | 330 | 0 | 0 | 64 | 75 | 90 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 1 | 207 | 0 | 0 | 0 |  | 24 | 8 | 0 | 10 | 65 | 28 | 20 | 2 | 0 | 0 | 0 | 280 | 0 | 173 | 8 | 100 | 27 | 0 | 0 | 0 | 0 | 41 | 36 | 16 | 5 | 21 | 20 | 110 | 142 | 0 | 20 | 2 | 44 | 42 | 0 | 0 | 110 | 113 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 228 | 0 | 0 | 74 | 0 | 149 | 13 | 25 | 200 | 0 | 400 | 98 | 105 | 105 | 6 | 235 | 54 | 92 | 114 | 28 | 25 | 385 | 90 | 37 | 144 | 108 | 0 | 17 | 0 | 54 | 55 |  | 923 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 418 | 12 | 0 | 45 | 42 | 70 | 0 | 7 | 95 | 740 | 200 | 0 | 17 | 4 | 106 | 6 |  | 7453 | 3498 | 10951 | 3678 | 923 | 1870 | 0 | 3111 | 915 | 30 | 0 | 139 | 110 | 175 | 0 | 74.21
13:00 | 0 | 0 | 0 | 180 | 270 | 98 | 0 | 0 | 272 |  | 0 | 225 | 130 | 81 | 80 | 40 | 280 | 0 | 0 | 83 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 23 | 205 | 0 | 0 | 0 |  | 24 | 8 | 0 | 10 | 79 | 18 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 100 | 25 | 0 | 0 | 0 | 0 | 39 | 34 | 16 | 5 | 21 | 20 | 112 | 130 | 0 | 20 | 1 | 44 | 42 | 0 | 0 | 110 | 111 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 233 | 0 | 0 | 120 | 0 | 149 | 15 | 25 | 200 | 0 | 402 | 98 | 105 | 105 | 5 | 252 | 54 | 92 | 114 | 29 | 25 | 400 | 90 | 46 | 144 | 108 | 0 | 17 | 0 | 72 | 55 |  | 924 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 27 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 375 | 53 | 0 | 97 | 50 | 85 | 0 | 7 | 113 | 820 | 166 | 0 | 17 | 4 | 47 | 52 |  | 7522 | 3664 | 11186 | 3637 | 924 | 1721 | 0 | 3480 | 995 | 30 | 0 | 162 | 112 | 125 | 0 | 74.24
14:00 | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 273 |  | 0 | 225 | 140 | 81 | 80 | 40 | 280 | 0 | 0 | 89 | 93 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 0 | 25 | 33 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 78 | 18 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 95 | 25 | 0 | 0 | 0 | 0 | 39 | 36 | 16 | 5 | 25 | 20 | 120 | 128 | 0 | 20 | 2 | 44 | 42 | 0 | 0 | 110 | 109 | 50 | 10 | 0 | 193 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 243 | 0 | 0 | 140 | 0 | 149 | 9 | 25 | 200 | 0 | 404 | 108 | 105 | 105 | 1 | 250 | 54 | 92 | 114 | 29 | 25 | 386 | 90 | 40 | 144 | 108 | 0 | 17 | 0 | 95 | 0 |  | 923 | 0 | 215 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 34 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 377 | 53 | 0 | 94 | 50 | 95 | 0 | 7 | 113 | 820 | 166 | 0 | 17 | 3 | 36 | 52 |  | 7428 | 3672 | 11100 | 3564 | 923 | 1734 | 0 | 3499 | 995 | 30 | 0 | 137 | 120 | 98 | 0 | 74.27
15:00 | 0 | 0 | 0 | 180 | 270 | 95 | 0 | 0 | 323 |  | 0 | 225 | 145 | 73 | 79 | 40 | 324 | 0 | 0 | 90 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 0 | 25 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 21 | 10 | 0 | 10 | 78 | 20 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 175 | 8 | 97 | 25 | 0 | 0 | 0 | 0 | 39 | 36 | 16 | 5 | 33 | 20 | 124 | 132 | 0 | 20 | 1 | 44 | 42 | 0 | 0 | 110 | 108 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 237 | 0 | 0 | 155 | 0 | 149 | 10 | 25 | 200 | 0 | 403 | 108 | 105 | 105 | 1 | 258 | 54 | 92 | 114 | 57 | 25 | 392 | 90 | 38 | 144 | 108 | 0 | 19 | 0 | 101 | 1 |  | 923 | 0 | 200 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 352 | 66 | 0 | 94 | 67 | 95 | 0 | 6 | 113 | 870 | 220 | 0 | 17 | 4 | 40 | 92 |  | 7626 | 3817 | 11443 | 3619 | 923 | 1834 | 0 | 3605 | 1045 | 30 | 0 | 163 | 124 | 100 | 0 | 74.3
16:00 | 0 | 0 | 0 | 180 | 270 | 93 | 0 | 0 | 322 |  | 0 | 225 | 125 | 72 | 78 | 40 | 325 | 0 | 0 | 89 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 17 | 25 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 206 | 0 | 0 | 0 |  | 24 | 40 | 0 | 10 | 78 | 24 | 22 | 2 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 99 | 26 | 0 | 0 | 0 | 0 | 39 | 36 | 16 | 5 | 33 | 20 | 128 | 146 | 0 | 20 | 1 | 44 | 42 | 0 | 0 | 110 | 109 | 50 | 10 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 230 | 0 | 0 | 155 | 0 | 149 | 6 | 25 | 200 | 0 | 403 | 98 | 105 | 95 | 2 | 261 | 54 | 92 | 114 | 108 | 25 | 392 | 90 | 15 | 144 | 108 | 0 | 35 | 0 | 100 | 53 |  | 924 | 0 | 200 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 25 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 16 | 16 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 322 | 70 | 0 | 113 | 67 | 101 | 0 | 4 | 113 | 860 | 213 | 0 | 17 | 1 | 16 | 92 |  | 7745 | 3822 | 11567 | 3665 | 924 | 1764 | 0 | 3749 | 1035 | 30 | 0 | 227 | 128 | 45 | 0 | 74.32
17:00 | 0 | 0 | 0 | 180 | 270 | 97 | 0 | 0 | 324 |  | 0 | 225 | 130 | 74 | 78 | 40 | 300 | 0 | 0 | 89 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 8 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 78 | 24 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 188 | 8 | 97 | 29 | 0 | 0 | 0 | 0 | 39 | 33 | 16 | 5 | 21 | 20 | 120 | 145 | 0 | 0 | 0 | 44 | 40 | 0 | 0 | 110 | 110 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 228 | 0 | 0 | 120 | 0 | 149 | 3 | 25 | 200 | 0 | 404 | 98 | 105 | 88 | 1 | 265 | 50 | 92 | 114 | 112 | 30 | 390 | 54 | 9 | 144 | 108 | 0 | 35 | 0 | 50 | 55 |  | 922 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 24 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 24 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 274 | 70 | 0 | 113 | 67 | 101 | 0 | 2 | 113 | 830 | 190 | 0 | 17 | 0 | 10 | 34 |  | 7458 | 3640 | 11098 | 3578 | 922 | 1703 | 0 | 3528 | 1005 | 30 | 0 | 187 | 120 | 25 | 0 | 74.34
18:00 | 0 | 0 | 0 | 180 | 270 | 100 | 0 | 0 | 272 |  | 0 | 225 | 130 | 73 | 78 | 40 | 240 | 0 | 0 | 90 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 25 | 25 | 17 | 46 | 0 | 30 | 0 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 80 | 24 | 22 | 5 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 99 | 29 | 0 | 0 | 0 | 0 | 40 | 41 | 16 | 5 | 33 | 20 | 120 | 146 | 0 | 0 | 0 | 44 | 40 | 0 | 0 | 110 | 111 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 247 | 0 | 0 | 120 | 0 | 149 | 0 | 50 | 200 | 0 | 351 | 108 | 105 | 100 | 0 | 265 | 36 | 92 | 114 | 114 | 50 | 360 | 54 | 3 | 108 | 108 | 0 | 35 | 0 | 17 | 55 |  | 923 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 37 | 15 | 8 | 85 | 23 | 32 | 0 | 0 | 0 | 34 | 5 | 0 | 0 | 0 | 40 | 24 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 277 | 35 | 0 | 113 | 67 | 101 | 0 | 0 | 113 | 790 | 220 | 0 | 17 | 0 | 3 | 34 |  | 7347 | 3680 | 11027 | 3499 | 923 | 1691 | 0 | 3524 | 965 | 30 | 0 | 269 | 120 | 6 | 0 | 74.36
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 319 |  | 0 | 225 | 140 | 72 | 79 | 40 | 326 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 17 | 48 | 0 | 30 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 2 | 0 | 51 | 10 | 81 | 24 | 22 | 5 | 0 | 0 | 0 | 280 | 0 | 186 | 8 | 99 | 29 | 0 | 0 | 0 | 0 | 40 | 41 | 16 | 6 | 33 | 20 | 136 | 149 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 50 | 35 | 0 | 220 | 0 | 0 | 10 | 300 | 12 | 0 | 150 | 242 | 290 | 86 | 163 | 95 | 149 | 0 | 50 | 200 | 0 | 403 | 108 | 105 | 105 | 0 | 282 | 35 | 92 | 114 | 113 | 50 | 394 | 72 | 0 | 127 | 108 | 0 | 35 | 0 | 47 | 55 |  | 924 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 37 | 63 | 8 | 85 | 32 | 32 | 0 | 0 | 0 | 34 | 5 | 85 | 0 | 43 | 40 | 43 | 38 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 175 | 0 | 414 | 58 | 91 | 113 | 105 | 102 | 0 | 0 | 113 | 840 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8489 | 4370 | 12859 | 3693 | 924 | 1940 | 727 | 3869 | 1015 | 30 | 0 | 525 | 136 | 0 | 0 | 74.42
19:30 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 329 |  | 0 | 225 | 135 | 74 | 79 | 40 | 328 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 17 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 20 | 18 | 51 | 10 | 84 | 24 | 22 | 5 | 0 | 0 | 0 | 280 | 0 | 193 | 8 | 100 | 27 | 0 | 0 | 0 | 0 | 33 | 41 | 16 | 6 | 33 | 20 | 120 | 150 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 50 | 35 | 0 | 220 | 0 | 0 | 10 | 290 | 12 | 0 | 200 | 242 | 105 | 97 | 181 | 98 | 149 | 0 | 50 | 200 | 0 | 403 | 108 | 105 | 105 | 0 | 282 | 35 | 92 | 114 | 114 | 50 | 394 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 922 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 45 | 66 | 8 | 85 | 28 | 48 | 0 | 0 | 0 | 43 | 9 | 85 | 0 | 43 | 40 | 43 | 38 | 21 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 175 | 0 | 418 | 105 | 154 | 113 | 85 | 102 | 0 | 0 | 113 | 970 | 217 | 0 | 17 | 0 | 0 | 115 |  | 8491 | 4669 | 13160 | 3694 | 922 | 1932 | 714 | 4044 | 1144 | 30 | 0 | 560 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 329 |  | 0 | 225 | 145 | 72 | 81 | 40 | 325 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 |  | 20 | 43 | 51 | 10 | 84 | 24 | 22 | 10 | 0 | 0 | 0 | 280 | 0 | 190 | 8 | 97 | 29 | 0 | 0 | 0 | 0 | 38 | 41 | 16 | 6 | 33 | 20 | 126 | 149 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 50 | 35 | 0 | 220 | 0 | 0 | 10 | 290 | 12 | 0 | 200 | 242 | 105 | 97 | 182 | 99 | 149 | 0 | 50 | 200 | 0 | 403 | 109 | 105 | 105 | 0 | 282 | 35 | 92 | 114 | 114 | 50 | 387 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 91 | 55 |  | 923 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 39 | 60 | 16 | 84 | 32 | 48 | 0 | 0 | 0 | 43 | 23 | 85 | 0 | 43 | 40 | 52 | 38 | 21 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 175 | 0 | 414 | 105 | 160 | 113 | 85 | 102 | 0 | 0 | 113 | 970 | 217 | 0 | 17 | 0 | 0 | 115 |  | 8516 | 4701 | 13217 | 3698 | 923 | 1947 | 721 | 4034 | 1146 | 30 | 0 | 592 | 126 | 0 | 0 | 74.4
21:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 |  | 0 | 225 | 138 | 71 | 96 | 40 | 327 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 213 | 0 | 0 | 0 |  | 24 | 43 | 51 | 10 | 85 | 24 | 22 | 20 | 0 | 0 | 0 | 280 | 0 | 127 | 8 | 98 | 29 | 0 | 0 | 0 | 0 | 33 | 42 | 16 | 6 | 33 | 20 | 128 | 148 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 55 | 35 | 0 | 220 | 0 | 0 | 10 | 305 | 12 | 0 | 200 | 242 | 235 | 98 | 195 | 98 | 149 | 0 | 50 | 200 | 0 | 403 | 108 | 105 | 105 | 0 | 283 | 35 | 92 | 114 | 113 | 50 | 391 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 923 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 39 | 61 | 16 | 85 | 32 | 48 | 0 | 0 | 0 | 43 | 27 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 174 | 0 | 415 | 105 | 168 | 113 | 105 | 102 | 0 | 0 | 113 | 1020 | 218 | 0 | 17 | 0 | 0 | 115 |  | 8645 | 4811 | 13456 | 3639 | 923 | 1960 | 889 | 4095 | 1195 | 35 | 0 | 592 | 128 | 0 | 0 | 74.42
22:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 |  | 0 | 225 | 130 | 71 | 96 | 40 | 330 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 20 | 43 | 51 | 10 | 85 | 25 | 22 | 23 | 0 | 0 | 0 | 280 | 0 | 117 | 8 | 101 | 32 | 0 | 0 | 0 | 0 | 40 | 42 | 16 | 6 | 33 | 20 | 120 | 146 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 55 | 35 | 0 | 220 | 0 | 0 | 10 | 290 | 12 | 0 | 200 | 250 | 103 | 99 | 195 | 99 | 149 | 0 | 50 | 200 | 0 | 403 | 109 | 105 | 105 | 0 | 283 | 35 | 92 | 114 | 114 | 50 | 394 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 917 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 33 | 60 | 40 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 27 | 85 | 0 | 43 | 40 | 52 | 38 | 0 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 174 | 0 | 415 | 105 | 168 | 113 | 105 | 102 | 0 | 0 | 113 | 1050 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8491 | 4848 | 13339 | 3635 | 917 | 1920 | 769 | 4126 | 1225 | 35 | 0 | 592 | 120 | 0 | 0 | 74.44
23:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 |  | 0 | 225 | 145 | 71 | 96 | 45 | 331 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 43 | 51 | 10 | 86 | 25 | 22 | 10 | 0 | 0 | 0 | 280 | 0 | 191 | 8 | 100 | 32 | 0 | 0 | 0 | 0 | 40 | 42 | 16 | 6 | 33 | 20 | 128 | 146 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 55 | 35 | 0 | 219 | 0 | 0 | 10 | 280 | 12 | 0 | 160 | 263 | 103 | 99 | 195 | 99 | 149 | 0 | 38 | 200 | 0 | 402 | 109 | 105 | 105 | 0 | 283 | 35 | 92 | 114 | 114 | 50 | 400 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 915 | 0 | 220 | 0 | 84 | 0 | 0 | 0 | 33 | 60 | 40 | 86 | 34 | 48 | 0 | 0 | 0 | 43 | 31 | 83 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 174 | 0 | 414 | 105 | 168 | 113 | 105 | 102 | 0 | 0 | 113 | 1060 | 219 | 0 | 17 | 0 | 0 | 115 |  | 8541 | 4780 | 13321 | 3708 | 915 | 1934 | 649 | 4123 | 1235 | 35 | 0 | 594 | 128 | 0 | 0 | 74.46
24:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 |  | 0 | 225 | 145 | 72 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 40 | 51 | 10 | 87 | 25 | 22 | 31 | 0 | 0 | 0 | 280 | 0 | 212 | 8 | 100 | 32 | 10 | 0 | 0 | 0 | 40 | 43 | 16 | 6 | 33 | 20 | 112 | 146 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 55 | 35 | 0 | 220 | 0 | 0 | 10 | 300 | 11 | 0 | 50 | 275 | 72 | 99 | 195 | 99 | 149 | 0 | 38 | 200 | 0 | 402 | 108 | 105 | 105 | 0 | 283 | 35 | 92 | 114 | 108 | 42 | 392 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 45 |  | 920 | 0 | 220 | 0 | 88 | 0 | 0 | 0 | 33 | 60 | 40 | 86 | 34 | 48 | 0 | 0 | 0 | 43 | 31 | 83 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 174 | 0 | 418 | 105 | 40 | 113 | 105 | 102 | 0 | 0 | 113 | 1060 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8444 | 4666 | 13110 | 3720 | 920 | 1990 | 380 | 4127 | 1235 | 35 | 0 | 591 | 112 | 0 | 0 | 74.48
KWH | 0 | 0 | 0 | 4347000 | 6171955 | 2381545 | 0 | 0 | 7596000 |  | 0 | 5120250 | 3174836 | 1738560 | 1339800 | 924018 | 7744522 | 0 | 0 | 1243200 | 1242288 | 1541760 | 0 | 0 | 0 | 0 | 1215000 | 886750 | 776583 | 386640 | 600000 | 577800 | 577700 | 638100 | 711840 | 0 | 752280 | 0 | 0 | 0 | 309423 | 4893480 | 0 | 0 | 0 |  | 384240 | 333032 | 273420 | 258960 | 1449600 | 798240 | 507216 | 362880 | 0 | 0 | 0 | 7250000 | 0 | 4212000 | 217454 | 2343700 | 660744 | 294720 | 0 | 0 | 0 | 504936 | 977683 | 405216 | 111060 | 705900 | 488620 | 2659200 | 3523200 | 0 | 348408 | 10850 | 1033000 | 961920 | 369000 | 462960 | 2677827 | 2176000 | 1235424 | 1037760 | 0 | 5270090 | 0 | 352840 | 247320 | 7069500 | 177360 | 67000 | 922752 | 3512726 | 817346 | 509868 | 2342400 | 511553 | 2499984 | 107190 | 892800 | 3138240 | 0 | 9544000 | 2308800 | 1833600 | 2029854 | 33600 | 6029345 | 1233766 | 2234754 | 2209320 | 1511160 | 834240 | 9366000 | 1534080 | 316690 | 2707200 | 2609455 | 0 | 611640 | 0 | 1155840 | 1261800 |  | 22216000 | 0 | 6071616 | 0 | 1752000 | 0 | 0 | 0 | 220320 | 337792 | 191625 | 2049944 | 624040 | 761184 | 0 | 0 | 0 | 311360 | 123849 | 481616 | 0 | 289300 | 266751 | 574080 | 192147 | 476880 | 0 | 194670 | 0 | 0 | 4297600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368640 | 4363600 | 0 | 9360581 | 1180800 | 799710 | 2073504 | 1065744 | 1582195 | 0 | 51045 | 1853472 | 21451500 | 4839409 | 0 | 453600 | 28500 | 508320 | 1035264 |  | 173730613 | 92448658 | 266179271 | 89003885 | 22216000 | 46665802 | 3929869 | 69559957 | 25749100 | 752280 | 0 | 4586983 | 2659200 | 1056195 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6912589.6 | 3167454.85 | 0 | 0 | 8203680 |  | 0 | 5581072.5 | 3524067.96 | 19437100.8 | 17752350 | 12243238.5 | 8673864.64 | 0 | 0 | 18175584 | 17478992.16 | 24991929.6 | 0 | 0 | 0 | 0 | 15454800 | 11971125 | 10413978.03 | 289980 | 450000 | 0 | 0 | 0 | 12108398.4 | 0 | 203115.6 | 0 | 0 | 0 | 5059066.05 | 5089219.2 | 0 | 0 | 0 |  | 5014332 | 5554973.76 | 4653608.4 | 3498549.6 | 18380928 | 9235636.8 | 644164.32 | 1208390.4 | 0 | 0 | 0 | 8047500 | 0 | 4885920 | 280515.66 | 2859314 | 746640.72 | 439132.8 | 0 | 0 | 0 | 8720244.72 | 13149836.35 | 555145.92 | 83295 | 1235325 | 366465 | 19093056 | 3840288 | 0 | 473834.88 | 172949 | 1415210 | 1269734.4 | 642060 | 800920.8 | 3079501.05 | 2328320 | 2396722.56 | 2366092.8 | 0 | 5322790.9 | 0 | 525731.6 | 489693.6 | 7069500 | 133020 | 50920 | 19340881.92 | 47948709.9 | 17131572.16 | 10538971.56 | 31575552 | 10573800.51 | 34624778.4 | 1253051.1 | 9213696 | 42868358.4 | 0 | 8780480 | 28075008 | 26513856 | 25677653.1 | 0 | 70784510.3 | 13435711.74 | 23755435.02 | 29980472.4 | 19478852.4 | 9827347.2 | 8616720 | 19866336 | 4576170.5 | 34354368 | 29695597.9 | 0 | 7988018.4 | 0 | 17302924.8 | 16617906 |  | 66648000 | 0 | 6800209.92 | 0 | 18238320 | 0 | 0 | 0 | 3967963.2 | 6080256 | 2753651.25 | 2295937.28 | 1210637.6 | 8296905.6 | 0 | 0 | 0 | 5221507.2 | 2166119.01 | 7532474.24 | 0 | 4790808 | 4510759.41 | 7824710.4 | 3241519.89 | 987141.6 | 0 | 147365.19 | 0 | 0 | 22734304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7734067.2 | 5061776 | 0 | 9266975.19 | 15869952 | 16769918.7 | 24529552.32 | 15400000.8 | 20093876.5 | 0 | 564047.25 | 22501150.08 | 193278015 | 4936197.18 | 0 | 3356640 | 322335 | 5962593.6 | 15870597.12 |  | 975085640.64 | 536966283.73 | 1512051924.37 | 96249782.53 | 66648000 | 53778765.59 | 82089212.05 | 888485171.72 | 216012319 | 203115.6 | 0 | 76641355.43 | 19093056 | 12851146.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 321 |  | 0 | 225 | 120 | 81 | 80 | 40 | 330 | 0 | 0 | 64 | 75 | 90 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 25 | 33 | 48 | 0 | 30 | 0 | 0 | 0 | 1 | 207 | 0 | 0 | 0 |  | 24 | 8 | 0 | 10 | 65 | 28 | 20 | 2 | 0 | 0 | 0 | 280 | 0 | 173 | 8 | 100 | 27 | 0 | 0 | 0 | 0 | 41 | 36 | 16 | 5 | 21 | 20 | 110 | 142 | 0 | 20 | 2 | 44 | 42 | 0 | 0 | 110 | 113 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 228 | 0 | 0 | 74 | 0 | 149 | 13 | 25 | 200 | 0 | 400 | 98 | 105 | 105 | 6 | 235 | 54 | 92 | 114 | 28 | 25 | 385 | 90 | 37 | 144 | 108 | 0 | 17 | 0 | 54 | 55 |  | 923 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 418 | 12 | 0 | 45 | 42 | 70 | 0 | 7 | 95 | 740 | 200 | 0 | 17 | 4 | 106 | 6 |  | 10951 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 | 0 | 0 | 225 | 138 | 71 | 96 | 40 | 327 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 213 | 0 | 0 | 0 | 0 | 24 | 43 | 51 | 10 | 85 | 24 | 22 | 20 | 0 | 0 | 0 | 280 | 0 | 127 | 8 | 98 | 29 | 0 | 0 | 0 | 0 | 33 | 42 | 16 | 6 | 33 | 20 | 128 | 148 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 80 | 55 | 35 | 0 | 220 | 0 | 0 | 10 | 305 | 12 | 0 | 200 | 242 | 235 | 98 | 195 | 98 | 149 | 0 | 50 | 200 | 0 | 403 | 108 | 105 | 105 | 0 | 283 | 35 | 92 | 114 | 113 | 50 | 391 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 923 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 39 | 61 | 16 | 85 | 32 | 48 | 0 | 0 | 0 | 43 | 27 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 174 | 0 | 415 | 105 | 168 | 113 | 105 | 102 | 0 | 0 | 113 | 1020 | 218 | 0 | 17 | 0 | 0 | 115 |  | 13456 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 350 | 330 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 43 | 51 | 10 | 86 | 50 | 22 | 25 | 0 | 0 | 0 | 340 | 0 | 170 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 43 | 22 | 11 | 33 | 20 | 166 | 140 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 80 | 0 | 220 | 0 | 0 | 10 | 341 | 12 | 0 | 200 | 280 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 0 | 400 | 115 | 105 | 105 | 0 | 280 | 35 | 110 | 110 | 113 | 50 | 400 | 90 | 0 | 144 | 110 | 0 | 17 |  | 100 | 55 |  | 927 | 0 | 230 | 0 | 115 | 220 | 0 | 0 | 35 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 180 | 0 | 410 | 105 | 160 | 113 | 105 | 103 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 25 | 340 | 0 | 0 | 225 | 150 | 72 | 96 | 55 | 335 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 43 | 51 | 10 | 86 | 50 | 22 | 10 | 0 | 0 | 0 | 340 | 0 | 175 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 43 | 22 | 11 | 33 | 20 | 143 | 140 | 0 | 20 | 1.6 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 80 | 0 | 220 | 0 | 0 | 10 | 300 | 12 | 0 | 200 | 270 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 0 | 400 | 115 | 105 | 105 | 5 | 280 | 35 | 92 | 110 | 28 | 25 | 400 | 90 | 50 | 144 | 110 | 0 | 17 | 30 | 100 | 55 |  | 927 | 0 | 230 | 0 | 115 | 150 | 0 | 0 | 35 | 0 | 40 | 86 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 160 | 113 | 105 | 103 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 300 | 0 | 0 | 225 | 150 | 72 | 15 | 30 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 8 | 25 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 50 | 25 | 22 | 8 | 0 | 0 | 0 | 340 | 0 | 190 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 5 | 33 | 20 | 98 | 159 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 160 | 0 | 0 | 10 | 295 | 12 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 34 | 2 | 38 | 17 | 0 | 352 | 60 | 17 | 68 | 1 | 245 | 35 | 92 | 17 | 28 | 25 | 330 | 70 | 13 | 72 | 108 | 0 | 17 | 0 | 0 | 17 | 0 | 911 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 383 | 53 | 0 | 75 | 15 | 78 | 0 | 2 | 70 | 780 | 183 | 0 | 17 | 2 | 46 | 0 | 0 |  |  |  |  | 78076809 |  | 0
78076809
| Minimum Generation |  | 8751 | 6:00
| Highest Generation |  | 13456 | 21:00
| Day Peak Generation |  | 10951 | 12:00
| Evening Peak Generation |  | 13456 | 21:00
| HVDC Max Flow |  | 924 | 13:00
| HVDC EvPeak Flow |  | 923 | 21:00
| Load factor L.F |  | 82.42%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-23
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10951 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9232 | MW
Evening Peak Generation : |  | 13456 | MW Hour : | 21:00 | Available Max Generation : |  | 14732 | MW
E.P. Demand (at gen end) : |  | 13456 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13456 | MW Hour : | 21:00 | Reserve(Generation end) |  | 732 | MW
Total Gen. (MKWH) : |  | 266.1793 | System Load Factor : | 82.42% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 456 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-23
Actual : | 74.58 | Ft.(MSL) , | Rule curve : | 77.8 | Ft.( MSL )
Gas Consumed : | Total = | 997.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 150028548.12
: |  | Coal : | 216012319 | Oil : | 1047215739.2 | Total : | 1413256606.32
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5014.0132 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1626.6633 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1585.4619 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1419.6733 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1294.5848 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1062.4954 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 520.2915 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 319.477 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 781.1061 |  |  | 0 | 0%
Total | 0 |  | 13623.7665 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bashundhara-Purbachal 132 kV under ground cable was charged at 12:56 from Bashundhara end.
b) Satmosjid 132/33 kV T-1 transformer was under shut down from 09:07 to 10:56 due to 33 kV GCB noise.
c) Kallyanpur-Lalbag 132 kV Ckt-1 was shut down at 10:05 due to 132 kV CB pole change.
d) Tongi-Milgate 132 kV Ckt-1 & 2 was under shut down from 11:05 to 17:27 for D/W.
e) Joydevpur 132/33 kV T-2 transformer was under shut down from 11:57 to 13:44 due to R/H maintenance | [5 empty] | About 05 MW power interruption occurred under
at 132 kV R-φ ,CT connection point. | [5 empty] | Joydevpur S/S area from 11:57 to 13:44.
f) Bheramara HVDC-Jhenaidah(N) 230 kV Ckt-1 was under shut down from 08:47 to 16:32 for C/M.
g) Faridpur 132/33 kV T-1 transformer was shut down at 08:32 to 13:13 for C/M.
h) Kallyanpur 132 kV main Bus was under shut down from 12:19 to 21:18 due to CB pole change.
i) Bhulta-Rampura 230 kV Ckt-1 was under shut down from 13:53 to 17:48 for D/W.
j) Khulna(S)-Satkhira 132 kV Ckt-1 was switched on at 13:01.
k) Comilla(S) 132 kV T-2 transformer tripped at 14:07 showing O/C,E/F due to 33 kV Barura feeder fault | [5 empty] | About 20 MW power interruption occurred under
and was switched on at 14:19. | [5 empty] | Comilla(S) S/S area from 14:07 to 14:19.
l) Polashbari-Mohasthangarh 132 kV Ckt-2 was under shut down from 14:11 to 15:25 for C/M.
m) Bheramara HVDC-Rajshahi 230 kV Ckt-2 was under shut down from 16:07 to 17:00 for removing
polythene paper.
n) Comilla(S) 132/33 kV T-2 transformer was under shut down from 16:55 to 18:02 for CB Maintenance of | [5 empty] | About 15 MW power interruption occurred under
33 kV Kosba PDB feeder. | [5 empty] | Comilla(S) S/S area from 16:55 to 18:02.
o) Juldah 132/33 kV T-2 transformer was under shut down from 20:10 to 21:34 due to R/H maintenance at
132 kV C-φ ,CT.
p) Shahjadpur 132/33 kV T-3 transformer was under shut down from 20:02 to 20:27 due to R/H maintenance
at 33 kV B-φ ,Bushing.
q) Barishal Electric P.P.-Payra P.P. 400 kV Ckt was switched on at 21:33 from Payra P.P. end.
r) Barishal Electric P.P. 400 kV Bus was switched on at 21:26.
s) Feni-Chaddogram 132 kV Ckt-2 tripped at 03:48(23/5/2022) showing Dist. A-φ,Lockout 21 relay and was
switched on at 04:32.
t) Mymensingh 132/33 kV T-2 transformer along with 33 kV Bus-2 was under shut down from | [5 empty] | About 35 MW power interruption occurred under
06:05(23/5/2022) to 07:35 for C/M. | [5 empty] | Mymensingh S/S area from 06:05(23/5/2022) to 07:35.
u) Bheramara HVDC 230 kV filter 20DF11 was under shut down from 06:43(23/5/2022) to 11:20.
v) Saidpur 132/33 kV T-3 transformer along with 33 kV Bus-3 was shut down at 07:10(23/5/2022) for C/M. | [5 empty] | About 10 MW power interruption occurred under
Saidpur S/S area since 07:10(23/5/2022) to till now.
w) Kushtia 132/33 kV T-1 transformer along with 33 kV Bus-1 was under shut down from 07:03(23/5/2022) | [5 empty] | About 22 MW power interruption occurred under
to 08:59 for C/M. | [5 empty] | Saidpur S/S area from 07:03(23/5/2022) to 08:59.
x) Khulna(C) 132/33 kV T-1 transformer was under shut down from 07:38(23/5/2022) to 11:48 for C/M. | [5 empty] | About 20 MW power interruption occurred under
Khulna(C) S/S area from 07:38(23/5/2022) to 11:48..
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6171955 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2381545
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7596000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5120250 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 71 | 1738560 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 138 | 3174836 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 1339800
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 924018 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 386640
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1243200 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7744522
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1242288 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1215000
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1541760 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 886750
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 776583 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1177800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 577700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 638100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 711840 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 242 | 3512726 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 235 | 817346 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 98 | 509868
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 511553
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2499984
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1833600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 1534080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2707200 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1261800
| Dhaka area Total |  |  |  | 5898 | 3611 | 66124304
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 309423
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 107190
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 798240 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 752280 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 213 | 4893480
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2029854
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 333032 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 273420 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258960 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 892800 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507216
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 362880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1449600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33600
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 283 | 6029345 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 1233766 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2234754 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 834240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2609455
| Chattogram area Total |  |  |  | 2382 | 1251 | 25943535
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 127 | 4212000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7250000 | Natural gas heater problem
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 660744 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 294720 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | 230 kV CB problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | 230 kV CB problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 504936 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 98 | 2343700 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3138240
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 405216 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 111060 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2659200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 705900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 977683 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 488620 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 922752
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2209320
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1511160
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 611640 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 1155840 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1582 | 30380185
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 148 | 3523200 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 348408
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 195 | 2342400
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2308800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 316690
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 384240
| Mymensingh Area Total |  |  |  | 622 | 495 | 9234588
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1033000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 961920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2677827 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 80 | 2176000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 369000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 462960 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 67000 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1235424 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 35 | 1037760 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5270090
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 352840 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 177360 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7069500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9544000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 391 | 9366000
| Sylhet Area Total |  |  |  | 2477 | 1706 | 42048001
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22216000
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1752000 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 220320 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 61 | 337792 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 220 | 6071616 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 16 | 191625 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 90 | 368640 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1180800
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1065744
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 508320
| Khulna Area Total |  |  |  | 2384 | 1658 | 33912857
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 761184 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 32 | 624040 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2049944 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 21451500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 218 | 4839409
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 453600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1420 | 30179677
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 311360 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 27 | 123849 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 289300 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 266751 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 174 | 4363600 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9360581
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 192147 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 476880
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 194670 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 574080
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 481616 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 168 | 799710 | Low demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2073504
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1853472
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28500
| Rajshahi Area Total |  |  |  | 2129 | 1341 | 21390020
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4297600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 1582195 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51045
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1035264
| Rangpur Area Total |  |  |  | 720 | 392 | 6966104
| Total |  |  |  | 21584 | 13456 | 266179271
| Eastern Grid Total |  |  |  | 14393 | 8645 | 173730613
| Western Grid Total |  |  |  | 7191 | 4811 | 92448658
| National Grid Total |  |  |  | 21584 | 13456 | 266179271
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-22
(a) ENTIRE EASTERN GRID : |  | 8973.12 | MW | (b) ENTIRE WESTERN GRID : |  | 4116 | MW
i) Dhaka area |  | 4758.62 | MW | i) Khulna area |  | 1613 | MW
ii) Chittagong area |  | 1411.5 | MW | ii) Rajshahi area |  | 1275 | MW
iii) Comilla area |  | 1299 | MW | iii) Barisal area |  | 407 | MW
iv) Mymensingh area |  | 1005 | MW | iv) Rangpur area |  | 821 | MW
v) Sylhet area |  | 499 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13089.12 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 31 | 19:30 | Hasnabad | 67 | 23:00 | Palashbari | 121 | 19:30
Agargaon | 87 | 13:00 | Hathazari | 100 | 20:00 | Panchagarh | 58 | 19:30
Agrabad | 88 | 18:30 | Ishurdi | 67 | 21:00 | Patuakhali | 133 | 23:00
AKS | 15 | 16:00 | Jaldhaka | 68 | 20:00 | PHP | 6 | 03:00
AKSML | 131 | 12:00 | Jamalpur | 131 | 22:00 | Purbachal | 19 | 19:30
Amnura | 38 | 21:00 | Jashore | 118 | 21:00 | Purbasadipur | 118 | 20:00
Ashuganj | 38 | 00:00 | Jhenaidah | 112 | 22:00 | Rahim | 19 | 18:30
Bagerhat | 111 | 22:00 | Joydebpur | 191 | 19:00 | Rajbari | 66 | 19:30
Bakulia | 128 | 19:00 | Joypurhat | 58 | 21:00 | Rajendrapur | 114 | 19:30
Banani | 48 | 12:00 | Juldah | 27 | 10:00 | Rajshahi | 150 | 21:00
Bangabhaban | 20 | 10:00 | Kabirpur | 295 | 18:30 | Rajshahi | 33 | 22:00
Barapukuria | 52 | 19:00 | Kachua | 72 | 22:00 | Ramganj | 114 | 22:00
Barguna | 20 | 21:00 | Kallyanpur | 102 | 21:00 | Rampur | 21 | 22:00
Barishal | 124 | 19:30 | Kalurghat | 6 | 18:00 | Rangamati | 12 | 19:00
Barishal | 58 | 22:00 | Kamrangirchar | 68 | 12:00 | Rangpur | 141 | 19:30
Baroaulia | 81 | 20:00 | Kaptai | 5 | 19:00 | Ruppur | 4.6 | 16:00
Baroirhat | 45 | 21:00 | Kazla | 88 | 20:00 | Saidpur | 83 | 21:00
Bashundhara | 164 | 19:00 | Keranigonj | 78 | 19:00 | Satkhira | 110 | 23:00
BashundharaCement | 13 | 07:00 | Khagrachori | 26 | 21:00 | Satmasjid | 91 | 19:00
Beanibazar | 54 | 20:00 | Khulna | 87 | 19:00 | Savar | 181 | 15:00
Benapole | 62 | 21:00 | Khulshi | 168 | 15:00 | Shahjadpur | 89 | 21:00
Bhaluka | 142 | 21:00 | Kishoreganj | 128 | 19:00 | Shahjibazar | 117 | 22:00
Bhandaria | 62 | 22:00 | Kodda | 317 | 18:30 | Shahmirpur | 49.3 | 19:00
Bhangura | 33 | 21:00 | KSRM | 31.1 | 13:00 | Shariatpur | 76 | 23:00
Bheramara(GK) | 51 | 23:00 | Kulaura | 44 | 19:30 | Sherpur | 120 | 22:00
Bhulta | 210 | 12:00 | Kurigram | 58 | 19:30 | Shikalbaha | 30 | 00:00
Bog-Sherpur | 60 | 20:00 | Kushtia | 106 | 20:00 | Shitalakhya | 114 | 12:00
Bogura | 155 | 23:00 | Lalbag | 91 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 42 | 22:00 | Lalmonirhat | 46 | 19:30 | Shyampur | 186 | 10:00
Brahmanbaria | 168 | 20:00 | Madanganj | 191 | 23:00 | Siddhirganj | 114 | 18:30
BSRM | 161 | 17:00 | Madaripur | 111 | 23:00 | Sirajganj | 107 | 20:00
Cantonment | 144 | 19:00 | Madartek | 82 | 23:00 | Sonargaon | 81 | 19:30
Chandpur | 90 | 23:00 | Madunaghat | 65 | 19:00 | Sreemongol | 61 | 19:00
Chandraghona | 34 | 20:00 | Magura | 60 | 21:00 | Srinagar | 45.92 | 21:00
Chapai | 73 | 21:00 | Mahasthangarh | 60 | 19:30 | SSM | 18 | 23:00
Charsaidpur | 45 | 11:00 | Manikganj | 81 | 22:00 | Sunamganj | 44 | 22:00
Chauddagram | 50 | 20:00 | Maniknagar | 76 | 13:00 | Sylhet | 127 | 19:30
Chhatak | 25 | 22:00 | Matarbari | 42 | 21:00 | Tangail | 198 | 23:00
Chowmuhani | 212 | 21:00 | Matuail | 60 | 09:00 | Thakurgaon | 83 | 20:00
Chuadanga | 110 | 20:00 | Millgate | 46 | 19:00 | TK | 31.1 | 21:00
Coxsbazar | 117 | 21:00 | Mirpur | 127 | 19:00 | Tongi | 138 | 15:00
Cumilla(N) | 163 | 15:00 | Mirsorai | N/A | N/A | Ullon | 41 | 23:00
Cumilla(S) | 161 | 19:00 | Mithapukur | 30 | 19:00 | Uttara | 93 | 19:00
Daudkandi | 156 | 22:00 | Modern | 0 | 00:00 | UttaraNew | 27 | 09:00
Dhaka | 36 | 11:00 | Mogbazar | 116 | 13:00 | Zigatola | 44 | 20:00
Dhamrai | 112 | 19:30 | Mongla | 40 | 09:00
Dhanmondi | 149 | 13:00 | Motijheel | 35 | 13:00
Dohazari | 102 | 22:00 | Munshiganj | 108 | 23:00
Faridpur | 151 | 21:00 | Mymensingh | 209 | 21:00
Fatullah | 65 | 12:00 | Naogaon | 100 | 19:30
Fenchuganj | 46 | 22:00 | Narail | 55 | 22:00
Feni | 131 | 19:00 | Narinda | 69 | 13:00
Ghorashal | 52 | 01:00 | Narshingdi | 185 | 23:00
Goalpara | 27 | 13:00 | Natore | 122 | 21:00
Gollamari | 57 | 23:00 | Nawabganj | 55.7 | 22:00
Gopalganj | 106 | 22:00 | Netrakona | 112 | 22:00
GPH | 88 | 13:00 | New | 122.2 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 9:00 | 400 | 5:00 | Kaliakoir | 390 | 0.75 | 375 | 0.33333
| Bheramara | 402 | 7:00 | 393 | 23:00 | Bhulta | 384 | 0.79167 | 373 | 0.33333
| Ashuganj(N) | 391 | 22:00 | 381 | 15:00 | Gopalganj | 417 | 0.625 | 404 | 0.875
| Payra | 419 | 18:00 | 412 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 15:00 | Hathazari | 232 | 21:00 | 223 | 6:00
| Ishurdi | 236 | 18:00 | 229 | 10:00 | Megnaghat | 228 | 9:00 | 222 | 12:00
| Ashuganj | 235 | 19:30 | 227 | 8:00 | Fenchuganj | 241 | 19:30 | 236 | 2:00
| Serajganj | 235 | 18:00 | 230 | 7:00 | Siddhirganj | 226 | 22:00 | 220 | 12:00
| Baghabari | 232 | 17:00 | 229 | 24:00 | Maniknagar | 224 | 22:00 | 217 | 8:00
| Barapukuria | 230 | 15:00 | 219 | 20:00 | Agargaon | 224 | 9:00 | 216 | 15:00
| Bogra | 232 | 18:00 | 224 | 8:00 | Barisal | 241 | 9:00 | 233 | 22:00
| Rajshahi | 239 | 18:00 | 230 | 8:00 | Bhola 225 MW | 244 | 6:00 | 233 | 22:00
| Khulna South | 238 | 18:00 | 225 | 10:00 | AKSML | 232 | 1:00 | 226 | 5:00
| Rampura | 224 | 22:00 | 216 | 15:00 | BSRM | 232 | 1:00 | 225 | 7:00
| Haripur | 226 | 21:00 | 216 | 8:00 | Bibiyana | 238 | 9:00 | 233 | 7:00
| Hasnabad | 224 | 22:00 | 213 | 8:00 | Bhulta | 226 | 13:00 | 218 | 8:00
| Shyampur | 224 | 22:00 | 216 | 15:00 | Ashuganj (S) | 231 | 23:00 | 225 | 8:00
| Aminbazar | 226 | 1:00 | 215 | 2:00 | Kaliakoir | 226 | 22:00 | 215 | 8:00
| Tongi | 226 | 13:00 | 217 | 15:00 | GPH | 231 | 3:00 | 225 | 15:00
| Comilla (N) | 228 | 8:00 | 224 | 4:00 | Jhenaidah | 234 | 18:00 | 225 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 131 | 01:00 | 126 | 12:00 | Manikganj | 132 | 06:00 | 124 | 19:00
| Agargaon | 129 | 01:00 | 124 | 15:00 | Maniknagar | 131 | 05:00 | 126 | 12:00
| Agrabad | 135 | 00:00 | 129 | 14:00 | Matarbari | 128 | 11:00 | 117 | 22:00
| AKS | 136 | 00:00 | 130 | 01:00 | Matuail | 132 | 23:00 | 127 | 08:00
| Aminbazar | 132 | 23:00 | 124 | 08:00 | Millgate | 132 | 22:00 | 126 | 08:00
| Amnura | 130 | 18:30 | 125 | 00:00 | Mirpur | 130 | 01:00 | 124 | 16:00
| Ashuganj | 135 | 00:00 | 132 | 19:00 | Mithapukur | 133 | 12:00 | 124 | 20:00
| Bagerhat | 135 | 18:00 | 125 | 11:00 | Modern | 136 | 00:00 | 132 | 12:00
| Bakulia | 137 | 00:00 | 130 | 08:00 | Mogbazar | 136 | 17:00 | 125 | 15:00
| Banani | 131 | 02:00 | 127 | 15:00 | Mongla | 136 | 16:00 | 126 | 11:00
| Bangabhaban | 131 | 22:00 | 126 | 14:00 | Motijheel | 131 | 22:00 | 120 | 06:00
| Barapukuria | 135 | 15:00 | 127 | 20:00 | Munshiganj | 135 | 19:00 | 126 | 08:00
| Barguna | 139 | 06:00 | 130 | 19:00 | Mymensingh | 132 | 10:00 | 122 | 21:00
| Barishal | 140 | 07:00 | 130 | 19:00 | Naogaon | 134 | 15:00 | 124 | 21:00
| Barishal | 140 | 07:00 | 133 | 20:00 | Narail | 134 | 06:00 | 125 | 20:00
| Baroaulia | 137 | 18:00 | 132 | 06:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 136 | 18:00 | 126 | 04:00 | Narshingdi | 128 | 18:30 | 120 | 13:00
| Bashundhara | 132 | 23:00 | 127 | 08:00 | Natore | 134 | 18:00 | 128 | 07:00
| BashundharaCement | 135 | 22:00 | 126 | 08:00 | Nawabganj | 134 | 22:00 | 127 | 16:00
| Beanibazar | 135 | 03:00 | 128 | 18:00 | Netrakona | 133 | 19:30 | 120 | 21:00
| Benapole | 135 | 18:00 | 127 | 11:00 | New | 138 | 09:00 | 127 | 16:00
| Bhaluka | 130 | 09:00 | 119 | 21:00 | Niamatpur | 132 | 12:00 | 120 | 21:00
| Bhandaria | 140 | 07:00 | 126 | 22:00 | Noapara | 138 | 18:00 | 129 | 10:00
| Bhangura | 138 | 18:00 | 134 | 21:00 | Pabna | 135 | 18:00 | 131 | 20:00
| Bheramara | 137 | 18:00 | 133 | 21:00 | Palashbari | 133 | 16:00 | 123 | 19:30
| Bheramara(GK) | 140 | 18:00 | 136 | 05:00 | Panchagarh | 135 | 15:00 | 122 | 20:00
| Bhulta | 126 | 18:00 | 122 | 12:00 | Patuakhali | 136 | 03:00 | 132 | 18:00
| Bog-Sherpur | 136 | 18:00 | 129 | 20:00 | PHP | 136 | 18:00 | 125 | 02:00
| Bogura | 137 | 14:00 | 130 | 07:00 | Purbachal | 132 | 22:00 | 126 | 12:00
| Bogura | 137 | 14:00 | 130 | 08:00 | Purbasadipur | 134 | 16:00 | 122 | 07:00
| Brahmanbaria | 131 | 09:00 | 125 | 21:00 | Rahim | 133 | 19:30 | 127 | 08:00
| Cantonment | 128 | 01:00 | 123 | 15:00 | Rajbari | 135 | 05:00 | 129 | 21:00
| Chandpur | 137 | 13:00 | 128 | 00:00 | Rajendrapur | 131 | 14:00 | 122 | 00:00
| Chandraghona | 138 | 18:00 | 133 | 03:00 | Rajshahi | 131 | 18:30 | 125 | 00:00
| Chapai | 130 | 18:30 | 125 | 00:00 | Rajshahi | 129 | 18:00 | 124 | 00:00
| Charsaidpur | 136 | 22:00 | 127 | 08:00 | Ramganj | 135 | 18:00 | 122 | 06:00
| Chauddagram | 136 | 18:00 | 127 | 02:00 | Rampur | 136 | 00:00 | 132 | 03:00
| Chhatak | 135 | 03:00 | 128 | 19:00 | Rampura | 131 | 02:00 | 125 | 13:00
| Chowmuhani | 135 | 18:00 | 121 | 02:00 | Rangamati | 136 | 00:00 | 132 | 03:00
| Chuadanga | 129 | 18:00 | 120 | 20:00 | Rangpur | 132 | 15:00 | 121 | 20:00
| Coxsbazar | 129 | 00:00 | 116 | 06:00 | Ruppur | 137 | 18:00 | 133 | 21:00
| Cumilla(N) | 135 | 18:00 | 131 | 00:00 | Saidpur | 132 | 01:00 | 121 | 20:00
| Cumilla(S) | 135 | 18:00 | 128 | 14:00 | Satkhira | 136 | 18:30 | 125 | 11:00
| Daudkandi | 135 | 20:00 | 126 | 00:00 | Satmasjid | 129 | 23:00 | 124 | 15:00
| Dhaka | 131 | 01:00 | 125 | 15:00 | Savar | 132 | 01:00 | 124 | 08:00
| Dhamrai | 130 | 23:00 | 125 | 15:00 | Shahjadpur | 142 | 04:00 | 138 | 00:00
| Dhanmondi | 133 | 22:00 | 127 | 08:00 | Shahjibazar | 135 | 08:00 | 129 | 21:00
| Dohazari | 136 | 00:00 | 130 | 04:00 | Shahmirpur | 138 | 01:00 | 131 | 14:00
| Faridpur | 135 | 05:00 | 128 | 23:00 | Shariatpur | 137 | 08:00 | 129 | 21:00
| Fatullah | 134 | 19:30 | 126 | 08:00 | Sherpur | 138 | 10:00 | 124 | 08:00
| Fenchuganj | 138 | 09:00 | 133 | 15:00 | Shikalbaha | 139 | 21:00 | 133 | 12:00
| Feni | 137 | 18:00 | 126 | 02:00 | Shikalbaha | 138 | 01:00 | 134 | 04:00
| Ghorashal | 137 | 19:00 | 135 | 15:00 | Shitalakhya | 137 | 20:00 | 126 | 08:00
| Goalpara | 139 | 18:00 | 131 | 11:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 139 | 18:00 | 131 | 10:00 | Shyampur | 133 | 19:30 | 126 | 10:00
| Gopalganj | 140 | 18:00 | 132 | 11:00 | Shyampur | 134 | 22:00 | 127 | 15:00
| Gopalganj_I | 140 | 18:00 | 132 | 23:00 | Siddhirganj | 133 | 22:00 | 127 | 08:00
| Gulshan | 131 | 02:00 | 125 | 14:00 | Sirajganj | 135 | 15:00 | 131 | 10:00
| Halishahar | 136 | 00:00 | 131 | 12:00 | Sonargaon | 135 | 22:00 | 127 | 04:00
| Haripur | 133 | 19:30 | 130 | 19:00 | Sreemongol | 137 | 09:00 | 132 | 19:00
| HaripurSBU | 133 | 19:30 | 129 | 00:00 | Srinagar | 134 | 22:00 | 129 | 03:00
| Hasnabad | 136 | 22:00 | 128 | 07:00 | SSM | 136 | 00:00 | 132 | 01:00
| Hathazari | 137 | 00:00 | 132 | 14:00 | Sunamganj | 134 | 10:00 | 126 | 19:00
| Ishurdi | 137 | 18:00 | 134 | 00:00 | Sylhet | 134 | 00:00 | 131 | 14:00
| Jaldhaka | 132 | 16:00 | 119 | 20:00 | Tangail | 134 | 13:00 | 123 | 19:00
| Jamalpur | 138 | 09:00 | 126 | 07:00 | Thakurgaon | 134 | 23:00 | 121 | 07:00
| Jashore | 136 | 18:00 | 126 | 11:00 | TK | 137 | 09:00 | 132 | 03:00
| Jhenaidah | 135 | 18:00 | 130 | 00:00 | Tongi | 132 | 04:00 | 128 | 17:00
| Jhenaidah | 135 | 18:00 | 130 | 00:00 | Ullon | 132 | 03:00 | 125 | 15:00
| Joydebpur | 144 | 13:00 | 129 | 07:00 | Uttara | 129 | 20:00 | 125 | 15:00
| Joypurhat | 134 | 12:00 | 122 | 21:00 | UttaraNew | 130 | 01:00 | 125 | 15:00
| Juldah | 138 | 18:00 | 133 | 04:00 | Zigatola | 135 | 23:00 | 128 | 16:00
| Kabirpur | 140 | 23:00 | 125 | 15:00
| Kachua | 137 | 18:00 | 126 | 02:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 131 | 23:00 | 125 | 17:00
| Kalurghat | 138 | 01:00 | 133 | 06:00
| Kamrangirchar | 135 | 22:00 | 127 | 08:00
| Kaptai | 138 | 00:00 | 132 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 530 | 8444 | 4666 | 13110 |  |  |  | QF-LDC-11
0:30 | 565 | 7563 | 4144.5 | 11707.5 | Date: | 2022-05-22
1:00 | 600 | 6682 | 3623 | 10305
1:30 | 628 | 6558.5 | 3579 | 10137.5
2:00 | 656 | 6435 | 3535 | 9970
2:30 | 655 | 6366.5 | 3485 | 9851.5 | [5 empty] | Gen. at Eve. Peak | 13456 | 13456 MW (21:00 )
3:00 | 654 | 6298 | 3435 | 9733 | [6 empty] | 21:00
3:30 | 676 | 6224 | 3397 | 9621 | [5 empty] | Gen. at Day Peak | 10951 | 10951 MW (12:00 )
4:00 | 698 | 6150 | 3359 | 9509 | [6 empty] | 12:00
4:30 | 714 | 6014.5 | 3286 | 9300.5 | [5 empty] | Highest Generation | 13456
5:00 | 730 | 5879 | 3213 | 9092 | [6 empty] | 21:00
5:30 | 714 | 5750.5 | 3171 | 8921.5
6:00 | 698 | 5622 | 3129 | 8751
6:30 | 645 | 5684.5 | 3113.5 | 8798
7:00 | 592 | 5747 | 3098 | 8845
7:30 | 651 | 5750.5 | 3129 | 8879.5
8:00 | 710 | 5754 | 3160 | 8914
8:30 | 624 | 6052.5 | 3120 | 9172.5
9:00 | 538 | 6351 | 3080 | 9431
9:30 | 502 | 6722 | 3076 | 9798
10:00 | 466 | 7093 | 3072 | 10165
10:30 | 488 | 7176 | 3113 | 10289
11:00 | 510 | 7259 | 3154 | 10413
11:30 | 618 | 7356 | 3326 | 10682
12:00 | 726 | 7453 | 3498 | 10951
12:30 | 638 | 7487.5 | 3581 | 11068.5
13:00 | 550 | 7522 | 3664 | 11186
13:30 | 613 | 7475 | 3668 | 11143
14:00 | 676 | 7428 | 3672 | 11100
14:30 | 714 | 7527 | 3744.5 | 11271.5
15:00 | 752 | 7626 | 3817 | 11443
15:30 | 738 | 7685.5 | 3819.5 | 11505
16:00 | 724 | 7745 | 3822 | 11567
16:30 | 685 | 7601.5 | 3731 | 11332.5
17:00 | 646 | 7458 | 3640 | 11098
17:30 | 639 | 7402.5 | 3660 | 11062.5
18:00 | 632 | 7347 | 3680 | 11027
18:30 | 591 | 7918 | 4025 | 11943
19:00 | 550 | 8489 | 4370 | 12859
19:30 | 478 | 8491 | 4669 | 13160
20:00 | 456 | 8516 | 4701 | 13217 |  |  |  | Executive Engineer
20:30 | 477 | 8580.5 | 4756 | 13336.5 |  |  |  | Network Operation Division
21:00 | 498 | 8645 | 4811 | 13456
21:30 | 502 | 8568 | 4829.5 | 13397.5
22:00 | 506 | 8491 | 4848 | 13339 |  |  |  |  | Page 6 of 7
22:30 | 513 | 8516 | 4814 | 13330
23:00 | 520 | 8541 | 4780 | 13321
23:30 | 525 | 8492.5 | 4723 | 13215.5
24:00 | 530 | 8444 | 4666 | 13110
13456 MW (21:00 )
10951 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-22 |  | Energy |  | 266179271
[13 empty] | 2022-05-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3720 | 920 | 1990 | 380 | 4127 | 1235 | 35 | 0 | 591 | 112 | 0 | 0
0:30 | 3717 | 916 | 2071 | 190 | 3284.5 | 1085 | 32.5 | 0 | 303.5 | 108 | 0 | 0 | Date: | 2022-05-22
1:00 | 3714 | 912 | 2152 | 0 | 2442 | 935 | 30 | 0 | 16 | 104 | 0 | 0
1:30 | 3746.5 | 911.5 | 2154.5 | 0 | 2258 | 925 | 30 | 0 | 8 | 104 | 0 | 0 | [8 empty] | Total Energy | 266.1793 | Total Energy Gen 266.179 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 266.179 MKWHr
2:00 | 3779 | 911 | 2157 | 0 | 2074 | 915 | 30 | 0 | 0 | 104 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3781 | 911 | 2160 | 0 | 1950.5 | 915 | 30 | 0 | 0 | 104 | 0 | 0 | [8 empty] | Energy Requirement | 266.1793
3:00 | 3783 | 911 | 2163 | 0 | 1827 | 915 | 30 | 0 | 0 | 104 | 0 | 0
3:30 | 3782 | 911 | 2153.5 | 0 | 1727.5 | 915 | 30 | 0 | 0 | 102 | 0 | 0 | [6 empty] | Shortage
4:00 | 3781 | 911 | 2144 | 0 | 1628 | 915 | 30 | 0 | 0 | 100 | 0 | 0
4:30 | 3768.5 | 911.5 | 2144.5 | 0 | 1433 | 915 | 30 | 0 | 0 | 98 | 0 | 0
5:00 | 3756 | 912 | 2145 | 0 | 1238 | 915 | 30 | 0 | 0 | 96 | 0 | 0
5:30 | 3719 | 912 | 2068.5 | 0 | 1179 | 915 | 30 | 0 | 0 | 94 | 4 | 0
6:00 | 3682 | 912 | 1992 | 0 | 1120 | 915 | 30 | 0 | 0 | 92 | 8 | 0
6:30 | 3741 | 912 | 1997.5 | 0 | 1113 | 895 | 30 | 0 | 0 | 89 | 20.5 | 0 |  |  |  |  | Coal
7:00 | 3800 | 912 | 2003 | 0 | 1106 | 875 | 30 | 0 | 0 | 86 | 33 | 0
7:30 | 3772.5 | 912 | 2046 | 0 | 1105 | 865 | 30 | 0 | 0 | 90 | 59 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3745 | 912 | 2089 | 0 | 1104 | 855 | 30 | 0 | 0 | 94 | 85 | 0
8:30 | 3733.5 | 914.5 | 1999 | 0 | 1417 | 855 | 30 | 0 | 24 | 96 | 103.5 | 0
9:00 | 3722 | 917 | 1909 | 0 | 1730 | 855 | 30 | 0 | 48 | 98 | 122 | 0
9:30 | 3699.5 | 918 | 1920.5 | 0 | 2117.5 | 830 | 30 | 0 | 52 | 102 | 128.5 | 0
10:00 | 3677 | 919 | 1932 | 0 | 2505 | 805 | 30 | 0 | 56 | 106 | 135 | 0
10:30 | 3682.5 | 921 | 1905 | 0 | 2648 | 810 | 30 | 0 | 65.5 | 106 | 121 | 0
11:00 | 3688 | 923 | 1878 | 0 | 2791 | 815 | 30 | 0 | 75 | 106 | 107 | 0
11:30 | 3683 | 923 | 1874 | 0 | 2951 | 865 | 30 | 0 | 107 | 108 | 141 | 0
12:00 | 3678 | 923 | 1870 | 0 | 3111 | 915 | 30 | 0 | 139 | 110 | 175 | 0
12:30 | 3657.5 | 923.5 | 1795.5 | 0 | 3295.5 | 955 | 30 | 0 | 150.5 | 111 | 150 | 0
13:00 | 3637 | 924 | 1721 | 0 | 3480 | 995 | 30 | 0 | 162 | 112 | 125 | 0
13:30 | 3637 | 924 | 1721 | 0 | 3480 | 995 | 30 | 0 | 162 | 112 | 125 | 0
14:00 | 3637 | 924 | 1721 | 0 | 3480 | 995 | 30 | 0 | 162 | 112 | 125 | 0
14:30 | 3628 | 923.5 | 1777.5 | 0 | 3542.5 | 1020 | 30 | 0 | 162.5 | 118 | 112.5 | 0
15:00 | 3619 | 923 | 1834 | 0 | 3605 | 1045 | 30 | 0 | 163 | 124 | 100 | 0
15:30 | 3642 | 923.5 | 1799 | 0 | 3677 | 1040 | 30 | 0 | 195 | 126 | 72.5 | 0
16:00 | 3665 | 924 | 1764 | 0 | 3749 | 1035 | 30 | 0 | 227 | 128 | 45 | 0
16:30 | 3578 | 923 | 1733.5 | 0 | 3638.5 | 1020 | 30 | 0 | 207 | 124 | 35 | 0
17:00 | 3578 | 922 | 1703 | 0 | 3528 | 1005 | 30 | 0 | 187 | 120 | 25 | 0
17:30 | 3538.5 | 922.5 | 1697 | 0 | 3526 | 985 | 30 | 0 | 228 | 120 | 15.5 | 0
18:00 | 3499 | 923 | 1691 | 0 | 3524 | 965 | 30 | 0 | 269 | 120 | 6 | 0
18:30 | 3596 | 923.5 | 1815.5 | 363.5 | 3696.5 | 990 | 30 | 0 | 397 | 128 | 3 | 0
19:00 | 3693 | 924 | 1940 | 727 | 3869 | 1015 | 30 | 0 | 525 | 136 | 0 | 0
19:30 | 3694 | 922 | 1932 | 714 | 4044 | 1144 | 30 | 0 | 560 | 120 | 0 | 0
20:00 | 3698 | 923 | 1947 | 721 | 4034 | 1146 | 30 | 0 | 592 | 126 | 0 | 0
20:30 | 3668.5 | 923 | 1953.5 | 805 | 4064.5 | 1170.5 | 32.5 | 0 | 592 | 127 | 0 | 0
21:00 | 3639 | 923 | 1960 | 889 | 4095 | 1195 | 35 | 0 | 592 | 128 | 0 | 0
21:30 | 3637 | 920 | 1940 | 829 | 4110.5 | 1210 | 35 | 0 | 592 | 124 | 0 | 0
22:00 | 3635 | 917 | 1920 | 769 | 4126 | 1225 | 35 | 0 | 592 | 120 | 0 | 0
22:30 | 3671.5 | 916 | 1927 | 709 | 4124.5 | 1230 | 35 | 0 | 593 | 124 | 0 | 0
23:00 | 3708 | 915 | 1934 | 649 | 4123 | 1235 | 35 | 0 | 594 | 128 | 0 | 0
23:30 | 3714 | 917.5 | 1962 | 514.5 | 4125 | 1235 | 35 | 0 | 592.5 | 120 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 3720 | 920 | 1990 | 380 | 4127 | 1235 | 35 | 0 | 591 | 112 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 266.179 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 266.179 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 35 | 35 | 35 | 35 | 752280
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | [10 empty] | 1 | 23 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 309423
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 8 | 11 | 13 | 15 | 13 | 15 | 9 | 10 | 6 | 3 | 0 | [8 empty] | 107190
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 201 | 202 | 202 | 202 | 202 | 204 | 203 | 203 | 206 | 207 | 207 | 205 | 216 | 203 | 206 | 203 | 205 |  | 216 | 203 | 215 | 213 | 203 | 203 | 203 | 4893480
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 273420
12 | Hathazari 100 MW peaking PP | [9 empty] | 8 | 8 | 8 | 8 | 0 | 10 | 40 | 0 |  |  |  | 18 | 43 | 43 | 43 | 43 | 40 | 333032
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 68 | 34 | 17 | 17 | 17 | 17 | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 95 | 88 | 100 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2029854
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 150 | 200 | 200 | 200 | 200 | 160 | 50 | 922752
14 | Titas 50 MW Peaking PP | [10 empty] | 19 | 41 | 39 | 39 | 39 | 39 | 39 | 40 |  | 40 | 33 | 38 | 33 | 40 | 40 | 40 | 504936
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 333 | 335 | 328 | 328 | 330 | 280 | 280 | 324 | 325 | 300 | 240 |  | 326 | 328 | 325 | 327 | 330 | 331 | 330 | 7744522
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 0 | [5 empty] | 0 | 5 | 134 | 170 | 228 | 233 | 243 | 237 | 230 | 228 | 247 |  | 242 | 242 | 242 | 242 | 250 | 263 | 275 | 3512726
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 230 | 230 | 230 | 200 | 200 | 250 | 250 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6171955
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 25 | 25 | 25 | 26 | 29 | 29 |  | 29 | 27 | 29 | 29 | 32 | 32 | 32 | 660744
33 | Ashuganj 225 MW CCPP | 182 | 182 | 181 | 183 | 182 | 191 | 193 | 170 | 146 | 144 | 161 | 173 | 182 | 180 | 175 | 182 | 188 | 185 |  | 186 | 193 | 190 | 127 | 117 | 191 | 212 | 4212000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 290 | 300 | 280 | 300 | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7250000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 5 | 5 | 0 | 0 | 0 | 0 | [10 empty] | 10 | 294720
36 | Chandpur 150 MW CCPP | 102 | 100 | 102 | 100 | 102 | 100 | 102 | 100 | 100 | 99 | 98 | 100 | 100 | 95 | 97 | 99 | 97 | 99 |  | 99 | 100 | 97 | 98 | 101 | 100 | 100 | 2343700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5120250
41 | Haripur 360MW CCPP(HPL) | 331 | 331 | 338 | 337 | 336 | 307 | 308 | 320 | 321 | 322 | 321 | 321 | 272 | 273 | 323 | 322 | 324 | 272 |  | 319 | 329 | 329 | 320 | 320 | 320 | 320 | 7596000
42 | RPCL 210MW CCPP | 160 | 160 | 160 | 160 | 161 | 160 | 158 | 157 | 159 | 148 | 143 | 142 | 130 | 128 | 132 | 146 | 145 | 146 |  | 149 | 150 | 149 | 148 | 146 | 146 | 146 | 3523200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 4 | 14 | 8 | 21 | 47 | 43 | 37 | 46 | 40 | 38 | 15 | 9 | 3 |  | 0 | [6 empty] | 316690
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1033000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 961920
46 | Shajibazar 330 MW CCPP | 70 | 109 | 110 | 111 | 110 | 111 | 110 | 112 | 110 | 112 | 111 | 113 | 111 | 109 | 108 | 109 | 110 | 111 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2176000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 55 |  | 50 | 50 | 50 | 55 | 55 | 55 | 55 | 1235424
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 40 | 40 | 73 | 78 | 75 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1037760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 220 | 220 | 220 | 193 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 219 | 220 | 5270090
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 39 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 0 | [17 empty] | 352840
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247320
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 3 | 0 | [14 empty] | 67000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 11 | 11 | 20 | 50 | 22 | 0 | [15 empty] | 369000
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | [5 empty] | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 177360
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 280 | 270 | 270 | 280 | 300 | 300 | 300 | 290 | 285 | 300 | 270 | 270 | 290 | 290 | 280 | 280 |  | 300 | 290 | 290 | 305 | 290 | 280 | 300 | 7069500
| Bibiyana South 400 MW | 401 | 401 | 401 | 401 | 401 | 360 | 401 | 400 | 386 | 391 | 399 | 385 | 400 | 386 | 392 | 392 | 390 | 360 |  | 394 | 394 | 387 | 391 | 394 | 400 | 392 | 9366000
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 | [6 empty] | 24 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 45 |  | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 776583
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 |  |  |  |  | 2 | 15 | 23 | 24 | 24 | 22 | 21 | 24 | 0 |  |  | 2 | 20 | 20 | 24 | 20 | 24 | 24 | 384240
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507216
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 |  |  |  | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 386640
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 348408
63 | Impoprt (Tripura) | 104 | 104 | 104 | 100 | 96 | 92 | 86 | 94 | 98 | 106 | 106 | 110 | 112 | 120 | 124 | 128 | 120 | 120 |  | 136 | 120 | 126 | 128 | 120 | 128 | 112 | 2659200
64 | Malancha, Ctg. EPZ (United) | 35 | 40 | 40 | 40 | 40 | 32 | 24 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 5 | 10 | 20 | 23 | 10 | 31 | 362880
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 405216
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 111060
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 25 | 33 | 33 | 21 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 705900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488620
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 26 | 26 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 28 | 28 | 20 | 25 |  | 20 | 25 | 28 | 28 | 28 | 28 | 28 | 577800
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 17 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 638100
73 | Ghorashal 108MW PP (Regent) | 105 | 105 | 104 | 104 | 104 | 104 | 104 | 105 | 102 | 96 | 96 | 102 | 98 | 96 | 95 | 93 | 97 | 100 |  | 101 | 101 | 101 | 102 | 102 | 102 | 102 | 2381545
| Feni Lanka Power | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 98 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2209320
| Chowmuhani 113 MW | 54 | 36 | 28 | 29 | 28 | 29 | 29 | 28 | 29 | 29 | 29 | 28 | 29 | 29 | 57 | 108 | 112 | 114 |  | 113 | 114 | 114 | 113 | 114 | 114 | 108 | 1511160
| Manikgonj 162MW PP(MPGL) | 162 | 126 | 90 | 17 |  |  |  |  | 66 | 134 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 108 |  | 127 | 144 | 144 | 144 | 144 | 144 | 144 | 2707200
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 11 | 24 | 54 | 64 | 83 | 89 | 90 | 89 | 89 | 90 |  | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 1243200
78 | Gazipur 52 MW PP | 25 | [7 empty] | 24 | 24 | 40 | 48 | 48 | 40 | 40 | 40 | 40 | 46 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 711840
79 | Kodda 150MW PP | 16 | [7 empty] | 48 | 48 | 48 | 90 | 115 | 82 | 98 | 98 | 98 | 98 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 1541760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 39 | 39 | 36 | 34 | 36 | 36 | 36 | 33 | 41 |  | 41 | 41 | 41 | 42 | 42 | 42 | 43 | 977683
| Gazipur 100 MW PP | 34 | 34 | 34 | 34 | 17 |  |  |  | 90 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1833600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 6 | 5 | 1 | 1 | 2 | 1 | 0 | [8 empty] | 33600
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 50 | 36 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1233766
| Karnaphuli Power Ltd. | 92 | 93 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 93 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2234754
82 | Madanganj 102 PP(Summit) | 32 | 16 | 16 | 16 | [5 empty] | 40 | 73 | 80 | 80 | 80 | 79 | 78 | 78 | 78 |  | 79 | 79 | 81 | 96 | 96 | 96 | 96 | 1339800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 110 | 125 | 115 | 110 | 110 | 135 | 135 | 140 | 120 | 120 | 125 | 120 | 130 | 140 | 145 | 125 | 130 | 130 |  | 140 | 135 | 145 | 138 | 130 | 145 | 145 | 3174836
87 | Meghnaghat 100 MW(IEL) | 83 | 82 | 82 | 82 | 82 | 50 | 40 | 40 | 68 | 81 | 81 | 81 | 81 | 81 | 73 | 72 | 74 | 73 |  | 72 | 74 | 72 | 71 | 71 | 71 | 72 | 1738560
| Meghnaghat 104 MW PP (OPCL) | 90 | 55 | 17 | 17 |  |  |  |  | 18 | 87 | 90 | 90 | 90 | 90 | 90 | 90 | 54 | 54 |  | 72 | 91 | 91 | 91 | 90 | 91 | 91 | 1534080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258960
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 20 | 20 | 0 | [15 empty] | 462960
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 7 | 24 | 58 | 75 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1242288
95 | Patenga 50MW PP (Baraka) | 41 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 43 | 28 | 18 | 18 | 20 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 798240
96 | Chattogram 108 MW PP (ECPV) | 81 | 39 | 26 | 23 | 24 | 15 | 11 | 11 | 29 | 68 | 67 | 65 | 79 | 78 | 78 | 78 | 78 | 80 |  | 81 | 84 | 84 | 85 | 85 | 86 | 87 | 1449600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 45 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 45 | 55 | 924018
100 | Manikganj 55 MW PP (Northern) | 35 | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 886750
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2677827
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 10850
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1215000
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 290 | 105 | 105 | 235 | 103 | 103 | 72 | 817346
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 86 | 97 | 97 | 98 | 99 | 99 | 99 | 509868
106 | Mymensingh 200 MW PP (United) | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 41 | 60 | 60 | 74 | 120 | 140 | 155 | 155 | 120 | 120 |  | 163 | 181 | 182 | 195 | 195 | 195 | 195 | 2342400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 95 | 98 | 99 | 98 | 99 | 99 | 99 | 511553
114 | Kodda 149 MW PP Unit-1 (Summit) | 50 | 26 | 17 | 17 | 17 | 17 | 17 | 17 | 49 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2499984
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 38 | 38 | 892800
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 23 | 17 | 17 | 17 | 38 | 117 | 176 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3138240
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 401 | 400 | 400 | 352 | 400 | 402 | 402 | 404 | 402 | 400 | 402 | 404 | 403 | 403 | 404 | 351 |  | 403 | 403 | 403 | 403 | 403 | 402 | 402 | 9544000
| Jamalpur 115 MW PP (United) | 109 | 109 | 109 | 109 | 75 | 35 | 35 | 35 | 98 | 109 | 99 | 98 | 98 | 108 | 108 | 98 | 98 | 108 |  | 108 | 108 | 109 | 108 | 109 | 109 | 108 | 2308800
| Anwara 300 MW PP (United) | 246 | 246 | 246 | 246 | 210 | 210 | 210 | 210 | 228 | 228 | 232 | 235 | 252 | 250 | 258 | 261 | 265 | 265 |  | 282 | 282 | 282 | 283 | 283 | 283 | 283 | 6029345
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 834240
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2609455
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 611640
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | [8 empty] | 4 | 17 | 42 | 54 | 72 | 95 | 101 | 100 | 50 | 17 |  | 47 | 100 | 91 | 100 | 100 | 100 | 100 | 1155840
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 1 | 53 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 1261800
120 | Eastern Zone Total | 6682 | 6435 | 6298 | 6150 | 5879 | 5622 | 5747 | 5754 | 6351 | 7093 | 7259 | 7453 | 7522 | 7428 | 7626 | 7745 | 7458 | 7347 |  | 8489 | 8491 | 8516 | 8645 | 8491 | 8541 | 8444 | 173730613
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 66 | 66 | 66 | 65 | 65 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 83 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 84 | 88 | 1752000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 37 |  | 37 | 45 | 39 | 39 | 33 | 33 | 33 | 220320
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 17 | 17 | 17 | [7 empty] | 12 | 53 | 53 | 66 | 70 | 70 | 35 |  | 58 | 105 | 105 | 105 | 105 | 105 | 105 | 1180800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 13 | 61 | 78 | 62 | 34 | 106 | 47 | 36 | 40 | 16 | 10 | 3 | [8 empty] | 508320
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 453600
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 202 | 203 | 201 | 206 | 203 | 203 | 203 | 160 | 210 | 217 | 200 | 166 | 166 | 220 | 213 | 190 | 220 |  | 220 | 217 | 217 | 218 | 220 | 219 | 220 | 4839409
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 761184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 88 | 88 | 88 | 86 | 87 | 86 | 87 | 85 | 88 | 85 | 84 | 85 | 84 | 83 | 84 | 84 | 84 | 85 |  | 85 | 85 | 84 | 85 | 86 | 86 | 86 | 2049944
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 29 | 28 | 25 | 21 | 19 | 19 | 19 | 21 | 22 | 23 | 24 | 26 | 25 | 25 | 24 | 23 |  | 32 | 28 | 32 | 32 | 32 | 34 | 34 | 624040
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [9 empty] | 15 | 60 | 60 | 90 | 100 | 20 | 20 | 368640
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 16 | 40 | 40 | 40 | 191625
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 15 |  | 63 | 66 | 60 | 61 | 60 | 60 | 60 | 337792
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | [7 empty] | 42 | 50 | 50 | 67 | 67 | 67 | 67 |  | 105 | 85 | 85 | 105 | 105 | 105 | 105 | 1065744
146 | Bheramara HVDC | 912 | 911 | 911 | 911 | 912 | 912 | 912 | 912 | 917 | 919 | 923 | 923 | 924 | 923 | 923 | 924 | 922 | 923 |  | 924 | 922 | 923 | 923 | 917 | 915 | 920 | 22216000
147 | Bheramara 410 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 270 | 260 | 250 | 245 | 225 | 225 | 215 | 200 | 200 | 210 | 215 |  | 220 | 220 | 225 | 220 | 225 | 220 | 220 | 6071616
148 | Payra 1320 MW | 760 | 740 | 740 | 740 | 740 | 740 | 700 | 680 | 680 | 630 | 640 | 740 | 820 | 820 | 870 | 860 | 830 | 790 |  | 840 | 970 | 970 | 1020 | 1050 | 1060 | 1060 | 21451500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 174 | 176 | 175 | 175 | 175 | 175 | 4297600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 34 | 34 | 34 |  | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 311360
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 2 | 3 | 4 | 4 | 3 | 4 | 1 | 0 | 0 | [8 empty] | 28500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 171 | 171 | 171 | 171 | 176 | 175 | 174 | 174 | 180 | 160 | 160 | 168 | 168 | 166 | 166 | 166 | 164 | 166 |  | 175 | 175 | 175 | 174 | 174 | 174 | 174 | 4363600
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 424 | 429 | 430 | 430 | 433 | 370 | 370 | 417 | 353 | 375 | 421 | 418 | 375 | 377 | 352 | 322 | 274 | 277 |  | 414 | 418 | 414 | 415 | 415 | 414 | 418 | 9360581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 5 | 9 | 23 | 27 | 27 | 31 | 31 | 123849
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 21 |  | 21 | 21 | 21 | 22 | 0 | 22 | 22 | 476880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194670
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 16 | 16 | 16 | 16 | 0 |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 289300
167 | Katakhali 50 MW Peaking PP | [13 empty] | 16 | 16 | 16 | 16 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 266751
168 | Santahar 50 MW Peaking PP | [19 empty] | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 192147
169 | Natore 52 MW PP (Rajlanka) | 16 | 16 | 16 | 16 | [7 empty] | 2 | 27 | 34 | 43 | 43 | 24 | 24 |  | 43 | 43 | 52 | 52 | 52 | 52 | 52 | 574080
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 481616
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 91 | 154 | 160 | 168 | 168 | 168 | 40 | 799710
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 97 | 94 | 94 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2073504
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | 35 | [5 empty] | 15 | 35 | 95 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1853472
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 110 | 90 | 75 | 40 | [6 empty] | 26 | 70 | 85 | 95 | 95 | 101 | 101 | 101 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1582195
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 7 | 7 | 7 | 6 | 4 | 2 | 0 | [8 empty] | 51045
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 6 | 52 | 52 | 92 | 92 | 34 | 34 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1035264
178