## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-24 | Tuesday
|  |  | Date (day): | 2022-05-24 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13567.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14668 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-23 | 2022-05-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 |  | 95 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 105 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 23 | 356 | 0 | 0 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 204 | 320 | 340 | 330
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 63 | 81 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 135 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 87 | 96 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 82 | 90 | 90 | 90 |  | 10 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 0 | 0 | 0 |  |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 115 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 19 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 52 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 255 | 276 | 290 | 290 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 62 | 266 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 90 | 99 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 98 | 98 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 134 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3313 | 3739 | 3523 | 3483 | 671 | 921
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 24 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 43 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 70 | 35 | 40 |  | 190 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 203 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 98 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 0 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 23 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 75 | 85 | 86 | 86 |  | 22 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 247 | 264 | 273 | 273 |  | 27 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 97 | 92 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 50 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1040 | 1262 | 1199 | 1313 | 601 | 455
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 148 | 191 | 194 | 194 | 71 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 270 | 340 | 340
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 33 | 30 | 30 |  | 15 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 128 | 140 | 140 |  | 150 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 41 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 113 | 130 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 8 | 8 | 8 |  | 44 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 110 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 114 | 28 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 82 | 83 | 83 |  | 32 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1062 | 1786 | 1683 | 1913 | 931 | 335
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 130 | 130 | 140 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 108 | 190 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 88 | 98 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 423 | 462 | 518.6 | 497 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 90 | 110 | 110 | 220 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 50 | 55 | 55
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 50 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 20 | 20 | 20
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 399 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1712 | 1732 | 1790 | 1831 | 321 | 228
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 904 | 913 | 913
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 115 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 235 | 245 | 320 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 32 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1467 | 1705 | 1833 | 2013 | 90 | 68
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 48 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 16 | 32 | 20 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 86 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 790 | 1020 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 216 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1156 | 1423 | 1443 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 43 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 29 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 2 | 32 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 220 |  |  | Running on HSD.
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 176 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 420 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 38 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 34 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 83 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 176 | 0 | 176 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 943 | 1328 | 1177 | 1576 | 421 | 138
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 101 | 101 | 103 | 103 |  | 10 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 67 | 97 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 350 | 373 | 401 | 393 | 99 | 180
|  | Total |  |  |  |  | 22348 | 21584 | 11466 | 13810 | 13567.6 | 14668 | 3304 | 2333
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11089.2908 | 13356.28 | 13121.8439 | 14186.0909
| A. |  | 2022-05-23 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13810 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9232 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13810 | MW
| 3 | Day peak Generation : |  |  | 11466 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13356.28 | MW
| 4 | Evening peak Generation : |  |  | 13810 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 285.6357 | MKWHr | By Solar | 1.3506 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 136.8461 | MKWHr |  | By Oil: | 94.0977 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 27.5519 | MKWHr |  | By Hydro: | 0.99572 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3304 | MW | Dhaka | 4907.08 | 4907.08 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2333 | MW | Chittagong | 1286 | 1286 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5637 | MW | Khulna | 1677 | 1677 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 999.49 | MMCFD |  |  | Rajshahi | 1344.2 | 1344.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 149494739.196 | ii) Oil : | Taka | 1285471662.09 | Comilla | 1341 | 1341 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 232310603 | Total | Taka | 1667277004.286 | Mymensingh | 1039 | 1039 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 500 | 500 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 320 | MW (E to W) at | 21:00 | hrs | Barisal | 406 | 406 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 302 | MW at | 22:00 | hrs | Rangpur | 856 | 856 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 13356.28 | 13356.28 |  | 0
| B. |  | 2022-05-24 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14668 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11600 | MW
| 4 | Reserve(Generation end) |  |  |  | 468 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 293.7021 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10276 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0211 | MKWHr. | ii) HVDC Flow at Peak Time |  | 904 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7725 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.58 |  | (b) Today: | 74.66 |  | (c) Rule Curve: |  | 77.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 320 |  | 0 | 225 | 145 | 72 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 23 | 30 | 51 | 10 | 86 | 25 | 22 | 31 | 0 | 0 | 0 | 270 | 0 | 184 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 40 | 43 | 16 | 5 | 33 | 20 | 116 | 146 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 300 | 11 | 0 | 50 | 275 | 52 | 60 | 195 | 60 | 149 | 0 | 38 | 200 | 0 | 402 | 108 | 105 | 105 | 0 | 264 | 35 | 97 | 98 | 51 | 40 | 396 | 91 | 0 | 144 | 108 | 0 | 35 | 0 | 91 | 55 |  | 922 | 0 | 220 | 0 | 93 | 0 | 0 | 0 | 25 | 55 | 0 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 31 | 83 | 0 | 43 | 32 | 43 | 37 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 421 | 105 | 0 | 113 | 105 | 102 | 0 | 0 | 113 | 1030 | 219 | 0 | 17 | 0 | 0 | 115 |  | 8222 | 4511 | 12733 | 3711 | 922 | 1970 | 222 | 3993 | 1205 | 35 | 0 | 559 | 116 | 0 | 0 | 74.5
2:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 324 |  | 0 | 225 | 145 | 74 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 25 | 17 | 49 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 86 | 25 | 22 | 31 | 0 | 0 | 0 | 270 | 0 | 182 | 8 | 99 | 32 | 15 | 0 | 0 | 0 | 40 | 43 | 16 | 5 | 33 | 20 | 116 | 158 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 108 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 285 | 11 | 0 | 0 | 275 | 0 | 0 | 120 | 0 | 149 | 0 | 38 | 200 | 0 | 402 | 75 | 105 | 105 | 0 | 264 | 35 | 92 | 44 | 31 | 40 | 396 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 94 | 55 |  | 922 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 53 | 0 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 43 | 0 | 43 | 37 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 423 | 105 | 0 | 113 | 105 | 102 | 0 | 0 | 113 | 1030 | 220 | 0 | 17 | 0 | 0 | 115 |  | 7732 | 4348 | 12080 | 3719 | 922 | 1962 | 0 | 3816 | 1205 | 35 | 0 | 305 | 116 | 0 | 0 | 74.52
3:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 310 |  | 0 | 225 | 140 | 72 | 96 | 55 | 333 | 0 | 0 | 59 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 25 | 17 | 16 | 0 | 35 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 86 | 25 | 22 | 23 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 0 | 43 | 16 | 5 | 33 | 20 | 114 | 162 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 270 | 11 | 0 | 0 | 278 | 0 | 0 | 8 | 0 | 149 | 0 | 38 | 200 | 0 | 401 | 55 | 105 | 105 | 0 | 264 | 35 | 92 | 17 | 29 | 38 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 75 | 55 |  | 921 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 429 | 105 | 0 | 113 | 105 | 102 | 0 | 0 | 113 | 980 | 219 | 0 | 17 | 0 | 0 | 17 |  | 7301 | 4013 | 11314 | 3743 | 921 | 1925 | 0 | 3389 | 1155 | 35 | 0 | 32 | 114 | 0 | 0 | 74.54
4:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 300 |  | 0 | 225 | 145 | 72 | 96 | 55 | 332 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 25 | 25 | 16 | 0 | 35 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 86 | 25 | 22 | 32 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 103 | 32 | 15 | 0 | 0 | 0 | 0 | 43 | 16 | 5 | 33 | 20 | 100 | 160 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 280 | 11 | 0 | 0 | 130 | 0 | 0 | 8 | 0 | 149 | 0 | 38 | 155 | 0 | 402 | 55 | 52 | 105 | 0 | 264 | 35 | 92 | 17 | 28 | 38 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 0 | 55 |  | 922 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 428 | 105 | 0 | 113 | 67 | 102 | 0 | 0 | 113 | 940 | 220 | 0 | 17 | 0 | 0 | 0 |  | 6868 | 3926 | 10794 | 3761 | 922 | 1937 | 0 | 2892 | 1115 | 35 | 0 | 32 | 100 | 0 | 0 | 74.56
5:00 | 0 | 0 | 0 | 180 | 270 | 100 | 0 | 0 | 310 |  | 0 | 225 | 140 | 72 | 96 | 55 | 333 | 0 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 25 | 33 | 16 | 0 | 35 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 86 | 25 | 22 | 32 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 0 | 43 | 16 | 5 | 33 | 20 | 104 | 160 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 219 | 0 | 0 | 10 | 285 | 11 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 140 | 0 | 38 | 68 | 0 | 401 | 55 | 52 | 105 | 0 | 264 | 35 | 92 | 17 | 28 | 39 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 0 | 55 |  | 921 | 0 | 230 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 432 | 105 | 0 | 113 | 60 | 97 | 0 | 0 | 113 | 930 | 200 | 0 | 17 | 0 | 0 | 0 |  | 6650 | 3891 | 10541 | 3771 | 921 | 1928 | 0 | 2645 | 1105 | 35 | 0 | 32 | 104 | 0 | 0 | 74.57
6:00 | 0 | 0 | 0 | 180 | 240 | 101 | 0 | 0 | 300 |  | 0 | 225 | 150 | 72 | 73 | 55 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 27 | 25 | 33 | 16 | 0 | 35 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 81 | 25 | 22 | 33 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 102 | 32 | 15 | 0 | 0 | 0 | 0 | 38 | 16 | 5 | 33 | 20 | 94 | 160 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 111 | 55 | 10 | 0 | 185 | 0 | 0 | 10 | 275 | 12 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 88 | 0 | 38 | 17 | 0 | 374 | 55 | 17 | 105 | 1 | 264 | 35 | 92 | 17 | 28 | 38 | 360 | 64 | 4 | 130 | 108 | 0 | 26 | 0 | 0 | 51 |  | 922 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 350 | 75 | 0 | 113 | 15 | 54 | 0 | 0 | 113 | 800 | 220 | 0 | 17 | 0 | 6 | 0 |  | 6152 | 3544 | 9696 | 3601 | 922 | 1853 | 0 | 2188 | 976 | 35 | 0 | 16 | 94 | 11 | 0 | 74.58
7:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 300 |  | 0 | 225 | 150 | 72 | 40 | 55 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 20 | 25 | 33 | 16 | 0 | 35 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 58 | 25 | 22 | 23 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 6 | 33 | 20 | 92 | 160 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 111 | 55 | 10 | 0 | 185 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 35 | 1 | 38 | 17 | 0 | 364 | 55 | 17 | 68 | 0 | 264 | 35 | 92 | 17 | 29 | 39 | 360 | 25 | 9 | 72 | 108 | 0 | 17 | 0 | 0 | 55 |  | 929 | 0 | 245 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 420 | 75 | 0 | 70 | 15 | 56 | 0 | 1 | 70 | 800 | 211 | 0 | 17 | 0 | 21 | 0 |  | 5921 | 3546 | 9467 | 3649 | 929 | 1926 | 0 | 1828 | 975 | 35 | 0 | 0 | 92 | 33 | 0 | 74.59
8:00 | 0 | 0 | 0 | 180 | 270 | 102 | 0 | 0 | 300 |  | 0 | 225 | 150 | 72 | 15 | 30 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 8 | 25 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 50 | 25 | 22 | 8 | 0 | 0 | 0 | 340 | 0 | 190 | 8 | 100 | 32 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 5 | 33 | 20 | 98 | 159 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 160 | 0 | 0 | 10 | 295 | 12 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 34 | 2 | 38 | 17 | 0 | 352 | 60 | 17 | 68 | 1 | 245 | 35 | 92 | 17 | 28 | 25 | 330 | 70 | 13 | 72 | 108 | 0 | 17 | 0 | 0 | 17 |  | 911 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 383 | 53 | 0 | 75 | 15 | 78 | 0 | 2 | 70 | 780 | 183 | 0 | 17 | 2 | 46 | 0 |  | 5776 | 3456 | 9232 | 3642 | 911 | 1840 | 0 | 1719 | 955 | 0 | 0 | 0 | 98 | 67 | 0 | 74.59
9:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 303 |  | 0 | 225 | 148 | 72 | 18 | 30 | 329 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 0 | 25 | 27 | 25 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 54 | 0 | 22 | 2 | 0 | 0 | 0 | 350 | 0 | 176 | 8 | 99 | 32 | 5 | 0 | 0 | 0 | 0 | 14 | 16 | 5 | 33 | 20 | 102 | 151 | 0 | 20 | 2 | 44 | 41 | 0 | 0 | 110 | 110 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 16 | 0 | 0 | 19 | 0 | 49 | 4 | 25 | 35 | 0 | 402 | 0 | 80 | 87 | 2 | 245 | 35 | 90 | 17 | 29 | 25 | 390 | 73 | 37 | 94 | 108 | 0 | 17 | 0 | 0 | 19 |  | 911 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 414 | 53 | 0 | 90 | 15 | 103 | 0 | 3 | 113 | 770 | 183 | 0 | 17 | 3 | 71 | 0 |  | 6199 | 3574 | 9773 | 3824 | 911 | 1867 | 0 | 1937 | 945 | 0 | 0 | 65 | 102 | 122 | 0 | 74.59
10:00 | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 303 |  | 0 | 225 | 140 | 68 | 62 | 40 | 335 | 0 | 0 | 26 | 64 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 28 | 25 | 33 | 42 | 0 | 0 | 30 | 0 | 0 | 1 | 202 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 75 | 6 | 20 | 2 | 0 | 0 | 0 | 330 | 0 | 159 | 8 | 100 | 32 | 5 | 0 | 0 | 0 | 0 | 28 | 16 | 5 | 33 | 20 | 108 | 146 | 0 | 20 | 2 | 44 | 41 | 0 | 0 | 110 | 110 | 60 | 10 | 0 | 220 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 86 | 0 | 0 | 70 | 0 | 132 | 5 | 25 | 95 | 0 | 400 | 56 | 105 | 105 | 2 | 247 | 35 | 88 | 17 | 28 | 25 | 400 | 88 | 37 | 144 | 94 | 0 | 17 | 0 | 1 | 42 |  | 910 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 417 | 53 | 0 | 106 | 15 | 102 | 0 | 4 | 113 | 770 | 213 | 0 | 17 | 4 | 89 | 14 |  | 6847 | 3656 | 10503 | 3793 | 910 | 1891 | 0 | 2584 | 945 | 30 | 0 | 99 | 108 | 143 | 0 | 74.59
11:00 | 0 | 0 | 0 | 180 | 270 | 98 | 0 | 4 | 232 |  | 0 | 225 | 150 | 64 | 80 | 55 | 328 | 0 | 0 | 60 | 93 | 90 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 28 | 25 | 24 | 42 | 0 | 0 | 30 | 0 | 0 | 9 | 212 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 68 | 22 | 20 | 5 | 0 | 0 | 0 | 300 | 0 | 151 | 8 | 100 | 31 | 5 | 0 | 0 | 0 | 6 | 34 | 16 | 5 | 0 | 20 | 112 | 132 | 0 | 17 | 2 | 44 | 41 | 0 | 0 | 110 | 112 | 60 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 12 | 0 | 0 | 232 | 0 | 0 | 100 | 0 | 149 | 8 | 25 | 104 | 0 | 402 | 78 | 105 | 105 | 2 | 247 | 35 | 89 | 17 | 29 | 25 | 393 | 90 | 54 | 144 | 106 | 0 | 23 | 0 | 58 | 55 |  | 910 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 32 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 415 | 103 | 0 | 113 | 15 | 102 | 0 | 6 | 113 | 770 | 216 | 0 | 17 | 4 | 99 | 17 |  | 7131 | 3786 | 10917 | 3699 | 910 | 1799 | 0 | 3124 | 945 | 30 | 0 | 123 | 112 | 175 | 0 | 74.6
12:00 | 0 | 0 | 0 | 180 | 270 | 98 | 0 | 23 | 204 |  | 0 | 225 | 142 | 63 | 87 | 55 | 329 | 0 | 0 | 82 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 19 | 19 | 25 | 20 | 25 | 24 | 41 | 0 | 0 | 30 | 0 | 0 | 24 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 25 | 22 | 4 | 0 | 0 | 0 | 300 | 0 | 148 | 8 | 100 | 30 | 5 | 0 | 0 | 0 | 24 | 34 | 16 | 5 | 0 | 20 | 113 | 130 | 0 | 17 | 2 | 44 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 255 | 62 | 90 | 108 | 98 | 149 | 10 | 25 | 103 | 0 | 401 | 88 | 105 | 98 | 2 | 247 | 35 | 97 | 17 | 29 | 25 | 399 | 90 | 54 | 144 | 108 | 0 | 35 | 0 | 75 | 55 |  | 911 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 32 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 8 | 2 | 43 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 105 | 0 | 113 | 32 | 101 | 0 | 7 | 113 | 790 | 216 | 0 | 17 | 5 | 101 | 67 |  | 7550 | 3916 | 11466 | 3695 | 911 | 1782 | 250 | 3343 | 965 | 30 | 0 | 196 | 113 | 181 | 0 | 74.6
13:00 | 0 | 0 | 0 | 180 | 270 | 98 | 0 | 37 | 314 |  | 0 | 225 | 135 | 68 | 87 | 55 | 326 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 22 | 22 | 25 | 20 | 25 | 24 | 41 | 0 | 30 | 30 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 87 | 25 | 22 | 4 | 0 | 0 | 0 | 300 | 0 | 148 | 8 | 100 | 30 | 5 | 0 | 0 | 0 | 24 | 34 | 16 | 5 | 0 | 20 | 117 | 118 | 0 | 17 | 2 | 44 | 41 | 0 | 0 | 110 | 108 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 275 | 12 | 0 | 0 | 273 | 33 | 95 | 120 | 60 | 149 | 10 | 25 | 103 | 0 | 401 | 89 | 105 | 87 | 4 | 265 | 35 | 110 | 17 | 28 | 25 | 400 | 90 | 52 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 910 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 32 | 0 | 0 | 0 | 43 | 4 | 12 | 0 | 8 | 16 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 105 | 0 | 113 | 88 | 101 | 0 | 7 | 113 | 810 | 210 | 0 | 17 | 4 | 91 | 92 |  | 7688 | 4035 | 11723 | 3695 | 910 | 1855 | 188 | 3512 | 985 | 60 | 0 | 231 | 117 | 170 | 0 | 74.61
14:00 | 0 | 0 | 0 | 180 | 270 | 103 | 0 | 106 | 338 |  | 0 | 225 | 138 | 72 | 79 | 55 | 280 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 25 | 24 | 45 | 0 | 40 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 81 | 25 | 22 | 2 | 0 | 0 | 0 | 300 | 0 | 167 | 8 | 99 | 29 | 5 | 0 | 0 | 0 | 18 | 34 | 16 | 5 | 33 | 20 | 123 | 110 | 0 | 20 | 2 | 44 | 41 | 0 | 0 | 110 | 107 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 276 | 12 | 25 | 120 | 25 | 149 | 10 | 25 | 103 | 0 | 401 | 98 | 105 | 87 | 3 | 247 | 35 | 110 | 17 | 29 | 25 | 400 | 90 | 47 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 910 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 32 | 0 | 0 | 0 | 43 | 22 | 43 | 0 | 8 | 16 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 105 | 0 | 113 | 88 | 101 | 0 | 7 | 113 | 820 | 213 | 0 | 17 | 4 | 90 | 92 |  | 7635 | 4102 | 11737 | 3755 | 910 | 1894 | 62 | 3521 | 995 | 40 | 0 | 274 | 123 | 163 | 0 | 74.62
15:00 | 0 | 0 | 0 | 180 | 270 | 100 | 0 | 269 | 322 |  | 0 | 225 | 135 | 76 | 79 | 55 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 7 | 25 | 24 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 206 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 80 | 25 | 22 | 2 | 0 | 0 | 0 | 300 | 0 | 166 | 8 | 99 | 27 | 5 | 0 | 3 | 0 | 24 | 34 | 16 | 5 | 33 | 20 | 128 | 110 | 0 | 20 | 2 | 44 | 41 | 0 | 0 | 110 | 109 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 274 | 171 | 97 | 140 | 99 | 149 | 10 | 25 | 103 | 5 | 404 | 88 | 105 | 87 | 2 | 247 | 35 | 110 | 17 | 36 | 25 | 394 | 90 | 39 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 903 | 0 | 225 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 32 | 0 | 0 | 0 | 43 | 27 | 43 | 0 | 8 | 16 | 43 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 105 | 0 | 113 | 105 | 97 | 0 | 5 | 113 | 870 | 211 | 0 | 17 | 3 | 88 | 110 |  | 7849 | 4156 | 12005 | 3611 | 903 | 1892 | 367 | 3585 | 1045 | 40 | 0 | 285 | 128 | 149 | 0 | 74.61
16:00 | 0 | 0 | 0 | 180 | 270 | 100 | 0 | 365 | 324 |  | 0 | 225 | 130 | 78 | 90 | 45 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 7 | 25 | 32 | 48 | 0 | 42 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 19 | 2 | 17 | 10 | 80 | 25 | 22 | 2 | 0 | 0 | 0 | 300 | 0 | 162 | 8 | 100 | 30 | 5 | 0 | 20 | 0 | 24 | 34 | 16 | 5 | 33 | 20 | 120 | 124 | 0 | 20 | 1 | 44 | 41 | 0 | 0 | 110 | 108 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 40 | 276 | 202 | 96 | 169 | 97 | 148 | 10 | 25 | 103 | 38 | 403 | 88 | 90 | 87 | 1 | 262 | 35 | 99 | 17 | 68 | 25 | 397 | 90 | 23 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 904 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 19 | 32 | 0 | 0 | 0 | 43 | 26 | 43 | 0 | 8 | 24 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 105 | 0 | 113 | 105 | 92 | 0 | 4 | 113 | 890 | 211 | 0 | 17 | 2 | 50 | 109 |  | 8109 | 4146 | 12255 | 3734 | 904 | 1887 | 435 | 3666 | 1065 | 42 | 0 | 311 | 120 | 91 | 0 | 74.62
17:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 367 | 324 |  | 0 | 225 | 140 | 77 | 93 | 40 | 0 | 0 | 0 | 90 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 6 | 25 | 32 | 48 | 0 | 42 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 19 | 8 | 17 | 10 | 83 | 25 | 22 | 3 | 0 | 0 | 0 | 300 | 0 | 166 | 8 | 98 | 30 | 5 | 0 | 35 | 0 | 30 | 34 | 18 | 5 | 33 | 20 | 124 | 124 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 109 | 50 | 10 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 0 | 0 | 276 | 0 | 0 | 169 | 0 | 149 | 0 | 38 | 145 | 81 | 403 | 98 | 105 | 87 | 1 | 264 | 35 | 92 | 70 | 112 | 25 | 391 | 90 | 13 | 144 | 108 | 0 | 35 | 0 | 78 | 55 |  | 905 | 0 | 225 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 32 | 0 | 0 | 0 | 43 | 27 | 43 | 0 | 8 | 32 | 25 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 70 | 0 | 113 | 105 | 80 | 0 | 2 | 113 | 850 | 200 | 0 | 17 | 1 | 24 | 52 |  | 7863 | 3953 | 11816 | 3728 | 905 | 1891 | 0 | 3762 | 1025 | 42 | 0 | 298 | 124 | 41 | 0 | 74.62
18:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 345 | 277 |  | 0 | 225 | 132 | 72 | 93 | 55 | 0 | 0 | 0 | 90 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 32 | 48 | 0 | 42 | 0 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 24 | 8 | 17 | 10 | 85 | 25 | 22 | 7 | 0 | 0 | 0 | 300 | 0 | 163 | 8 | 100 | 31 | 5 | 0 | 51 | 0 | 30 | 34 | 18 | 5 | 33 | 20 | 116 | 126 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 110 | 60 | 10 | 0 | 220 | 0 | 0 | 10 | 260 | 16 | 0 | 0 | 275 | 0 | 0 | 120 | 0 | 124 | 0 | 50 | 170 | 110 | 352 | 98 | 105 | 87 | 0 | 264 | 35 | 92 | 70 | 114 | 25 | 360 | 90 | 2 | 144 | 90 | 0 | 35 | 0 | 55 | 55 |  | 904 | 0 | 225 | 0 | 76 | 0 | 0 | 0 | 30 | 2 | 0 | 85 | 21 | 32 | 0 | 0 | 0 | 43 | 26 | 43 | 0 | 8 | 40 | 34 | 33 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 326 | 53 | 0 | 70 | 50 | 70 | 0 | 0 | 70 | 800 | 167 | 0 | 17 | 0 | 5 | 52 |  | 7702 | 3635 | 11337 | 3635 | 904 | 1730 | 0 | 3558 | 975 | 42 | 0 | 370 | 116 | 7 | 0 | 74.62
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 104 | 0 | 332 | 332 |  | 0 | 225 | 150 | 80 | 95 | 55 | 0 | 0 | 0 | 87 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 18 | 25 | 33 | 48 | 0 | 42 | 30 | 0 | 0 | 25 | 220 | 0 | 0 | 0 |  | 24 | 47 | 51 | 10 | 85 | 21 | 22 | 10 | 0 | 0 | 0 | 270 | 0 | 177 | 8 | 97 | 34 | 5 | 0 | 51 | 0 | 36 | 33 | 18 | 5 | 33 | 20 | 136 | 127 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 40 | 0 | 220 | 0 | 0 | 10 | 290 | 20 | 0 | 120 | 275 | 230 | 97 | 136 | 98 | 131 | 0 | 50 | 184 | 123 | 404 | 98 | 105 | 87 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 388 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 68 | 55 |  | 905 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 45 | 31 | 16 | 83 | 30 | 32 | 0 | 0 | 0 | 43 | 27 | 83 | 0 | 43 | 40 | 43 | 36 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 159 | 0 | 414 | 75 | 14 | 90 | 67 | 101 | 0 | 0 | 90 | 820 | 220 | 0 | 17 | 0 | 0 | 69 |  | 8712 | 4131 | 12843 | 3695 | 905 | 2019 | 571 | 3879 | 995 | 72 | 0 | 571 | 136 | 0 | 0 | 74.63
19:30 | 0 | 0 | 0 | 180 | 270 | 104 | 0 | 354 | 329 |  | 0 | 225 | 140 | 80 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 48 | 0 | 42 | 30 | 0 | 0 | 25 | 205 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 86 | 48 | 22 | 16 | 0 | 0 | 0 | 270 | 0 | 185 | 8 | 97 | 33 | 5 | 0 | 51 | 0 | 41 | 33 | 18 | 5 | 33 | 20 | 132 | 127 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 40 | 0 | 220 | 0 | 0 | 10 | 315 | 20 | 0 | 150 | 275 | 263 | 99 | 190 | 98 | 149 | 0 | 50 | 200 | 125 | 402 | 98 | 105 | 105 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 393 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 904 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 33 | 52 | 40 | 84 | 30 | 48 | 0 | 0 | 0 | 43 | 26 | 83 | 0 | 43 | 40 | 34 | 36 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 176 | 0 | 414 | 105 | 155 | 113 | 85 | 101 | 0 | 0 | 113 | 1000 | 220 | 0 | 17 | 0 | 0 | 95 |  | 8978 | 4734 | 13712 | 3736 | 904 | 2038 | 850 | 4217 | 1175 | 72 | 0 | 588 | 132 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 270 | 104 | 0 | 357 | 328 |  | 0 | 225 | 130 | 81 | 96 | 55 | 0 | 0 | 0 | 82 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 49 | 0 | 40 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 86 | 42 | 22 | 18 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 41 | 33 | 18 | 5 | 33 | 20 | 134 | 127 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 91 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 310 | 20 | 0 | 150 | 275 | 260 | 99 | 190 | 98 | 149 | 0 | 50 | 200 | 125 | 402 | 98 | 105 | 101 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 395 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 81 | 55 |  | 904 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 33 | 58 | 40 | 85 | 30 | 48 | 0 | 0 | 0 | 43 | 29 | 83 | 0 | 43 | 40 | 34 | 38 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 176 | 0 | 414 | 105 | 166 | 113 | 105 | 101 | 0 | 0 | 113 | 1010 | 220 | 0 | 17 | 0 | 0 | 99 |  | 8969 | 4796 | 13765 | 3753 | 904 | 2034 | 863 | 4223 | 1185 | 70 | 0 | 599 | 134 | 0 | 0 | 74.63
21:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 356 | 320 |  | 0 | 225 | 135 | 81 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 85 | 43 | 22 | 23 | 0 | 0 | 0 | 270 | 0 | 191 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 130 | 130 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 295 | 20 | 0 | 200 | 276 | 266 | 99 | 190 | 98 | 149 | 0 | 50 | 200 | 128 | 402 | 98 | 105 | 105 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 400 | 90 | 0 | 134 | 108 | 0 | 35 | 0 | 82 | 55 |  | 904 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 33 | 58 | 40 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 29 | 83 | 0 | 43 | 32 | 34 | 37 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 176 | 0 | 420 | 105 | 176 | 113 | 105 | 101 | 0 | 0 | 113 | 1020 | 220 | 0 | 17 | 0 | 0 | 97 |  | 8981 | 4829 | 13810 | 3765 | 904 | 2030 | 939 | 4204 | 1195 | 70 | 0 | 573 | 130 | 0 | 0 | 74.63
22:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 351 | 320 |  | 0 | 225 | 140 | 80 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 35 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 87 | 44 | 22 | 29 | 0 | 0 | 0 | 270 | 0 | 193 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 134 | 128 | 0 | 0 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 280 | 20 | 0 | 200 | 290 | 266 | 99 | 190 | 98 | 148 | 0 | 50 | 200 | 125 | 402 | 98 | 105 | 105 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 400 | 90 | 0 | 126 | 108 | 0 | 35 | 0 | 82 | 55 |  | 904 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 33 | 49 | 8 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 29 | 83 | 0 | 43 | 32 | 34 | 36 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 175 | 0 | 417 | 105 | 174 | 113 | 105 | 101 | 0 | 0 | 113 | 990 | 220 | 0 | 17 | 0 | 0 | 97 |  | 8966 | 4754 | 13720 | 3743 | 904 | 2023 | 937 | 4176 | 1165 | 65 | 0 | 573 | 134 | 0 | 0 | 74.64
23:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 359 | 326 |  | 0 | 225 | 150 | 81 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 35 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 87 | 44 | 22 | 29 | 0 | 0 | 0 | 270 | 0 | 199 | 8 | 101 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 122 | 128 | 0 | 0 | 0 | 44 | 41 | 0 | 0 | 110 | 91 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 270 | 20 | 0 | 170 | 294 | 277 | 99 | 191 | 98 | 149 | 0 | 38 | 200 | 142 | 402 | 98 | 105 | 105 | 0 | 264 | 35 | 93 | 114 | 113 | 26 | 394 | 90 | 0 | 142 | 108 | 0 | 35 | 0 | 83 | 55 |  | 900 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 33 | 49 | 0 | 87 | 33 | 48 | 0 | 0 | 0 | 43 | 29 | 83 | 0 | 43 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 178 | 0 | 416 | 105 | 100 | 113 | 105 | 101 | 0 | 0 | 113 | 1000 | 220 | 0 | 17 | 0 | 0 | 97 |  | 8989 | 4659 | 13648 | 3762 | 900 | 2030 | 814 | 4199 | 1175 | 65 | 0 | 581 | 122 | 0 | 0 | 74.64
24:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 369 | 334 |  | 0 | 225 | 135 | 80 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 88 | 44 | 22 | 27 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 132 | 129 | 0 | 0 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 20 | 0 | 170 | 290 | 169 | 99 | 191 | 98 | 149 | 0 | 38 | 200 | 145 | 402 | 108 | 105 | 105 | 0 | 265 | 35 | 93 | 17 | 70 | 25 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 900 | 0 | 260 | 0 | 96 | 0 | 0 | 0 | 33 | 49 | 8 | 88 | 32 | 48 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 43 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 178 | 0 | 417 | 105 | 100 | 113 | 105 | 101 | 0 | 0 | 113 | 980 | 222 | 0 | 17 | 0 | 0 | 97 |  | 8750 | 4640 | 13390 | 3780 | 900 | 2043 | 706 | 4059 | 1155 | 35 | 0 | 580 | 132 | 0 | 0 | 74.64
KWH | 0 | 0 | 0 | 4410000 | 6437064 | 2379454 | 0 | 5087230 | 7286000 |  | 0 | 5104500 | 3527447 | 1788480 | 1945272 | 1265492 | 4701411 | 0 | 0 | 1502746 | 1699200 | 2233440 | 0 | 0 | 0 | 0 | 1285560 | 1193773 | 827795 | 397728 | 600000 | 534420 | 616500 | 662800 | 936480 | 0 | 711720 | 284000 | 0 | 0 | 400181 | 4927223 | 0 | 0 | 0 |  | 569760 | 343200 | 431487 | 258720 | 1920960 | 666240 | 531120 | 366240 | 0 | 0 | 0 | 7344400 | 0 | 4301000 | 217454 | 2361580 | 758808 | 230400 | 0 | 411743 | 0 | 493816 | 699931 | 388656 | 117720 | 669800 | 467640 | 2772480 | 3222720 | 0 | 384588 | 15000 | 1035000 | 946816 | 0 | 0 | 2670300 | 2422000 | 1293984 | 527040 | 0 | 5058580 | 0 | 0 | 250740 | 7141000 | 310656 | 0 | 1034496 | 5168725 | 1792760 | 1035688 | 2772000 | 1001557 | 3169440 | 73035 | 856320 | 3243840 | 1027054 | 9490000 | 1926000 | 2209200 | 2320072 | 19201 | 6217527 | 911331 | 2298317 | 1144560 | 1405320 | 700800 | 9328700 | 2051520 | 365560 | 3283200 | 2578091 | 0 | 791640 | 0 | 1361280 | 1283760 |  | 22021090 | 0 | 5667264 | 0 | 2106240 | 0 | 0 | 0 | 242400 | 397568 | 110625 | 2085543 | 571461 | 850464 | 0 | 0 | 0 | 618880 | 324919 | 810784 | 0 | 369168 | 328305 | 796800 | 319569 | 47472 | 0 | 197388 | 0 | 0 | 4282800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461760 | 4516945 | 0 | 9793818 | 2353920 | 790468 | 2591808 | 1746576 | 2272771 | 0 | 57389 | 2591904 | 23269100 | 5045782 | 0 | 447600 | 34920 | 785520 | 1518144 |  | 185208489 | 100427165 | 285635654 | 91275284 | 22021090 | 45570851 | 6116729 | 81436607 | 27551900 | 995720 | 0 | 6544368 | 2772480 | 1350625 | 0
Fuel Cost | 0 | 0 | 0 | 6570900 | 7209511.68 | 3164673.82 | 0 | 5341591.5 | 7868880 |  | 0 | 5563905 | 3915466.17 | 19995206.4 | 25774854 | 16767769 | 5265580.32 | 0 | 0 | 21970146.52 | 23907744 | 36204062.4 | 0 | 0 | 0 | 0 | 16352323.2 | 16115935.5 | 11100730.95 | 298296 | 450000 | 0 | 0 | 0 | 15929524.8 | 0 | 192164.4 | 76680 | 0 | 0 | 6542959.35 | 5124311.92 | 0 | 0 | 0 |  | 7435368 | 5724576 | 7343908.74 | 3495307.2 | 24357772.8 | 7708396.8 | 674522.4 | 1219579.2 | 0 | 0 | 0 | 8152284 | 0 | 4989160 | 280515.66 | 2881127.6 | 857453.04 | 343296 | 0 | 687610.81 | 0 | 8528202.32 | 9414071.95 | 532458.72 | 88290 | 1172150 | 350730 | 19906406.4 | 3512764.8 | 0 | 523039.68 | 239100 | 1417950 | 1249797.12 | 0 | 0 | 3070845 | 2591540 | 2510328.96 | 1201651.2 | 0 | 5109165.8 | 0 | 0 | 496465.2 | 7141000 | 232992 | 0 | 21683036.16 | 70553096.25 | 37576249.6 | 21407670.96 | 37366560 | 20702183.19 | 43896744 | 853779.15 | 8837222.4 | 44310854.4 | 13629006.58 | 8730800 | 23420160 | 31945032 | 29348910.8 | 0 | 72993766.98 | 9924394.59 | 24431109.71 | 15531679.2 | 18114574.8 | 8255424 | 8582404 | 26567184 | 5282342 | 41663808 | 29338675.58 | 0 | 10338818.4 | 0 | 20378361.6 | 16907119.2 |  | 66063270 | 0 | 6347335.68 | 0 | 21925958.4 | 0 | 0 | 0 | 4365624 | 7156224 | 1589681.25 | 2335808.16 | 1108634.34 | 9270057.6 | 0 | 0 | 0 | 10378617.6 | 5682833.31 | 12680661.76 | 0 | 6113422.08 | 5551637.55 | 10860384 | 5391129.03 | 98267.04 | 0 | 149422.716 | 0 | 0 | 22656012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9687724.8 | 5239656.2 | 0 | 9695879.82 | 31636684.8 | 16576113.96 | 30661088.64 | 25238023.2 | 28864191.7 | 0 | 634148.45 | 31465714.56 | 209654591 | 5146697.64 | 0 | 3312240 | 394945.2 | 9214149.6 | 23273147.52 |  | 1129714011.88 | 640419977.606 | 1770133989.486 | 98491372.296 | 66063270 | 51003366.9 | 127632978.67 | 1048831206.71 | 232310603 | 268844.4 | 0 | 109007476.71 | 19906406.4 | 16618464.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 270 | 98 | 0 | 23 | 204 |  | 0 | 225 | 142 | 63 | 87 | 55 | 329 | 0 | 0 | 82 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 19 | 19 | 25 | 20 | 25 | 24 | 41 | 0 | 0 | 30 | 0 | 0 | 24 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 25 | 22 | 4 | 0 | 0 | 0 | 300 | 0 | 148 | 8 | 100 | 30 | 5 | 0 | 0 | 0 | 24 | 34 | 16 | 5 | 0 | 20 | 113 | 130 | 0 | 17 | 2 | 44 | 41 | 0 | 0 | 110 | 110 | 55 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 255 | 62 | 90 | 108 | 98 | 149 | 10 | 25 | 103 | 0 | 401 | 88 | 105 | 98 | 2 | 247 | 35 | 97 | 17 | 29 | 25 | 399 | 90 | 54 | 144 | 108 | 0 | 35 | 0 | 75 | 55 |  | 911 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 32 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 8 | 2 | 43 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 105 | 0 | 113 | 32 | 101 | 0 | 7 | 113 | 790 | 216 | 0 | 17 | 5 | 101 | 67 |  | 11466 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 356 | 320 | 0 | 0 | 225 | 135 | 81 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 10 | 85 | 43 | 22 | 23 | 0 | 0 | 0 | 270 | 0 | 191 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 130 | 130 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 50 | 0 | 220 | 0 | 0 | 10 | 295 | 20 | 0 | 200 | 276 | 266 | 99 | 190 | 98 | 149 | 0 | 50 | 200 | 128 | 402 | 98 | 105 | 105 | 0 | 264 | 35 | 92 | 114 | 114 | 25 | 400 | 90 | 0 | 134 | 108 | 0 | 35 | 0 | 82 | 55 |  | 904 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 33 | 58 | 40 | 86 | 32 | 48 | 0 | 0 | 0 | 43 | 29 | 83 | 0 | 43 | 32 | 34 | 37 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 176 | 0 | 420 | 105 | 176 | 113 | 105 | 101 | 0 | 0 | 113 | 1020 | 220 | 0 | 17 | 0 | 0 | 97 |  | 13810 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 330 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 10 | 86 | 50 | 22 | 25 | 0 | 0 | 0 | 340 | 0 | 194 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 166 | 140 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 110 | 55 | 80 | 0 | 220 | 0 | 0 | 10 | 341 | 20 | 0 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 273 | 35 | 110 | 114 | 113 | 50 | 400 | 90 | 0 | 144 | 110 | 0 | 35 |  | 83 | 55 |  | 913 | 0 | 320 | 0 | 115 | 220 | 0 | 0 | 35 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 100 | 180 | 0 | 410 | 105 | 176 | 113 | 105 | 103 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 0 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 10 | 86 | 50 | 22 | 10 | 0 | 0 | 0 | 340 | 0 | 194 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 143 | 140 | 0 | 20 | 1.6 | 44 | 41 | 0 | 0 | 110 | 110 | 55 | 80 | 0 | 220 | 0 | 0 | 10 | 300 | 20 | 0 | 100 | 290 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 140 | 400 | 115 | 105 | 105 | 5 | 273 | 35 | 92 | 110 | 28 | 25 | 400 | 90 | 50 | 144 | 110 | 0 | 17 | 30 | 83 | 55 |  | 913 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 35 | 0 | 40 | 86 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 0 | 113 | 105 | 103 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 250 | 0 | 0 | 225 | 138 | 80 | 96 | 50 | 0 | 0 | 0 | 50 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 17 | 33 | 0 | 35 | 0 | 0 | 0 | 8 | 216 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 74 | 15 | 0 | 7 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 100 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 0 | 104 | 143 | 0 | 0 | 1 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 179 | 0 | 0 | 10 | 280 | 20 | 0 | 0 | 290 | 0 | 0 | 100 | 0 | 135 | 0 | 25 | 200 | 140 | 374 | 108 | 105 | 100 | 1 | 273 | 35 | 92 | 17 | 9 | 25 | 370 | 90 | 28 | 126 | 108 | 0 | 17 | 0 | 83 | 55 | 0 | 898 | 0 | 320 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 238 | 53 | 0 | 70 | 67 | 102 | 0 | 2 | 70 | 660 | 217 | 0 | 17 | 2 | 50 | 30 | 0 |  |  |  |  | 94097704 |  | 0
94097704
| Minimum Generation |  | 9232 | 8:00
| Highest Generation |  | 13810 | 21:00
| Day Peak Generation |  | 11466 | 12:00
| Evening Peak Generation |  | 13810 | 21:00
| HVDC Max Flow |  | 929 | 7:00
| HVDC EvPeak Flow |  | 904 | 21:00
| Load factor L.F |  | 86.18%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-24
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11466 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10276 | MW
Evening Peak Generation : |  | 13810 | MW Hour : | 21:00 | Available Max Generation : |  | 14668 | MW
E.P. Demand (at gen end) : |  | 13810 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 13810 | MW Hour : | 21:00 | Reserve(Generation end) |  | 468 | MW
Total Gen. (MKWH) : |  | 285.6357 | System Load Factor : | 86.18% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 302 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-24
Actual : | 74.66 | Ft.(MSL) , | Rule curve : | 77.6 | Ft.( MSL )
Gas Consumed : | Total = | 999.49 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 149494739.196
: |  | Coal : | 232310603 | Oil : | 1285471662.09 | Total : | 1667277004.286
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5056.8434 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1641.5384 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1598.8449 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1431.7856 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1305.5196 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1071.3202 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 524.8264 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 321.7386 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 787.9141 |  |  | 0 | 0%
Total | 0 |  | 13740.3312 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Daudkandi 132/33 kV T-1 transformer was shut down at 08:16 to 16:38 for C/M.
b) Mymensing 132 kV T-1 & T-2 transformer tripped at 08:17 due to 33 kV Gofargaon feeder fault | [5 empty] | About 84 MW power interruption occurred under
and were switched on at 08:24. | [5 empty] | Mymensing S/S area from 08:17 to 08:24.
c) Sherpur-UMPL 132 kV Ckt-1,2 tripped at 08:17 due to O/V and were switched on at 08:24. | [5 empty] | About 62 MW power interruption occurred under
Sherpur S/S area from 08:17 to 08:24.
d) Kulshi-Sholoshahar 132 kV Ckt-1 was under shut down from 09:52 to 17:46 for C/M.
e) Tongi-Milgate 132 kV Ckt-1 was under shut down from 10:17 to 16:54 for C/M.
f) Cumilla(N) 132/33 kV T-4 transformer under 33 kV bus was shut down at 11:01 to 12:44 for C/M by PDB. | [5 empty] | About 65 MW power interruption occurred under
Cumilla(N) S/S area from 11:01 to 12:44.
g) Bheramara HVDC-Jhenaidah 230 kV Ckt-2 was under shut down from 08:48 to 16:48 for C/M.
h) Bheramara-Rajbari 132 kV Ckt-2 tripped at 09:39 showing dist Z1,A phase relay and was switched on at 09:58.
i) Cumilla(s)-Surjomoni Nagar 132 kV Ckt-2 was under shut down from 11:40 to 14:26 for D/W.
j) Ashuganj 132 kV bus-1 was under shut down from 10:10 to 12:19 for C/M.
k) Naogaon-Santahar 132 kV Ckt was under shut down from 10:55 to 15:15 for C/M.
l) Naogaon-Joypurhat 132 kV Ckt was under shut down from 12:19 to 13:08 for PT maint works.
m) Haripur 412 MW GT & ST were synchronize at 10:35,13:12 respectively.
n) Ashuganj NCR-Midland 230 kV GIS was switched on at 13:06.
o) Siddhirganj 335 MW CCPP was shut down at 14:43 due to Gas shortage.
p) Haripur 412 MW was under shut down at 02:00(24-05-22) due to GBC problem.
q) Shahmirpur 132/33 kV T-2 transformer 33 kV side tripped at 06:43(24-05-22) due to 33 kV SM steel | [5 empty] | About 22 MW power interruption occurred under
feeder fault and was switched on at 07:08. | [5 empty] | Shahmirpur S/S area from 06:43 to 07:08.
r) Tangail 132/33 kV T-3 transformer was under shut down at 07:45 to 10:48 for 33 kV DS change by PBS. | [5 empty] | About 10 MW power interruption occurred under
Tangail S/S area from 07:45 to 10:48.
s) Bhola 225 MW was shut down at 07:54 due to air compressor trip.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4410000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6437064 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2379454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 356 | 5087230 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7286000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5104500 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 81 | 1788480 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 135 | 3527447 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 1945272
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1265492
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 397728
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1502746 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 4701411
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1699200 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1285560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 2233440 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1193773
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 827795
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1134420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 616500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 662800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 936480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 276 | 5168725 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 266 | 1792760 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 99 | 1035688
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 1001557
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3169440
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2209200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2051520 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 134 | 3283200 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1283760
| Dhaka area Total |  |  |  | 5898 | 3739 | 77418642
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 400181
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 73035
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 666240 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 995720 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4927223
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2320072
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 343200 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 431487 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258720 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 856320 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 531120
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 366240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1920960 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19201
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 264 | 6217527 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 911331 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2298317 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 700800
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2578091
| Chattogram area Total |  |  |  | 2382 | 1262 | 26815785
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4301000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7344400 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 758808 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 230400 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 411743
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 1027054 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 493816 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2361580 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3243840
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 388656 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 117720 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2772480
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 669800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 699931 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 467640 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1034496
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1144560
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 1405320
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 791640 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 82 | 1361280 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1786 | 31243618
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 130 | 3222720 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 384588
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 190 | 2772000
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1926000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 365560
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 569760
| Mymensingh Area Total |  |  |  | 622 | 462 | 9255628
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1035000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 946816 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2670300 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 90 | 2422000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1293984 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 527040 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5058580
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 20 | 310656 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7141000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9490000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250740
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9328700
| Sylhet Area Total |  |  |  | 2477 | 1732 | 40474816
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 904 | 22021090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2106240
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 242400 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 58 | 397568 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 5667264 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 110625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 461760
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2353920
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1746576
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 785520
| Khulna Area Total |  |  |  | 2384 | 1705 | 35892963
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 850464 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 32 | 571461 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2085543 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 23269100 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5045782
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 447600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1423 | 32269950
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 618880 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 29 | 324919 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 369168 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 328305 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4516945 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 9793818
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 319569 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 47472
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 197388 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 796800 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 83 | 810784 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 176 | 790468 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2591808
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2591904
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
| Rajshahi Area Total |  |  |  | 2129 | 1328 | 24133148
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4282800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 2272771 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 57389
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 97 | 1518144 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 373 | 8131104
| Total |  |  |  | 21584 | 13810 | 285635654
| Eastern Grid Total |  |  |  | 14393 | 8981 | 185208489
| Western Grid Total |  |  |  | 7191 | 4829 | 100427165
| National Grid Total |  |  |  | 21584 | 13810 | 285635654
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-23
(a) ENTIRE EASTERN GRID : |  | 9073.08 | MW | (b) ENTIRE WESTERN GRID : |  | 4283.2 | MW
i) Dhaka area |  | 4907.08 | MW | i) Khulna area |  | 1677 | MW
ii) Chittagong area |  | 1286 | MW | ii) Rajshahi area |  | 1344.2 | MW
iii) Comilla area |  | 1341 | MW | iii) Barisal area |  | 406 | MW
iv) Mymensingh area |  | 1039 | MW | iv) Rangpur area |  | 856 | MW
v) Sylhet area |  | 500 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13356.28 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 13:00 | Hasnabad | 115 | 14:00 | Palashbari | 124 | 21:00
Agargaon | 94 | 13:00 | Hathazari | 98 | 21:00 | Panchagarh | 50 | 22:00
Agrabad | 84 | 15:00 | Ishurdi | 92 | 19:30 | Patuakhali | 132 | 00:00
AKS | 18 | 05:00 | Jaldhaka | 64 | 20:00 | PHP | 4 | 17:00
AKSML | 108 | 08:00 | Jamalpur | 150 | 21:00 | Purbachal | 19 | 20:00
Amnura | 36 | 00:00 | Jashore | 123 | 22:00 | Purbasadipur | 120 | 21:00
Ashuganj | 34 | 00:00 | Jhenaidah | 124 | 19:30 | Rahim | 25 | 10:00
Bagerhat | 107 | 00:00 | Joydebpur | 199 | 16:00 | Rajbari | 70 | 19:30
Bakulia | 120 | 19:30 | Joypurhat | 61 | 21:00 | Rajendrapur | 110 | 22:00
Banani | 49 | 18:30 | Juldah | 29 | 00:00 | Rajshahi | 146 | 21:00
Bangabhaban | 22 | 11:00 | Kabirpur | 293 | 12:00 | Rajshahi | 32 | 00:00
Barapukuria | 51 | 19:30 | Kachua | 78 | 19:00 | Ramganj | 114 | 22:00
Barguna | 20 | 00:00 | Kallyanpur | 105 | 19:00 | Rampur | 20 | 18:00
Barishal | 124 | 19:30 | Kalurghat | 6 | 15:00 | Rangamati | 14 | 19:30
Barishal | 55 | 22:00 | Kamrangirchar | 72 | 19:00 | Rangpur | 144 | 20:00
Baroaulia | 72 | 00:00 | Kaptai | 4 | 18:30 | Ruppur | 4.6 | 10:00
Baroirhat | 52 | 19:00 | Kazla | 88 | 19:00 | Saidpur | 97 | 20:00
Bashundhara | 172 | 15:00 | Keranigonj | 78 | 19:00 | Satkhira | 119 | 21:00
BashundharaCement | 13 | 19:00 | Khagrachori | 28 | 19:00 | Satmasjid | 95 | 20:00
Beanibazar | 55 | 19:00 | Khulna | 99 | 07:00 | Savar | 191 | 15:00
Benapole | 66 | 21:00 | Khulshi | 187 | 16:00 | Shahjadpur | 99 | 19:30
Bhaluka | 138 | 16:00 | Kishoreganj | 136 | 23:00 | Shahjibazar | 111 | 23:00
Bhandaria | 60 | 00:00 | Kodda | 334 | 12:00 | Shahmirpur | 48 | 20:00
Bhangura | 37 | 21:00 | KSRM | 20.5 | 23:00 | Shariatpur | 74 | 00:00
Bheramara(GK) | 55 | 22:00 | Kulaura | 42 | 19:30 | Sherpur | 134 | 22:00
Bhulta | 227 | 22:00 | Kurigram | 66 | 20:00 | Shikalbaha | 25 | 00:00
Bog-Sherpur | 58 | 19:30 | Kushtia | 120 | 21:00 | Shitalakhya | 117 | 16:00
Bogura | 153 | 22:00 | Lalbag | 93 | 12:00 | Sholosohor | N/A | N/A
Borhanuddin | 44 | 00:00 | Lalmonirhat | 47 | 20:00 | Shyampur | 172 | 12:00
Brahmanbaria | 164 | 00:00 | Madanganj | 192 | 23:00 | Siddhirganj | 118 | 12:00
BSRM | 165 | 02:00 | Madaripur | 113 | 23:00 | Sirajganj | 110 | 21:00
Cantonment | 150 | 19:00 | Madartek | 85 | 23:00 | Sonargaon | 91 | 22:00
Chandpur | 89 | 21:00 | Madunaghat | 57 | 15:00 | Sreemongol | 51 | 19:30
Chandraghona | 34 | 19:00 | Magura | 62 | 19:30 | Srinagar | 46.92 | 22:00
Chapai | 70 | 20:00 | Mahasthangarh | 68 | 19:30 | SSM | 18 | 01:00
Charsaidpur | 39 | 06:00 | Manikganj | 86 | 21:00 | Sunamganj | 46 | 21:00
Chauddagram | 54 | 00:00 | Maniknagar | 79 | 16:00 | Sylhet | 135 | 19:30
Chhatak | 26 | 20:00 | Matarbari | 41 | 21:00 | Tangail | 212 | 22:00
Chowmuhani | 216 | 20:00 | Matuail | 66 | 10:00 | Thakurgaon | 89 | 21:00
Chuadanga | 116 | 19:30 | Millgate | 64 | 10:00 | TK | 29 | 22:00
Coxsbazar | 120 | 21:00 | Mirpur | 129 | 19:00 | Tongi | 136 | 16:00
Cumilla(N) | 177 | 22:00 | Mirsorai | N/A | N/A | Ullon | 133 | 11:00
Cumilla(S) | 161 | 19:00 | Mithapukur | 32 | 20:00 | Uttara | 93 | 19:00
Daudkandi | 162 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 20 | 00:00
Dhaka | 40 | 12:00 | Mogbazar | 130 | 17:00 | Zigatola | 44 | 15:00
Dhamrai | 116 | 19:30 | Mongla | 36 | 00:00
Dhanmondi | 157 | 13:00 | Motijheel | 38 | 16:00
Dohazari | 100 | 19:30 | Munshiganj | 106 | 00:00
Faridpur | 153 | 21:00 | Mymensingh | 209 | 20:00
Fatullah | 68 | 15:00 | Naogaon | 120 | 20:00
Fenchuganj | 45 | 20:00 | Narail | 57 | 20:00
Feni | 140 | 19:00 | Narinda | 72 | 12:00
Ghorashal | 59 | 19:00 | Narshingdi | 181 | 21:00
Goalpara | 28 | 13:00 | Natore | 133 | 21:00
Gollamari | 60 | 23:00 | Nawabganj | 57.6 | 22:00
Gopalganj | 109 | 20:00 | Netrakona | 118 | 21:00
GPH | 91 | 04:00 | New | 79.2 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 5:00 | 400 | 15:00 | Kaliakoir | 394 | 0.75 | 378 | 0.625
| Bheramara | 400 | 7:00 | 393 | 17:00 | Bhulta | 396 | 0.20833 | 372 | 0.45833
| Ashuganj(N) | 393 | 3:00 | 379 | 15:00 | Gopalganj | 417 | 0.625 | 403 | 0.041667
| Payra | 420 | 6:00 | 412 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 230 | 5:00 | 223 | 14:00
| Ishurdi | 234 | 6:00 | 227 | 19:30 | Megnaghat | 228 | 6:00 | 221 | 15:00
| Ashuganj | 235 | 1:00 | 227 | 9:00 | Fenchuganj | 241 | 2:00 | 238 | 23:00
| Serajganj | 234 | 2:00 | 229 | 19:30 | Siddhirganj | 228 | 1:00 | 220 | 9:00
| Baghabari | 232 | 7:00 | 227 | 11:00 | Maniknagar | 224 | 1:00 | 215 | 15:00
| Barapukuria | 229 | 13:00 | 216 | 19:30 | Agargaon | 226 | 18:00 | 214 | 9:00
| Bogra | 232 | 6:00 | 221 | 19:30 | Barisal | 240 | 18:00 | 232 | 24:00
| Rajshahi | 239 | 18:00 | 228 | 11:00 | Bhola 225 MW | 245 | 18:00 | 232 | 24:00
| Khulna South | 236 | 7:00 | 222 | 15:00 | AKSML | 237 | 7:00 | 224 | 15:00
| Rampura | 224 | 1:00 | 215 | 17:00 | BSRM | 234 | 7:00 | 221 | 16:00
| Haripur | 225 | 4:00 | 216 | 17:00 | Bibiyana | 239 | 3:00 | 233 | 12:00
| Hasnabad | 224 | 1:00 | 214 | 9:00 | Bhulta | 228 | 5:00 | 217 | 11:00
| Shyampur | 225 | 1:00 | 215 | 9:00 | Ashuganj (S) | 232 | 3:00 | 224 | 9:00
| Aminbazar | 226 | 1:00 | 217 | 2:00 | Kaliakoir | 227 | 2:00 | 217 | 15:00
| Tongi | 226 | 1:00 | 213 | 9:00 | GPH | 236 | 7:00 | 223 | 16:00
| Comilla (N) | 229 | 22:00 | 222 | 9:00 | Jhenaidah | 232 | 7:00 | 219 | 19:30
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 02:00 | 124 | 15:00 | Manikganj | 133 | 05:00 | 120 | 08:00
| Agargaon | 131 | 03:00 | 123 | 09:00 | Maniknagar | 133 | 04:00 | 124 | 15:00
| Agrabad | 138 | 06:00 | 129 | 16:00 | Matarbari | 140 | 07:00 | 116 | 19:00
| AKS | 136 | 06:00 | 126 | 14:00 | Matuail | 131.6 | 04:00 | 126 | 09:00
| Aminbazar | 132 | 00:00 | 132 | 00:00 | Millgate | 134 | 15:00 | 123 | 08:00
| Amnura | 132 | 18:30 | 124 | 03:00 | Mirpur | 133 | 04:00 | 124 | 09:00
| Ashuganj | 137 | 10:00 | 132 | 15:00 | Mithapukur | 133 | 02:00 | 121 | 19:30
| Bagerhat | 135 | 05:00 | 128 | 19:00 | Modern | 138 | 21:00 | 128 | 15:00
| Bakulia | 138 | 06:00 | 130 | 15:00 | Mogbazar | 134 | 03:00 | 125 | 11:00
| Banani | 134 | 03:00 | 124 | 09:00 | Mongla | 137 | 07:00 | 128 | 23:00
| Bangabhaban | 133 | 02:00 | 124 | 17:00 | Motijheel | 133 | 03:00 | 124 | 17:00
| Barapukuria | 135 | 13:00 | 124 | 19:30 | Munshiganj | 136 | 22:00 | 128 | 09:00
| Barguna | 137 | 18:00 | 128 | 19:00 | Mymensingh | 132 | 03:00 | 121 | 19:00
| Barishal | 139 | 08:00 | 127 | 19:00 | Naogaon | 132 | 10:00 | 115 | 01:00
| Barishal | 139 | 08:00 | 133 | 00:00 | Narail | 134 | 06:00 | 125 | 15:00
| Baroaulia | 138 | 06:00 | 130 | 22:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 18:00 | 126 | 14:00 | Narshingdi | 127 | 03:00 | 122 | 09:00
| Bashundhara | 134 | 02:00 | 124 | 09:00 | Natore | 133 | 07:00 | 127 | 19:30
| BashundharaCement | 135 | 00:00 | 127 | 09:00 | Nawabganj | 134 | 00:00 | 126 | 17:00
| Beanibazar | 133 | 03:00 | 128 | 19:00 | Netrakona | 135 | 02:00 | 120 | 09:00
| Benapole | 135 | 05:00 | 126 | 12:00 | New | 134 | 02:00 | 124 | 15:00
| Bhaluka | 131 | 02:00 | 118 | 19:30 | Niamatpur | 131 | 05:00 | 119 | 20:00
| Bhandaria | 139 | 09:00 | 126 | 00:00 | Noapara | 139 | 07:00 | 128 | 15:00
| Bhangura | 138 | 05:00 | 133 | 19:30 | Pabna | 135 | 06:00 | 130 | 19:30
| Bheramara | 136 | 05:00 | 132 | 15:00 | Palashbari | 133 | 05:00 | 120 | 19:30
| Bheramara(GK) | 140 | 06:00 | 133 | 15:00 | Panchagarh | 135 | 13:00 | 120 | 19:30
| Bhulta | 126 | 00:00 | 122 | 07:00 | Patuakhali | 136 | 05:00 | 130 | 23:00
| Bog-Sherpur | 135 | 06:00 | 128 | 19:30 | PHP | 134 | 18:30 | 124 | 15:00
| Bogura | 136 | 04:00 | 128 | 20:00 | Purbachal | 134 | 02:00 | 123 | 09:00
| Bogura | 136 | 05:00 | 129 | 19:30 | Purbasadipur | 136 | 13:00 | 120 | 19:30
| Brahmanbaria | 133 | 07:00 | 125 | 23:00 | Rahim | 133 | 22:00 | 128 | 10:00
| Cantonment | 130 | 03:00 | 121 | 17:00 | Rajbari | 135 | 07:00 | 128 | 19:30
| Chandpur | 140 | 18:30 | 125 | 09:00 | Rajendrapur | 134 | 03:00 | 120 | 09:00
| Chandraghona | 141 | 07:00 | 129 | 15:00 | Rajshahi | 131 | 18:00 | 125 | 03:00
| Chapai | 131 | 18:00 | 122 | 11:00 | Rajshahi | 130 | 18:00 | 124 | 11:00
| Charsaidpur | 137 | 01:00 | 128 | 09:00 | Ramganj | 135 | 18:00 | 126 | 05:00
| Chauddagram | 133 | 18:00 | 125 | 15:00 | Rampur | 137 | 06:00 | 127 | 15:00
| Chhatak | 133 | 06:00 | 128 | 00:00 | Rampura | 132 | 07:00 | 124 | 15:00
| Chowmuhani | 133 | 17:00 | 124 | 02:00 | Rangamati | 139 | 07:00 | 129 | 15:00
| Chuadanga | 130 | 06:00 | 119 | 19:00 | Rangpur | 133 | 12:00 | 117 | 19:30
| Coxsbazar | 130 | 06:00 | 115 | 02:00 | Ruppur | 137 | 18:00 | 132 | 15:00
| Cumilla(N) | 134 | 20:00 | 130 | 09:00 | Saidpur | 134 | 13:00 | 119 | 19:30
| Cumilla(S) | 135 | 18:00 | 122 | 14:00 | Satkhira | 137 | 05:00 | 127 | 15:00
| Daudkandi | 134 | 21:00 | 127 | 09:00 | Satmasjid | 131 | 03:00 | 123 | 09:00
| Dhaka | 133 | 02:00 | 124 | 15:00 | Savar | 132 | 00:00 | 125 | 08:00
| Dhamrai | 132 | 03:00 | 123 | 09:00 | Shahjadpur | 140 | 04:00 | 135 | 19:30
| Dhanmondi | 133 | 01:00 | 125 | 11:00 | Shahjibazar | 135 | 07:00 | 130 | 00:00
| Dohazari | 140 | 07:00 | 126 | 14:00 | Shahmirpur | 137 | 08:00 | 130 | 16:00
| Faridpur | 135 | 06:00 | 129 | 00:00 | Shariatpur | 137 | 18:00 | 130 | 16:00
| Fatullah | 134 | 22:00 | 126 | 09:00 | Sherpur | 136 | 02:00 | 117 | 09:00
| Fenchuganj | 136 | 06:00 | 133 | 01:00 | Shikalbaha | 140 | 06:00 | 132 | 16:00
| Feni | 135 | 18:00 | 127 | 14:00 | Shikalbaha | 140 | 07:00 | 132 | 14:00
| Ghorashal | 137 | 00:00 | 135 | 08:00 | Shitalakhya | 136 | 01:00 | 128 | 09:00
| Goalpara | 140 | 07:00 | 131 | 15:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 139 | 05:00 | 131 | 15:00 | Shyampur | 133 | 00:00 | 127 | 09:00
| Gopalganj | 138 | 05:00 | 133 | 19:00 | Shyampur | 134 | 00:00 | 127 | 10:00
| Gopalganj_I | 138 | 07:00 | 133 | 00:00 | Siddhirganj | 133 | 01:00 | 127 | 09:00
| Gulshan | 133 | 05:00 | 123 | 17:00 | Sirajganj | 135 | 06:00 | 128 | 19:30
| Halishahar | 139 | 06:00 | 129 | 15:00 | Sonargaon | 134 | 00:00 | 129 | 09:00
| Haripur | 133 | 22:00 | 128 | 10:00 | Sreemongol | 136 | 06:00 | 132 | 00:00
| HaripurSBU | 133 | 00:00 | 127 | 09:00 | Srinagar | 135 | 04:00 | 127 | 09:00
| Hasnabad | 135 | 00:00 | 129 | 09:00 | SSM | 140 | 22:00 | 131 | 14:00
| Hathazari | 138 | 19:30 | 132 | 08:00 | Sunamganj | 133 | 06:00 | 126 | 19:00
| Ishurdi | 137 | 07:00 | 132 | 11:00 | Sylhet | 133 | 06:00 | 131 | 00:00
| Jaldhaka | 155 | 19:30 | 115 | 19:30 | Tangail | 134 | 02:00 | 126 | 09:00
| Jamalpur | 140 | 01:00 | 118 | 09:00 | Thakurgaon | 137 | 13:00 | 120 | 19:30
| Jashore | 136 | 04:00 | 125 | 13:00 | TK | 137 | 19:30 | 132 | 16:00
| Jhenaidah | 137 | 05:00 | 128 | 15:00 | Tongi | 134 | 01:00 | 127 | 09:00
| Jhenaidah | 137 | 06:00 | 129 | 12:00 | Ullon | 133 | 04:00 | 124 | 15:00
| Joydebpur | 139 | 19:00 | 130 | 08:00 | Uttara | 133 | 03:00 | 123 | 09:00
| Joypurhat | 131 | 10:00 | 120 | 19:30 | UttaraNew | 133 | 03:00 | 124 | 14:00
| Juldah | 137 | 07:00 | 130 | 15:00 | Zigatola | 135 | 00:00 | 128 | 10:00
| Kabirpur | 138 | 00:00 | 122 | 09:00
| Kachua | 136 | 18:30 | 129 | 06:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 133 | 02:00 | 125 | 15:00
| Kalurghat | 138 | 07:00 | 130 | 15:00
| Kamrangirchar | 135 | 00:00 | 127 | 17:00
| Kaptai | 140 | 07:00 | 130 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 358 | 8750 | 4640 | 13390 |  |  |  | QF-LDC-11
0:30 | 546 | 8486 | 4575.5 | 13061.5 | Date: | 2022-05-23
1:00 | 734 | 8222 | 4511 | 12733
1:30 | 711.5 | 7977 | 4429.5 | 12406.5
2:00 | 689 | 7732 | 4348 | 12080
2:30 | 572.5 | 7516.5 | 4180.5 | 11697 | [5 empty] | Gen. at Eve. Peak | 13810 | 13810 MW (21:00 )
3:00 | 456 | 7301 | 4013 | 11314 | [6 empty] | 21:00
3:30 | 491 | 7084.5 | 3969.5 | 11054 | [5 empty] | Gen. at Day Peak | 11466 | 11466 MW (12:00 )
4:00 | 526 | 6868 | 3926 | 10794 | [6 empty] | 12:00
4:30 | 534 | 6759 | 3908.5 | 10667.5 | [5 empty] | Highest Generation | 13810
5:00 | 542 | 6650 | 3891 | 10541 | [6 empty] | 21:00
5:30 | 541 | 6401 | 3717.5 | 10118.5
6:00 | 540 | 6152 | 3544 | 9696
6:30 | 547 | 6036.5 | 3545 | 9581.5
7:00 | 554 | 5921 | 3546 | 9467
7:30 | 649 | 5848.5 | 3501 | 9349.5
8:00 | 744 | 5776 | 3456 | 9232
8:30 | 788 | 5987.5 | 3515 | 9502.5
9:00 | 832 | 6199 | 3574 | 9773
9:30 | 799 | 6523 | 3615 | 10138
10:00 | 766 | 6847 | 3656 | 10503
10:30 | 818 | 6989 | 3721 | 10710
11:00 | 870 | 7131 | 3786 | 10917
11:30 | 812 | 7340.5 | 3851 | 11191.5
12:00 | 754 | 7550 | 3916 | 11466
12:30 | 736 | 7619 | 3975.5 | 11594.5
13:00 | 718 | 7688 | 4035 | 11723
13:30 | 739 | 7661.5 | 4068.5 | 11730
14:00 | 760 | 7635 | 4102 | 11737
14:30 | 766 | 7742 | 4129 | 11871
15:00 | 772 | 7849 | 4156 | 12005
15:30 | 762 | 7979 | 4151 | 12130
16:00 | 752 | 8109 | 4146 | 12255
16:30 | 735 | 7986 | 4049.5 | 12035.5
17:00 | 718 | 7863 | 3953 | 11816
17:30 | 643 | 7782.5 | 3794 | 11576.5
18:00 | 568 | 7702 | 3635 | 11337
18:30 | 482 | 8207 | 3883 | 12090
19:00 | 396 | 8712 | 4131 | 12843
19:30 | 322 | 8978 | 4734 | 13712
20:00 | 324 | 8969 | 4796 | 13765 |  |  |  | Executive Engineer
20:30 | 322 | 8975 | 4812.5 | 13787.5 |  |  |  | Network Operation Division
21:00 | 320 | 8981 | 4829 | 13810
21:30 | 311 | 8973.5 | 4791.5 | 13765
22:00 | 302 | 8966 | 4754 | 13720 |  |  |  |  | Page 6 of 7
22:30 | 317 | 8977.5 | 4706.5 | 13684
23:00 | 332 | 8989 | 4659 | 13648
23:30 | 345 | 8869.5 | 4649.5 | 13519
24:00 | 358 | 8750 | 4640 | 13390
13810 MW (21:00 )
11466 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-23 |  | Energy |  | 285635654
[13 empty] | 2022-05-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3780 | 900 | 2043 | 706 | 4059 | 1155 | 35 | 0 | 580 | 132 | 0 | 0
0:30 | 3745.5 | 911 | 2006.5 | 464 | 4026 | 1180 | 35 | 0 | 569.5 | 124 | 0 | 0 | Date: | 2022-05-23
1:00 | 3711 | 922 | 1970 | 222 | 3993 | 1205 | 35 | 0 | 559 | 116 | 0 | 0
1:30 | 3715 | 922 | 1966 | 111 | 3904.5 | 1205 | 35 | 0 | 432 | 116 | 0 | 0 | [8 empty] | Total Energy | 285.6357 | Total Energy Gen 285.636 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 285.636 MKWHr
2:00 | 3719 | 922 | 1962 | 0 | 3816 | 1205 | 35 | 0 | 305 | 116 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3731 | 921.5 | 1943.5 | 0 | 3602.5 | 1180 | 35 | 0 | 168.5 | 115 | 0 | 0 | [8 empty] | Energy Requirement | 285.6357
3:00 | 3743 | 921 | 1925 | 0 | 3389 | 1155 | 35 | 0 | 32 | 114 | 0 | 0
3:30 | 3752 | 921.5 | 1931 | 0 | 3140.5 | 1135 | 35 | 0 | 32 | 107 | 0 | 0 | [6 empty] | Shortage
4:00 | 3761 | 922 | 1937 | 0 | 2892 | 1115 | 35 | 0 | 32 | 100 | 0 | 0
4:30 | 3766 | 921.5 | 1932.5 | 0 | 2768.5 | 1110 | 35 | 0 | 32 | 102 | 0 | 0
5:00 | 3771 | 921 | 1928 | 0 | 2645 | 1105 | 35 | 0 | 32 | 104 | 0 | 0
5:30 | 3686 | 921.5 | 1890.5 | 0 | 2416.5 | 1040.5 | 35 | 0 | 24 | 99 | 5.5 | 0
6:00 | 3601 | 922 | 1853 | 0 | 2188 | 976 | 35 | 0 | 16 | 94 | 11 | 0
6:30 | 3625 | 925.5 | 1889.5 | 0 | 2008 | 975.5 | 35 | 0 | 8 | 93 | 22 | 0 |  |  |  |  | Coal
7:00 | 3649 | 929 | 1926 | 0 | 1828 | 975 | 35 | 0 | 0 | 92 | 33 | 0
7:30 | 3645.5 | 920 | 1883 | 0 | 1773.5 | 965 | 17.5 | 0 | 0 | 95 | 50 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3642 | 911 | 1840 | 0 | 1719 | 955 | 0 | 0 | 0 | 98 | 67 | 0
8:30 | 3733 | 911 | 1853.5 | 0 | 1828 | 950 | 0 | 0 | 32.5 | 100 | 94.5 | 0
9:00 | 3824 | 911 | 1867 | 0 | 1937 | 945 | 0 | 0 | 65 | 102 | 122 | 0
9:30 | 3808.5 | 910.5 | 1879 | 0 | 2260.5 | 945 | 15 | 0 | 82 | 105 | 132.5 | 0
10:00 | 3793 | 910 | 1891 | 0 | 2584 | 945 | 30 | 0 | 99 | 108 | 143 | 0
10:30 | 3746 | 910 | 1845 | 0 | 2854 | 945 | 30 | 0 | 111 | 110 | 159 | 0
11:00 | 3699 | 910 | 1799 | 0 | 3124 | 945 | 30 | 0 | 123 | 112 | 175 | 0
11:30 | 3697 | 910.5 | 1790.5 | 125 | 3233.5 | 955 | 30 | 0 | 159.5 | 112.5 | 178 | 0
12:00 | 3695 | 911 | 1782 | 250 | 3343 | 965 | 30 | 0 | 196 | 113 | 181 | 0
12:30 | 3695 | 910.5 | 1818.5 | 219 | 3427.5 | 975 | 45 | 0 | 213.5 | 115 | 175.5 | 0
13:00 | 3695 | 910 | 1855 | 188 | 3512 | 985 | 60 | 0 | 231 | 117 | 170 | 0
13:30 | 3695 | 910 | 1855 | 188 | 3512 | 985 | 60 | 0 | 231 | 117 | 170 | 0
14:00 | 3695 | 910 | 1855 | 188 | 3512 | 985 | 60 | 0 | 231 | 117 | 170 | 0
14:30 | 3653 | 906.5 | 1873.5 | 277.5 | 3548.5 | 1015 | 50 | 0 | 258 | 122.5 | 159.5 | 0
15:00 | 3611 | 903 | 1892 | 367 | 3585 | 1045 | 40 | 0 | 285 | 128 | 149 | 0
15:30 | 3672.5 | 903.5 | 1889.5 | 401 | 3625.5 | 1055 | 41 | 0 | 298 | 124 | 120 | 0
16:00 | 3734 | 904 | 1887 | 435 | 3666 | 1065 | 42 | 0 | 311 | 120 | 91 | 0
16:30 | 3728 | 904.5 | 1889 | 217.5 | 3714 | 1045 | 42 | 0 | 304.5 | 122 | 66 | 0
17:00 | 3728 | 905 | 1891 | 0 | 3762 | 1025 | 42 | 0 | 298 | 124 | 41 | 0
17:30 | 3681.5 | 904.5 | 1810.5 | 0 | 3660 | 1000 | 42 | 0 | 334 | 120 | 24 | 0
18:00 | 3635 | 904 | 1730 | 0 | 3558 | 975 | 42 | 0 | 370 | 116 | 7 | 0
18:30 | 3665 | 904.5 | 1874.5 | 285.5 | 3718.5 | 985 | 57 | 0 | 470.5 | 126 | 3.5 | 0
19:00 | 3695 | 905 | 2019 | 571 | 3879 | 995 | 72 | 0 | 571 | 136 | 0 | 0
19:30 | 3736 | 904 | 2038 | 850 | 4217 | 1175 | 72 | 0 | 588 | 132 | 0 | 0
20:00 | 3753 | 904 | 2034 | 863 | 4223 | 1185 | 70 | 0 | 599 | 134 | 0 | 0
20:30 | 3759 | 904 | 2032 | 901 | 4213.5 | 1190 | 70 | 0 | 586 | 132 | 0 | 0
21:00 | 3765 | 904 | 2030 | 939 | 4204 | 1195 | 70 | 0 | 573 | 130 | 0 | 0
21:30 | 3754 | 904 | 2026.5 | 938 | 4190 | 1180 | 67.5 | 0 | 573 | 132 | 0 | 0
22:00 | 3743 | 904 | 2023 | 937 | 4176 | 1165 | 65 | 0 | 573 | 134 | 0 | 0
22:30 | 3752.5 | 902 | 2026.5 | 875.5 | 4187.5 | 1170 | 65 | 0 | 577 | 128 | 0 | 0
23:00 | 3762 | 900 | 2030 | 814 | 4199 | 1175 | 65 | 0 | 581 | 122 | 0 | 0
23:30 | 3771 | 900 | 2036.5 | 760 | 4129 | 1165 | 50 | 0 | 580.5 | 127 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.2° C
24:00 | 3780 | 900 | 2043 | 706 | 4059 | 1155 | 35 | 0 | 580 | 132 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 285.636 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 285.636 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 |  |  |  |  | 30 | 40 | 40 | 42 | 42 | 42 |  | 42 | 42 | 40 | 40 | 35 | 35 | 35 | 711720
2 | Karnaphuli Hydro PP Unit-4 & 5 | [8 empty] | 0 | 30 | 30 | 30 | 30 | 0 |  |  |  | 0 |  | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 284000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 0 | [6 empty] | 1 | 9 | 24 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 400181
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 2 | 4 | 5 | 8 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | [8 empty] | 73035
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 202 | 203 | 216 | 229 | 202 | 212 | 203 | 202 | 202 | 206 | 203 | 203 | 202 |  | 220 | 205 | 203 | 203 | 203 | 203 | 203 | 4927223
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 0 | [6 empty] | 17 | 17 | 17 | 0 |  |  |  | 17 | 17 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 431487
12 | Hathazari 100 MW peaking PP | 30 | 0 | [13 empty] | 2 | 8 | 8 |  | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 343200
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 87 | 105 | 105 | 98 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 105 | 101 | 105 | 105 | 105 | 105 | 2320072
| Daudkandi 200 MW PP (B.Trac) | 50 | 0 | [12 empty] | 0 | 40 | 0 |  |  | 120 | 150 | 150 | 200 | 200 | 170 | 170 | 1034496
14 | Titas 50 MW Peaking PP | 40 | 40 | 0 | [7 empty] | 6 | 24 | 24 | 18 | 24 | 24 | 30 | 30 |  | 36 | 41 | 41 | 41 | 41 | 41 | 41 | 493816
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 330 | 330 | 333 | 332 | 333 | 280 | 332 | 327 | 329 | 335 | 328 | 329 | 326 | 280 | 0 | [11 empty] | 4701411
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 275 | 278 | 130 | 15 | 15 | 15 | 15 | 16 | 86 | 232 | 255 | 273 | 276 | 274 | 276 | 276 | 275 |  | 275 | 275 | 275 | 276 | 290 | 294 | 290 | 5168725
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4410000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 240 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6437064
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 30 | 29 | 27 | 30 | 30 | 31 |  | 34 | 33 | 33 | 33 | 34 | 34 | 34 | 758808
33 | Ashuganj 225 MW CCPP | 184 | 182 | 182 | 182 | 182 | 182 | 180 | 190 | 176 | 159 | 151 | 148 | 148 | 167 | 166 | 162 | 166 | 163 |  | 177 | 185 | 194 | 191 | 193 | 199 | 190 | 4301000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 340 | 350 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7344400
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 230400
36 | Chandpur 150 MW CCPP | 100 | 99 | 100 | 103 | 100 | 102 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 99 | 99 | 100 | 98 | 100 |  | 97 | 97 | 100 | 100 | 100 | 101 | 100 | 2361580
37 | Tongi 80 MW GTPP | [8 empty] | 0
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [10 empty] | 4 | 23 | 37 | 106 | 269 | 365 | 367 | 345 |  | 332 | 354 | 357 | 356 | 351 | 359 | 369 | 5087230
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5104500
41 | Haripur 360MW CCPP(HPL) | 320 | 324 | 310 | 300 | 310 | 300 | 300 | 300 | 303 | 303 | 232 | 204 | 314 | 338 | 322 | 324 | 324 | 277 |  | 332 | 329 | 328 | 320 | 320 | 326 | 334 | 7286000
42 | RPCL 210MW CCPP | 146 | 158 | 162 | 160 | 160 | 160 | 160 | 159 | 151 | 146 | 132 | 130 | 118 | 110 | 110 | 124 | 124 | 126 |  | 127 | 127 | 127 | 130 | 128 | 128 | 129 | 3222720
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 4 | 9 | 13 | 37 | 37 | 54 | 54 | 52 | 47 | 39 | 23 | 13 | 2 | [8 empty] | 365560
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1035000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 946816
46 | Shajibazar 330 MW CCPP | 110 | 108 | 110 | 110 | 110 | 111 | 111 | 110 | 110 | 110 | 112 | 110 | 108 | 107 | 109 | 108 | 109 | 110 |  | 90 | 90 | 91 | 90 | 90 | 91 | 90 | 2422000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 60 | 60 | 55 | 55 | 50 | 50 | 50 | 50 | 60 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1293984
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 527040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 185 | 185 | 160 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5058580
51 | Sylhet 20 MW GTPP | [9 empty] | 0
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250740
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 | 8 | 8 | 8 | 16 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 310656
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 285 | 270 | 280 | 285 | 275 | 300 | 295 | 315 | 315 | 280 | 300 | 275 | 280 | 300 | 280 | 270 | 260 |  | 290 | 315 | 310 | 295 | 280 | 270 | 290 | 7141000
| Bibiyana South 400 MW | 396 | 396 | 400 | 400 | 400 | 360 | 360 | 330 | 390 | 400 | 393 | 399 | 400 | 400 | 394 | 397 | 391 | 360 |  | 388 | 393 | 395 | 400 | 400 | 394 | 400 | 9328700
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 0 |  | 19 | 22 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 827795
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 19 | 19 | 19 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 569760
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531120
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 397728
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 0 |  | 0 | 384588
63 | Impoprt (Tripura) | 116 | 116 | 114 | 100 | 104 | 94 | 92 | 98 | 102 | 108 | 112 | 113 | 117 | 123 | 128 | 120 | 124 | 116 |  | 136 | 132 | 134 | 130 | 134 | 122 | 132 | 2772480
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 23 | 32 | 32 | 33 | 23 | 8 | 2 | 2 | 5 | 4 | 4 | 2 | 2 | 2 | 3 | 7 |  | 10 | 16 | 18 | 23 | 29 | 29 | 27 | 366240
65 | Feni 22MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 388656
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 117720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  |  | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 669800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467640
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 20 | 8 | 27 | 28 | 28 | 20 | 20 | 26 | 7 | 7 | 6 | 25 |  | 18 | 24 | 24 | 27 | 27 | 27 | 28 | 534420
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 616500
72 | Rupganj 33 MW PP(Summit) | 17 | 17 | 17 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 662800
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 100 | 101 | 102 | 102 | 101 | 96 | 98 | 98 | 98 | 103 | 100 | 100 | 101 | 101 |  | 104 | 104 | 104 | 105 | 105 | 105 | 105 | 2379454
| Feni Lanka Power | 98 | 44 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 70 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 1144560
| Chowmuhani 113 MW | 51 | 31 | 29 | 28 | 28 | 28 | 29 | 28 | 29 | 28 | 29 | 29 | 28 | 29 | 36 | 68 | 112 | 114 |  | 114 | 114 | 114 | 114 | 114 | 113 | 70 | 1405320
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 130 | 72 | 72 | 94 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 134 | 126 | 142 | 144 | 3283200
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 59 | 0 |  |  |  |  | 0 | 26 | 60 | 82 | 91 | 90 | 90 | 90 | 90 | 90 |  | 87 | 90 | 82 | 90 | 90 | 91 | 91 | 1502746
78 | Gazipur 52 MW PP | 49 | 49 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 42 | 42 | 41 | 41 | 45 | 48 | 48 | 48 | 48 |  | 48 | 48 | 49 | 50 | 50 | 50 | 50 | 936480
79 | Kodda 150MW PP | 132 | 132 | 32 | 32 | 32 | 16 | 0 |  | 48 | 82 | 90 | 132 | 132 | 132 | 132 | 132 | 98 | 98 |  | 132 | 132 | 132 | 115 | 125 | 132 | 132 | 2233440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 38 | 8 | 8 | 14 | 28 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 699931
| Gazipur 100 MW PP | 105 | 105 | 105 | 52 | 52 | 17 | 17 | 17 | 80 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2209200
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 1 | 0 | 1 | 2 | 2 | 2 | 2 | 4 | 3 | 2 | 1 | 1 | [9 empty] | 19201
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 911331
| Karnaphuli Power Ltd. | 97 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 88 | 89 | 97 | 110 | 110 | 110 | 99 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 93 | 93 | 2298317
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 73 | 40 | 15 | 18 | 62 | 80 | 87 | 87 | 79 | 79 | 90 | 93 | 93 |  | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 1945272
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 145 | 145 | 140 | 145 | 140 | 150 | 150 | 150 | 148 | 140 | 150 | 142 | 135 | 138 | 135 | 130 | 140 | 132 |  | 150 | 140 | 130 | 135 | 140 | 150 | 135 | 3527447
87 | Meghnaghat 100 MW(IEL) | 72 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 68 | 64 | 63 | 68 | 72 | 76 | 78 | 77 | 72 |  | 80 | 80 | 81 | 81 | 80 | 81 | 80 | 1788480
| Meghnaghat 104 MW PP (OPCL) | 91 | 90 | 90 | 90 | 90 | 64 | 25 | 70 | 73 | 88 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2051520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | [14 empty] | 3 | 20 | 35 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 411743
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 32 | 7 | 0 |  |  | 16 | 64 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1699200
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 6 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 21 | 48 | 42 | 43 | 44 | 44 | 44 | 666240
96 | Chattogram 108 MW PP (ECPV) | 86 | 86 | 86 | 86 | 86 | 81 | 58 | 50 | 54 | 75 | 68 | 75 | 87 | 81 | 80 | 80 | 83 | 85 |  | 85 | 86 | 86 | 85 | 87 | 87 | 88 | 1920960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 40 | 55 | 55 | 55 | 55 | 55 | 45 | 40 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1265492
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1193773
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2670300
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1285560
104 | Keranigonj 300 MW PP (APR) | 52 | 0 | [9 empty] | 62 | 33 | 12 | 171 | 202 |  |  |  | 230 | 263 | 260 | 266 | 266 | 277 | 169 | 1792760
105 | Bramhangoan 100 MW PP (Aggreko) | 60 | 0 | [9 empty] | 90 | 95 | 25 | 97 | 96 |  |  |  | 97 | 99 | 99 | 99 | 99 | 99 | 99 | 1035688
106 | Mymensingh 200 MW PP (United) | 195 | 120 | 8 | 8 | 8 | 8 | 8 | 10 | 19 | 70 | 100 | 108 | 120 | 120 | 140 | 169 | 169 | 120 |  | 136 | 190 | 190 | 190 | 190 | 191 | 191 | 2772000
112 | Aurahati 100MW PP (Aggreko) | 60 | 0 | [9 empty] | 98 | 60 | 25 | 99 | 97 |  |  |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1001557
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 140 | 88 | 35 | 34 | 49 | 132 | 149 | 149 | 149 | 149 | 149 | 148 | 149 | 124 |  | 131 | 149 | 149 | 149 | 148 | 149 | 149 | 3169440
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 50 |  | 50 | 50 | 50 | 50 | 50 | 38 | 38 | 856320
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 155 | 68 | 17 | 17 | 17 | 35 | 95 | 104 | 103 | 103 | 103 | 103 | 103 | 145 | 170 |  | 184 | 200 | 200 | 200 | 200 | 200 | 200 | 3243840
117 | Ashuganj 150MW PP (Midland) | [14 empty] | 5 | 38 | 81 | 110 |  | 123 | 125 | 125 | 128 | 125 | 142 | 145 | 1027054
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 401 | 402 | 401 | 374 | 364 | 352 | 402 | 400 | 402 | 401 | 401 | 401 | 404 | 403 | 403 | 352 |  | 404 | 402 | 402 | 402 | 402 | 402 | 402 | 9490000
| Jamalpur 115 MW PP (United) | 108 | 75 | 55 | 55 | 55 | 55 | 55 | 60 | 0 | 56 | 78 | 88 | 89 | 98 | 88 | 88 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 108 | 1926000
| Anwara 300 MW PP (United) | 264 | 264 | 264 | 264 | 264 | 264 | 264 | 245 | 245 | 247 | 247 | 247 | 265 | 247 | 247 | 262 | 264 | 264 |  | 264 | 264 | 264 | 264 | 264 | 264 | 265 | 6217527
| Juldah unit-2 (Acorn) | 40 | 40 | 38 | 38 | 39 | 38 | 39 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 700800
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 94 | 106 | 108 | 108 | 108 | 108 | 108 | 108 | 90 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2578091
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 26 | 17 | 17 | 17 | 17 | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 791640
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 91 | 94 | 75 | 0 | [5 empty] | 1 | 58 | 75 | 83 | 83 | 83 | 83 | 78 | 55 |  | 68 | 83 | 81 | 82 | 82 | 83 | 83 | 1361280
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 51 | 55 | 17 | 19 | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1283760
120 | Eastern Zone Total | 8222 | 7732 | 7301 | 6868 | 6650 | 6152 | 5921 | 5776 | 6199 | 6847 | 7131 | 7550 | 7688 | 7635 | 7849 | 8109 | 7863 | 7702 |  | 8712 | 8978 | 8969 | 8981 | 8966 | 8989 | 8750 | 185208489
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 93 | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 90 | 76 |  | 83 | 115 | 115 | 115 | 115 | 115 | 96 | 2106240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 25 | 0 | [15 empty] | 30 |  | 45 | 33 | 33 | 33 | 33 | 33 | 33 | 242400
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 75 | 75 | 53 | 53 | 53 | 103 | 105 | 105 | 105 | 105 | 105 | 70 | 53 |  | 75 | 105 | 105 | 105 | 105 | 105 | 105 | 2353920
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 6 | 21 | 46 | 71 | 89 | 99 | 101 | 91 | 90 | 88 | 50 | 24 | 5 | [8 empty] | 785520
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 447600
133 | Bhola Nutan Biddut BD LTD (GAS) | 219 | 220 | 219 | 220 | 200 | 220 | 211 | 183 | 183 | 213 | 216 | 216 | 210 | 213 | 211 | 211 | 200 | 167 |  | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 5045782
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 850464
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 87 | 87 | 86 | 87 | 88 | 86 | 83 | 86 | 86 | 85 | 85 | 85 | 82 | 84 | 84 | 85 |  | 83 | 84 | 85 | 86 | 86 | 87 | 88 | 2085543
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 32 | 30 | 29 | 24 | 20 | 19 | 14 | 15 | 15 | 16 | 18 | 19 | 19 | 19 | 17 | 21 |  | 30 | 30 | 30 | 32 | 32 | 33 | 32 | 571461
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [9 empty] | 12 | 85 | 90 | 100 | 100 | 70 | 70 | 461760
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 16 | 40 | 40 | 40 | 8 | 0 | 8 | 110625
143 | Gopalganj 100 MW Peaking PP | 55 | 53 | 0 | [14 empty] | 2 |  | 31 | 52 | 58 | 58 | 49 | 49 | 49 | 397568
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 67 | 60 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 88 | 88 | 105 | 105 | 105 | 50 |  | 67 | 85 | 105 | 105 | 105 | 105 | 105 | 1746576
146 | Bheramara HVDC | 922 | 922 | 921 | 922 | 921 | 922 | 929 | 911 | 911 | 910 | 910 | 911 | 910 | 910 | 903 | 904 | 905 | 904 |  | 905 | 904 | 904 | 904 | 904 | 900 | 900 | 22021090
147 | Bheramara 410 MW CCPP | 220 | 220 | 220 | 225 | 230 | 240 | 245 | 240 | 240 | 235 | 235 | 235 | 235 | 230 | 225 | 230 | 225 | 225 |  | 240 | 240 | 240 | 245 | 245 | 250 | 260 | 5667264
148 | Payra 1320 MW | 1030 | 1030 | 980 | 940 | 930 | 800 | 800 | 780 | 770 | 770 | 770 | 790 | 810 | 820 | 870 | 890 | 850 | 800 |  | 820 | 1000 | 1010 | 1020 | 990 | 1000 | 980 | 23269100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 176 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4282800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 0 | [7 empty] | 10 | 34 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 618880
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 173 | 174 | 174 | 178 | 179 | 179 | 180 | 184 | 182 | 179 | 179 | 179 | 179 | 180 | 180 | 180 | 179 | 150 |  | 159 | 176 | 176 | 176 | 175 | 178 | 178 | 4516945
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 421 | 423 | 429 | 428 | 432 | 350 | 420 | 383 | 414 | 417 | 415 | 414 | 414 | 414 | 414 | 414 | 414 | 326 |  | 414 | 414 | 414 | 420 | 417 | 416 | 417 | 9793818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 0 | [9 empty] | 4 | 4 | 22 | 27 | 26 | 27 | 26 |  | 27 | 26 | 29 | 29 | 29 | 29 | 29 | 324919
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 20 | 20 | 19 | 19 | 18 | 19 | 19 | 20 |  | 20 | 21 | 21 | 21 | 21 | 22 | 22 | 47472
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 197388
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 0 | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 369168
167 | Katakhali 50 MW Peaking PP | 32 | 0 | [9 empty] | 2 | 16 | 16 | 16 | 24 | 32 | 40 |  | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 328305
168 | Santahar 50 MW Peaking PP | 37 | 37 | 0 | [14 empty] | 33 |  | 36 | 36 | 38 | 37 | 36 | 37 | 37 | 319569
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 10 | 43 | 43 | 43 | 52 | 43 | 43 | 25 | 34 |  | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 796800
170 | Chapainawabganj 100 MW Peaking PP | 83 | 0 | [10 empty] | 12 | 43 | 43 | 43 | 43 | 43 |  | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 810784
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 14 | 155 | 166 | 176 | 174 | 100 | 100 | 790468
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 75 | 90 | 106 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2591808
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2591904
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 102 | 102 | 102 | 102 | 97 | 54 | 56 | 78 | 103 | 102 | 102 | 101 | 101 | 101 | 97 | 92 | 80 | 70 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 2272771
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 7 | 7 | 5 | 4 | 2 | 0 | [8 empty] | 57389
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 17 | 0 | [5 empty] | 14 | 17 | 67 | 92 | 92 | 110 | 109 | 52 | 52 |  | 69 | 95 | 99 | 97 | 97 | 97 | 97 | 1518144
178