## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-25 | Wednesday
|  |  | Date (day): | 2022-05-25 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13889.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14762 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-24 | 2022-05-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 |  | 95 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 105 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 328 | 340 | 330
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 71 | 65 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 96 | 96 | 96 | 96
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 36 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 91 | 90 | 90 |  | 10 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 330 | 330 | 330 |  |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 52 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 48 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 290 | 293 | 290 | 293 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 255 | 302 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 94 | 96 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 98 | 98 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 135 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 73 | 104 | 90 | 104 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 144 | 162 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 33 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3410 | 3844 | 3853 | 3848 | 671 | 921
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 70 | 40 | 40 |  | 190 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 204 | 0 | 0 |  |  | S/D due to HGPI,24-05-22 |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 42 | 51 | 0 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 25 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 78 | 82 | 86 | 86 |  | 22 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 262 | 283 | 273 | 283 |  | 17 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 36 | 35 | 35 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 106 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 65 | 25 | 50 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 92 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1122 | 1327 | 1084 | 1203 | 501 | 445
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 179 | 194 | 194 | 71 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 270 | 340 | 340
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 35 | 30 | 30 |  | 15 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 130 | 138 | 140 | 140 |  | 150 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 32 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 103 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 134 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 100 | 200 | 150 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 110 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 105 | 28 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 64 | 83 | 83 | 83 |  | 32 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1363 | 1777 | 1733 | 1913 | 931 | 335
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 120 | 128 | 140 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 151 | 197 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 106 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 467 | 477 | 518.6 | 497 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 92 | 157 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 60 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 50 | 80 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 22 | 22 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 290 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 386 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1697 | 1807 | 1847 | 1890 | 271 | 228
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 899 | 906 | 913 | 913
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 108 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 70 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 285 | 320 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 85 | 94 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1561 | 1666 | 1833 | 2013 | 90 | 68
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 48 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 16 | 33 | 20 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 65 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 820 | 1020 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 213 | 226 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1098 | 1409 | 1443 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 25 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Running on HSD.
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 168 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 417 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 38 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 82 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 14 | 120 | 0 | 176 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 95 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 918 | 1240 | 1177 | 1356 | 421 | 138
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 9 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 80 | 81 | 103 | 103 |  | 10 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 95 | 111 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 357 | 376 | 401 | 393 | 99 | 180
|  | Total |  |  |  |  | 22348 | 21584 | 11993 | 13923 | 13889.6 | 14762 | 3154 | 2323
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11488.1191 | 13336.87 | 13304.8761 | 14140.5498
| A. |  | 2022-05-24 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13923 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10276 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13923 | MW
| 3 | Day peak Generation : |  |  | 11993 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13336.87 | MW
| 4 | Evening peak Generation : |  |  | 13923 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 294.79 | MKWHr | By Solar | 1.2481 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 131.3555 | MKWHr |  | By Oil: | 109.4652 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 27.0398 | MKWHr |  | By Hydro: | 1.052 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3154 | MW | Dhaka | 4922.57 | 4922.57 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2323 | MW | Chittagong | 1399.9 | 1399.9 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5477 | MW | Khulna | 1646 | 1646 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1008.5 | MMCFD |  |  | Rajshahi | 1311.4 | 1311.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145106566.03 | ii) Oil : | Taka | 1531439246.46 | Comilla | 1255 | 1255 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 227661986 | Total | Taka | 1904207798.49 | Mymensingh | 956 | 956 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.011 | MKWHr. | Sylhet | 533 | 533 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 94 | MW (E to W) at | 21:00 | hrs | Barisal | 425 | 425 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 70 | MW at | 23:00 | hrs | Rangpur | 888 | 888 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.0° C |  |  | Total | 13336.87 | 13336.87 |  | 0
| B. |  | 2022-05-25 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14762 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12100 | MW
| 4 | Reserve(Generation end) |  |  |  | 662 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 298.5376 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9931 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8051 | MKWHr. | ii) HVDC Flow at Peak Time |  | 906 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8243 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.66 |  | (b) Today: | 74.71 |  | (c) Rule Curve: |  | 77.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 372 | 333 |  | 0 | 225 | 135 | 79 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 23 | 51 | 20 | 10 | 87 | 44 | 22 | 6 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 118 | 138 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 50 | 0 | 219 | 0 | 0 | 10 | 275 | 20 | 0 | 100 | 293 | 86 | 99 | 191 | 98 | 149 | 0 | 38 | 200 | 145 | 402 | 108 | 105 | 105 | 0 | 264 | 35 | 105 | 17 | 25 | 25 | 399 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 82 | 55 |  | 901 | 0 | 260 | 0 | 100 | 0 | 0 | 0 | 33 | 49 | 0 | 86 | 31 | 48 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 43 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 178 | 0 | 421 | 105 | 30 | 70 | 105 | 101 | 0 | 0 | 95 | 960 | 220 | 0 | 17 | 0 | 0 | 98 |  | 8489 | 4426 | 12915 | 3787 | 901 | 2007 | 423 | 3960 | 1135 | 35 | 0 | 549 | 118 | 0 | 0 | 74.65
2:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 179 | 333 |  | 0 | 225 | 140 | 80 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 206 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 87 | 44 | 22 | 36 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 112 | 144 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 10 | 0 | 219 | 0 | 0 | 10 | 275 | 20 | 0 | 70 | 293 | 85 | 99 | 191 | 98 | 149 | 0 | 38 | 200 | 145 | 402 | 108 | 105 | 105 | 0 | 265 | 35 | 104 | 17 | 9 | 25 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 66 | 55 |  | 901 | 0 | 260 | 0 | 96 | 0 | 0 | 0 | 33 | 49 | 0 | 86 | 31 | 48 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 43 | 24 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 420 | 105 | 0 | 70 | 105 | 101 | 0 | 0 | 70 | 950 | 222 | 0 | 17 | 0 | 0 | 99 |  | 8216 | 4341 | 12557 | 3608 | 901 | 2003 | 352 | 3900 | 1125 | 35 | 0 | 521 | 112 | 0 | 0 | 74.65
3:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 333 |  | 0 | 225 | 140 | 80 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 87 | 44 | 22 | 39 | 0 | 0 | 0 | 270 | 0 | 199 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 41 | 8 | 18 | 5 | 33 | 20 | 114 | 145 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 10 | 0 | 219 | 0 | 0 | 10 | 285 | 20 | 0 | 0 | 293 | 23 | 25 | 182 | 25 | 141 | 0 | 25 | 200 | 138 | 401 | 108 | 105 | 105 | 0 | 265 | 35 | 110 | 17 | 9 | 25 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 78 | 55 |  | 901 | 0 | 265 | 0 | 113 | 0 | 0 | 0 | 33 | 49 | 0 | 87 | 29 | 32 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 43 | 24 | 34 | 37 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 420 | 105 | 0 | 70 | 105 | 101 | 0 | 0 | 70 | 950 | 222 | 0 | 17 | 0 | 0 | 99 |  | 7738 | 4335 | 12073 | 3426 | 901 | 2014 | 73 | 3864 | 1125 | 35 | 0 | 521 | 114 | 0 | 0 | 74.65
4:00 | 0 | 0 | 0 | 180 | 270 | 104 | 0 | 0 | 333 |  | 0 | 225 | 130 | 79 | 96 | 55 | 0 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 87 | 44 | 22 | 39 | 0 | 0 | 0 | 270 | 0 | 199 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 20 | 112 | 146 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 219 | 0 | 0 | 10 | 290 | 20 | 0 | 0 | 293 | 0 | 0 | 182 | 0 | 134 | 0 | 25 | 200 | 140 | 401 | 108 | 105 | 105 | 0 | 265 | 35 | 103 | 17 | 9 | 25 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 83 | 55 |  | 902 | 0 | 275 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 32 | 0 | 0 | 0 | 34 | 0 | 82 | 0 | 43 | 0 | 34 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 427 | 105 | 0 | 70 | 105 | 101 | 0 | 0 | 70 | 920 | 222 | 0 | 17 | 0 | 0 | 99 |  | 7599 | 4135 | 11734 | 3432 | 902 | 2004 | 0 | 3855 | 1095 | 35 | 0 | 299 | 112 | 0 | 0 | 74.66
5:00 | 0 | 0 | 0 | 180 | 270 | 104 | 0 | 0 | 333 |  | 0 | 225 | 120 | 80 | 96 | 55 | 0 | 0 | 0 | 91 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 25 | 33 | 33 | 0 | 35 | 0 | 0 | 0 | 8 | 202 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 77 | 44 | 22 | 40 | 0 | 0 | 0 | 270 | 0 | 199 | 8 | 100 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 20 | 104 | 155 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 219 | 0 | 0 | 10 | 265 | 20 | 0 | 0 | 293 | 0 | 0 | 160 | 0 | 133 | 0 | 25 | 200 | 135 | 401 | 108 | 105 | 105 | 0 | 265 | 35 | 110 | 17 | 8 | 25 | 400 | 90 | 0 | 141 | 108 | 0 | 35 | 0 | 83 | 55 |  | 899 | 0 | 275 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 355 | 105 | 0 | 70 | 105 | 101 | 0 | 0 | 70 | 890 | 212 | 0 | 17 | 0 | 0 | 72 |  | 7438 | 3869 | 11307 | 3434 | 899 | 1884 | 0 | 3709 | 1065 | 35 | 0 | 177 | 104 | 0 | 0 | 74.66
6:00 | 0 | 0 | 0 | 180 | 250 | 104 | 0 | 0 | 251 |  | 0 | 225 | 140 | 80 | 80 | 55 | 0 | 0 | 0 | 91 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 25 | 33 | 33 | 0 | 35 | 0 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 0 | 22 | 30 | 0 | 0 | 0 | 270 | 0 | 204 | 8 | 100 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 20 | 100 | 155 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 179 | 0 | 0 | 10 | 260 | 12 | 0 | 0 | 284 | 0 | 0 | 100 | 0 | 132 | 1 | 25 | 200 | 133 | 352 | 108 | 105 | 105 | 0 | 265 | 35 | 95 | 17 | 9 | 25 | 350 | 90 | 3 | 125 | 108 | 0 | 32 | 0 | 83 | 55 |  | 899 | 0 | 280 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 254 | 70 | 0 | 70 | 85 | 91 | 0 | 0 | 70 | 740 | 185 | 0 | 17 | 0 | 6 | 17 |  | 6944 | 3386 | 10330 | 3239 | 899 | 1676 | 0 | 3358 | 915 | 35 | 0 | 98 | 100 | 10 | 0 | 74.66
7:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 250 |  | 0 | 225 | 135 | 80 | 93 | 55 | 0 | 0 | 0 | 82 | 32 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 33 | 0 | 35 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 80 | 0 | 22 | 36 | 0 | 0 | 0 | 270 | 0 | 198 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 20 | 98 | 150 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 92 | 50 | 0 | 0 | 179 | 0 | 0 | 10 | 280 | 20 | 0 | 0 | 281 | 0 | 0 | 100 | 0 | 132 | 1 | 25 | 200 | 138 | 352 | 108 | 105 | 94 | 0 | 273 | 35 | 92 | 17 | 9 | 25 | 350 | 90 | 15 | 129 | 108 | 0 | 17 | 0 | 83 | 55 |  | 899 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 253 | 70 | 0 | 70 | 67 | 102 | 0 | 1 | 70 | 690 | 186 | 0 | 17 | 0 | 27 | 0 |  | 6969 | 3362 | 10331 | 3287 | 899 | 1693 | 0 | 3346 | 865 | 35 | 0 | 64 | 98 | 44 | 0 | 74.67
8:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 250 |  | 0 | 225 | 138 | 80 | 96 | 50 | 0 | 0 | 0 | 50 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 17 | 33 | 0 | 35 | 0 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 74 | 15 | 0 | 7 | 0 | 0 | 0 | 270 | 0 | 194 | 8 | 100 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 33 | 0 | 104 | 143 | 0 | 0 | 1 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 179 | 0 | 0 | 10 | 280 | 20 | 0 | 0 | 290 | 0 | 0 | 100 | 0 | 135 | 0 | 25 | 200 | 140 | 374 | 108 | 105 | 100 | 1 | 273 | 35 | 92 | 17 | 9 | 25 | 370 | 90 | 28 | 126 | 108 | 0 | 17 | 0 | 83 | 55 |  | 898 | 0 | 320 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 238 | 53 | 0 | 70 | 67 | 102 | 0 | 2 | 70 | 660 | 217 | 0 | 17 | 2 | 50 | 30 |  | 6975 | 3301 | 10276 | 3201 | 898 | 1681 | 0 | 3340 | 835 | 35 | 0 | 98 | 104 | 84 | 0 | 74.67
9:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 328 |  | 0 | 225 | 135 | 80 | 96 | 55 | 0 | 0 | 22 | 85 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 0 | 46 | 0 | 35 | 0 | 0 | 0 | 20 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 73 | 37 | 20 | 3 | 0 | 0 | 0 | 270 | 0 | 193 | 8 | 100 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 5 | 30 | 18 | 108 | 130 | 0 | 0 | 1 | 44 | 41 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 219 | 0 | 0 | 10 | 275 | 22 | 0 | 0 | 292 | 0 | 0 | 127 | 0 | 129 | 4 | 25 | 159 | 135 | 402 | 108 | 105 | 105 | 1 | 273 | 35 | 92 | 17 | 9 | 25 | 400 | 90 | 15 | 126 | 108 | 0 | 17 | 0 | 83 | 55 |  | 900 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 419 | 64 | 0 | 70 | 67 | 101 | 0 | 4 | 70 | 690 | 220 | 0 | 17 | 3 | 74 | 98 |  | 7267 | 3653 | 10920 | 3330 | 900 | 1927 | 0 | 3538 | 865 | 35 | 0 | 115 | 108 | 102 | 0 | 74.67
10:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 130 | 77 | 96 | 55 | 0 | 0 | 95 | 90 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 16 | 40 | 0 | 35 | 0 | 0 | 0 | 25 | 229 | 0 | 0 | 0 |  | 24 | 17 | 0 | 10 | 79 | 41 | 20 | 3 | 0 | 0 | 0 | 345 | 0 | 175 | 8 | 98 | 27 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 16 | 20 | 112 | 123 | 0 | 0 | 2 | 44 | 40 | 0 | 0 | 110 | 90 | 50 | 0 | 0 | 220 | 0 | 0 | 10 | 290 | 22 | 0 | 25 | 292 | 150 | 96 | 130 | 96 | 127 | 0 | 25 | 103 | 140 | 403 | 107 | 105 | 105 | 2 | 251 | 35 | 92 | 17 | 9 | 25 | 400 | 75 | 19 | 126 | 94 | 0 | 17 | 0 | 66 | 55 |  | 900 | 0 | 315 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 8 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 70 | 0 | 70 | 50 | 101 | 0 | 0 | 70 | 710 | 212 | 0 | 17 | 4 | 86 | 95 |  | 7743 | 3676 | 11419 | 3492 | 900 | 1922 | 367 | 3418 | 885 | 35 | 0 | 175 | 112 | 113 | 0 | 74.67
11:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 140 | 72 | 96 | 45 | 0 | 0 | 93 | 90 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 45 | 0 | 40 | 0 | 0 | 0 | 25 | 211 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 78 | 43 | 22 | 3 | 0 | 0 | 0 | 345 | 0 | 182 | 8 | 97 | 27 | 5 | 0 | 51 | 0 | 23 | 8 | 19 | 5 | 25 | 20 | 114 | 122 | 0 | 0 | 2 | 43 | 41 | 0 | 0 | 110 | 91 | 50 | 0 | 0 | 221 | 0 | 0 | 10 | 290 | 22 | 0 | 30 | 275 | 157 | 93 | 134 | 97 | 128 | 0 | 25 | 103 | 135 | 405 | 106 | 105 | 105 | 3 | 262 | 35 | 93 | 17 | 9 | 25 | 385 | 72 | 19 | 126 | 90 | 0 | 25 | 0 | 64 | 0 |  | 899 | 0 | 305 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 10 | 0 | 50 | 0 | 8 | 0 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 53 | 0 | 70 | 50 | 81 | 0 | 7 | 70 | 790 | 211 | 0 | 17 | 5 | 98 | 95 |  | 7745 | 3789 | 11534 | 3513 | 899 | 1930 | 377 | 3304 | 965 | 40 | 0 | 258 | 114 | 134 | 0 | 74.67
12:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 150 | 71 | 96 | 45 | 0 | 0 | 95 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 42 | 0 | 10 | 78 | 44 | 22 | 5 | 0 | 0 | 0 | 305 | 0 | 182 | 8 | 96 | 23 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 5 | 25 | 20 | 118 | 120 | 0 | 20 | 2 | 44 | 42 | 0 | 0 | 110 | 92 | 50 | 0 | 0 | 221 | 0 | 0 | 10 | 315 | 22 | 0 | 100 | 290 | 255 | 94 | 151 | 98 | 135 | 3 | 25 | 103 | 130 | 405 | 106 | 105 | 105 | 3 | 262 | 35 | 92 | 17 | 9 | 25 | 386 | 73 | 44 | 144 | 90 | 0 | 35 | 0 | 64 | 0 |  | 899 | 0 | 305 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 34 | 4 | 50 | 0 | 8 | 0 | 43 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 414 | 85 | 14 | 70 | 105 | 80 | 0 | 7 | 70 | 820 | 213 | 0 | 17 | 5 | 101 | 95 |  | 8059 | 3934 | 11993 | 3482 | 899 | 1968 | 561 | 3463 | 995 | 40 | 0 | 302 | 118 | 165 | 0 | 74.67
13:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 150 | 69 | 94 | 55 | 0 | 0 | 97 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 25 | 25 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 |  | 24 | 42 | 0 | 10 | 78 | 43 | 22 | 10 | 0 | 0 | 0 | 280 | 0 | 161 | 8 | 97 | 27 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 5 | 28 | 20 | 126 | 114 | 0 | 17 | 2 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 0 | 0 | 221 | 0 | 0 | 10 | 310 | 22 | 0 | 150 | 290 | 303 | 95 | 169 | 98 | 135 | 6 | 25 | 103 | 130 | 404 | 106 | 105 | 105 | 3 | 262 | 35 | 92 | 17 | 9 | 25 | 392 | 72 | 53 | 126 | 90 | 0 | 35 | 0 | 64 | 0 |  | 899 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 32 | 0 | 0 | 0 | 34 | 5 | 51 | 0 | 8 | 8 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 173 | 0 | 414 | 105 | 54 | 70 | 105 | 79 | 0 | 7 | 70 | 850 | 212 | 0 | 17 | 5 | 98 | 95 |  | 8134 | 4072 | 12206 | 3439 | 899 | 1967 | 720 | 3504 | 1025 | 40 | 0 | 312 | 126 | 174 | 0 | 74.67
14:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 150 | 72 | 94 | 55 | 0 | 0 | 94 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 27 | 25 | 33 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 24 | 42 | 0 | 10 | 78 | 43 | 20 | 6 | 0 | 0 | 0 | 275 | 0 | 169 | 8 | 100 | 32 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 5 | 33 | 20 | 126 | 110 | 0 | 17 | 2 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 0 | 0 | 221 | 0 | 0 | 10 | 280 | 22 | 0 | 100 | 280 | 300 | 95 | 168 | 100 | 134 | 2 | 25 | 103 | 127 | 404 | 105 | 105 | 105 | 4 | 262 | 35 | 92 | 17 | 9 | 25 | 396 | 73 | 42 | 108 | 90 | 0 | 35 | 0 | 64 | 0 |  | 896 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 23 | 32 | 0 | 0 | 0 | 34 | 5 | 50 | 0 | 8 | 16 | 43 | 0 | 16 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 170 | 0 | 371 | 105 | 70 | 70 | 105 | 76 | 0 | 7 | 70 | 840 | 205 | 0 | 17 | 4 | 88 | 110 |  | 8022 | 4100 | 12122 | 3484 | 896 | 1888 | 695 | 3502 | 1015 | 40 | 0 | 327 | 126 | 149 | 0 | 74.67
15:00 | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 150 | 70 | 92 | 55 | 0 | 0 | 94 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 27 | 25 | 33 | 18 | 0 | 40 | 0 | 0 | 0 | 9 | 219 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 78 | 43 | 20 | 2 | 0 | 0 | 0 | 335 | 0 | 167 | 8 | 95 | 29 | 5 | 0 | 51 | 0 | 48 | 8 | 18 | 5 | 33 | 20 | 130 | 110 | 0 | 17 | 2 | 43 | 41 | 0 | 0 | 110 | 110 | 55 | 0 | 0 | 221 | 0 | 0 | 10 | 300 | 22 | 0 | 100 | 292 | 302 | 93 | 168 | 95 | 136 | 4 | 25 | 103 | 127 | 380 | 105 | 105 | 105 | 1 | 262 | 35 | 76 | 17 | 10 | 25 | 374 | 72 | 27 | 122 | 90 | 0 | 35 | 0 | 67 | 0 |  | 896 | 0 | 285 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 24 | 32 | 0 | 0 | 0 | 34 | 24 | 50 | 0 | 8 | 23 | 43 | 0 | 16 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 170 | 0 | 414 | 105 | 70 | 70 | 105 | 78 | 0 | 7 | 70 | 840 | 210 | 0 | 17 | 3 | 72 | 108 |  | 7986 | 4133 | 12119 | 3489 | 896 | 1953 | 690 | 3436 | 1015 | 40 | 0 | 354 | 130 | 116 | 0 | 74.68
16:00 | 0 | 0 | 0 | 180 | 270 | 100 | 0 | 0 | 327 |  | 0 | 225 | 150 | 56 | 85 | 55 | 5 | 0 | 94 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 27 | 25 | 33 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 77 | 46 | 22 | 4 | 0 | 0 | 0 | 305 | 0 | 162 | 8 | 96 | 29 | 5 | 0 | 51 | 0 | 48 | 8 | 18 | 5 | 33 | 19 | 120 | 137 | 0 | 17 | 1 | 43 | 41 | 0 | 0 | 110 | 145 | 55 | 0 | 0 | 213 | 0 | 0 | 10 | 310 | 16 | 0 | 200 | 290 | 205 | 95 | 186 | 98 | 134 | 3 | 25 | 103 | 126 | 405 | 105 | 105 | 105 | 1 | 262 | 35 | 76 | 17 | 65 | 25 | 390 | 72 | 18 | 140 | 90 | 0 | 35 | 0 | 64 | 0 |  | 897 | 0 | 285 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 22 | 32 | 0 | 0 | 0 | 34 | 24 | 50 | 0 | 8 | 23 | 52 | 0 | 16 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 94 | 122 | 70 | 105 | 75 | 0 | 5 | 70 | 860 | 211 | 0 | 17 | 2 | 50 | 108 |  | 8150 | 4130 | 12280 | 3543 | 897 | 1963 | 720 | 3528 | 1035 | 40 | 0 | 354 | 120 | 80 | 0 | 74.68
17:00 | 0 | 0 | 0 | 180 | 270 | 103 | 0 | 0 | 329 |  | 0 | 225 | 150 | 56 | 95 | 55 | 18 | 0 | 95 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 75 | 50 | 22 | 3 | 0 | 0 | 0 | 280 | 0 | 169 | 8 | 94 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 5 | 33 | 19 | 122 | 134 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 153 | 55 | 0 | 0 | 213 | 0 | 0 | 10 | 290 | 22 | 0 | 10 | 281 | 56 | 95 | 195 | 50 | 134 | 3 | 38 | 155 | 125 | 404 | 105 | 105 | 105 | 0 | 276 | 36 | 73 | 80 | 103 | 25 | 385 | 72 | 5 | 157 | 105 | 0 | 35 | 0 | 64 | 0 |  | 897 | 0 | 280 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 24 | 32 | 0 | 0 | 0 | 25 | 25 | 50 | 0 | 8 | 29 | 52 | 0 | 17 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 94 | 10 | 84 | 105 | 77 | 0 | 4 | 70 | 860 | 211 | 0 | 17 | 1 | 26 | 108 |  | 7980 | 4052 | 12032 | 3549 | 897 | 1950 | 221 | 3827 | 1035 | 40 | 0 | 352 | 122 | 39 | 0 | 74.68
18:00 | 0 | 0 | 0 | 180 | 270 | 55 | 0 | 0 | 262 |  | 0 | 225 | 130 | 61 | 96 | 55 | 27 | 0 | 34 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 45 | 10 | 82 | 50 | 22 | 8 | 0 | 0 | 0 | 280 | 0 | 179 | 8 | 100 | 29 | 5 | 0 | 51 | 0 | 31 | 8 | 19 | 5 | 33 | 19 | 98 | 129 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 260 | 22 | 0 | 0 | 292 | 0 | 25 | 196 | 0 | 134 | 1 | 38 | 200 | 128 | 315 | 106 | 105 | 105 | 0 | 276 | 36 | 86 | 114 | 105 | 50 | 300 | 86 | 2 | 162 | 108 | 0 | 35 | 0 | 70 | 0 |  | 900 | 0 | 280 | 0 | 91 | 0 | 0 | 0 | 30 | 42 | 40 | 62 | 22 | 32 | 0 | 0 | 0 | 25 | 24 | 50 | 0 | 8 | 31 | 52 | 20 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 280 | 94 | 0 | 113 | 105 | 80 | 0 | 0 | 95 | 810 | 150 | 0 | 17 | 0 | 7 | 108 |  | 7621 | 3933 | 11554 | 3344 | 900 | 1595 | 25 | 4076 | 985 | 40 | 0 | 481 | 98 | 10 | 0 | 74.68
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 68 | 96 | 55 | 33 | 0 | 94 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 25 | 17 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 18 | 55 | 51 | 10 | 85 | 50 | 22 | 16 | 0 | 0 | 0 | 280 | 0 | 194 | 8 | 100 | 27 | 5 | 0 | 51 | 0 | 31 | 8 | 19 | 5 | 33 | 17 | 132 | 129 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 50 | 0 | 221 | 0 | 0 | 10 | 280 | 22 | 0 | 156 | 293 | 300 | 90 | 197 | 98 | 149 | 0 | 50 | 200 | 132 | 397 | 107 | 105 | 105 | 0 | 276 | 36 | 90 | 114 | 105 | 50 | 400 | 94 | 0 | 158 | 108 | 0 | 35 | 0 | 80 | 0 |  | 903 | 0 | 285 | 0 | 109 | 0 | 0 | 0 | 37 | 70 | 40 | 58 | 31 | 42 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 34 | 32 | 52 | 37 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 141 | 0 | 414 | 94 | 4 | 113 | 105 | 80 | 0 | 0 | 95 | 810 | 220 | 0 | 17 | 0 | 0 | 110 |  | 8850 | 4291 | 13141 | 3585 | 903 | 2033 | 659 | 4188 | 985 | 70 | 0 | 586 | 132 | 0 | 0 | 74.69
19:30 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 73 | 96 | 55 | 65 | 0 | 95 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 20 | 55 | 51 | 10 | 85 | 50 | 22 | 21 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 100 | 35 | 5 | 0 | 51 | 0 | 31 | 8 | 19 | 5 | 33 | 20 | 130 | 126 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 295 | 22 | 0 | 200 | 293 | 300 | 93 | 196 | 99 | 149 | 0 | 50 | 200 | 135 | 403 | 107 | 105 | 105 | 0 | 276 | 36 | 90 | 114 | 105 | 63 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 0 |  | 906 | 0 | 285 | 0 | 109 | 0 | 0 | 0 | 45 | 71 | 40 | 64 | 31 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 165 | 0 | 414 | 94 | 73 | 113 | 105 | 81 | 0 | 0 | 95 | 1000 | 200 | 0 | 17 | 0 | 0 | 110 |  | 8996 | 4648 | 13644 | 3656 | 906 | 2034 | 835 | 4243 | 1175 | 70 | 0 | 595 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 342 |  | 0 | 225 | 150 | 69 | 96 | 55 | 149 | 0 | 62 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 203 | 0 | 0 | 0 |  | 20 | 59 | 51 | 10 | 87 | 50 | 22 | 29 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 99 | 35 | 5 | 0 | 51 | 0 | 31 | 8 | 19 | 5 | 33 | 20 | 134 | 131 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 270 | 22 | 0 | 200 | 293 | 167 | 95 | 197 | 99 | 149 | 0 | 50 | 200 | 133 | 402 | 108 | 105 | 105 | 0 | 262 | 36 | 105 | 114 | 105 | 65 | 395 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 0 |  | 906 | 0 | 285 | 0 | 109 | 0 | 0 | 0 | 38 | 71 | 40 | 64 | 32 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 166 | 0 | 417 | 94 | 120 | 113 | 105 | 81 | 0 | 0 | 95 | 1000 | 213 | 0 | 17 | 0 | 0 | 110 |  | 8911 | 4677 | 13588 | 3707 | 906 | 2039 | 721 | 4244 | 1175 | 70 | 0 | 592 | 134 | 0 | 0 | 74.68
21:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 328 |  | 0 | 225 | 150 | 65 | 96 | 55 | 330 | 0 | 36 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 82 | 50 | 22 | 25 | 0 | 0 | 0 | 270 | 0 | 179 | 8 | 103 | 35 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 20 | 134 | 128 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 22 | 0 | 200 | 293 | 302 | 96 | 197 | 98 | 149 | 0 | 50 | 200 | 138 | 403 | 108 | 105 | 105 | 0 | 283 | 36 | 106 | 114 | 105 | 65 | 400 | 104 | 0 | 162 | 92 | 0 | 35 | 0 | 83 | 33 |  | 906 | 0 | 285 | 0 | 108 | 0 | 0 | 0 | 38 | 70 | 40 | 65 | 33 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 20 | 168 | 0 | 417 | 94 | 120 | 113 | 105 | 81 | 0 | 0 | 95 | 1020 | 226 | 0 | 17 | 0 | 0 | 111 |  | 9232 | 4691 | 13923 | 3851 | 906 | 2055 | 836 | 4283 | 1195 | 70 | 9 | 584 | 134 | 0 | 0 | 74.69
22:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 328 |  | 0 | 225 | 150 | 68 | 96 | 55 | 323 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 17 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 226 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 81 | 50 | 22 | 35 | 0 | 0 | 0 | 270 | 0 | 183 | 8 | 99 | 35 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 20 | 126 | 124 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 156 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 22 | 0 | 80 | 293 | 180 | 98 | 200 | 99 | 149 | 0 | 50 | 200 | 140 | 400 | 108 | 105 | 105 | 0 | 283 | 36 | 92 | 114 | 104 | 65 | 385 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 55 |  | 908 | 0 | 285 | 0 | 108 | 0 | 0 | 0 | 38 | 70 | 40 | 65 | 34 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 415 | 94 | 0 | 113 | 105 | 82 | 0 | 0 | 95 | 1050 | 217 | 0 | 17 | 0 | 0 | 115 |  | 8970 | 4579 | 13549 | 3797 | 908 | 2055 | 457 | 4318 | 1225 | 70 | 9 | 584 | 126 | 0 | 0 | 74.69
23:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 329 |  | 0 | 225 | 150 | 72 | 96 | 55 | 335 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 33 | 50 | 0 | 38 | 30 | 0 | 0 | 25 | 202 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 82 | 50 | 22 | 38 | 0 | 0 | 0 | 280 | 0 | 184 | 8 | 101 | 36 | 5 | 0 | 51 | 0 | 31 | 8 | 16 | 5 | 33 | 20 | 126 | 124 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 160 | 55 | 50 | 0 | 220 | 0 | 0 | 10 | 310 | 22 | 0 | 170 | 291 | 280 | 98 | 187 | 99 | 149 | 0 | 50 | 200 | 145 | 403 | 107 | 105 | 105 | 0 | 283 | 36 | 93 | 114 | 104 | 43 | 398 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 55 |  | 910 | 0 | 285 | 0 | 93 | 0 | 0 | 0 | 38 | 65 | 40 | 59 | 34 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 20 | 166 | 0 | 419 | 94 | 16 | 113 | 105 | 81 | 0 | 0 | 95 | 1040 | 218 | 0 | 17 | 0 | 0 | 115 |  | 9178 | 4593 | 13771 | 3823 | 910 | 2084 | 683 | 4275 | 1215 | 68 | 9 | 578 | 126 | 0 | 0 | 74.69
24:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 72 | 96 | 55 | 335 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 39 | 0 | 0 | 0 | 25 | 130 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 82 | 36 | 22 | 41 | 0 | 0 | 0 | 270 | 0 | 183 | 8 | 100 | 36 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 8 | 114 | 126 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 275 | 22 | 0 | 170 | 293 | 283 | 97 | 188 | 99 | 149 | 0 | 38 | 200 | 140 | 402 | 107 | 105 | 105 | 0 | 283 | 36 | 92 | 34 | 74 | 32 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 55 |  | 910 | 0 | 290 | 0 | 93 | 0 | 0 | 0 | 38 | 65 | 40 | 54 | 34 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 24 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 165 | 0 | 423 | 94 | 60 | 70 | 105 | 81 | 0 | 0 | 113 | 1020 | 216 | 0 | 17 | 0 | 0 | 115 |  | 8795 | 4576 | 13371 | 3735 | 910 | 2063 | 729 | 4100 | 1195 | 39 | 0 | 486 | 114 | 0 | 0 | 74.69
KWH | 0 | 0 | 0 | 4378500 | 6443109 | 2403500 | 0 | 581630 | 7630000 |  | 0 | 5094350 | 3538822 | 1748160 | 2268504 | 1311999 | 1430810 | 0 | 1106000 | 2142720 | 2031408 | 3005760 | 0 | 0 | 0 | 0 | 1305720 | 1242096 | 1265853 | 360756 | 600000 | 603360 | 626160 | 714900 | 1078560 | 0 | 904020 | 148000 | 0 | 0 | 539726 | 4914483 | 0 | 0 | 0 |  | 574800 | 695534 | 355354 | 258480 | 1929600 | 1002720 | 508608 | 451680 | 0 | 0 | 0 | 7193500 | 0 | 4473000 | 200727 | 2348270 | 737352 | 144000 | 0 | 1202909 | 0 | 640608 | 204926 | 458820 | 126360 | 754600 | 403460 | 2824320 | 3068160 | 0 | 209916 | 15400 | 1031000 | 940944 | 0 | 0 | 2640190 | 2654000 | 1275072 | 407040 | 0 | 5169110 | 0 | 0 | 248940 | 7078000 | 507216 | 0 | 1971456 | 6965234 | 3411279 | 1568921 | 4005600 | 1553467 | 3378240 | 30510 | 769920 | 4030560 | 3253454 | 9438000 | 2523600 | 2596800 | 2531672 | 21600 | 6383127 | 912489 | 2275736 | 1046520 | 1028160 | 785280 | 9250500 | 2117760 | 302280 | 3448800 | 2463927 | 0 | 800640 | 0 | 1820160 | 802800 |  | 21805090 | 0 | 7106976 | 0 | 2211840 | 0 | 0 | 0 | 345120 | 552064 | 302250 | 1172000 | 584906 | 924000 | 0 | 0 | 0 | 583504 | 366287 | 1205180 | 0 | 475696 | 336498 | 1031520 | 377022 | 459600 | 0 | 147420 | 0 | 0 | 4292100 | 0 | 35000 | 0 | 0 | 0 | 0 | 0 | 327360 | 4219527 | 0 | 9280291 | 2265600 | 919728 | 2072160 | 2332656 | 2124076 | 0 | 57168 | 1963488 | 22747700 | 5037000 | 0 | 445200 | 35580 | 785520 | 2220864 |  | 193642014 | 101147991 | 294790005 | 84953519 | 21805090 | 46401955 | 9752211 | 91215101 | 27039800 | 1052020 | 35000 | 8462931 | 2824320 | 1248058 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 7216282.08 | 3196655 | 0 | 610711.5 | 8240400 |  | 0 | 5552841.5 | 3928092.42 | 19544428.8 | 30057678 | 17383986.75 | 1602507.2 | 0 | 1935500 | 31326566.4 | 28581910.56 | 48723369.6 | 0 | 0 | 0 | 0 | 16608758.4 | 16768296 | 16975088.73 | 270567 | 450000 | 0 | 0 | 0 | 18346305.6 | 0 | 244085.4 | 39960 | 0 | 0 | 8824520.1 | 5111062.32 | 0 | 0 | 0 |  | 7501140 | 11601507.12 | 6048125.08 | 3492064.8 | 24467328 | 11601470.4 | 645932.16 | 1504094.4 | 0 | 0 | 0 | 7984785 | 0 | 5188680 | 258937.83 | 2864889.4 | 833207.76 | 214560 | 0 | 2008858.03 | 0 | 11063300.16 | 2756254.7 | 628583.4 | 94770 | 1320550 | 302595 | 20278617.6 | 3344294.4 | 0 | 285485.76 | 245476 | 1412470 | 1242046.08 | 0 | 0 | 3036218.5 | 2839780 | 2473639.68 | 928051.2 | 0 | 5220801.1 | 0 | 0 | 492901.2 | 7078000 | 380412 | 0 | 41321717.76 | 95075444.1 | 71500407.84 | 32429597.07 | 53995488 | 32110162.89 | 46788624 | 356661.9 | 7945574.4 | 55057449.6 | 43173334.58 | 8682960 | 30686976 | 37549728 | 32025650.8 | 0 | 74937910.98 | 9937005.21 | 24191073.68 | 14201276.4 | 13252982.4 | 9250598.4 | 8510460 | 27424992 | 4367946 | 43765272 | 28039489.26 | 0 | 10456358.4 | 0 | 27247795.2 | 10572876 |  | 65415270 | 0 | 7959813.12 | 0 | 23025254.4 | 0 | 0 | 0 | 6215611.2 | 9937152 | 4343332.5 | 1312640 | 1134717.64 | 10071600 | 0 | 0 | 0 | 9785362.08 | 6406359.63 | 18849015.2 | 0 | 7877525.76 | 5690181.18 | 14059617.6 | 6360361.14 | 951372 | 0 | 111596.94 | 0 | 0 | 22705209 | 0 | 1230250 | 0 | 0 | 0 | 0 | 0 | 6868012.8 | 4894651.32 | 0 | 9187488.09 | 30449664 | 19286696.16 | 24513652.8 | 33706879.2 | 26975765.2 | 0 | 631706.4 | 23836744.32 | 204956777 | 5137740 | 0 | 3294480 | 402409.8 | 9214149.6 | 34045845.12 |  | 1344559177.99 | 660844903.2 | 2005404081.19 | 92255638.22 | 65415270 | 52850927.81 | 203516594.52 | 1186012057.55 | 227661986 | 284045.4 | 1230250 | 140680344.39 | 20278617.6 | 15218349.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 270 | 101 | 0 | 0 | 327 |  | 0 | 225 | 150 | 71 | 96 | 45 | 0 | 0 | 95 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 48 | 0 | 40 | 0 | 0 | 0 | 25 | 216 | 0 | 0 | 0 |  | 24 | 42 | 0 | 10 | 78 | 44 | 22 | 5 | 0 | 0 | 0 | 305 | 0 | 182 | 8 | 96 | 23 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 5 | 25 | 20 | 118 | 120 | 0 | 20 | 2 | 44 | 42 | 0 | 0 | 110 | 92 | 50 | 0 | 0 | 221 | 0 | 0 | 10 | 315 | 22 | 0 | 100 | 290 | 255 | 94 | 151 | 98 | 135 | 3 | 25 | 103 | 130 | 405 | 106 | 105 | 105 | 3 | 262 | 35 | 92 | 17 | 9 | 25 | 386 | 73 | 44 | 144 | 90 | 0 | 35 | 0 | 64 | 0 |  | 899 | 0 | 305 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 34 | 4 | 50 | 0 | 8 | 0 | 43 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 414 | 85 | 14 | 70 | 105 | 80 | 0 | 7 | 70 | 820 | 213 | 0 | 17 | 5 | 101 | 95 |  | 11993 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 328 | 0 | 0 | 225 | 150 | 65 | 96 | 55 | 330 | 0 | 36 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 30 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 10 | 82 | 50 | 22 | 25 | 0 | 0 | 0 | 270 | 0 | 179 | 8 | 103 | 35 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 20 | 134 | 128 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 22 | 0 | 200 | 293 | 302 | 96 | 197 | 98 | 149 | 0 | 50 | 200 | 138 | 403 | 108 | 105 | 105 | 0 | 283 | 36 | 106 | 114 | 105 | 65 | 400 | 104 | 0 | 162 | 92 | 0 | 35 | 0 | 83 | 33 |  | 906 | 0 | 285 | 0 | 108 | 0 | 0 | 0 | 38 | 70 | 40 | 65 | 33 | 48 | 0 | 0 | 0 | 34 | 25 | 82 | 0 | 43 | 32 | 52 | 37 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 20 | 168 | 0 | 417 | 94 | 120 | 113 | 105 | 81 | 0 | 0 | 95 | 1020 | 226 | 0 | 17 | 0 | 0 | 111 |  | 13923 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 330 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 330 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 10 | 86 | 50 | 22 | 25 | 0 | 0 | 0 | 340 | 0 | 194 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 166 | 140 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 160 | 60 | 80 | 0 | 220 | 0 | 0 | 10 | 341 | 24 | 0 | 200 | 293 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 283 | 35 | 110 | 114 | 113 | 50 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 83 | 55 |  | 913 | 0 | 320 | 0 | 115 | 220 | 0 | 0 | 35 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 176 | 113 | 105 | 103 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 330 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 10 | 86 | 50 | 22 | 10 | 0 | 0 | 0 | 340 | 0 | 194 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 143 | 140 | 0 | 20 | 1.6 | 44 | 41 | 0 | 0 | 110 | 160 | 60 | 80 | 0 | 220 | 0 | 0 | 10 | 300 | 22 | 0 | 150 | 290 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 140 | 400 | 115 | 105 | 105 | 5 | 273 | 35 | 92 | 110 | 28 | 25 | 400 | 90 | 50 | 144 | 110 | 0 | 17 | 30 | 83 | 55 |  | 913 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 35 | 0 | 40 | 86 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 0 | 113 | 105 | 103 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 190 | 105 | 0 | 0 | 298 | 0 | 0 | 225 | 150 | 69 | 65 | 40 | 280 | 0 | 0 | 7 | 7 | 98 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 24 | 17 | 33 | 24 | 0 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 52 | 50 | 22 | 13 | 0 | 0 | 0 | 270 | 0 | 185 | 8 | 99 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 96 | 133 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 158 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 145 | 0 | 0 | 80 | 0 | 65 | 5 | 25 | 100 | 100 | 351 | 108 | 90 | 68 | 1 | 265 | 36 | 73 | 17 | 9 | 25 | 360 | 70 | 15 | 144 | 108 | 0 | 17 | 0 | 17 | 38 | 0 | 910 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 58 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 35 | 0 | 70 | 15 | 81 | 0 | 2 | 75 | 740 | 222 | 0 | 17 | 0 | 49 | 34 | 0 |  |  |  |  | 109465243 |  | 0
109465243
| Minimum Generation |  | 10276 | 8:00
| Highest Generation |  | 13923 | 21:00
| Day Peak Generation |  | 11993 | 12:00
| Evening Peak Generation |  | 13923 | 21:00
| HVDC Max Flow |  | 910 | 23:00
| HVDC EvPeak Flow |  | 906 | 21:00
| Load factor L.F |  | 88.22%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-25
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11993 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9931 | MW
Evening Peak Generation : |  | 13923 | MW Hour : | 21:00 | Available Max Generation : |  | 14762 | MW
E.P. Demand (at gen end) : |  | 13923 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14100 | MW
Maximum Generation : |  | 13923 | MW Hour : | 21:00 | Reserve(Generation end) |  | 662 | MW
Total Gen. (MKWH) : |  | 294.79 | System Load Factor : | 88.22% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 70 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-25
Actual : | 74.71 | Ft.(MSL) , | Rule curve : | 77.4 | Ft.( MSL )
Gas Consumed : | Total = | 1008.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145106566.03
: |  | Coal : | 227661986 | Oil : | 1531439246.46 | Total : | 1904207798.49
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4974.2749 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1612.8619 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1573.0451 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1408.4354 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1284.4393 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1054.3076 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 516.0841 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 317.3787 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 774.7895 |  |  | 0 | 0%
Total | 0 |  | 13515.6165 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1
9) Sikalbaha 225 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sherpur 132/33 kV T-2 transformer was shut down at 08:18 to 15:13 for C/M.
b) Kallyanpur 132 kV main bus was under shut down from 08:10 to 21:12 for C/M.
c) Bogura-Natore 132 kV Ckt-2 tripped at 10:21 showing dist Z1,AB phase at Bogura end & dist Z2,R
phase at Natore end and was switched on at 10:38.
d) Tongi-Milgate 132 kV Ckt-2 was under shut down from 10:47 to 16:02 for C/M.
e) Kallyanpur-Lalbagh 132 kV Ckt-2 was under shut down at 10:51 for C/M.
f) Madunaghat-Sholoshahar 132 kV Ckt-1 was under shut down from 11:27 to 13:24 for C/M.
g) Jaldhaka 132/33 kV T-1 transformer was shut down at 09:18 to 18:21 for C/M.
h) Saidpur 132/33 kV T-2 transformer was shut down at 12:20 to 13:40 for C/M by PBS.
i) Thakurgaon 132/33 kV T-1 transformer was shut down at 12:05 to 12:30 for C/M.
j) Faridpur-Rajbari 132 kV Ckt-1 was shut down at 08:46 to 17:56 for C/M.
k) Bheramara-Rajbari 132 kV Ckt-1 was shut down at 08:49 to 17:54 for C/M.
l) Rajbari 132/33 kV T-1 transformer was shut down at 08:59 to 18:52 for C/M.
m) Rajbari 132 kV bus-1 was under shut down from 09:21 to 18:54 for C/M.
n) Siddhirganj S/S-Siddhirganj 335 MW CCPP 230 kV Ckt-1 was under shut down from 09:20 to 13:22 for C/M.
o) Madunaghat-Kulshi 132 kV Ckt-2 was under shut down from 13:42 to 18:43 for C/M.
p) Thakurgaon 132/33 kV T-2 transformer was shut down at 12:40 to 13:15 for C/M.
q) Thakurgaon 132/33 kV T-3 transformer was shut down at 13:30 to 14:20 for C/M.
r) Ghorasal 230/132 kV AT-2 transformer was shut down at 19:35 to 21:35 due to air leakage | [5 empty] | About 80 MW power interruption occurred under
at B-phase CB. | [5 empty] | Tongi,Joydevpur,Kodda S/S area from 19:35 to 21:35.
s) Shajadpur 132/33 kV T-4 transformer was shut down at 20:35 to 21:34 due to red hot maint at 33 kV side.
t) Siddhirganj 335 MW GT & ST were synchronized at 15:49,19:03 respectively.
u) Kabirpur 132/33 kV T-2 transformer was shut down at 00:20(25-05-22) to 01:10 due to red hot maint at | [5 empty] | About 40 MW power interruption occurred under
133 kV side bus isolator. | [5 empty] | Kabirpur S/S area from 00:20 to 01:10.
v) Barapukuria 132/33 kV T-6 transformer was shut down at 05:06(25-05-22) to 07:43 due to red hot maint .
w) Barapukuria S/S-Barapukuria P/S 230 kV Ckt-2 was under shut down from 05:22(25-05-2022) to 07:41
for red hot maint.
x) Mogbazar-Rampura 132 kV Ckt-2 was under shut down since at 23:00 for red hot maint.
for red hot maint.
y) Savar 33 kV bus-A was under shut down from 07:24 to 08:54 for C/M by PBS.
z) Satkhira 132/33 kV T-1 transformer with 33 kV bus were under shut down from 06:57(25-05-22) to | [5 empty] | About 10 MW power interruption occurred under
09:31 for C/M. | [5 empty] | Satkhira S/S area from 06:57 to 09:31.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6443109 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2403500
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 581630 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 328 | 7630000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5094350 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 65 | 1748160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3538822 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 2268504
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1311999
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 360756
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 36 | 1106000 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 2142720 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 1430810
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2031408 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1305720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 3005760 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1242096
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1265853
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1203360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 626160 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 714900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1078560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 293 | 6965234
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 302 | 3411279
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 96 | 1568921
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 1553467
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3378240
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2596800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2117760
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3448800
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 33 | 802800 | Engine problem
| Dhaka area Total |  |  |  | 5898 | 3844 | 78755978
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 539726
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 30510
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1002720
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1052020 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4914483
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2531672
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 695534 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 355354 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258480 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 769920 | Engine problem + Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508608
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 451680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 1929600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21600
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 283 | 6383127 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 912489 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 2275736
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 65 | 785280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 2463927 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1327 | 27882466
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4473000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7193500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 737352 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 144000 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1202909
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 3253454 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 640608 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 2348270 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4030560
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 458820 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 126360 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 2824320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 754600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 204926 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 403460 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1971456
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1046520
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1028160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 800640 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 1820160 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1777 | 35663802
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 128 | 3068160 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 209916
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 197 | 4005600
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2523600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 302280
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 574800
| Mymensingh Area Total |  |  |  | 622 | 477 | 10699756
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1031000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 940944 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2640190 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 2654000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1275072 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 407040 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5169110
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 22 | 507216 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7078000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9438000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248940
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9250500
| Sylhet Area Total |  |  |  | 2477 | 1807 | 40640012
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 906 | 21805090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 108 | 2211840 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 345120 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 552064 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 285 | 7106976 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 302250
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 20 | 327360 | Low Demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 2265600 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2332656
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 785520
| Khulna Area Total |  |  |  | 2384 | 1666 | 38034476
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 924000 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 33 | 584906 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1172000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 22747700 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 226 | 5037000
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 445200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1409 | 30910806
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 583504 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 25 | 366287 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 475696 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 336498 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 168 | 4219527 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 417 | 9280291
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 377022 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 459600
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 147420 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1031520
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 1205180 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 120 | 919728 | Low Demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2072160
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1963488 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35580
| Rajshahi Area Total |  |  |  | 2129 | 1240 | 23473501
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4292100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 9 | 35000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 81 | 2124076 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 57168
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 111 | 2220864
| Rangpur Area Total |  |  |  | 720 | 376 | 8729208
| Total |  |  |  | 21584 | 13923 | 294790005
| Eastern Grid Total |  |  |  | 14393 | 9232 | 193642014
| Western Grid Total |  |  |  | 7191 | 4691 | 101147991
| National Grid Total |  |  |  | 21584 | 13923 | 294790005
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-24
(a) ENTIRE EASTERN GRID : |  | 9066.47 | MW | (b) ENTIRE WESTERN GRID : |  | 4270.4 | MW
i) Dhaka area |  | 4922.57 | MW | i) Khulna area |  | 1646 | MW
ii) Chittagong area |  | 1399.9 | MW | ii) Rajshahi area |  | 1311.4 | MW
iii) Comilla area |  | 1255 | MW | iii) Barisal area |  | 425 | MW
iv) Mymensingh area |  | 956 | MW | iv) Rangpur area |  | 888 | MW
v) Sylhet area |  | 533 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13336.87 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 00:00 | Hasnabad | 73 | 17:00 | Palashbari | 126 | 19:30
Agargaon | 98 | 12:00 | Hathazari | 98 | 19:30 | Panchagarh | 66 | 20:00
Agrabad | 90 | 19:30 | Ishurdi | 79 | 21:00 | Patuakhali | 134 | 23:00
AKS | 14 | 00:00 | Jaldhaka | 74 | 19:30 | PHP | 7 | 10:00
AKSML | 123 | 05:00 | Jamalpur | 144 | 01:00 | Purbachal | 20 | 07:00
Amnura | 37 | 21:00 | Jashore | 127 | 21:00 | Purbasadipur | 108 | 00:00
Ashuganj | 36 | 10:00 | Jhenaidah | 124 | 19:30 | Rahim | 112 | 02:00
Bagerhat | 112 | 19:30 | Joydebpur | 194 | 10:00 | Rajbari | 72 | 19:30
Bakulia | 123 | 17:00 | Joypurhat | 67 | 21:00 | Rajendrapur | 114 | 19:30
Banani | 49 | 10:00 | Juldah | 23 | 00:00 | Rajshahi | 164 | 21:00
Bangabhaban | 22 | 10:00 | Kabirpur | 292 | 19:00 | Rajshahi | 34 | 22:00
Barapukuria | 51 | 21:00 | Kachua | 76 | 22:00 | Ramganj | 116 | 21:00
Barguna | 22 | 23:00 | Kallyanpur | 108 | 23:00 | Rampur | 20 | 23:00
Barishal | 118 | 00:00 | Kalurghat | 6 | 10:00 | Rangamati | 12 | 18:30
Barishal | 74 | 23:00 | Kamrangirchar | 74 | 19:30 | Rangpur | 146 | 21:00
Baroaulia | 73 | 23:00 | Kaptai | 4 | 18:00 | Ruppur | 4.2 | 09:00
Baroirhat | 52 | 19:30 | Kazla | 87 | 20:00 | Saidpur | 100 | 21:00
Bashundhara | 181 | 12:00 | Keranigonj | 80 | 19:30 | Satkhira | 121 | 23:00
BashundharaCement | 13 | 13:00 | Khagrachori | 26 | 19:00 | Satmasjid | 95 | 19:30
Beanibazar | 65 | 19:30 | Khulna | 93 | 00:00 | Savar | 189 | 12:00
Benapole | 62 | 21:00 | Khulshi | 185 | 17:00 | Shahjadpur | 111 | 22:00
Bhaluka | 138 | 10:00 | Kishoreganj | 130 | 23:00 | Shahjibazar | 110 | 23:00
Bhandaria | 60 | 21:00 | Kodda | 308 | 19:00 | Shahmirpur | 49.6 | 15:00
Bhangura | 36 | 20:00 | KSRM | 22 | 01:00 | Shariatpur | 80 | 22:00
Bheramara(GK) | 57 | 22:00 | Kulaura | 48 | 21:00 | Sherpur | 140 | 23:00
Bhulta | 238 | 23:00 | Kurigram | 68 | 19:30 | Shikalbaha | 37 | 19:00
Bog-Sherpur | 62 | 19:30 | Kushtia | 124 | 19:30 | Shitalakhya | 118 | 19:00
Bogura | 177 | 21:00 | Lalbag | 99 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 44 | 23:00 | Lalmonirhat | 48 | 22:00 | Shyampur | 176 | 11:00
Brahmanbaria | 160 | 01:00 | Madanganj | 192 | 00:00 | Siddhirganj | 116 | 10:00
BSRM | 164 | 04:00 | Madaripur | 110 | 00:00 | Sirajganj | 106 | 20:00
Cantonment | 152 | 13:00 | Madartek | 84 | 00:00 | Sonargaon | 89 | 00:00
Chandpur | 84 | 00:00 | Madunaghat | 59 | 19:00 | Sreemongol | 61 | 21:00
Chandraghona | 32 | 19:00 | Magura | 58 | 00:00 | Srinagar | 48.07 | 21:00
Chapai | 69 | 22:00 | Mahasthangarh | 70 | 23:00 | SSM | 16 | 01:00
Charsaidpur | 38 | 16:00 | Manikganj | 88 | 21:00 | Sunamganj | 50 | 22:00
Chauddagram | 50 | 00:00 | Maniknagar | 83 | 13:00 | Sylhet | 152 | 19:00
Chhatak | 32 | 21:00 | Matarbari | 40 | 23:00 | Tangail | 207 | 23:00
Chowmuhani | 222 | 21:00 | Matuail | 68 | 12:00 | Thakurgaon | 84 | 22:00
Chuadanga | 115 | 00:00 | Millgate | 61 | 12:00 | TK | 30.2 | 21:00
Coxsbazar | 114 | 22:00 | Mirpur | 139 | 12:00 | Tongi | 134 | 11:00
Cumilla(N) | 163 | 21:00 | Mirsorai | N/A | N/A | Ullon | 43 | 00:00
Cumilla(S) | 159 | 19:00 | Mithapukur | 34 | 21:00 | Uttara | 95 | 13:00
Daudkandi | 162 | 21:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 00:00
Dhaka | 42 | 12:00 | Mogbazar | 127 | 12:00 | Zigatola | 45 | 19:30
Dhamrai | 124 | 19:30 | Mongla | 28 | 01:00
Dhanmondi | 147 | 13:00 | Motijheel | 39 | 11:00
Dohazari | 100 | 20:00 | Munshiganj | 108 | 23:00
Faridpur | 151 | 19:30 | Mymensingh | 221 | 23:00
Fatullah | 68 | 00:00 | Naogaon | 118 | 20:00
Fenchuganj | 52 | 19:30 | Narail | 53 | 00:00
Feni | 134 | 21:00 | Narinda | 75 | 12:00
Ghorashal | 52 | 00:00 | Narshingdi | 190 | 22:00
Goalpara | 29 | 23:00 | Natore | 135 | 21:00
Gollamari | 58 | 13:00 | Nawabganj | 57.7 | 21:00
Gopalganj | 102 | 00:00 | Netrakona | 109 | 00:00
GPH | 92 | 11:00 | New | 82.8 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 5:00 | 400 | 11:00 | Kaliakoir | 398 | 0.25 | 379 | 0.45833
| Bheramara | 400 | 5:00 | 391 | 17:00 | Bhulta | 394 | 0.20833 | 372 | 0.45833
| Ashuganj(N) | 397 | 6:00 | 377 | 11:00 | Gopalganj | 419 | 0.625 | 402 | 0.91667
| Payra | 421 | 6:00 | 412 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 10:00 | Hathazari | 234 | 23:00 | 220 | 15:00
| Ishurdi | 237 | 6:00 | 225 | 11:00 | Megnaghat | 230 | 7:00 | 220 | 17:00
| Ashuganj | 240 | 5:00 | 228 | 11:00 | Fenchuganj | 243 | 13:00 | 234 | 16:00
| Serajganj | 235 | 5:00 | 226 | 11:00 | Siddhirganj | 230 | 6:00 | 216 | 11:00
| Baghabari | 234 | 6:00 | 225 | 22:00 | Maniknagar | 227 | 6:00 | 213 | 11:00
| Barapukuria | 229 | 5:00 | 215 | 21:00 | Agargaon | 228 | 6:00 | 211 | 11:00
| Bogra | 232 | 18:00 | 220 | 22:00 | Barisal | 240 | 6:00 | 232 | 21:00
| Rajshahi | 238 | 6:00 | 226 | 22:00 | Bhola 225 MW | 244 | 18:30 | 232 | 21:00
| Khulna South | 234 | 8:00 | 221 | 22:00 | AKSML | 236 | 7:00 | 223 | 15:00
| Rampura | 227 | 6:00 | 215 | 11:00 | BSRM | 235 | 18:00 | 220 | 15:00
| Haripur | 227 | 24:00 | 214 | 11:00 | Bibiyana | 243 | 6:00 | 233 | 11:00
| Hasnabad | 226 | 7:00 | 212 | 11:00 | Bhulta | 230 | 23:00 | 217 | 11:00
| Shyampur | 227 | 6:00 | 213 | 11:00 | Ashuganj (S) | 236 | 7:00 | 224 | 11:00
| Aminbazar | 229 | 1:00 | 216 | 2:00 | Kaliakoir | 230 | 7:00 | 216 | 11:00
| Tongi | 230 | 1:00 | 215 | 11:00 | GPH | 236 | 18:00 | 221 | 15:00
| Comilla (N) | 231 | 7:00 | 222 | 11:00 | Jhenaidah | 421 | 6:00 | 217 | 22:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 21:00 | 125 | 10:00 | Manikganj | 133 | 03:00 | 120 | 11:00
| Agargaon | 132 | 05:00 | 130 | 13:00 | Maniknagar | 139 | 19:00 | 122 | 11:00
| Agrabad | 138 | 07:00 | 129 | 15:00 | Matarbari | 130 | 18:00 | 111 | 14:00
| AKS | 138 | 18:00 | 130 | 12:00 | Matuail | 134 | 04:00 | 126 | 10:00
| Aminbazar | 135 | 05:00 | 128 | 12:00 | Millgate | 135 | 07:00 | 125 | 11:00
| Amnura | 131 | 03:00 | 126 | 13:00 | Mirpur | 136 | 09:00 | 121 | 11:00
| Ashuganj | 137 | 07:00 | 132 | 11:00 | Mithapukur | 133 | 04:00 | 121 | 20:00
| Bagerhat | 135 | 05:00 | 125 | 22:00 | Modern | 138 | 23:00 | 129 | 15:00
| Bakulia | 139 | 07:00 | 128 | 15:00 | Mogbazar | 135 | 04:00 | 123 | 11:00
| Banani | 135 | 05:00 | 122 | 11:00 | Mongla | 135 | 07:00 | 125 | 22:00
| Bangabhaban | 134 | 07:00 | 123 | 11:00 | Motijheel | 134 | 07:00 | 123 | 11:00
| Barapukuria | 135 | 10:00 | 125 | 19:30 | Munshiganj | 137 | 01:00 | 128 | 11:00
| Barguna | 137 | 07:00 | 129 | 22:00 | Mymensingh | 134 | 08:00 | 123 | 23:00
| Barishal | 140 | 06:00 | 129 | 22:00 | Naogaon | 132 | 05:00 | 119 | 20:00
| Barishal | 140 | 06:00 | 133 | 22:00 | Narail | 136 | 08:00 | 125 | 22:00
| Baroaulia | 140 | 06:00 | 131 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 136 | 18:00 | 124 | 15:00 | Narshingdi | 131 | 05:00 | 117 | 11:00
| Bashundhara | 135 | 05:00 | 125 | 10:00 | Natore | 135 | 06:00 | 127 | 20:00
| BashundharaCement | 136 | 01:00 | 130 | 11:00 | Nawabganj | 137 | 07:00 | 127 | 11:00
| Beanibazar | 133 | 06:00 | 127 | 19:00 | Netrakona | 135 | 08:00 | 121 | 23:00
| Benapole | 136 | 05:00 | 125 | 22:00 | New | 136 | 07:00 | 124 | 11:00
| Bhaluka | 132 | 08:00 | 122 | 00:00 | Niamatpur | 130 | 18:00 | 116 | 21:00
| Bhandaria | 137 | 07:00 | 127 | 21:00 | Noapara | 138 | 05:00 | 128 | 12:00
| Bhangura | 139 | 05:00 | 132 | 21:00 | Pabna | 137 | 05:00 | 129 | 22:00
| Bheramara | 137 | 06:00 | 131 | 22:00 | Palashbari | 132 | 05:00 | 118 | 20:00
| Bheramara(GK) | 139 | 06:00 | 133 | 13:00 | Panchagarh | 136 | 04:00 | 120 | 20:00
| Bhulta | 128 | 05:00 | 118 | 11:00 | Patuakhali | 136 | 06:00 | 130 | 22:00
| Bog-Sherpur | 136 | 05:00 | 126 | 20:00 | PHP | 136 | 18:00 | 122 | 15:00
| Bogura | 136 | 04:00 | 127 | 20:00 | Purbachal | 135 | 05:00 | 123 | 11:00
| Bogura | 138 | 06:00 | 128 | 19:30 | Purbasadipur | 134 | 02:00 | 122 | 07:00
| Brahmanbaria | 131 | 06:00 | 126 | 00:00 | Rahim | 134 | 05:00 | 114 | 04:00
| Cantonment | 131 | 05:00 | 120 | 11:00 | Rajbari | 136 | 06:00 | 127 | 22:00
| Chandpur | 140 | 18:00 | 129 | 15:00 | Rajendrapur | 134 | 06:00 | 122 | 11:00
| Chandraghona | 139 | 07:00 | 130 | 15:00 | Rajshahi | 132 | 05:00 | 125 | 12:00
| Chapai | 132 | 06:00 | 125 | 13:00 | Rajshahi | 130 | 06:00 | 124 | 13:00
| Charsaidpur | 137 | 01:00 | 130 | 12:00 | Ramganj | 137 | 18:00 | 124 | 14:00
| Chauddagram | 136 | 18:00 | 125 | 15:00 | Rampur | 137 | 05:00 | 129 | 15:00
| Chhatak | 139 | 19:00 | 127 | 21:00 | Rampura | 135 | 22:00 | 126 | 09:00
| Chowmuhani | 134 | 18:00 | 120 | 15:00 | Rangamati | 139 | 18:00 | 128 | 15:00
| Chuadanga | 132 | 09:00 | 119 | 22:00 | Rangpur | 131 | 09:00 | 118 | 20:00
| Coxsbazar | 132 | 07:00 | 116 | 02:00 | Ruppur | 139 | 05:00 | 131 | 22:00
| Cumilla(N) | 136 | 23:00 | 129 | 11:00 | Saidpur | 134 | 18:00 | 131 | 03:00
| Cumilla(S) | 137 | 18:00 | 127 | 15:00 | Satkhira | 135 | 06:00 | 123 | 22:00
| Daudkandi | 135 | 19:30 | 126 | 11:00 | Satmasjid | 132 | 07:00 | 120 | 11:00
| Dhaka | 135 | 21:00 | 122 | 11:00 | Savar | 135 | 06:00 | 122 | 11:00
| Dhamrai | 134 | 06:00 | 124 | 12:00 | Shahjadpur | 140 | 05:00 | 133 | 22:00
| Dhanmondi | 135 | 05:00 | 125 | 11:00 | Shahjibazar | 135 | 11:00 | 130 | 01:00
| Dohazari | 135 | 18:00 | 125 | 14:00 | Shahmirpur | 139 | 18:00 | 130 | 15:00
| Faridpur | 136 | 06:00 | 130 | 21:00 | Shariatpur | 137 | 07:00 | 128 | 00:00
| Fatullah | 135 | 02:00 | 127 | 11:00 | Sherpur | 138 | 10:00 | 125 | 23:00
| Fenchuganj | 136 | 06:00 | 132 | 23:00 | Shikalbaha | 140 | 07:00 | 131 | 02:00
| Feni | 137 | 18:00 | 125 | 15:00 | Shikalbaha | 139 | 08:00 | 131 | 15:00
| Ghorashal | 139 | 01:00 | 135 | 10:00 | Shitalakhya | 137 | 02:00 | 128 | 11:00
| Goalpara | 139 | 06:00 | 130 | 22:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 05:00 | 129 | 22:00 | Shyampur | 135 | 22:00 | 127 | 10:00
| Gopalganj | 141 | 18:00 | 134 | 01:00 | Shyampur | 136 | 21:00 | 126 | 11:00
| Gopalganj_I | 143 | 08:00 | 132 | 22:00 | Siddhirganj | 134 | 03:00 | 125 | 11:00
| Gulshan | 134 | 05:00 | 122 | 11:00 | Sirajganj | 137 | 05:00 | 127 | 20:00
| Halishahar | 139 | 18:00 | 128 | 15:00 | Sonargaon | 135 | 19:00 | 130 | 17:00
| Haripur | 134 | 04:00 | 126 | 11:00 | Sreemongol | 136 | 05:00 | 132 | 00:00
| HaripurSBU | 135 | 01:00 | 126 | 11:00 | Srinagar | 136 | 02:00 | 129 | 09:00
| Hasnabad | 137 | 00:00 | 128 | 10:00 | SSM | 140 | 05:00 | 130 | 15:00
| Hathazari | 138 | 23:00 | 130 | 15:00 | Sunamganj | 131 | 07:00 | 124 | 22:00
| Ishurdi | 138 | 06:00 | 131 | 22:00 | Sylhet | 133 | 03:00 | 130 | 20:00
| Jaldhaka | 133 | 04:00 | 116 | 20:00 | Tangail | 135 | 06:00 | 126 | 23:00
| Jamalpur | 139 | 05:00 | 129 | 23:00 | Thakurgaon | 136 | 02:00 | 122 | 20:00
| Jashore | 137 | 05:00 | 126 | 22:00 | TK | 140 | 18:00 | 130 | 14:00
| Jhenaidah | 139 | 07:00 | 128 | 22:00 | Tongi | 137 | 02:00 | 127 | 11:00
| Jhenaidah | 139 | 06:00 | 129 | 22:00 | Ullon | 135 | 21:00 | 125 | 10:00
| Joydebpur | 140 | 02:00 | 133 | 11:00 | Uttara | 134 | 07:00 | 121 | 11:00
| Joypurhat | 132 | 05:00 | 116 | 22:00 | UttaraNew | 135 | 05:00 | 122 | 10:00
| Juldah | 139 | 21:00 | 129 | 15:00 | Zigatola | 136 | 02:00 | 128 | 12:00
| Kabirpur | 136 | 07:00 | 123 | 11:00
| Kachua | 137 | 18:00 | 129 | 13:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 135 | 02:00 | 124 | 12:00
| Kalurghat | 139 | 18:00 | 130 | 15:00
| Kamrangirchar | 136 | 06:00 | 128 | 17:00
| Kaptai | 137 | 18:00 | 130 | 14:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 110 | 8795 | 4576 | 13371 |  |  |  | QF-LDC-11
0:30 | 242 | 8642 | 4501 | 13143 | Date: | 2022-05-24
1:00 | 374 | 8489 | 4426 | 12915
1:30 | 386 | 8352.5 | 4383.5 | 12736
2:00 | 398 | 8216 | 4341 | 12557
2:30 | 457 | 7977 | 4338 | 12315 | [5 empty] | Gen. at Eve. Peak | 13923 | 13923 MW (21:00 )
3:00 | 516 | 7738 | 4335 | 12073 | [6 empty] | 21:00
3:30 | 509 | 7668.5 | 4235 | 11903.5 | [5 empty] | Gen. at Day Peak | 11993 | 11993 MW (12:00 )
4:00 | 502 | 7599 | 4135 | 11734 | [6 empty] | 12:00
4:30 | 496 | 7518.5 | 4002 | 11520.5 | [5 empty] | Highest Generation | 13923
5:00 | 490 | 7438 | 3869 | 11307 | [6 empty] | 21:00
5:30 | 469 | 7191 | 3627.5 | 10818.5
6:00 | 448 | 6944 | 3386 | 10330
6:30 | 415 | 6956.5 | 3374 | 10330.5
7:00 | 382 | 6969 | 3362 | 10331
7:30 | 389 | 6972 | 3331.5 | 10303.5
8:00 | 396 | 6975 | 3301 | 10276
8:30 | 605 | 7121 | 3477 | 10598
9:00 | 814 | 7267 | 3653 | 10920
9:30 | 765 | 7505 | 3664.5 | 11169.5
10:00 | 716 | 7743 | 3676 | 11419
10:30 | 729 | 7744 | 3732.5 | 11476.5
11:00 | 742 | 7745 | 3789 | 11534
11:30 | 693 | 7902 | 3861.5 | 11763.5
12:00 | 644 | 8059 | 3934 | 11993
12:30 | 648 | 8096.5 | 4003 | 12099.5
13:00 | 652 | 8134 | 4072 | 12206
13:30 | 623 | 8078 | 4086 | 12164
14:00 | 594 | 8022 | 4100 | 12122
14:30 | 635 | 8004 | 4116.5 | 12120.5
15:00 | 676 | 7986 | 4133 | 12119
15:30 | 698 | 8068 | 4131.5 | 12199.5
16:00 | 720 | 8150 | 4130 | 12280
16:30 | 753 | 8065 | 4091 | 12156
17:00 | 786 | 7980 | 4052 | 12032
17:30 | 731 | 7800.5 | 3992.5 | 11793
18:00 | 676 | 7621 | 3933 | 11554
18:30 | 574 | 8235.5 | 4112 | 12347.5
19:00 | 472 | 8850 | 4291 | 13141
19:30 | 286 | 8996 | 4648 | 13644
20:00 | 228 | 8911 | 4677 | 13588 |  |  |  | Executive Engineer
20:30 | 161 | 9071.5 | 4684 | 13755.5 |  |  |  | Network Operation Division
21:00 | 94 | 9232 | 4691 | 13923
21:30 | 106 | 9101 | 4635 | 13736
22:00 | 118 | 8970 | 4579 | 13549 |  |  |  |  | Page 6 of 7
22:30 | 94 | 9074 | 4586 | 13660
23:00 | 70 | 9178 | 4593 | 13771
23:30 | 90 | 8986.5 | 4584.5 | 13571
24:00 | 110 | 8795 | 4576 | 13371
13923 MW (21:00 )
11993 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-24 |  | Energy |  | 294790005
[13 empty] | 2022-05-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3735 | 910 | 2063 | 729 | 4100 | 1195 | 39 | 0 | 486 | 114 | 0 | 0
0:30 | 3761 | 905.5 | 2035 | 576 | 4030 | 1165 | 37 | 0 | 517.5 | 116 | 0 | 0 | Date: | 2022-05-24
1:00 | 3787 | 901 | 2007 | 423 | 3960 | 1135 | 35 | 0 | 549 | 118 | 0 | 0
1:30 | 3697.5 | 901 | 2005 | 387.5 | 3930 | 1130 | 35 | 0 | 535 | 115 | 0 | 0 | [8 empty] | Total Energy | 294.79 | Total Energy Gen 294.790 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 294.790 MKWHr
2:00 | 3608 | 901 | 2003 | 352 | 3900 | 1125 | 35 | 0 | 521 | 112 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3517 | 901 | 2008.5 | 212.5 | 3882 | 1125 | 35 | 0 | 521 | 113 | 0 | 0 | [8 empty] | Energy Requirement | 294.79
3:00 | 3426 | 901 | 2014 | 73 | 3864 | 1125 | 35 | 0 | 521 | 114 | 0 | 0
3:30 | 3429 | 901.5 | 2009 | 36.5 | 3859.5 | 1110 | 35 | 0 | 410 | 113 | 0 | 0 | [6 empty] | Shortage
4:00 | 3432 | 902 | 2004 | 0 | 3855 | 1095 | 35 | 0 | 299 | 112 | 0 | 0
4:30 | 3433 | 900.5 | 1944 | 0 | 3782 | 1080 | 35 | 0 | 238 | 108 | 0 | 0
5:00 | 3434 | 899 | 1884 | 0 | 3709 | 1065 | 35 | 0 | 177 | 104 | 0 | 0
5:30 | 3336.5 | 899 | 1780 | 0 | 3533.5 | 990 | 35 | 0 | 137.5 | 102 | 5 | 0
6:00 | 3239 | 899 | 1676 | 0 | 3358 | 915 | 35 | 0 | 98 | 100 | 10 | 0
6:30 | 3263 | 899 | 1684.5 | 0 | 3352 | 890 | 35 | 0 | 81 | 99 | 27 | 0 |  |  |  |  | Coal
7:00 | 3287 | 899 | 1693 | 0 | 3346 | 865 | 35 | 0 | 64 | 98 | 44 | 0
7:30 | 3244 | 898.5 | 1687 | 0 | 3343 | 850 | 35 | 0 | 81 | 101 | 64 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3201 | 898 | 1681 | 0 | 3340 | 835 | 35 | 0 | 98 | 104 | 84 | 0
8:30 | 3265.5 | 899 | 1804 | 0 | 3439 | 850 | 35 | 0 | 106.5 | 106 | 93 | 0
9:00 | 3330 | 900 | 1927 | 0 | 3538 | 865 | 35 | 0 | 115 | 108 | 102 | 0
9:30 | 3411 | 900 | 1924.5 | 183.5 | 3478 | 875 | 35 | 0 | 145 | 110 | 107.5 | 0
10:00 | 3492 | 900 | 1922 | 367 | 3418 | 885 | 35 | 0 | 175 | 112 | 113 | 0
10:30 | 3502.5 | 899.5 | 1926 | 372 | 3361 | 925 | 37.5 | 0 | 216.5 | 113 | 123.5 | 0
11:00 | 3513 | 899 | 1930 | 377 | 3304 | 965 | 40 | 0 | 258 | 114 | 134 | 0
11:30 | 3497.5 | 899 | 1949 | 469 | 3383.5 | 980 | 40 | 0 | 280 | 116 | 149.5 | 0
12:00 | 3482 | 899 | 1968 | 561 | 3463 | 995 | 40 | 0 | 302 | 118 | 165 | 0
12:30 | 3460.5 | 899 | 1967.5 | 640.5 | 3483.5 | 1010 | 40 | 0 | 307 | 122 | 169.5 | 0
13:00 | 3439 | 899 | 1967 | 720 | 3504 | 1025 | 40 | 0 | 312 | 126 | 174 | 0
13:30 | 3439 | 899 | 1967 | 720 | 3504 | 1025 | 40 | 0 | 312 | 126 | 174 | 0
14:00 | 3439 | 899 | 1967 | 720 | 3504 | 1025 | 40 | 0 | 312 | 126 | 174 | 0
14:30 | 3464 | 897.5 | 1960 | 705 | 3470 | 1020 | 40 | 0 | 333 | 128 | 145 | 0
15:00 | 3489 | 896 | 1953 | 690 | 3436 | 1015 | 40 | 0 | 354 | 130 | 116 | 0
15:30 | 3516 | 896.5 | 1958 | 705 | 3482 | 1025 | 40 | 0 | 354 | 125 | 98 | 0
16:00 | 3543 | 897 | 1963 | 720 | 3528 | 1035 | 40 | 0 | 354 | 120 | 80 | 0
16:30 | 3549 | 897 | 1956.5 | 470.5 | 3677.5 | 1035 | 40 | 0 | 353 | 121 | 59.5 | 0
17:00 | 3549 | 897 | 1950 | 221 | 3827 | 1035 | 40 | 0 | 352 | 122 | 39 | 0
17:30 | 3446.5 | 898.5 | 1772.5 | 123 | 3951.5 | 1010 | 40 | 0 | 416.5 | 110 | 24.5 | 0
18:00 | 3344 | 900 | 1595 | 25 | 4076 | 985 | 40 | 0 | 481 | 98 | 10 | 0
18:30 | 3464.5 | 901.5 | 1814 | 342 | 4132 | 985 | 55 | 0 | 533.5 | 115 | 5 | 0
19:00 | 3585 | 903 | 2033 | 659 | 4188 | 985 | 70 | 0 | 586 | 132 | 0 | 0
19:30 | 3656 | 906 | 2034 | 835 | 4243 | 1175 | 70 | 0 | 595 | 130 | 0 | 0
20:00 | 3707 | 906 | 2039 | 721 | 4244 | 1175 | 70 | 0 | 592 | 134 | 0 | 0
20:30 | 3779 | 906 | 2047 | 778.5 | 4263.5 | 1185 | 70 | 4.5 | 588 | 134 | 0 | 0
21:00 | 3851 | 906 | 2055 | 836 | 4283 | 1195 | 70 | 9 | 584 | 134 | 0 | 0
21:30 | 3824 | 907 | 2055 | 646.5 | 4300.5 | 1210 | 70 | 9 | 584 | 130 | 0 | 0
22:00 | 3797 | 908 | 2055 | 457 | 4318 | 1225 | 70 | 9 | 584 | 126 | 0 | 0
22:30 | 3810 | 909 | 2069.5 | 570 | 4296.5 | 1220 | 69 | 9 | 581 | 126 | 0 | 0
23:00 | 3823 | 910 | 2084 | 683 | 4275 | 1215 | 68 | 9 | 578 | 126 | 0 | 0
23:30 | 3779 | 910 | 2073.5 | 706 | 4187.5 | 1205 | 53.5 | 4.5 | 532 | 120 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.0° C
24:00 | 3735 | 910 | 2063 | 729 | 4100 | 1195 | 39 | 0 | 486 | 114 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 294.790 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 294.790 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 38 | 39 | 904020
2 | Karnaphuli Hydro PP Unit-4 & 5 | [19 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 148000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 20 | 25 | 25 | 25 | 25 | 25 | 9 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 539726
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 1 |  | 4 |  |  | 3 | 6 | 2 | 4 | 3 | 3 | 1 | [8 empty] | 30510
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 206 | 203 | 203 | 202 | 203 | 204 | 216 | 203 | 229 | 211 | 216 | 215 | 203 | 219 | 215 | 204 | 204 |  | 221 | 203 | 203 | 204 | 226 | 202 | 130 | 4914483
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 20 | 0 | [15 empty] | 45 |  | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 355354
12 | Hathazari 100 MW peaking PP | 51 | 51 | 51 | 51 | 0 |  |  |  |  | 17 | 43 | 42 | 42 | 42 | 43 | 43 | 51 | 51 |  | 55 | 55 | 59 | 51 | 51 | 51 | 0 | 695534
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 94 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2531672
| Daudkandi 200 MW PP (B.Trac) | 100 | 70 | 0 | [6 empty] | 25 | 30 | 100 | 150 | 100 | 100 | 200 | 10 | 0 |  | 156 | 200 | 200 | 200 | 80 | 170 | 170 | 1971456
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 0 | [6 empty] | 23 | 40 | 40 | 48 | 48 | 48 | 40 | 31 |  | 31 | 31 | 31 | 32 | 32 | 31 | 32 | 640608
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [8 empty] | 22 | 95 | 93 | 95 | 97 | 94 | 94 | 94 | 95 | 34 |  | 94 | 95 | 62 | 36 | 0 |  | 0 | 1106000
17 | Siddhirganj 335 MW CCPP | [15 empty] | 5 | 18 | 27 |  | 33 | 65 | 149 | 330 | 323 | 335 | 335 | 1430810
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 293 | 293 | 293 | 293 | 284 | 281 | 290 | 292 | 292 | 275 | 290 | 290 | 280 | 292 | 290 | 281 | 292 |  | 293 | 293 | 293 | 293 | 293 | 291 | 293 | 6965234
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 250 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6443109
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 32 | 30 | 32 | 32 | 27 | 27 | 23 | 27 | 32 | 29 | 29 | 30 | 29 |  | 27 | 35 | 35 | 35 | 35 | 36 | 36 | 737352
33 | Ashuganj 225 MW CCPP | 190 | 194 | 199 | 199 | 199 | 204 | 198 | 194 | 193 | 175 | 182 | 182 | 161 | 169 | 167 | 162 | 169 | 179 |  | 194 | 182 | 180 | 179 | 183 | 184 | 183 | 4473000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 345 | 345 | 305 | 280 | 275 | 335 | 305 | 280 | 280 |  | 280 | 280 | 280 | 270 | 270 | 280 | 270 | 7193500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144000
36 | Chandpur 150 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 97 | 96 | 97 | 100 | 95 | 96 | 94 | 100 |  | 100 | 100 | 99 | 103 | 99 | 101 | 100 | 2348270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 179 | 0 | [23 empty] | 581630
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5094350
41 | Haripur 360MW CCPP(HPL) | 333 | 333 | 333 | 333 | 333 | 251 | 250 | 250 | 328 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 329 | 262 |  | 338 | 338 | 342 | 328 | 328 | 329 | 338 | 7630000
42 | RPCL 210MW CCPP | 138 | 144 | 145 | 146 | 155 | 155 | 150 | 143 | 130 | 123 | 122 | 120 | 114 | 110 | 110 | 137 | 134 | 129 |  | 129 | 126 | 131 | 128 | 124 | 124 | 126 | 3068160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 15 | 28 | 15 | 19 | 19 | 44 | 53 | 42 | 27 | 18 | 5 | 2 | [8 empty] | 302280
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 44 | 43 | 44 | 44 | 1031000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 42 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 940944
46 | Shajibazar 330 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 92 | 90 | 90 | 90 | 91 | 92 | 110 | 110 | 110 | 145 | 153 | 158 |  | 158 | 157 | 158 | 157 | 156 | 160 | 157 | 2654000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 60 | 60 | 60 | 60 | 55 | 60 | 1275072
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 407040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 179 | 179 | 179 | 219 | 220 | 221 | 221 | 221 | 221 | 221 | 213 | 213 | 220 |  | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 5169110
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248940
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 20 | 20 | 20 | 20 | 20 | 12 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507216
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 275 | 285 | 290 | 265 | 260 | 280 | 280 | 275 | 290 | 290 | 315 | 310 | 280 | 300 | 310 | 290 | 260 |  | 280 | 295 | 270 | 290 | 290 | 310 | 275 | 7078000
| Bibiyana South 400 MW | 399 | 400 | 400 | 400 | 400 | 350 | 350 | 370 | 400 | 400 | 385 | 386 | 392 | 396 | 374 | 390 | 385 | 300 |  | 400 | 400 | 395 | 400 | 385 | 398 | 400 | 9250500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1265853
59 | Tangail Palli Power Gen 22 MW | 23 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 18 | 20 | 20 | 24 | 24 | 24 | 24 | 574800
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 20 | 20 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508608
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  |  | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 360756
62 | Tangail 22 MW PP (Doreen) | [11 empty] | 20 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 209916
63 | Impoprt (Tripura) | 118 | 112 | 114 | 112 | 104 | 100 | 98 | 104 | 108 | 112 | 114 | 118 | 126 | 126 | 130 | 120 | 122 | 98 |  | 132 | 130 | 134 | 134 | 126 | 126 | 114 | 2824320
64 | Malancha, Ctg. EPZ (United) | 6 | 36 | 39 | 39 | 40 | 30 | 36 | 7 | 3 | 3 | 3 | 5 | 10 | 6 | 2 | 4 | 3 | 8 |  | 16 | 21 | 29 | 25 | 35 | 38 | 41 | 451680
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 16 | 19 | 458820
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 126360
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 16 | 25 | 25 | 28 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 |  | 17 | 20 | 20 | 20 | 20 | 20 | 8 | 403460
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 22 | 24 | 25 | 27 | 27 | 27 | 25 | 25 |  | 23 | 28 | 27 | 27 | 17 | 26 | 27 | 603360
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 626160
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 0 | 16 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 714900
73 | Ghorashal 108MW PP (Regent) | 105 | 105 | 105 | 104 | 104 | 104 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 100 | 103 | 55 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2403500
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 80 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 34 | 1046520
| Chowmuhani 113 MW | 25 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 65 | 103 | 105 |  | 105 | 105 | 105 | 105 | 104 | 104 | 74 | 1028160
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 141 | 125 | 129 | 126 | 126 | 126 | 126 | 144 | 126 | 108 | 122 | 140 | 157 | 162 |  | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 3448800
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 91 | 91 | 91 | 91 | 82 | 50 | 85 | 90 | 90 | 90 | 91 | 91 | 91 | 90 | 90 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2142720
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 33 | 33 | 33 | 33 | 46 | 40 | 45 | 48 | 48 | 48 | 18 | 48 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1078560
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 98 | 64 | 98 | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3005760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 204926
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2596800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 1 | 2 | 3 | 3 | 3 | 4 | 1 | 1 | 0 | [9 empty] | 21600
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 912489
| Karnaphuli Power Ltd. | 105 | 104 | 110 | 103 | 110 | 95 | 92 | 92 | 92 | 92 | 93 | 92 | 92 | 92 | 76 | 76 | 73 | 86 |  | 90 | 90 | 105 | 106 | 92 | 93 | 92 | 2275736
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 80 | 93 | 96 | 96 | 96 | 96 | 96 | 94 | 94 | 92 | 85 | 95 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2268504
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 135 | 140 | 140 | 130 | 120 | 140 | 135 | 138 | 135 | 130 | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 130 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3538822
87 | Meghnaghat 100 MW(IEL) | 79 | 80 | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 77 | 72 | 71 | 69 | 72 | 70 | 56 | 56 | 61 |  | 68 | 73 | 69 | 65 | 68 | 72 | 72 | 1748160
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 72 | 73 | 72 | 73 | 72 | 72 | 72 | 86 |  | 94 | 104 | 104 | 104 | 104 | 104 | 104 | 2117760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258480
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1202909
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 85 | 32 | 32 | 32 | 85 | 85 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2031408
95 | Patenga 50MW PP (Baraka) | 44 | 44 | 44 | 44 | 44 | 0 |  | 15 | 37 | 41 | 43 | 44 | 43 | 43 | 43 | 46 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 36 | 1002720
96 | Chattogram 108 MW PP (ECPV) | 87 | 87 | 87 | 87 | 77 | 75 | 80 | 74 | 73 | 79 | 78 | 78 | 78 | 78 | 78 | 77 | 75 | 82 |  | 85 | 85 | 87 | 82 | 81 | 82 | 82 | 1929600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 55 | 45 | 45 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1311999
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1242096
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2640190
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1305720
104 | Keranigonj 300 MW PP (APR) | 86 | 85 | 23 | 0 | [5 empty] | 150 | 157 | 255 | 303 | 300 | 302 | 205 | 56 | 0 |  | 300 | 300 | 167 | 302 | 180 | 280 | 283 | 3411279
105 | Bramhangoan 100 MW PP (Aggreko) | 99 | 99 | 25 | 0 | [5 empty] | 96 | 93 | 94 | 95 | 95 | 93 | 95 | 95 | 25 |  | 90 | 93 | 95 | 96 | 98 | 98 | 97 | 1568921
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 182 | 182 | 160 | 100 | 100 | 100 | 127 | 130 | 134 | 151 | 169 | 168 | 168 | 186 | 195 | 196 |  | 197 | 196 | 197 | 197 | 200 | 187 | 188 | 4005600
112 | Aurahati 100MW PP (Aggreko) | 98 | 98 | 25 | 0 | [5 empty] | 96 | 97 | 98 | 98 | 100 | 95 | 98 | 50 | 0 |  | 98 | 99 | 99 | 98 | 99 | 99 | 99 | 1553467
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 141 | 134 | 133 | 132 | 132 | 135 | 129 | 127 | 128 | 135 | 135 | 134 | 136 | 134 | 134 | 134 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3378240
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 |  | 50 | 50 | 50 | 50 | 50 | 50 | 38 | 769920
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 159 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 155 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4030560
117 | Ashuganj 150MW PP (Midland) | 145 | 145 | 138 | 140 | 135 | 133 | 138 | 140 | 135 | 140 | 135 | 130 | 130 | 127 | 127 | 126 | 125 | 128 |  | 132 | 135 | 133 | 138 | 140 | 145 | 140 | 3253454
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 401 | 401 | 401 | 352 | 352 | 374 | 402 | 403 | 405 | 405 | 404 | 404 | 380 | 405 | 404 | 315 |  | 397 | 403 | 402 | 403 | 400 | 403 | 402 | 9438000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 106 | 106 | 106 | 105 | 105 | 105 | 105 | 106 |  | 107 | 107 | 108 | 108 | 108 | 107 | 107 | 2523600
| Anwara 300 MW PP (United) | 264 | 265 | 265 | 265 | 265 | 265 | 273 | 273 | 273 | 251 | 262 | 262 | 262 | 262 | 262 | 262 | 276 | 276 |  | 276 | 276 | 262 | 283 | 283 | 283 | 283 | 6383127
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 63 | 65 | 65 | 65 | 43 | 32 | 785280
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 94 | 90 | 90 | 90 | 90 | 90 | 90 | 105 | 108 |  | 108 | 108 | 108 | 92 | 108 | 108 | 108 | 2463927
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 32 | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 800640
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 82 | 66 | 78 | 83 | 83 | 83 | 83 | 83 | 83 | 66 | 64 | 64 | 64 | 64 | 67 | 64 | 64 | 70 |  | 80 | 83 | 83 | 83 | 83 | 83 | 83 | 1820160
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | [12 empty] | 33 | 55 | 55 | 55 | 802800
120 | Eastern Zone Total | 8489 | 8216 | 7738 | 7599 | 7438 | 6944 | 6969 | 6975 | 7267 | 7743 | 7745 | 8059 | 8134 | 8022 | 7986 | 8150 | 7980 | 7621 |  | 8850 | 8996 | 8911 | 9232 | 8970 | 9178 | 8795 | 193642014
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 100 | 96 | 113 | 112 | 112 | 101 | 99 | 88 | 99 | 72 | 66 | 66 | 83 | 99 | 88 | 76 | 76 | 91 |  | 109 | 109 | 109 | 108 | 108 | 93 | 93 | 2211840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 33 | 33 | [14 empty] | 30 |  | 37 | 45 | 38 | 38 | 38 | 38 | 38 | 345120
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 53 | 64 | 70 | 53 | 85 | 105 | 105 | 105 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2265600
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 27 | 50 | 74 | 86 | 98 | 101 | 98 | 88 | 72 | 50 | 26 | 7 | [8 empty] | 785520
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 222 | 222 | 222 | 212 | 185 | 186 | 217 | 220 | 212 | 211 | 213 | 212 | 205 | 210 | 211 | 211 | 150 |  | 220 | 200 | 213 | 226 | 217 | 218 | 216 | 5037000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 42 | 48 | 48 | 48 | 48 | 48 | 48 | 924000
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 87 | 88 | 87 | 87 | 87 | [5 empty] | 15 | 64 | 58 | 52 | 60 | 62 |  | 58 | 64 | 64 | 65 | 65 | 59 | 54 | 1172000
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 29 | 28 | 24 | 21 | 21 | 19 | 15 | 15 | 16 | 16 | 17 | 23 | 24 | 22 | 24 | 22 |  | 31 | 31 | 32 | 33 | 34 | 34 | 34 | 584906
141 | Noapara 100 MW PP (Bangla Trac) | 10 | [8 empty] | 0 |  |  | 20 | 30 | 30 | 0 |  |  |  | 11 | 70 | 40 | 20 | 0 | 20 | 20 | 327360
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 302250
143 | Gopalganj 100 MW Peaking PP | 49 | 49 | 49 | [14 empty] | 42 |  | 70 | 71 | 71 | 70 | 70 | 65 | 65 | 552064
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 85 | 67 | 67 | 67 | 50 | 50 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2332656
146 | Bheramara HVDC | 901 | 901 | 901 | 902 | 899 | 899 | 899 | 898 | 900 | 900 | 899 | 899 | 899 | 896 | 896 | 897 | 897 | 900 |  | 903 | 906 | 906 | 906 | 908 | 910 | 910 | 21805090
147 | Bheramara 410 MW CCPP | 260 | 260 | 265 | 275 | 275 | 280 | 310 | 320 | 320 | 315 | 305 | 305 | 300 | 290 | 285 | 285 | 280 | 280 |  | 285 | 285 | 285 | 285 | 285 | 285 | 290 | 7106976
148 | Payra 1320 MW | 960 | 950 | 950 | 920 | 890 | 740 | 690 | 660 | 690 | 710 | 790 | 820 | 850 | 840 | 840 | 860 | 860 | 810 |  | 810 | 1000 | 1000 | 1020 | 1050 | 1040 | 1020 | 22747700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4292100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 43 | 34 | 0 | [5 empty] | 10 | 34 | 34 | 34 | 34 | 34 | 25 | 25 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 583504
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 35580
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 178 | 178 | 172 | 167 | 130 | 130 | 130 | 146 | 170 | 194 | 177 | 173 | 170 | 170 | 170 | 170 | 160 |  | 141 | 165 | 166 | 168 | 169 | 166 | 165 | 4219527
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 421 | 420 | 420 | 427 | 355 | 254 | 253 | 238 | 419 | 415 | 414 | 414 | 414 | 371 | 414 | 414 | 414 | 280 |  | 414 | 414 | 417 | 417 | 415 | 419 | 423 | 9280291
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 29 | 29 | 29 | 0 | [7 empty] | 4 | 5 | 5 | 24 | 24 | 25 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 366287
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 18 | 17 | 16 | 16 | 16 | 17 | 19 |  | 20 | 21 | 22 | 22 | 22 | 22 | 22 | 459600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | [5 empty] | 5 | 5 | 0 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 0 |  | 11 | 11 | 147420
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 43 | 0 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 475696
167 | Katakhali 50 MW Peaking PP | 32 | 24 | 24 | 0 | [8 empty] | 8 | 16 | 23 | 23 | 29 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 336498
168 | Santahar 50 MW Peaking PP | 37 | 37 | 37 | 0 | [13 empty] | 20 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 377022
169 | Natore 52 MW PP (Rajlanka) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1031520
170 | Chapainawabganj 100 MW Peaking PP | 82 | 82 | 82 | 82 | 45 | 0 |  |  |  | 26 | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1205180
171 | Baghabari 200 MW PP (Paramount) | 30 | 0 | [9 empty] | 14 | 54 | 70 | 70 | 122 | 10 | 0 |  | 4 | 73 | 120 | 120 | 0 | 16 | 60 | 919728
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 84 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2072160
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 113 | 1963488
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [22 empty] | 9 | 9 | 9 |  | 35000
176 | Rangpur 113 MW PP (Confidence) | 101 | 101 | 101 | 101 | 101 | 91 | 102 | 102 | 101 | 101 | 81 | 80 | 79 | 76 | 78 | 75 | 77 | 80 |  | 80 | 81 | 81 | 81 | 82 | 81 | 81 | 2124076
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 0 | 7 | 7 | 7 | 7 | 7 | 5 | 4 | 0 | [8 empty] | 57168
178 | Energypac Power Venture Thakurgaon Ltd. | 98 | 99 | 99 | 99 | 72 | 17 | 0 | 30 | 98 | 95 | 95 | 95 | 95 | 110 | 108 | 108 | 108 | 108 |  | 110 | 110 | 110 | 111 | 115 | 115 | 115 | 2220864
178