## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-26 | Thursday
|  |  | Date (day): | 2022-05-26 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13894.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14906 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-25 | 2022-05-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 270 | 280 | 280 |  | 85 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 99 | 96 | 105 | 105
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 328 | 348 | 340 | 340
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 56 | 81 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 96 | 96 | 96 | 96 |  |  | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 78 | 91 | 90 | 90 |  | 10 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 337 | 330 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 94 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 132 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 47 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 266 | 278 | 290 | 290 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 81 | 40 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 95 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 97 | 98 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 114 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 104 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 144 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3482 | 3552 | 3863 | 3865 | 671 | 879
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 7 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 75 | 40 | 75 |  | 155 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | S/D due to HGPI,24-05-22 |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 59 | 0 | 60 |  | 38 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 24 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 60 | 77 | 86 | 86 |  | 22 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 260 | 278 | 273 | 283 |  | 17 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 35 | 35 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 87 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 65 | 25 | 50 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 917 | 1222 | 1084 | 1247 | 501 | 401
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 158 | 210 | 190 | 210 | 71 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 290 | 340 | 340 |  |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 20 | 30 | 30 |  | 15 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 130 | 100 | 140 | 140 |  | 150 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 32 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 100 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 6 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 114 | 126 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 32 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 50 | 20 | 150 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 110 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 116 | 28 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 45 | 63 | 83 | 83 |  | 32 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1222 | 1576 | 1729 | 1928 | 931 | 335
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 140 | 140 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 179 | 181 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 108 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 3 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 466 | 470 | 518.6 | 497 | 62 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 157 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 60 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 50 | 0 | 50 |  |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 206 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 22 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 398 | 398 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1721 | 1774 | 1767 | 1860 | 271 | 228
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 922 | 942 | 942
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 47 | 84 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 32 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 275 | 320 | 320 | 90 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 94 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 67 | 89 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 32 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1479 | 1573 | 1862 | 2042 | 90 | 68
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 19 | 26 | 20 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 57 | 56 | 86 | 86 | 108 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 840 | 900 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 217 | 218 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1166 | 1265 | 1443 | 1649 | 108 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 2 | 29 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 34 | 43 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Running on HSD.
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 166 | 200 | 180 | 200 | 20 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 415 | 414 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 38 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 43 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 10 | 47 | 0 | 175 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 798 | 1220 | 1177 | 1375 | 401 | 138
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 225 | 225 | 49 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 81 | 101 | 103 | 103 |  | 10 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 111 | 96 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 373 | 372 | 451 | 443 | 49 | 180
|  | Total |  |  |  |  | 22348 | 21584 | 11624 | 13024 | 13894.6 | 14906 | 3084 | 2237
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11243.837 | 12598.05 | 13440.177 | 14418.4992
| A. |  | 2022-05-25 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13024 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9931 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13024 | MW
| 3 | Day peak Generation : |  |  | 11624 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12598.05 | MW
| 4 | Evening peak Generation : |  |  | 13024 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 282.0778 | MKWHr | By Solar | 1.1761 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 133.423 | MKWHr |  | By Oil: | 95.0765 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 26.5623 | MKWHr |  | By Hydro: | 1.12 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3084 | MW | Dhaka | 4797.59 | 4797.59 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2237 | MW | Chittagong | 1444.8 | 1444.8 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5321 | MW | Khulna | 1487.76 | 1487.76 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1006.15 | MMCFD |  |  | Rajshahi | 1109.9 | 1109.9 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 148671950.97 | ii) Oil : | Taka | 1279793405.38 | Comilla | 1099 | 1099 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 223402491 | Total | Taka | 1651867847.35 | Mymensingh | 1052 | 1052 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.001 | MKWHr. | Sylhet | 507 | 507 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 488 | MW (E to W) at | 19:30 | hrs | Barisal | 339 | 339 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 100 | MW at | 1:00 | hrs | Rangpur | 761 | 761 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.8° C |  |  | Total | 12598.05 | 12598.05 |  | 0
| B. |  | 2022-05-26 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14906 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 906 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 303.2163 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9258 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1491 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5709 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.71 |  | (b) Today: | 74.72 |  | (c) Rule Curve: |  | 77.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 72 | 96 | 55 | 337 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 39 | 0 | 0 | 0 | 25 | 20 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 83 | 44 | 22 | 38 | 0 | 0 | 0 | 270 | 0 | 184 | 8 | 99 | 35 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 32 | 20 | 106 | 129 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 170 | 293 | 230 | 97 | 189 | 99 | 149 | 0 | 38 | 200 | 133 | 401 | 107 | 105 | 105 | 0 | 265 | 36 | 88 | 17 | 17 | 39 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 |  | 909 | 0 | 290 | 0 | 95 | 0 | 0 | 0 | 38 | 65 | 40 | 52 | 32 | 48 | 0 | 0 | 0 | 34 | 25 | 18 | 0 | 43 | 24 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 165 | 0 | 420 | 94 | 60 | 70 | 105 | 82 | 0 | 0 | 70 | 1010 | 200 | 0 | 17 | 0 | 0 | 115 |  | 8458 | 4438 | 12896 | 3610 | 909 | 2004 | 676 | 3962 | 1185 | 39 | 0 | 405 | 106 | 0 | 0 | 74.7
2:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 74 | 96 | 55 | 336 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 8 | 25 | 33 | 50 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 83 | 46 | 22 | 40 | 0 | 0 | 0 | 270 | 0 | 186 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 20 | 106 | 132 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 160 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 255 | 0 | 0 | 40 | 293 | 61 | 97 | 188 | 49 | 149 | 0 | 38 | 200 | 133 | 401 | 108 | 105 | 105 | 0 | 265 | 36 | 73 | 17 | 9 | 39 | 400 | 104 | 0 | 159 | 108 | 0 | 35 | 0 | 73 | 16 |  | 910 | 0 | 285 | 0 | 95 | 0 | 0 | 0 | 38 | 65 | 40 | 55 | 30 | 48 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 43 | 24 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 415 | 94 | 18 | 70 | 105 | 82 | 0 | 0 | 70 | 1030 | 220 | 0 | 17 | 0 | 0 | 115 |  | 7983 | 4390 | 12373 | 3575 | 910 | 1984 | 265 | 3901 | 1205 | 40 | 0 | 387 | 106 | 0 | 0 | 74.7
3:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 339 |  | 0 | 225 | 150 | 73 | 96 | 55 | 337 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 83 | 50 | 22 | 41 | 0 | 0 | 0 | 270 | 0 | 186 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 5 | 33 | 20 | 106 | 131 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 291 | 0 | 25 | 188 | 24 | 149 | 0 | 25 | 200 | 142 | 401 | 108 | 105 | 105 | 0 | 264 | 36 | 73 | 17 | 9 | 39 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 82 | 33 |  | 909 | 0 | 285 | 0 | 95 | 0 | 0 | 0 | 0 | 65 | 40 | 55 | 29 | 48 | 0 | 0 | 0 | 34 | 25 | 0 | 0 | 43 | 24 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 415 | 94 | 0 | 70 | 105 | 82 | 0 | 0 | 70 | 960 | 220 | 0 | 17 | 0 | 0 | 115 |  | 7854 | 4262 | 12116 | 3590 | 909 | 2010 | 49 | 3928 | 1135 | 40 | 0 | 349 | 106 | 0 | 0 | 74.7
4:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 338 |  | 0 | 225 | 150 | 69 | 96 | 40 | 336 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 0 | 5 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 83 | 50 | 22 | 42 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 106 | 134 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 293 | 0 | 0 | 189 | 0 | 134 | 0 | 25 | 200 | 142 | 401 | 108 | 90 | 105 | 0 | 264 | 36 | 73 | 17 | 9 | 39 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 83 | 37 |  | 909 | 0 | 290 | 0 | 95 | 0 | 0 | 0 | 0 | 50 | 40 | 55 | 28 | 48 | 0 | 0 | 0 | 34 | 17 | 0 | 0 | 43 | 6 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 415 | 94 | 0 | 70 | 89 | 77 | 0 | 0 | 70 | 930 | 190 | 0 | 17 | 0 | 0 | 115 |  | 7735 | 4146 | 11881 | 3610 | 909 | 1969 | 0 | 3866 | 1105 | 40 | 0 | 276 | 106 | 0 | 0 | 74.71
5:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 337 |  | 0 | 225 | 150 | 73 | 96 | 40 | 335 | 0 | 0 | 40 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 80 | 50 | 22 | 42 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 102 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 100 | 134 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 55 | 0 | 0 | 219 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 230 | 0 | 0 | 188 | 0 | 132 | 0 | 25 | 155 | 143 | 400 | 108 | 90 | 105 | 0 | 265 | 36 | 73 | 17 | 9 | 39 | 400 | 104 | 0 | 148 | 108 | 0 | 29 | 0 | 44 | 37 |  | 909 | 0 | 290 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 422 | 94 | 0 | 70 | 72 | 82 | 0 | 0 | 75 | 930 | 220 | 0 | 17 | 0 | 0 | 115 |  | 7421 | 3923 | 11344 | 3592 | 909 | 2002 | 0 | 3464 | 1105 | 40 | 0 | 132 | 100 | 0 | 0 | 74.71
6:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 298 |  | 0 | 225 | 150 | 73 | 68 | 40 | 280 | 0 | 0 | 7 | 32 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 27 | 17 | 33 | 32 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 79 | 50 | 22 | 42 | 0 | 0 | 0 | 270 | 0 | 189 | 8 | 100 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 86 | 138 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 110 | 158 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 260 | 0 | 0 | 0 | 195 | 0 | 0 | 80 | 0 | 107 | 0 | 25 | 120 | 100 | 352 | 108 | 90 | 96 | 0 | 265 | 36 | 73 | 17 | 9 | 39 | 360 | 90 | 3 | 162 | 108 | 0 | 17 | 0 | 17 | 37 |  | 909 | 0 | 290 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 354 | 70 | 0 | 70 | 15 | 76 | 0 | 0 | 75 | 820 | 208 | 0 | 17 | 0 | 3 | 72 |  | 6811 | 3544 | 10355 | 3477 | 909 | 1869 | 0 | 2858 | 995 | 40 | 0 | 115 | 86 | 6 | 0 | 74.71
7:00 | 0 | 0 | 0 | 180 | 270 | 105 | 0 | 0 | 299 |  | 0 | 225 | 150 | 73 | 65 | 40 | 280 | 0 | 0 | 7 | 7 | 98 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 24 | 17 | 33 | 24 | 0 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 65 | 50 | 22 | 38 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 101 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 90 | 137 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 157 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 145 | 0 | 0 | 80 | 0 | 72 | 4 | 25 | 100 | 100 | 351 | 108 | 90 | 68 | 0 | 262 | 36 | 73 | 17 | 9 | 37 | 360 | 70 | 16 | 149 | 108 | 0 | 17 | 0 | 17 | 38 |  | 909 | 0 | 300 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 55 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 70 | 0 | 70 | 15 | 79 | 0 | 1 | 75 | 770 | 208 | 0 | 17 | 0 | 24 | 34 |  | 6619 | 3477 | 10096 | 3506 | 909 | 1875 | 0 | 2587 | 945 | 40 | 0 | 98 | 90 | 46 | 0 | 74.72
8:00 | 0 | 0 | 0 | 180 | 190 | 105 | 0 | 0 | 298 |  | 0 | 225 | 150 | 69 | 65 | 40 | 280 | 0 | 0 | 7 | 7 | 98 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 24 | 17 | 33 | 24 | 0 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 52 | 50 | 22 | 13 | 0 | 0 | 0 | 270 | 0 | 185 | 8 | 99 | 33 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 96 | 133 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 158 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 145 | 0 | 0 | 80 | 0 | 65 | 5 | 25 | 100 | 100 | 351 | 108 | 90 | 68 | 1 | 265 | 36 | 73 | 17 | 9 | 25 | 360 | 70 | 15 | 144 | 108 | 0 | 17 | 0 | 17 | 38 |  | 910 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 58 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 35 | 0 | 70 | 15 | 81 | 0 | 2 | 75 | 740 | 222 | 0 | 17 | 0 | 49 | 34 |  | 6472 | 3459 | 9931 | 3413 | 910 | 1860 | 0 | 2526 | 915 | 40 | 0 | 98 | 96 | 73 | 0 | 74.72
9:00 | 0 | 0 | 0 | 180 | 190 | 101 | 0 | 0 | 326 |  | 0 | 225 | 150 | 72 | 67 | 40 | 335 | 0 | 0 | 7 | 16 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 33 | 24 | 0 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 67 | 26 | 22 | 5 | 0 | 0 | 0 | 270 | 0 | 193 | 8 | 103 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 106 | 111 | 0 | 17 | 2 | 43 | 41 | 0 | 0 | 110 | 159 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 295 | 0 | 0 | 0 | 145 | 0 | 0 | 110 | 0 | 72 | 8 | 25 | 100 | 110 | 402 | 108 | 90 | 81 | 3 | 264 | 36 | 73 | 17 | 9 | 25 | 400 | 74 | 9 | 155 | 108 | 0 | 17 | 0 | 17 | 55 |  | 909 | 0 | 295 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 414 | 53 | 0 | 70 | 15 | 81 | 0 | 4 | 75 | 760 | 224 | 0 | 17 | 0 | 64 | 34 |  | 6796 | 3585 | 10381 | 3561 | 909 | 1963 | 0 | 2679 | 935 | 40 | 0 | 98 | 106 | 90 | 0 | 74.72
10:00 | 0 | 0 | 0 | 180 | 190 | 98 | 0 | 0 | 331 |  | 0 | 225 | 150 | 69 | 86 | 40 | 335 | 0 | 0 | 12 | 58 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 33 | 30 | 0 | 40 | 0 | 100 | 0 | 1 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 61 | 50 | 20 | 5 | 0 | 0 | 0 | 270 | 0 | 190 | 8 | 103 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 110 | 111 | 0 | 17 | 1 | 43 | 41 | 0 | 0 | 110 | 158 | 50 | 0 | 0 | 220 | 0 | 0 | 10 | 305 | 0 | 0 | 20 | 218 | 173 | 25 | 144 | 25 | 110 | 19 | 25 | 100 | 130 | 402 | 99 | 90 | 85 | 5 | 262 | 35 | 73 | 17 | 9 | 25 | 400 | 92 | 22 | 162 | 94 | 0 | 20 | 0 | 23 | 55 |  | 913 | 0 | 295 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 32 | 52 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 78 | 1 | 70 | 50 | 77 | 0 | 5 | 75 | 780 | 220 | 0 | 17 | 0 | 81 | 105 |  | 7363 | 3745 | 11108 | 3548 | 913 | 1972 | 244 | 3061 | 955 | 40 | 0 | 132 | 110 | 133 | 0 | 74.72
11:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 0 | 332 |  | 0 | 225 | 150 | 55 | 87 | 40 | 332 | 0 | 0 | 70 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 61 | 50 | 22 | 5 | 0 | 0 | 0 | 270 | 0 | 174 | 8 | 98 | 32 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 0 | 20 | 116 | 106 | 0 | 0 | 2 | 43 | 41 | 0 | 0 | 110 | 157 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 275 | 0 | 0 | 20 | 258 | 0 | 25 | 180 | 25 | 132 | 0 | 25 | 100 | 137 | 402 | 99 | 90 | 85 | 5 | 260 | 35 | 73 | 17 | 9 | 25 | 388 | 92 | 17 | 162 | 90 | 0 | 35 | 0 | 43 | 55 |  | 916 | 0 | 290 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 56 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 414 | 93 | 10 | 70 | 67 | 80 | 0 | 5 | 75 | 770 | 220 | 0 | 17 | 0 | 98 | 113 |  | 7438 | 3819 | 11257 | 3593 | 916 | 1944 | 80 | 3364 | 945 | 40 | 0 | 132 | 116 | 127 | 0 | 74.72
12:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 328 |  | 0 | 225 | 150 | 56 | 96 | 40 | 332 | 0 | 0 | 78 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 10 | 60 | 50 | 22 | 5 | 0 | 0 | 0 | 290 | 0 | 158 | 8 | 98 | 36 | 5 | 0 | 51 | 0 | 24 | 8 | 19 | 5 | 0 | 20 | 114 | 109 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 110 | 157 | 50 | 0 | 0 | 220 | 0 | 0 | 9 | 290 | 0 | 0 | 50 | 266 | 81 | 95 | 179 | 97 | 132 | 7 | 25 | 100 | 130 | 403 | 108 | 90 | 85 | 4 | 260 | 36 | 73 | 17 | 9 | 25 | 398 | 92 | 52 | 162 | 90 | 0 | 35 | 0 | 45 | 55 |  | 920 | 0 | 280 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 57 | 19 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 8 | 0 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 415 | 93 | 10 | 70 | 67 | 81 | 0 | 6 | 75 | 840 | 217 | 0 | 17 | 1 | 32 | 111 |  | 7808 | 3816 | 11624 | 3612 | 920 | 1953 | 333 | 3376 | 1015 | 40 | 0 | 158 | 114 | 103 | 0 | 74.72
13:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 329 |  | 0 | 225 | 150 | 57 | 96 | 40 | 337 | 0 | 0 | 74 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 60 | 50 | 22 | 8 | 0 | 0 | 0 | 290 | 0 | 158 | 8 | 100 | 36 | 5 | 0 | 51 | 0 | 24 | 8 | 16 | 5 | 0 | 20 | 114 | 102 | 0 | 17 | 1 | 44 | 41 | 0 | 0 | 110 | 158 | 50 | 0 | 0 | 219 | 0 | 0 | 9 | 270 | 0 | 0 | 15 | 290 | 39 | 95 | 140 | 96 | 132 | 5 | 25 | 100 | 130 | 402 | 108 | 90 | 88 | 5 | 277 | 36 | 73 | 17 | 8 | 25 | 390 | 92 | 19 | 162 | 90 | 0 | 35 | 0 | 45 | 41 |  | 922 | 0 | 280 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 52 | 21 | 16 | 0 | 0 | 0 | 34 | 4 | 0 | 0 | 8 | 11 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 93 | 10 | 70 | 67 | 81 | 0 | 7 | 75 | 830 | 165 | 0 | 17 | 1 | 101 | 111 |  | 7675 | 3869 | 11544 | 3577 | 922 | 1889 | 255 | 3398 | 1005 | 40 | 0 | 205 | 114 | 139 | 0 | 74.72
14:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 351 |  | 0 | 225 | 150 | 55 | 96 | 40 | 326 | 0 | 0 | 74 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 0 | 25 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 6 | 0 | 10 | 60 | 50 | 22 | 6 | 0 | 0 | 0 | 290 | 0 | 160 | 8 | 102 | 34 | 5 | 0 | 51 | 0 | 24 | 8 | 16 | 5 | 0 | 20 | 122 | 102 | 0 | 17 | 1 | 44 | 41 | 0 | 0 | 110 | 160 | 55 | 0 | 0 | 220 | 0 | 0 | 9 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 100 | 0 | 133 | 10 | 25 | 100 | 122 | 353 | 75 | 90 | 105 | 5 | 277 | 36 | 73 | 17 | 16 | 25 | 360 | 92 | 26 | 162 | 90 | 0 | 35 | 0 | 45 | 55 |  | 922 | 0 | 280 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 23 | 16 | 0 | 0 | 0 | 34 | 20 | 0 | 0 | 8 | 24 | 24 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 362 | 93 | 0 | 70 | 67 | 83 | 0 | 7 | 75 | 790 | 168 | 0 | 17 | 5 | 87 | 108 |  | 7308 | 3826 | 11134 | 3470 | 922 | 1852 | 0 | 3382 | 965 | 40 | 0 | 240 | 122 | 141 | 0 | 74.72
15:00 | 0 | 0 | 0 | 180 | 280 | 100 | 0 | 0 | 342 |  | 0 | 225 | 150 | 55 | 96 | 40 | 336 | 0 | 0 | 74 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 17 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 22 | 0 | 10 | 60 | 48 | 22 | 3 | 0 | 0 | 0 | 290 | 0 | 146 | 8 | 101 | 20 | 5 | 0 | 51 | 0 | 24 | 8 | 16 | 6 | 0 | 0 | 98 | 106 | 0 | 17 | 1 | 44 | 41 | 0 | 0 | 110 | 157 | 58 | 0 | 0 | 220 | 0 | 0 | 10 | 310 | 0 | 0 | 0 | 280 | 0 | 0 | 115 | 0 | 131 | 13 | 25 | 100 | 130 | 403 | 84 | 90 | 105 | 4 | 277 | 36 | 73 | 17 | 24 | 25 | 393 | 92 | 37 | 162 | 90 | 0 | 25 | 0 | 45 | 55 |  | 921 | 0 | 275 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 22 | 16 | 0 | 0 | 0 | 34 | 22 | 0 | 0 | 8 | 24 | 24 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 415 | 93 | 0 | 70 | 67 | 80 | 0 | 5 | 75 | 830 | 210 | 0 | 17 | 4 | 71 | 111 |  | 7411 | 3950 | 11361 | 3548 | 921 | 1982 | 0 | 3408 | 1005 | 40 | 0 | 224 | 98 | 135 | 0 | 74.72
16:00 | 0 | 0 | 0 | 180 | 280 | 100 | 0 | 0 | 342 |  | 0 | 225 | 150 | 55 | 96 | 40 | 337 | 0 | 0 | 76 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 24 | 17 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 28 | 0 | 10 | 60 | 44 | 22 | 3 | 0 | 0 | 0 | 290 | 0 | 165 | 8 | 98 | 20 | 5 | 0 | 51 | 0 | 24 | 8 | 16 | 6 | 0 | 12 | 100 | 110 | 0 | 17 | 1 | 44 | 41 | 0 | 0 | 110 | 158 | 58 | 0 | 0 | 220 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 230 | 0 | 0 | 120 | 0 | 117 | 7 | 25 | 100 | 140 | 389 | 107 | 90 | 105 | 1 | 278 | 36 | 73 | 17 | 57 | 38 | 400 | 92 | 11 | 162 | 90 | 0 | 27 | 0 | 45 | 55 |  | 922 | 0 | 265 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 40 | 51 | 21 | 16 | 0 | 0 | 0 | 34 | 22 | 12 | 0 | 8 | 24 | 24 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 421 | 93 | 0 | 70 | 67 | 80 | 0 | 4 | 75 | 850 | 183 | 0 | 17 | 2 | 51 | 72 |  | 7454 | 3898 | 11352 | 3595 | 922 | 1927 | 0 | 3390 | 1025 | 40 | 0 | 276 | 100 | 77 | 0 | 74.72
17:00 | 0 | 0 | 0 | 180 | 200 | 12 | 0 | 0 | 342 |  | 0 | 225 | 150 | 65 | 86 | 40 | 337 | 0 | 0 | 40 | 64 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 24 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 36 | 0 | 10 | 60 | 44 | 22 | 10 | 0 | 0 | 0 | 290 | 0 | 180 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 98 | 110 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 58 | 0 | 0 | 220 | 0 | 0 | 10 | 260 | 0 | 0 | 0 | 230 | 71 | 0 | 70 | 0 | 95 | 3 | 25 | 142 | 80 | 389 | 107 | 90 | 105 | 2 | 278 | 36 | 73 | 52 | 113 | 38 | 398 | 104 | 8 | 162 | 104 | 0 | 35 | 0 | 37 | 55 |  | 921 | 0 | 260 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 13 | 16 | 0 | 0 | 0 | 43 | 22 | 72 | 0 | 8 | 24 | 24 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 380 | 70 | 0 | 70 | 50 | 82 | 0 | 3 | 95 | 780 | 214 | 0 | 17 | 0 | 25 | 34 |  | 7244 | 3765 | 11009 | 3483 | 921 | 1810 | 71 | 3231 | 955 | 40 | 0 | 359 | 98 | 41 | 0 | 74.72
18:00 | 0 | 0 | 0 | 180 | 200 | 12 | 0 | 0 | 333 |  | 0 | 225 | 150 | 70 | 94 | 40 | 335 | 0 | 0 | 55 | 64 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 0 | 25 | 22 | 17 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 0 | 10 | 65 | 45 | 22 | 12 | 0 | 0 | 0 | 290 | 0 | 152 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 0 | 0 | 25 | 20 | 104 | 111 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 158 | 58 | 0 | 0 | 192 | 0 | 0 | 10 | 260 | 0 | 0 | 0 | 195 | 100 | 50 | 85 | 50 | 104 | 0 | 50 | 170 | 80 | 364 | 107 | 96 | 105 | 0 | 278 | 36 | 87 | 52 | 115 | 38 | 350 | 104 | 1 | 162 | 108 | 0 | 35 | 0 | 37 | 55 |  | 922 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 16 | 51 | 23 | 16 | 0 | 0 | 0 | 43 | 27 | 82 | 0 | 8 | 24 | 43 | 21 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 264 | 70 | 0 | 70 | 50 | 75 | 0 | 1 | 70 | 730 | 159 | 0 | 17 | 0 | 2 | 34 |  | 7361 | 3542 | 10903 | 3375 | 922 | 1643 | 200 | 3298 | 905 | 40 | 0 | 412 | 104 | 4 | 0 | 74.72
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 234 | 73 | 0 | 0 | 348 |  | 0 | 225 | 150 | 78 | 96 | 40 | 337 | 0 | 0 | 90 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 20 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 73 | 50 | 22 | 18 | 0 | 0 | 0 | 290 | 0 | 213 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 6 | 32 | 21 | 108 | 141 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 158 | 60 | 50 | 0 | 206 | 0 | 0 | 9 | 270 | 13 | 0 | 50 | 238 | 76 | 93 | 110 | 100 | 114 | 0 | 50 | 185 | 83 | 402 | 107 | 105 | 105 | 0 | 278 | 36 | 87 | 114 | 116 | 63 | 397 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 37 | 55 |  | 922 | 0 | 270 | 0 | 80 | 0 | 0 | 0 | 15 | 25 | 40 | 56 | 26 | 24 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 34 | 32 | 43 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 158 | 0 | 414 | 80 | 1 | 80 | 50 | 100 | 0 | 0 | 113 | 750 | 220 | 0 | 17 | 0 | 0 | 34 |  | 8318 | 3984 | 12302 | 3673 | 922 | 1999 | 321 | 3750 | 925 | 75 | 0 | 529 | 108 | 0 | 0 | 74.72
19:30 | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 348 |  | 0 | 225 | 150 | 81 | 96 | 55 | 337 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 59 | 51 | 10 | 77 | 50 | 22 | 24 | 0 | 0 | 0 | 290 | 0 | 210 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 6 | 32 | 21 | 126 | 140 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 206 | 0 | 0 | 10 | 280 | 16 | 0 | 20 | 278 | 40 | 100 | 181 | 98 | 114 | 0 | 50 | 200 | 100 | 402 | 108 | 105 | 105 | 0 | 278 | 36 | 87 | 114 | 116 | 65 | 398 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 63 | 55 |  | 922 | 0 | 275 | 0 | 84 | 0 | 0 | 0 | 27 | 32 | 40 | 56 | 26 | 48 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 34 | 32 | 43 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 200 | 0 | 414 | 94 | 47 | 113 | 89 | 101 | 0 | 0 | 113 | 900 | 218 | 0 | 17 | 0 | 0 | 96 |  | 8594 | 4430 | 13024 | 3757 | 922 | 2037 | 315 | 4161 | 1075 | 75 | 0 | 556 | 126 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 342 |  | 0 | 225 | 150 | 80 | 96 | 55 | 337 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 59 | 51 | 10 | 78 | 50 | 22 | 23 | 0 | 0 | 0 | 290 | 0 | 207 | 8 | 99 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 6 | 32 | 21 | 124 | 140 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 206 | 0 | 0 | 9 | 270 | 16 | 0 | 20 | 280 | 23 | 70 | 180 | 70 | 114 | 0 | 50 | 200 | 120 | 402 | 108 | 105 | 105 | 0 | 278 | 36 | 87 | 114 | 115 | 65 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 60 | 55 |  | 922 | 0 | 275 | 0 | 85 | 0 | 0 | 0 | 42 | 43 | 40 | 52 | 32 | 48 | 0 | 0 | 0 | 43 | 31 | 82 | 0 | 34 | 32 | 43 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 192 | 0 | 414 | 94 | 20 | 113 | 89 | 101 | 0 | 0 | 113 | 920 | 197 | 0 | 17 | 0 | 0 | 98 |  | 8533 | 4427 | 12960 | 3753 | 922 | 2013 | 213 | 4181 | 1095 | 75 | 0 | 584 | 124 | 0 | 0 | 74.72
21:00 | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 344 |  | 0 | 225 | 150 | 82 | 96 | 55 | 337 | 0 | 0 | 91 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 19 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 51 | 10 | 81 | 50 | 22 | 31 | 0 | 0 | 0 | 290 | 0 | 206 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 21 | 110 | 139 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 159 | 60 | 50 | 0 | 211 | 0 | 0 | 10 | 260 | 16 | 0 | 0 | 278 | 0 | 0 | 189 | 0 | 124 | 0 | 50 | 200 | 143 | 402 | 107 | 105 | 105 | 0 | 278 | 36 | 87 | 114 | 115 | 65 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 81 | 55 |  | 921 | 0 | 275 | 0 | 85 | 0 | 0 | 0 | 33 | 64 | 40 | 52 | 39 | 48 | 0 | 0 | 0 | 43 | 13 | 82 | 0 | 34 | 32 | 43 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 94 | 0 | 113 | 89 | 101 | 0 | 0 | 113 | 950 | 220 | 0 | 17 | 0 | 0 | 99 |  | 8349 | 4453 | 12802 | 3758 | 921 | 2044 | 0 | 4247 | 1125 | 75 | 0 | 522 | 110 | 0 | 0 | 74.72
22:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 342 |  | 0 | 225 | 150 | 89 | 96 | 55 | 335 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 19 | 25 | 33 | 50 | 0 | 40 | 34 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 81 | 50 | 22 | 38 | 0 | 0 | 0 | 290 | 0 | 208 | 8 | 102 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 21 | 110 | 138 | 0 | 17 | 0 | 43 | 41 | 0 | 0 | 110 | 159 | 60 | 50 | 0 | 218 | 0 | 0 | 10 | 290 | 16 | 0 | 0 | 278 | 0 | 0 | 181 | 0 | 127 | 0 | 50 | 200 | 143 | 389 | 107 | 105 | 105 | 0 | 283 | 36 | 95 | 114 | 115 | 65 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 81 | 55 |  | 921 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 28 | 50 | 0 | 55 | 39 | 48 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 416 | 94 | 0 | 113 | 89 | 101 | 0 | 0 | 113 | 850 | 200 | 0 | 17 | 0 | 0 | 99 |  | 8355 | 4192 | 12547 | 3754 | 921 | 2058 | 0 | 4193 | 1025 | 74 | 0 | 412 | 110 | 0 | 0 | 74.72
23:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 342 |  | 0 | 225 | 150 | 81 | 96 | 55 | 335 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 19 | 25 | 33 | 50 | 0 | 40 | 33 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 10 | 81 | 50 | 22 | 39 | 0 | 0 | 0 | 290 | 0 | 203 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 21 | 108 | 139 | 0 | 0 | 0 | 44 | 41 | 0 | 0 | 110 | 159 | 58 | 50 | 0 | 210 | 0 | 0 | 10 | 300 | 16 | 0 | 0 | 275 | 0 | 0 | 181 | 0 | 134 | 0 | 50 | 200 | 145 | 389 | 107 | 105 | 105 | 0 | 283 | 36 | 110 | 114 | 115 | 58 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 81 | 55 |  | 924 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 0 | 53 | 0 | 60 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 416 | 53 | 0 | 113 | 67 | 101 | 0 | 0 | 113 | 860 | 201 | 0 | 17 | 0 | 0 | 99 |  | 8303 | 4002 | 12305 | 3725 | 924 | 2062 | 0 | 4077 | 1035 | 73 | 0 | 301 | 108 | 0 | 0 | 74.72
24:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 342 |  | 0 | 225 | 150 | 81 | 96 | 55 | 335 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 19 | 25 | 33 | 33 | 0 | 40 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 10 | 83 | 50 | 22 | 39 | 0 | 0 | 0 | 290 | 0 | 196 | 8 | 102 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 108 | 139 | 0 | 0 | 0 | 44 | 41 | 0 | 0 | 110 | 158 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 16 | 0 | 0 | 278 | 0 | 0 | 181 | 0 | 133 | 0 | 38 | 200 | 147 | 388 | 107 | 105 | 105 | 0 | 283 | 36 | 110 | 17 | 61 | 38 | 400 | 104 | 0 | 162 | 106 | 0 | 35 | 0 | 80 | 55 |  | 924 | 0 | 275 | 0 | 99 | 0 | 0 | 0 | 0 | 53 | 0 | 56 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 383 | 53 | 0 | 70 | 67 | 85 | 0 | 0 | 76 | 870 | 221 | 0 | 17 | 0 | 0 | 99 |  | 8021 | 3855 | 11876 | 3724 | 924 | 2041 | 0 | 3773 | 1045 | 40 | 0 | 221 | 108 | 0 | 0 | 74.72
KWH | 0 | 0 | 0 | 4347000 | 6158282 | 2237272 | 0 | 0 | 7950000 |  | 0 | 5234850 | 3598371 | 1689600 | 2192592 | 1106088 | 7906776 | 0 | 0 | 1564800 | 1807920 | 2978400 | 0 | 0 | 0 | 0 | 1260360 | 1227307 | 1136643 | 354816 | 600000 | 484380 | 553440 | 815600 | 1106880 | 0 | 955980 | 164000 | 1800000 | 0 | 437547 | 100630 | 0 | 0 | 0 |  | 537600 | 287472 | 245201 | 258000 | 1713600 | 1155840 | 531360 | 543840 | 0 | 0 | 0 | 7322100 | 0 | 4435000 | 234181 | 2371430 | 674424 | 145440 | 0 | 1190473 | 0 | 390144 | 203309 | 399636 | 129420 | 367400 | 434610 | 2570880 | 2901120 | 0 | 345240 | 10100 | 1030000 | 835112 | 0 | 0 | 2692881 | 3516000 | 1372224 | 339840 | 0 | 5206480 | 0 | 0 | 240840 | 6839500 | 74448 | 0 | 464448 | 6077016 | 989705 | 680376 | 3561600 | 690336 | 2907360 | 93555 | 772800 | 3709920 | 3066109 | 9350000 | 2496000 | 2311200 | 2391153 | 31199 | 6463418 | 908131 | 1952064 | 940500 | 1097040 | 906240 | 9402100 | 2372160 | 266090 | 3879360 | 2480236 | 0 | 770760 | 0 | 1248960 | 1191240 |  | 22149090 | 0 | 6908256 | 0 | 1824000 | 0 | 0 | 0 | 184800 | 512768 | 674625 | 1323000 | 596854 | 727488 | 0 | 0 | 0 | 454960 | 287890 | 549472 | 0 | 336988 | 296242 | 789120 | 303702 | 494880 | 0 | 181800 | 0 | 0 | 4280600 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 63360 | 4411009 | 0 | 9497745 | 2028480 | 202379 | 2009568 | 1610352 | 2025686 | 0 | 51061 | 1996512 | 22281700 | 4942909 | 0 | 448800 | 17760 | 706320 | 2120832 |  | 184785755 | 97292008 | 282077763 | 86643093 | 22149090 | 46779876 | 3090604 | 85493804 | 26562300 | 1119980 | 1000 | 6491051 | 2570880 | 1176085 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6897275.84 | 2975571.76 | 0 | 0 | 8586000 |  | 0 | 5705986.5 | 3994191.81 | 18889728 | 29051844 | 14655666 | 8855589.12 | 0 | 0 | 22877376 | 25437434.4 | 48279864 | 0 | 0 | 0 | 0 | 16031779.2 | 16568644.5 | 15242382.63 | 266112 | 450000 | 0 | 0 | 0 | 18828028.8 | 0 | 258114.6 | 44280 | 3402000 | 0 | 7153893.45 | 104655.2 | 0 | 0 | 0 |  | 7015680 | 4795032.96 | 4173321.02 | 3485580 | 21728448 | 13373068.8 | 674827.2 | 1810987.2 | 0 | 0 | 0 | 8127531 | 0 | 5144600 | 302093.49 | 2893144.6 | 762099.12 | 216705.6 | 0 | 1988089.91 | 0 | 6737786.88 | 2734506.05 | 547501.32 | 97065 | 642950 | 325957.5 | 18458918.4 | 3162220.8 | 0 | 469526.4 | 160994 | 1411100 | 1102347.84 | 0 | 0 | 3096813.15 | 3762120 | 2662114.56 | 774835.2 | 0 | 5258544.8 | 0 | 0 | 476863.2 | 6839500 | 55836 | 0 | 9734830.08 | 82951268.4 | 20744216.8 | 14063371.92 | 48010368 | 14269245.12 | 40266936 | 1093657.95 | 7975296 | 50677507.2 | 40687266.43 | 8602000 | 30351360 | 33419952 | 30248085.45 | 0 | 75880527.32 | 9889546.59 | 20750440.32 | 12762585 | 14140845.6 | 10675507.2 | 8649932 | 30719472 | 3845000.5 | 49229078.4 | 28225085.68 | 0 | 10066125.6 | 0 | 18696931.2 | 15688630.8 |  | 66447270 | 0 | 7737246.72 | 0 | 18987840 | 0 | 0 | 0 | 3328248 | 9229824 | 9694361.25 | 1481760 | 1157896.76 | 7929619.2 | 0 | 0 | 0 | 7629679.2 | 5035196.1 | 8593742.08 | 0 | 5580521.28 | 5009452.22 | 10755705.6 | 5123452.74 | 1024401.6 | 0 | 137622.6 | 0 | 0 | 22644374 | 0 | 35150 | 0 | 0 | 0 | 0 | 0 | 1329292.8 | 5116770.44 | 0 | 9402767.55 | 27262771.2 | 4243887.63 | 23773189.44 | 23269586.4 | 25726212.2 | 0 | 564224.05 | 24237655.68 | 200758117 | 5041767.18 | 0 | 3321120 | 200865.6 | 8285133.6 | 32512354.56 |  | 1158617227.37 | 592609078.68 | 1751226306.05 | 95277480.06 | 66447270 | 53394470.91 | 64384844.35 | 1107437811.83 | 223402491 | 302394.6 | 35150 | 107935599.2 | 18458918.4 | 14149875.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 328 |  | 0 | 225 | 150 | 56 | 96 | 40 | 332 | 0 | 0 | 78 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 10 | 60 | 50 | 22 | 5 | 0 | 0 | 0 | 290 | 0 | 158 | 8 | 98 | 36 | 5 | 0 | 51 | 0 | 24 | 8 | 19 | 5 | 0 | 20 | 114 | 109 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 110 | 157 | 50 | 0 | 0 | 220 | 0 | 0 | 9 | 290 | 0 | 0 | 50 | 266 | 81 | 95 | 179 | 97 | 132 | 7 | 25 | 100 | 130 | 403 | 108 | 90 | 85 | 4 | 260 | 36 | 73 | 17 | 9 | 25 | 398 | 92 | 52 | 162 | 90 | 0 | 35 | 0 | 45 | 55 |  | 920 | 0 | 280 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 57 | 19 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 8 | 0 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 415 | 93 | 10 | 70 | 67 | 81 | 0 | 6 | 75 | 840 | 217 | 0 | 17 | 1 | 32 | 111 |  | 11624 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 270 | 96 | 0 | 0 | 348 | 0 | 0 | 225 | 150 | 81 | 96 | 55 | 337 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 59 | 51 | 10 | 77 | 50 | 22 | 24 | 0 | 0 | 0 | 290 | 0 | 210 | 8 | 100 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 19 | 6 | 32 | 21 | 126 | 140 | 0 | 17 | 0 | 44 | 41 | 0 | 0 | 110 | 157 | 60 | 50 | 0 | 206 | 0 | 0 | 10 | 280 | 16 | 0 | 20 | 278 | 40 | 100 | 181 | 98 | 114 | 0 | 50 | 200 | 100 | 402 | 108 | 105 | 105 | 0 | 278 | 36 | 87 | 114 | 116 | 65 | 398 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 63 | 55 |  | 922 | 0 | 275 | 0 | 84 | 0 | 0 | 0 | 27 | 32 | 40 | 56 | 26 | 48 | 0 | 0 | 0 | 43 | 29 | 82 | 0 | 34 | 32 | 43 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 200 | 0 | 414 | 94 | 47 | 113 | 89 | 101 | 0 | 0 | 113 | 900 | 218 | 0 | 17 | 0 | 0 | 96 |  | 13024 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 330 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 51 | 10 | 86 | 50 | 22 | 25 | 0 | 0 | 0 | 340 | 0 | 210 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 165 | 140 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 110 | 160 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 341 | 24 | 0 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 283 | 35 | 110 | 114 | 113 | 50 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 83 | 55 |  | 942 | 0 | 320 | 0 | 115 | 220 | 0 | 0 | 35 | 60 | 40 | 86 | 33 | 110 | 0 | 0 | 0 | 43 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 200 | 0 | 410 | 105 | 175 | 113 | 105 | 103 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 80 | 96 | 55 | 330 | 0 | 0 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 10 | 86 | 50 | 22 | 10 | 0 | 0 | 0 | 340 | 0 | 190 | 8 | 100 | 30 | 5 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 143 | 140 | 0 | 20 | 1.6 | 44 | 41 | 0 | 0 | 110 | 160 | 60 | 0 | 0 | 220 | 0 | 0 | 10 | 300 | 22 | 0 | 150 | 290 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 140 | 400 | 115 | 105 | 105 | 5 | 273 | 35 | 92 | 110 | 28 | 25 | 400 | 90 | 50 | 144 | 110 | 0 | 17 | 30 | 83 | 55 |  | 942 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 35 | 0 | 40 | 86 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 43 | 40 | 52 | 38 | 22 | 0 | 11 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 0 | 113 | 105 | 103 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 53 | 0 | 0 | 294 | 0 | 0 | 225 | 150 | 81 | 32 | 30 | 250 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 25 | 6 | 25 | 33 | 3 | 0 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 10 | 60 | 44 | 22 | 7 | 0 | 0 | 0 | 290 | 0 | 173 | 8 | 98 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 16 | 90 | 134 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 159 | 62 | 0 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 7 | 0 | 0 | 70 | 0 | 82 | 3 | 25 | 68 | 58 | 352 | 105 | 70 | 84 | 3 | 247 | 36 | 92 | 17 | 8 | 25 | 360 | 53 | 25 | 115 | 108 | 0 | 17 | 0 | 0 | 35 | 0 | 925 | 0 | 270 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 70 | 15 | 58 | 0 | 3 | 76 | 720 | 185 | 0 | 0 | 2 | 46 | 0 | 0 |  |  |  |  | 95076459 |  | 0
95076459
| Minimum Generation |  | 9931 | 8:00
| Highest Generation |  | 13024 | 19:30
| Day Peak Generation |  | 11624 | 12:00
| Evening Peak Generation |  | 13024 | 19:30
| HVDC Max Flow |  | 924 | 23:00
| HVDC EvPeak Flow |  | 922 | 19:30
| Load factor L.F |  | 90.24%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-26
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11624 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9258 | MW
Evening Peak Generation : |  | 13024 | MW Hour : | 19:30 | Available Max Generation : |  | 14906 | MW
E.P. Demand (at gen end) : |  | 13024 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13024 | MW Hour : | 19:30 | Reserve(Generation end) |  | 906 | MW
Total Gen. (MKWH) : |  | 282.0778 | System Load Factor : | 90.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 100 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-26
Actual : | 74.72 | Ft.(MSL) , | Rule curve : | 77.2 | Ft.( MSL )
Gas Consumed : | Total = | 1006.15 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 148671950.97
: |  | Coal : | 223402491 | Oil : | 1279793405.38 | Total : | 1651867847.35
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4986.5325 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1617.1191 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1576.8751 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1411.9018 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1287.5687 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1056.8332 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 517.3819 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 318.0259 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 776.7379 |  |  | 0 | 0%
Total | 0 |  | 13548.9761 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4,5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Ashuganj South-360 MW
8) Sirajganj Unit-1
9) Sikalbaha 225 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Keraniganj-Hasnabad 230 kV Ckt-2 was under shut down from 09:56 to 12:41 for D/W.
b) Bheramara-Rajbari 132 kV Ckt-2 was shut down 08:23 to 17:59 for D/W.
c) Rajbari-Faridpur 132 kV Ckt-2 was under shut down 08:29 to 18:53 for D/W.
d) Rajbari 132/33 kV T-2 transformer was shut down at 08:10 to 18:08 for D/W.
e) Madunaghat-Sikalbaha 132 kV Ckt was under shut down from 10:46 to 13:12 for D/W.
f) Manikganj 132/33 kV T-4 transformer was shut down at 11:19 to 13:35 for D/W.
g) Ponchagarh 132/33 kV T-1 transformer was under shut down from 12:09 to 12:54 due to energy
meter test.
h) Ponchagarh 132/33 kV T-2 transformer was under shut down from 13:01 to 13:22 due to energy
meter test.
i) Choddagram 132/33 T2 transformer was under shut down from 12:18 to 13:35 for C/M. | [5 empty] | About 25 MW power interruption occurred under
Choddagram S/S area from 12:18 to 13:25.
j) Rampura-Mogbazar 132 kV Ckt-2 was switched on at 16:07.
k) Kabirpur 132 kV main Bus was under shut down from 15:36 to 16:20 due to tempature of main Bus
isolator of 132/33 kV T2 was high.
l) Kabirpur 132/33 kV T2 transformer was under shut down from 15:06 to 16:26 due to loop changing
of 33 kV PBS feeder.
m) Cumilla(N) 132/33 kV T3 & T4 transformers tripped at 16:33 showing O/C relays & 33 kV breaker | [5 empty] | About 80 MW power interruption occurred under
bust of PDB Balutopa feeder and were switched on at 16:49,16:45 respectively. | [5 empty] | Cumilla(N) S/S area from 16:33 to 16:45.
n) Ghorasal-Bhulta 230 kV Ckt-2 was under shut down from 17:14 to 18:46 due to air leakage from
230 kV breaker at Ghorasal end.
o) Mongla 132/33 kV T1 transformer was under shut down from 19:43 to 21:06 due to red hot maintenance | [5 empty] | About 25 MW power interruption occurred under
at 33 kV R-phase isolator of Bus sectionalizer. | [5 empty] | Mongla S/S area from 19:43 to 21:06.
p) Sikalbaha-Dohazari 132 kV Ckt-1 was shut down from 06:33(26-05-2022) to 08:18 for C/M.
q) Bogura(O)-Naogaon 132 kV Ckt-1 was shut down at 06:25(26-05-22) due to red hot maint at Bogura end.
r) B.Baria 132/33 kV T-1 transformer was shut down at 00:08(26-05-22) to 00:48 due to red hot maint . | [5 empty] | About 40 MW power interruption occurred under
for red hot maint. | [5 empty] | B.Baria S/S area from 00:08 to 00:48.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6158282 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2237272 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7950000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5234850 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 81 | 1689600 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3598371 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 2192592 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1106088
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 354816
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1564800 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 337 | 7906776
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1807920 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1260360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2978400 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1227307
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1136643
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1084380 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 553440 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815600
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1106880 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 6077016 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 40 | 989705 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 680376
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 690336
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 2907360 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2311200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2372160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3879360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1191240
| Dhaka area Total |  |  |  | 5898 | 3552 | 77410130
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 1800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 437547
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 93555
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1155840
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1119980 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 100630 | HGPI
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2391153
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 287472 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 245201 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258000 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 772800 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 531360
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 543840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 77 | 1713600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 278 | 6463418 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 908131 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 87 | 1952064 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 65 | 906240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2480236 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1222 | 24192266
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4435000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7322100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 674424 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 145440 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 234181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1190473
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 3066109 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 390144 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2371430 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3709920
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 399636 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 129420 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2570880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 367400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 203309 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 434610 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 464448 | Low Demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 940500
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 116 | 1097040
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 770760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 63 | 1248960 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1576 | 32166184
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 2901120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 345240
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 181 | 3561600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2496000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 266090
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 537600
| Mymensingh Area Total |  |  |  | 622 | 470 | 10117750
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1030000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 835112 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2692881 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3516000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1372224 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 339840 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 5206480
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 74448 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6839500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9350000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 398 | 9402100
| Sylhet Area Total |  |  |  | 2477 | 1774 | 40899425
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22149090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 84 | 1824000 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 184800 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 32 | 512768 | Low Demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 275 | 6908256 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 674625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 63360 | Low Demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 2028480 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 1610352 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 706320
| Khulna Area Total |  |  |  | 2384 | 1573 | 36662051
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 727488 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 26 | 596854 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 56 | 1323000 | Gas shortage+ST under maintenance
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 22281700 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 218 | 4942909
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 448800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1265 | 30320751
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 454960 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 29 | 287890 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 336988 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 296242 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 200 | 4411009 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9497745
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 303702 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 494880
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 181800
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 789120
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 549472 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 47 | 202379 | Low Demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2009568
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1996512
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17760
| Rajshahi Area Total |  |  |  | 2129 | 1220 | 21830027
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4280600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 1000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 2025686 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51061
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 96 | 2120832 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 372 | 8479179
| Total |  |  |  | 21584 | 13024 | 282077763
| Eastern Grid Total |  |  |  | 14393 | 8594 | 184785755
| Western Grid Total |  |  |  | 7191 | 4430 | 97292008
| National Grid Total |  |  |  | 21584 | 13024 | 282077763
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-25
(a) ENTIRE EASTERN GRID : |  | 8900.39 | MW | (b) ENTIRE WESTERN GRID : |  | 3697.66 | MW
i) Dhaka area |  | 4797.59 | MW | i) Khulna area |  | 1487.76 | MW
ii) Chittagong area |  | 1444.8 | MW | ii) Rajshahi area |  | 1109.9 | MW
iii) Comilla area |  | 1099 | MW | iii) Barisal area |  | 339 | MW
iv) Mymensingh area |  | 1052 | MW | iv) Rangpur area |  | 761 | MW
v) Sylhet area |  | 507 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12598.05 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 31 | 00:00 | Hasnabad | 73 | 21:00 | Palashbari | 126 | 19:00
Agargaon | 93 | 11:00 | Hathazari | 98 | 21:00 | Panchagarh | 59 | 00:00
Agrabad | 94 | 18:30 | Ishurdi | 74 | 20:00 | Patuakhali | 133 | 00:00
AKS | 11 | 01:00 | Jaldhaka | 60 | 19:30 | PHP | 10 | 17:00
AKSML | 129 | 22:00 | Jamalpur | 148 | 20:00 | Purbachal | 20 | 11:00
Amnura | 32 | 00:00 | Jashore | 126 | 19:00 | Purbasadipur | 102 | 13:00
Ashuganj | 37 | 05:00 | Jhenaidah | 112 | 00:00 | Rahim | 22 | 18:00
Bagerhat | 114 | 20:00 | Joydebpur | 192 | 20:00 | Rajbari | 68 | 19:30
Bakulia | 127 | 19:00 | Joypurhat | 61 | 00:00 | Rajendrapur | 112 | 19:30
Banani | 47 | 10:00 | Juldah | 23 | 10:00 | Rajshahi | 151 | 00:00
Bangabhaban | 22 | 10:00 | Kabirpur | 261 | 19:00 | Rajshahi | 35 | 00:00
Barapukuria | 50 | 00:00 | Kachua | 70 | 23:00 | Ramganj | 90 | 20:00
Barguna | 22 | 00:00 | Kallyanpur | 108 | 00:00 | Rampur | 19 | 00:00
Barishal | 119 | 22:00 | Kalurghat | 6 | 12:00 | Rangamati | 14 | 19:00
Barishal | 74 | 00:00 | Kamrangirchar | 70 | 18:30 | Rangpur | 152 | 19:30
Baroaulia | 73 | 23:00 | Kaptai | 4.5 | 19:00 | Ruppur | 4.6 | 15:00
Baroirhat | 48 | 15:00 | Kazla | 86 | 00:00 | Saidpur | 100 | 19:30
Bashundhara | 164 | 11:00 | Keranigonj | 78 | 00:00 | Satkhira | 118 | 00:00
BashundharaCement | 13 | 17:00 | Khagrachori | 22 | 13:00 | Satmasjid | 95 | 00:00
Beanibazar | 62 | 21:00 | Khulna | 96 | 20:00 | Savar | 181 | 10:00
Benapole | 60 | 00:00 | Khulshi | 192 | 16:00 | Shahjadpur | 92 | 00:00
Bhaluka | 132 | 19:30 | Kishoreganj | 136 | 21:00 | Shahjibazar | 105 | 00:00
Bhandaria | 60 | 22:00 | Kodda | 316 | 18:30 | Shahmirpur | 48 | 20:00
Bhangura | 34 | 19:30 | KSRM | 27.25 | 17:00 | Shariatpur | 74 | 00:00
Bheramara(GK) | 56 | 00:00 | Kulaura | 44 | 19:00 | Sherpur | 144 | 00:00
Bhulta | 241 | 00:00 | Kurigram | 66 | 19:30 | Shikalbaha | 32 | 00:00
Bog-Sherpur | 60 | 00:00 | Kushtia | 130 | 20:00 | Shitalakhya | 122 | 12:00
Bogura | 164 | 20:00 | Lalbag | 94 | 12:00 | Sholosohor | N/A | N/A
Borhanuddin | 43 | 00:00 | Lalmonirhat | 46 | 20:00 | Shyampur | 188 | 11:00
Brahmanbaria | 150 | 21:00 | Madanganj | 190 | 19:30 | Siddhirganj | 114 | 12:00
BSRM | 162 | 12:00 | Madaripur | 97 | 00:00 | Sirajganj | 105 | 20:00
Cantonment | 148 | 11:00 | Madartek | 83 | 00:00 | Sonargaon | 84 | 22:00
Chandpur | 64 | 21:00 | Madunaghat | 55 | 19:30 | Sreemongol | 64 | 19:00
Chandraghona | 34 | 20:00 | Magura | 62 | 20:00 | Srinagar | 43 | 01:00
Chapai | 65 | 00:00 | Mahasthangarh | 68 | 00:00 | SSM | 18 | 01:00
Charsaidpur | 37 | 01:00 | Manikganj | 84 | 00:00 | Sunamganj | 51 | 22:00
Chauddagram | 48 | 20:00 | Maniknagar | 79 | 12:00 | Sylhet | 154 | 19:00
Chhatak | 30 | 20:00 | Matarbari | 40 | 21:00 | Tangail | 213 | 00:00
Chowmuhani | 202 | 22:00 | Matuail | 66 | 10:00 | Thakurgaon | 80 | 00:00
Chuadanga | 114 | 00:00 | Millgate | 60 | 19:00 | TK | 30 | 21:00
Coxsbazar | 121 | 19:30 | Mirpur | 127.5 | 12:00 | Tongi | 129 | 12:00
Cumilla(N) | 151 | 00:00 | Mirsorai | N/A | N/A | Ullon | 44 | 19:00
Cumilla(S) | 158 | 19:30 | Mithapukur | 34 | 19:30 | Uttara | 79 | 10:00
Daudkandi | 152 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 17 | 00:00
Dhaka | 38 | 11:00 | Mogbazar | 114 | 11:00 | Zigatola | 43 | 00:00
Dhamrai | 116 | 00:00 | Mongla | 40 | 16:00
Dhanmondi | 157 | 12:00 | Motijheel | 37 | 12:00
Dohazari | 92 | 19:30 | Munshiganj | 104 | 00:00
Faridpur | 138 | 00:00 | Mymensingh | 224 | 20:00
Fatullah | 67 | 12:00 | Naogaon | 114 | 00:00
Fenchuganj | 46 | 00:00 | Narail | 56 | 20:00
Feni | 125 | 19:00 | Narinda | 75 | 12:00
Ghorashal | 53 | 00:00 | Narshingdi | 190 | 00:00
Goalpara | 29 | 19:30 | Natore | 124 | 00:00
Gollamari | 64 | 21:00 | Nawabganj | 53.2 | 00:00
Gopalganj | 103.2 | 21:00 | Netrakona | 118 | 21:00
GPH | 93 | 13:00 | New | 78 | 09:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 4:00 | 401 | 11:00 | Kaliakoir | 396 | 0.77083 | 381 | 0.41667
| Bheramara | 398 | 8:00 | 392 | 15:00 | Bhulta | 392 | 0.79167 | 374 | 0.45833
| Ashuganj(N) | 399 | 1:00 | 381 | 10:00 | Gopalganj | 420 | 0.625 | 406 | 0.041667
| Payra | 421 | 18:30 | 415 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 237 | 6:00 | 221 | 15:00
| Ishurdi | 235 | 6:00 | 228 | 11:00 | Megnaghat | 231 | 5:00 | 222 | 11:00
| Ashuganj | 240 | 1:00 | 227 | 22:00 | Fenchuganj | 241 | 1:00 | 234 | 11:00
| Serajganj | 236 | 6:00 | 230 | 1:00 | Siddhirganj | 230 | 4:00 | 218 | 11:00
| Baghabari | 232 | 8:00 | 227 | 1:00 | Maniknagar | 228 | 4:00 | 216 | 11:00
| Barapukuria | 230 | 6:00 | 217 | 1:00 | Agargaon | 228 | 18:00 | 215 | 11:00
| Bogra | 232 | 6:00 | 221 | 1:00 | Barisal | 243 | 18:00 | 235 | 1:00
| Rajshahi | 242 | 18:30 | 226 | 15:00 | Bhola 225 MW | 245 | 16:00 | 235 | 1:00
| Khulna South | 238 | 19:30 | 226 | 12:00 | AKSML | 237 | 6:00 | 221 | 12:00
| Rampura | 229 | 5:00 | 217 | 11:00 | BSRM | 234 | 6:00 | 220 | 12:00
| Haripur | 227 | 1:00 | 220 | 9:00 | Bibiyana | 242 | 4:00 | 233 | 11:00
| Hasnabad | 228 | 1:00 | 214 | 11:00 | Bhulta | 231 | 20:00 | 219 | 11:00
| Shyampur | 228 | 1:00 | 216 | 11:00 | Ashuganj (S) | 237 | 3:00 | 227 | 11:00
| Aminbazar | 229 | 1:00 | 220 | 2:00 | Kaliakoir | 231 | 3:00 | 218 | 11:00
| Tongi | 229 | 4:00 | 219 | 15:00 | GPH | 237 | 3:00 | 222 | 12:00
| Comilla (N) | 231 | 3:00 | 219 | 11:00 | Jhenaidah | 232 | 18:30 | 221 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 01:00 | 127 | 11:00 | Manikganj | 135 | 04:00 | 124 | 17:00
| Agargaon | 133 | 04:00 | 123 | 11:00 | Maniknagar | 134 | 01:00 | 125 | 11:00
| Agrabad | 138 | 01:00 | 127 | 12:00 | Matarbari | 130 | 05:00 | 117 | 02:00
| AKS | 138 | 06:00 | 125 | 12:00 | Matuail | 134 | 20:00 | 127 | 09:00
| Aminbazar | 134 | 03:00 | 122 | 02:00 | Millgate | 135 | 01:00 | 125 | 11:00
| Amnura | 136 | 18:00 | 125 | 15:00 | Mirpur | 134 | 03:00 | 123 | 11:00
| Ashuganj | 136 | 07:00 | 133 | 01:00 | Mithapukur | 133 | 09:00 | 125 | 00:00
| Bagerhat | 134 | 07:00 | 128 | 00:00 | Modern | 138 | 00:00 | 128 | 11:00
| Bakulia | 138 | 00:00 | 135 | 04:00 | Mogbazar | 136 | 04:00 | 126 | 11:00
| Banani | 135 | 01:00 | 125 | 09:00 | Mongla | 134 | 17:00 | 127 | 00:00
| Bangabhaban | 134 | 01:00 | 124 | 11:00 | Motijheel | 134 | 01:00 | 124 | 11:00
| Barapukuria | 136 | 04:00 | 127 | 07:00 | Munshiganj | 138 | 01:00 | 131 | 08:00
| Barguna | 138 | 06:00 | 129 | 23:00 | Mymensingh | 133 | 13:00 | 119 | 19:00
| Barishal | 141 | 18:00 | 129 | 12:00 | Naogaon | 134 | 18:00 | 121 | 00:00
| Barishal | 141 | 18:00 | 133 | 00:00 | Narail | 135 | 18:00 | 129 | 00:00
| Baroaulia | 140 | 01:00 | 127 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 135 | 17:00 | 124 | 15:00 | Narshingdi | 130 | 18:30 | 123 | 09:00
| Bashundhara | 136 | 03:00 | 126 | 09:00 | Natore | 136 | 18:30 | 129 | 00:00
| BashundharaCement | 136 | 00:00 | 130 | 09:00 | Nawabganj | 138 | 01:00 | 128 | 11:00
| Beanibazar | 131 | 06:00 | 127 | 01:00 | Netrakona | 131 | 07:00 | 117 | 19:00
| Benapole | 136 | 21:00 | 125 | 11:00 | New | 135 | 00:00 | 126 | 11:00
| Bhaluka | 131 | 10:00 | 116 | 19:00 | Niamatpur | 135 | 18:00 | 117 | 00:00
| Bhandaria | 139 | 18:30 | 127 | 00:00 | Noapara | 137 | 18:00 | 130 | 12:00
| Bhangura | 139 | 05:00 | 134 | 11:00 | Pabna | 136 | 18:00 | 131 | 00:00
| Bheramara | 137 | 18:30 | 133 | 00:00 | Palashbari | 133 | 10:00 | 122 | 00:00
| Bheramara(GK) | 140 | 18:00 | 134 | 00:00 | Panchagarh | 137 | 04:00 | 120 | 07:00
| Bhulta | 126 | 13:00 | 122 | 10:00 | Patuakhali | 136 | 06:00 | 131 | 00:00
| Bog-Sherpur | 136 | 06:00 | 127 | 00:00 | PHP | 135 | 18:30 | 124 | 11:00
| Bogura | 136 | 06:00 | 131 | 01:00 | Purbachal | 137 | 05:00 | 124 | 11:00
| Bogura | 137 | 18:30 | 129 | 01:00 | Purbasadipur | 136 | 10:00 | 124 | 08:00
| Brahmanbaria | 132 | 15:00 | 127 | 00:00 | Rahim | 134 | 00:00 | 129 | 09:00
| Cantonment | 132 | 03:00 | 121 | 11:00 | Rajbari | 138 | 22:00 | 130 | 00:00
| Chandpur | 140 | 15:00 | 132 | 11:00 | Rajendrapur | 134 | 14:00 | 122 | 09:00
| Chandraghona | 138 | 02:00 | 129 | 11:00 | Rajshahi | 133 | 18:00 | 126 | 15:00
| Chapai | 135 | 17:00 | 126 | 15:00 | Rajshahi | 132 | 17:00 | 125 | 13:00
| Charsaidpur | 138 | 00:00 | 132 | 12:00 | Ramganj | 136 | 00:00 | 126 | 12:00
| Chauddagram | 135 | 18:00 | 128 | 11:00 | Rampur | 138 | 02:00 | 129 | 11:00
| Chhatak | 132 | 06:00 | 126 | 22:00 | Rampura | 136 | 05:00 | 126 | 11:00
| Chowmuhani | 135 | 17:00 | 123 | 11:00 | Rangamati | 139 | 06:00 | 129 | 12:00
| Chuadanga | 133 | 18:30 | 124 | 00:00 | Rangpur | 133 | 10:00 | 124 | 00:00
| Coxsbazar | 129 | 06:00 | 114 | 23:00 | Ruppur | 138 | 18:00 | 133 | 13:00
| Cumilla(N) | 136 | 06:00 | 127 | 11:00 | Saidpur | 132 | 10:00 | 123 | 07:00
| Cumilla(S) | 137 | 18:00 | 128 | 14:00 | Satkhira | 135 | 07:00 | 127 | 12:00
| Daudkandi | 135 | 00:00 | 125 | 11:00 | Satmasjid | 132 | 02:00 | 122 | 11:00
| Dhaka | 137 | 05:00 | 127 | 10:00 | Savar | 135 | 06:00 | 124 | 11:00
| Dhamrai | 134 | 05:00 | 124 | 11:00 | Shahjadpur | 140 | 06:00 | 135 | 00:00
| Dhanmondi | 134 | 00:00 | 126 | 11:00 | Shahjibazar | 134 | 13:00 | 130 | 22:00
| Dohazari | 134 | 01:00 | 127 | 11:00 | Shahmirpur | 141 | 06:00 | 130 | 12:00
| Faridpur | 137 | 22:00 | 130 | 03:00 | Shariatpur | 138 | 10:00 | 131 | 00:00
| Fatullah | 135 | 00:00 | 127 | 11:00 | Sherpur | 138 | 12:00 | 125 | 19:00
| Fenchuganj | 137 | 07:00 | 132 | 01:00 | Shikalbaha | 140 | 07:00 | 131 | 11:00
| Feni | 137 | 18:00 | 126 | 15:00 | Shikalbaha | 139 | 02:00 | 131 | 15:00
| Ghorashal | 139 | 01:00 | 137 | 00:00 | Shitalakhya | 138 | 02:00 | 130 | 11:00
| Goalpara | 138 | 18:00 | 131 | 12:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 18:30 | 132 | 11:00 | Shyampur | 135 | 01:00 | 127 | 09:00
| Gopalganj | 141 | 22:00 | 134 | 09:00 | Shyampur | 136 | 00:00 | 127 | 11:00
| Gopalganj_I | 140 | 18:30 | 135 | 01:00 | Siddhirganj | 135 | 01:00 | 127 | 10:00
| Gulshan | 136 | 05:00 | 126 | 11:00 | Sirajganj | 137 | 18:30 | 129 | 00:00
| Halishahar | 139 | 01:00 | 128 | 12:00 | Sonargaon | 135 | 20:00 | 127 | 11:00
| Haripur | 134 | 00:00 | 129 | 09:00 | Sreemongol | 135 | 07:00 | 130 | 01:00
| HaripurSBU | 139 | 19:30 | 127 | 11:00 | Srinagar | 137 | 04:00 | 127 | 11:00
| Hasnabad | 138 | 23:00 | 132 | 09:00 | SSM | 140 | 01:00 | 128 | 12:00
| Hathazari | 140 | 18:00 | 131 | 15:00 | Sunamganj | 130 | 06:00 | 124 | 22:00
| Ishurdi | 138 | 18:30 | 133 | 00:00 | Sylhet | 132 | 07:00 | 130 | 00:00
| Jaldhaka | 132 | 10:00 | 120 | 07:00 | Tangail | 133 | 13:00 | 123 | 19:00
| Jamalpur | 140 | 10:00 | 125 | 19:00 | Thakurgaon | 137 | 04:00 | 121 | 07:00
| Jashore | 135 | 18:30 | 127 | 11:00 | TK | 139 | 06:00 | 130 | 11:00
| Jhenaidah | 138 | 18:30 | 132 | 00:00 | Tongi | 136 | 04:00 | 130 | 09:00
| Jhenaidah | 138 | 18:00 | 132 | 00:00 | Ullon | 136 | 05:00 | 126 | 11:00
| Joydebpur | 141 | 04:00 | 134 | 09:00 | Uttara | 133 | 02:00 | 125 | 10:00
| Joypurhat | 135 | 18:30 | 117 | 00:00 | UttaraNew | 134 | 01:00 | 124 | 11:00
| Juldah | 139 | 06:00 | 130 | 12:00 | Zigatola | 137 | 01:00 | 126 | 11:00
| Kabirpur | 135 | 02:00 | 123 | 09:00
| Kachua | 137 | 18:00 | 130 | 11:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 135 | 04:00 | 126 | 11:00
| Kalurghat | 139 | 01:00 | 129 | 15:00
| Kamrangirchar | 137 | 00:00 | 130 | 09:00
| Kaptai | 137 | 00:00 | 130 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 238 | 8021 | 3855 | 11876 |  |  |  | QF-LDC-11
0:30 | 169 | 8239.5 | 4146.5 | 12386 | Date: | 2022-05-25
1:00 | 100 | 8458 | 4438 | 12896
1:30 | 163 | 8220.5 | 4414 | 12634.5
2:00 | 226 | 7983 | 4390 | 12373
2:30 | 218 | 7918.5 | 4326 | 12244.5 | [5 empty] | Gen. at Eve. Peak | 13024 | 13024 MW (19:30 )
3:00 | 210 | 7854 | 4262 | 12116 | [6 empty] | 19:30
3:30 | 243 | 7794.5 | 4204 | 11998.5 | [5 empty] | Gen. at Day Peak | 11624 | 11624 MW (12:00 )
4:00 | 276 | 7735 | 4146 | 11881 | [6 empty] | 12:00
4:30 | 296 | 7578 | 4034.5 | 11612.5 | [5 empty] | Highest Generation | 13024
5:00 | 316 | 7421 | 3923 | 11344 | [6 empty] | 19:30
5:30 | 366 | 7116 | 3733.5 | 10849.5
6:00 | 416 | 6811 | 3544 | 10355
6:30 | 401.5 | 6715 | 3510.5 | 10225.5
7:00 | 387 | 6619 | 3477 | 10096
7:30 | 454.5 | 6545.5 | 3468 | 10013.5
8:00 | 522 | 6472 | 3459 | 9931
8:30 | 591 | 6634 | 3522 | 10156
9:00 | 660 | 6796 | 3585 | 10381
9:30 | 643 | 7079.5 | 3665 | 10744.5
10:00 | 626 | 7363 | 3745 | 11108
10:30 | 627 | 7400.5 | 3782 | 11182.5
11:00 | 628 | 7438 | 3819 | 11257
11:30 | 563.5 | 7623 | 3817.5 | 11440.5
12:00 | 499 | 7808 | 3816 | 11624
12:30 | 469.5 | 7741.5 | 3842.5 | 11584
13:00 | 440 | 7675 | 3869 | 11544
13:30 | 445 | 7491.5 | 3847.5 | 11339
14:00 | 450 | 7308 | 3826 | 11134
14:30 | 521 | 7359.5 | 3888 | 11247.5
15:00 | 592 | 7411 | 3950 | 11361
15:30 | 616 | 7432.5 | 3924 | 11356.5
16:00 | 640 | 7454 | 3898 | 11352
16:30 | 685 | 7349 | 3831.5 | 11180.5
17:00 | 730 | 7244 | 3765 | 11009
17:30 | 660 | 7302.5 | 3653.5 | 10956
18:00 | 590 | 7361 | 3542 | 10903
18:30 | 546 | 7839.5 | 3763 | 11602.5
19:00 | 502 | 8318 | 3984 | 12302
19:30 | 488 | 8594 | 4430 | 13024
20:00 | 510 | 8533 | 4427 | 12960 |  |  |  | Executive Engineer
20:30 | 570 | 8441 | 4440 | 12881 |  |  |  | Network Operation Division
21:00 | 630 | 8349 | 4453 | 12802
21:30 | 595 | 8352 | 4322.5 | 12674.5
22:00 | 560 | 8355 | 4192 | 12547 |  |  |  |  | Page 6 of 7
22:30 | 474 | 8329 | 4097 | 12426
23:00 | 388 | 8303 | 4002 | 12305
23:30 | 313 | 8162 | 3928.5 | 12090.5
24:00 | 238 | 8021 | 3855 | 11876
13024 MW (19:30 )
11624 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-25 |  | Energy |  | 282077763
[13 empty] | 2022-05-25 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3724 | 924 | 2041 | 0 | 3773 | 1045 | 40 | 0 | 221 | 108 | 0 | 0
0:30 | 3667 | 916.5 | 2022.5 | 338 | 3867.5 | 1115 | 39.5 | 0 | 313 | 107 | 0 | 0 | Date: | 2022-05-25
1:00 | 3610 | 909 | 2004 | 676 | 3962 | 1185 | 39 | 0 | 405 | 106 | 0 | 0
1:30 | 3592.5 | 909.5 | 1994 | 470.5 | 3931.5 | 1195 | 39.5 | 0 | 396 | 106 | 0 | 0 | [7 empty] | Total Energy | 282.0778 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3575 | 910 | 1984 | 265 | 3901 | 1205 | 40 | 0 | 387 | 106 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3582.5 | 909.5 | 1997 | 157 | 3914.5 | 1170 | 40 | 0 | 368 | 106 | 0 | 0 | [7 empty] | Energy Requirement | 282.0778
3:00 | 3590 | 909 | 2010 | 49 | 3928 | 1135 | 40 | 0 | 349 | 106 | 0 | 0
3:30 | 3600 | 909 | 1989.5 | 24.5 | 3897 | 1120 | 40 | 0 | 312.5 | 106 | 0 | 0 | [5 empty] | Shortage
4:00 | 3610 | 909 | 1969 | 0 | 3866 | 1105 | 40 | 0 | 276 | 106 | 0 | 0
4:30 | 3601 | 909 | 1985.5 | 0 | 3665 | 1105 | 40 | 0 | 204 | 103 | 0 | 0
5:00 | 3592 | 909 | 2002 | 0 | 3464 | 1105 | 40 | 0 | 132 | 100 | 0 | 0
5:30 | 3534.5 | 909 | 1935.5 | 0 | 3161 | 1050 | 40 | 0 | 123.5 | 93 | 3 | 0
6:00 | 3477 | 909 | 1869 | 0 | 2858 | 995 | 40 | 0 | 115 | 86 | 6 | 0
6:30 | 3491.5 | 909 | 1872 | 0 | 2722.5 | 970 | 40 | 0 | 106.5 | 88 | 26 | 0 |  |  |  | Coal
7:00 | 3506 | 909 | 1875 | 0 | 2587 | 945 | 40 | 0 | 98 | 90 | 46 | 0
7:30 | 3459.5 | 909.5 | 1867.5 | 0 | 2556.5 | 930 | 40 | 0 | 98 | 93 | 59.5 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3413 | 910 | 1860 | 0 | 2526 | 915 | 40 | 0 | 98 | 96 | 73 | 0
8:30 | 3487 | 909.5 | 1911.5 | 0 | 2602.5 | 925 | 40 | 0 | 98 | 101 | 81.5 | 0
9:00 | 3561 | 909 | 1963 | 0 | 2679 | 935 | 40 | 0 | 98 | 106 | 90 | 0
9:30 | 3554.5 | 911 | 1967.5 | 122 | 2870 | 945 | 40 | 0 | 115 | 108 | 111.5 | 0
10:00 | 3548 | 913 | 1972 | 244 | 3061 | 955 | 40 | 0 | 132 | 110 | 133 | 0
10:30 | 3570.5 | 914.5 | 1958 | 162 | 3212.5 | 950 | 40 | 0 | 132 | 113 | 130 | 0
11:00 | 3593 | 916 | 1944 | 80 | 3364 | 945 | 40 | 0 | 132 | 116 | 127 | 0
11:30 | 3602.5 | 918 | 1948.5 | 206.5 | 3370 | 980 | 40 | 0 | 145 | 115 | 115 | 0
12:00 | 3612 | 920 | 1953 | 333 | 3376 | 1015 | 40 | 0 | 158 | 114 | 103 | 0
12:30 | 3594.5 | 921 | 1921 | 294 | 3387 | 1010 | 40 | 0 | 181.5 | 114 | 121 | 0
13:00 | 3577 | 922 | 1889 | 255 | 3398 | 1005 | 40 | 0 | 205 | 114 | 139 | 0
13:30 | 3577 | 922 | 1889 | 255 | 3398 | 1005 | 40 | 0 | 205 | 114 | 139 | 0
14:00 | 3577 | 922 | 1889 | 255 | 3398 | 1005 | 40 | 0 | 205 | 114 | 139 | 0
14:30 | 3562.5 | 921.5 | 1935.5 | 127.5 | 3403 | 1005 | 40 | 0 | 214.5 | 106 | 137 | 0
15:00 | 3548 | 921 | 1982 | 0 | 3408 | 1005 | 40 | 0 | 224 | 98 | 135 | 0
15:30 | 3571.5 | 921.5 | 1954.5 | 0 | 3399 | 1015 | 40 | 0 | 250 | 99 | 106 | 0
16:00 | 3595 | 922 | 1927 | 0 | 3390 | 1025 | 40 | 0 | 276 | 100 | 77 | 0
16:30 | 3483 | 921.5 | 1868.5 | 35.5 | 3310.5 | 990 | 40 | 0 | 317.5 | 99 | 59 | 0
17:00 | 3483 | 921 | 1810 | 71 | 3231 | 955 | 40 | 0 | 359 | 98 | 41 | 0
17:30 | 3429 | 921.5 | 1726.5 | 135.5 | 3264.5 | 930 | 40 | 0 | 385.5 | 101 | 22.5 | 0
18:00 | 3375 | 922 | 1643 | 200 | 3298 | 905 | 40 | 0 | 412 | 104 | 4 | 0
18:30 | 3524 | 922 | 1821 | 260.5 | 3524 | 915 | 57.5 | 0 | 470.5 | 106 | 2 | 0
19:00 | 3673 | 922 | 1999 | 321 | 3750 | 925 | 75 | 0 | 529 | 108 | 0 | 0
19:30 | 3757 | 922 | 2037 | 315 | 4161 | 1075 | 75 | 0 | 556 | 126 | 0 | 0
20:00 | 3753 | 922 | 2013 | 213 | 4181 | 1095 | 75 | 0 | 584 | 124 | 0 | 0
20:30 | 3755.5 | 921.5 | 2028.5 | 106.5 | 4214 | 1110 | 75 | 0 | 553 | 117 | 0 | 0
21:00 | 3758 | 921 | 2044 | 0 | 4247 | 1125 | 75 | 0 | 522 | 110 | 0 | 0
21:30 | 3756 | 921 | 2051 | 0 | 4220 | 1075 | 74.5 | 0 | 467 | 110 | 0 | 0
22:00 | 3754 | 921 | 2058 | 0 | 4193 | 1025 | 74 | 0 | 412 | 110 | 0 | 0
22:30 | 3739.5 | 922.5 | 2060 | 0 | 4135 | 1030 | 73.5 | 0 | 356.5 | 109 | 0 | 0
23:00 | 3725 | 924 | 2062 | 0 | 4077 | 1035 | 73 | 0 | 301 | 108 | 0 | 0
23:30 | 3724.5 | 924 | 2051.5 | 0 | 3925 | 1040 | 56.5 | 0 | 261 | 108 | 0 | 0 | Max Temp. in Dhaka |  | 32.8° C
24:00 | 3724 | 924 | 2041 | 0 | 3773 | 1045 | 40 | 0 | 221 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 955980
2 | Karnaphuli Hydro PP Unit-4 & 5 | [19 empty] | 35 | 35 | 35 | 35 | 34 | 33 | 0 | 164000
3 | Chattogram TPP-1 |  |  | 0 | 5 | 40 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 0 |  |  |  |  | 1 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 437547
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 5 | 8 | 19 | 0 | 7 | 5 | 10 | 13 | 7 | 3 | 0 | [8 empty] | 93555
6 | Sikalbaha 225MW CCPP (Gas) | 20 | 0 | [23 empty] | 0 | 100630
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 34 | 0 | 245201
12 | Hathazari 100 MW peaking PP | [13 empty] | 6 | 22 | 28 | 36 | 51 |  | 51 | 59 | 59 | 52 | 0 |  |  | 287472
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 96 | 68 | 68 | 81 | 85 | 85 | 85 | 88 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2391153
| Daudkandi 200 MW PP (B.Trac) | 170 | 40 | 0 | [6 empty] | 20 | 20 | 50 | 15 | 0 | [5 empty] | 50 | 20 | 20 |  |  |  |  | 464448
14 | Titas 50 MW Peaking PP | 32 | 32 | 32 | 0 | [6 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 30 | 32 |  | 32 | 32 | 32 |  |  |  | 0 | 390144
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 337 | 336 | 337 | 336 | 335 | 280 | 280 | 280 | 335 | 335 | 332 | 332 | 337 | 326 | 336 | 337 | 337 | 335 |  | 337 | 337 | 337 | 337 | 335 | 335 | 335 | 7906776
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 293 | 291 | 293 | 230 | 195 | 145 | 145 | 145 | 218 | 258 | 266 | 290 | 280 | 280 | 230 | 230 | 195 |  | 238 | 278 | 280 | 278 | 278 | 275 | 278 | 6077016
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 234181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 190 | 190 | 190 | 280 | 280 | 280 | 280 | 280 | 280 | 200 | 200 |  | 234 | 270 | 280 | 280 | 280 | 280 | 280 | 6158282
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 29 | 32 | 36 | 36 | 34 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 674424
33 | Ashuganj 225 MW CCPP | 184 | 186 | 186 | 190 | 190 | 189 | 190 | 185 | 193 | 190 | 174 | 158 | 158 | 160 | 146 | 165 | 180 | 152 |  | 213 | 210 | 207 | 206 | 208 | 203 | 196 | 4435000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7322100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 145440
36 | Chandpur 150 MW CCPP | 99 | 100 | 100 | 100 | 102 | 100 | 101 | 99 | 103 | 103 | 98 | 98 | 100 | 102 | 101 | 98 | 100 | 100 |  | 100 | 100 | 99 | 100 | 102 | 100 | 102 | 2371430
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5234850
41 | Haripur 360MW CCPP(HPL) | 338 | 338 | 339 | 338 | 337 | 298 | 299 | 298 | 326 | 331 | 332 | 328 | 329 | 351 | 342 | 342 | 342 | 333 |  | 348 | 348 | 342 | 344 | 342 | 342 | 342 | 7950000
42 | RPCL 210MW CCPP | 129 | 132 | 131 | 134 | 134 | 138 | 137 | 133 | 111 | 111 | 106 | 109 | 102 | 102 | 106 | 110 | 110 | 111 |  | 141 | 140 | 140 | 139 | 138 | 139 | 139 | 2901120
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 3 | 16 | 15 | 9 | 22 | 17 | 52 | 19 | 26 | 37 | 11 | 8 | 1 | [8 empty] | 266090
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 43 | 43 | 44 | 44 | 1030000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 835112
46 | Shajibazar 330 MW CCPP | 158 | 160 | 158 | 158 | 158 | 158 | 157 | 158 | 159 | 158 | 157 | 157 | 158 | 160 | 157 | 158 | 157 | 158 |  | 158 | 157 | 157 | 159 | 159 | 159 | 158 | 3516000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 60 | 50 | 55 | 50 | 50 | 55 | 58 | 58 | 58 | 58 |  | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 1372224
48 | Shahjibazar 86MW PP (Shahjibazar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 339840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 219 | 220 | 220 | 220 | 220 | 192 |  | 206 | 206 | 206 | 211 | 218 | 210 | 220 | 5206480
51 | Sylhet 20 MW GTPP | [17 empty] | 0
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 9 | 10 | 10 |  | 9 | 10 | 9 | 10 | 10 | 10 | 10 | 240840
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | [19 empty] | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 74448
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 255 | 280 | 270 | 270 | 260 | 270 | 270 | 295 | 305 | 275 | 290 | 270 | 260 | 310 | 280 | 260 | 260 |  | 270 | 280 | 270 | 260 | 290 | 300 | 290 | 6839500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 360 | 360 | 360 | 400 | 400 | 388 | 398 | 390 | 360 | 393 | 400 | 398 | 350 |  | 397 | 398 | 400 | 400 | 400 | 400 | 400 | 9402100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 35 | 17 |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 1136643
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 3 | 18 | 24 | 24 | 24 | 24 | 18 |  | 23 | 24 | 24 | 24 | 24 | 24 | 13 | 537600
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531360
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 15 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 354816
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 17 | 17 | 0 | 14 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 345240
63 | Impoprt (Tripura) | 106 | 106 | 106 | 106 | 100 | 86 | 90 | 96 | 106 | 110 | 116 | 114 | 114 | 122 | 98 | 100 | 98 | 104 |  | 108 | 126 | 124 | 110 | 110 | 108 | 108 | 2570880
64 | Malancha, Ctg. EPZ (United) | 38 | 40 | 41 | 42 | 42 | 42 | 38 | 13 | 5 | 5 | 5 | 5 | 8 | 6 | 3 | 3 | 10 | 12 |  | 18 | 24 | 23 | 31 | 38 | 39 | 39 | 543840
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 0 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 399636
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 0 |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 129420
67 | Jangalia 33MW PP (Summit) | 32 | 33 | 33 | 33 | 0 | [10 empty] | 0 |  | 25 |  | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 367400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 12 | 0 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 434610
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 8 | 25 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 20 | 24 | 24 | 22 |  | 20 | 22 | 22 | 19 | 19 | 19 | 19 | 484380
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 25 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 553440
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815600
73 | Ghorashal 108MW PP (Regent) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 101 | 98 | 98 | 99 | 102 | 103 | 100 | 100 | 12 | 12 |  | 73 | 96 | 105 | 105 | 102 | 102 | 102 | 2237272
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 940500
| Chowmuhani 113 MW | 17 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 16 | 24 | 57 | 113 | 115 |  | 116 | 116 | 115 | 115 | 115 | 115 | 61 | 1097040
| Manikgonj 162MW PP(MPGL) | 162 | 159 | 162 | 162 | 148 | 162 | 149 | 144 | 155 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3879360
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 91 | 91 | 40 | 7 | 7 | 7 | 7 | 12 | 70 | 78 | 74 | 74 | 74 | 76 | 40 | 55 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 1564800
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 32 | 24 | 24 | 24 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 33 | 1106880
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 115 | 98 | 98 | 98 | 132 | 132 | 132 | 132 | 132 | 98 | 132 | 132 | 132 |  | 132 | 132 | 132 | 115 | 132 | 132 | 132 | 2978400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 203309
| Gazipur 100 MW PP | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 96 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2311200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 5 | 5 | 4 | 5 | 5 | 4 | 1 | 2 | 0 | [8 empty] | 31199
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 908131
| Karnaphuli Power Ltd. | 88 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 87 |  | 87 | 87 | 87 | 87 | 95 | 110 | 110 | 1952064
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 68 | 65 | 65 | 67 | 86 | 87 | 96 | 96 | 96 | 96 | 96 | 86 | 94 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2192592
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3598371
87 | Meghnaghat 100 MW(IEL) | 72 | 74 | 73 | 69 | 73 | 73 | 73 | 69 | 72 | 69 | 55 | 56 | 57 | 55 | 55 | 55 | 65 | 70 |  | 78 | 81 | 80 | 82 | 89 | 81 | 81 | 1689600
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 90 | 70 | 70 | 74 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2372160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1190473
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 48 | 32 | 7 | 7 | 16 | 58 | 93 | 93 | 93 | 93 | 94 | 94 | 64 | 64 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1807920
95 | Patenga 50MW PP (Baraka) | 44 | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 26 | 50 | 50 | 50 | 50 | 50 | 48 | 44 | 44 | 45 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1155840
96 | Chattogram 108 MW PP (ECPV) | 83 | 83 | 83 | 83 | 80 | 79 | 65 | 52 | 67 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 60 | 65 |  | 73 | 77 | 78 | 81 | 81 | 81 | 83 | 1713600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 1106088
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1227307
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2692881
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 |  | 0 | [8 empty] | 10100
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1260360
104 | Keranigonj 300 MW PP (APR) | 230 | 61 | 0 | [6 empty] | 173 | 0 | 81 | 39 |  |  |  | 71 | 100 |  | 76 | 40 | 23 |  |  |  | 0 | 989705
105 | Bramhangoan 100 MW PP (Aggreko) | 97 | 97 | 25 | 0 | [5 empty] | 25 | 25 | 95 | 95 |  |  |  |  | 50 |  | 93 | 100 | 70 |  |  |  | 0 | 680376
106 | Mymensingh 200 MW PP (United) | 189 | 188 | 188 | 189 | 188 | 80 | 80 | 80 | 110 | 144 | 180 | 179 | 140 | 100 | 115 | 120 | 70 | 85 |  | 110 | 181 | 180 | 189 | 181 | 181 | 181 | 3561600
112 | Aurahati 100MW PP (Aggreko) | 99 | 49 | 24 | 0 | [5 empty] | 25 | 25 | 97 | 96 |  |  |  |  | 50 |  | 100 | 98 | 70 |  |  |  | 0 | 690336
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 134 | 132 | 107 | 72 | 65 | 72 | 110 | 132 | 132 | 132 | 133 | 131 | 117 | 95 | 104 |  | 114 | 114 | 114 | 124 | 127 | 134 | 133 | 2907360
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 38 | 772800
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 155 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 142 | 170 |  | 185 | 200 | 200 | 200 | 200 | 200 | 200 | 3709920
117 | Ashuganj 150MW PP (Midland) | 133 | 133 | 142 | 142 | 143 | 100 | 100 | 100 | 110 | 130 | 137 | 130 | 130 | 122 | 130 | 140 | 80 | 80 |  | 83 | 100 | 120 | 143 | 143 | 145 | 147 | 3066109
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 401 | 401 | 400 | 352 | 351 | 351 | 402 | 402 | 402 | 403 | 402 | 353 | 403 | 389 | 389 | 364 |  | 402 | 402 | 402 | 402 | 389 | 389 | 388 | 9350000
| Jamalpur 115 MW PP (United) | 107 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 99 | 99 | 108 | 108 | 75 | 84 | 107 | 107 | 107 |  | 107 | 108 | 108 | 107 | 107 | 107 | 107 | 2496000
| Anwara 300 MW PP (United) | 265 | 265 | 264 | 264 | 265 | 265 | 262 | 265 | 264 | 262 | 260 | 260 | 277 | 277 | 277 | 278 | 278 | 278 |  | 278 | 278 | 278 | 278 | 283 | 283 | 283 | 6463418
| Juldah unit-2 (Acorn) | 39 | 39 | 39 | 39 | 39 | 39 | 37 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 | 38 |  | 63 | 65 | 65 | 65 | 65 | 58 | 38 | 906240
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 94 | 90 | 90 | 90 | 90 | 90 | 90 | 104 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 106 | 2480236
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 29 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 25 | 27 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 770760
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 73 | 73 | 82 | 83 | 44 | 17 | 17 | 17 | 17 | 23 | 43 | 45 | 45 | 45 | 45 | 45 | 37 | 37 |  | 37 | 63 | 60 | 81 | 81 | 81 | 80 | 1248960
| Kanchan Purbachal Power Generation Ltd. | 55 | 16 | 33 | 37 | 37 | 37 | 38 | 38 | 55 | 55 | 55 | 55 | 41 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1191240
120 | Eastern Zone Total | 8458 | 7983 | 7854 | 7735 | 7421 | 6811 | 6619 | 6472 | 6796 | 7363 | 7438 | 7808 | 7675 | 7308 | 7411 | 7454 | 7244 | 7361 |  | 8318 | 8594 | 8533 | 8349 | 8355 | 8303 | 8021 | 184785755
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 95 | 95 | 95 | 95 | 79 | 80 | 80 | 66 | 66 | 48 | 47 | 47 | 47 | 79 | 78 | 78 | 78 | 80 |  | 80 | 84 | 85 | 85 | 99 | 99 | 99 | 1824000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 38 | 38 | 0 | [16 empty] | 15 | 27 | 42 | 33 | 28 |  |  | 184800
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 94 | 94 | 70 | 70 | 35 | 53 | 78 | 93 | 93 | 93 | 93 | 93 | 93 | 70 | 70 |  | 80 | 94 | 94 | 94 | 94 | 53 | 53 | 2028480
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 24 | 49 | 64 | 81 | 98 | 32 | 101 | 87 | 71 | 51 | 25 | 2 | [8 empty] | 706320
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 448800
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 220 | 220 | 190 | 220 | 208 | 208 | 222 | 224 | 220 | 220 | 217 | 165 | 168 | 210 | 183 | 214 | 159 |  | 220 | 218 | 197 | 220 | 200 | 201 | 221 | 4942909
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 48 | 48 | 48 | 48 | 32 | 32 | 727488
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 52 | 55 | 55 | 55 | 52 | 52 | 55 | 58 | 60 | 52 | 56 | 57 | 52 | 51 | 60 | 51 | 52 | 51 |  | 56 | 56 | 52 | 52 | 55 | 60 | 56 | 1323000
140 | Bhola 33 MW PP (Venture) | 32 | 30 | 29 | 28 | 25 | 21 | 21 | 18 | 17 | 18 | 19 | 19 | 21 | 23 | 22 | 21 | 13 | 23 |  | 26 | 26 | 32 | 39 | 39 | 31 | 33 | 596854
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 0 | [17 empty] | 1 | 10 | 10 |  |  |  | 0 | 63360
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 32 | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 16 |  | 40 | 40 | 40 | 40 |  |  | 0 | 674625
143 | Gopalganj 100 MW Peaking PP | 65 | 65 | 65 | 50 | 0 | [14 empty] | 25 | 32 | 43 | 64 | 50 | 53 | 53 | 512768
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 89 | 72 | 15 | 15 | 15 | 15 | 50 | 67 | 67 | 67 | 67 | 67 | 67 | 50 | 50 |  | 50 | 89 | 89 | 89 | 89 | 67 | 67 | 1610352
146 | Bheramara HVDC | 909 | 910 | 909 | 909 | 909 | 909 | 909 | 910 | 909 | 913 | 916 | 920 | 922 | 922 | 921 | 922 | 921 | 922 |  | 922 | 922 | 922 | 921 | 921 | 924 | 924 | 22149090
147 | Bheramara 410 MW CCPP | 290 | 285 | 285 | 290 | 290 | 290 | 300 | 300 | 295 | 295 | 290 | 280 | 280 | 280 | 275 | 265 | 260 | 260 |  | 270 | 275 | 275 | 275 | 275 | 275 | 275 | 6908256
148 | Payra 1320 MW | 1010 | 1030 | 960 | 930 | 930 | 820 | 770 | 740 | 760 | 780 | 770 | 840 | 830 | 790 | 830 | 850 | 780 | 730 |  | 750 | 900 | 920 | 950 | 850 | 860 | 870 | 22281700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4280600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 0 | [7 empty] | 34 | 34 | 34 | 34 | 43 | 43 |  | 43 | 43 | 43 | 43 |  |  |  | 454960
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 5 | 4 | 2 | 0 | 0 | [8 empty] | 17760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 165 | 165 | 165 | 167 | 171 | 140 | 140 | 140 | 158 | 169 | 174 | 166 | 166 | 169 | 174 | 194 | 193 | 180 |  | 158 | 200 | 192 | 194 | 192 | 190 | 190 | 4411009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 415 | 415 | 415 | 422 | 354 | 353 | 353 | 414 | 414 | 414 | 415 | 414 | 362 | 415 | 421 | 380 | 264 |  | 414 | 414 | 414 | 414 | 416 | 416 | 383 | 9497745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 25 | 25 | 25 | 17 | 0 | [6 empty] | 2 | 4 | 20 | 22 | 22 | 22 | 27 |  | 29 | 29 | 31 | 13 |  |  |  | 287890
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 19 | 20 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  |  |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 181800
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 43 | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 34 | 34 | 34 |  |  |  | 336988
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 6 | 0 | [7 empty] | 11 | 24 | 24 | 24 | 24 | 24 |  | 32 | 32 | 32 | 32 | 32 |  |  | 296242
168 | Santahar 50 MW Peaking PP | 37 | 37 | 37 | 37 | 0 | [12 empty] | 21 |  | 37 | 37 | 37 | 37 | 37 |  |  | 303702
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 43 |  | 43 | 43 | 43 | 43 | 34 | 8 | 8 | 789120
170 | Chapainawabganj 100 MW Peaking PP | 18 | 0 | [13 empty] | 12 | 72 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 36 | 549472
171 | Baghabari 200 MW PP (Paramount) | 60 | 18 | 0 | [6 empty] | 1 | 10 | 10 | 10 | 0 | [5 empty] | 1 | 47 | 20 |  |  |  |  | 202379
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 80 | 113 | 113 | 113 | 113 | 113 | 70 | 2009568
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 70 | 70 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 95 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 76 | 1996512
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [26 empty] | 1000
176 | Rangpur 113 MW PP (Confidence) | 82 | 82 | 82 | 77 | 82 | 76 | 79 | 81 | 81 | 77 | 80 | 81 | 81 | 83 | 80 | 80 | 82 | 75 |  | 100 | 101 | 101 | 101 | 101 | 101 | 85 | 2025686
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 6 | 7 | 7 | 5 | 4 | 3 | 1 |  | 0 | [6 empty] | 51061
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 72 | 34 | 34 | 34 | 105 | 113 | 111 | 111 | 108 | 111 | 72 | 34 | 34 |  | 34 | 96 | 98 | 99 | 99 | 99 | 99 | 2120832
178