## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-29 | Sunday
|  |  | Date (day): | 2022-05-29 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13856.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14964 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-28 | 2022-05-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 280 | 280 | 280 |  | 85 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 106 | 105 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 330 | 340 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-2 S/D due to Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 20 | 88 | 88 | 85 |  | 15 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 150 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 95 | 96 | 96 | 96 |  |  | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 0 | 100 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 48 | 91 | 90 | 91 |  | 9 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 333 | 330 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 76 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 142 | 132 | 142 |  | 7 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 53 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 225 | 275 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 29 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 75 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 75 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 80 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 92 | 92
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 126 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 2965 | 3478 | 4004 | 3895 | 671 | 1252
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 2 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 9 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 29 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 68 | 40 | 40 |  | 190 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 0 | 60 |  | 38 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85 | 17 |  | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 16 | 10 | 15
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 75 | 67 | 75 | 85 |  | 23 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 267 | 285 | 280 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 35 | 36 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 90 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 64 | 30 | 70 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 105 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 911 | 1222 | 1052 | 1273 | 467 | 645
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 213 | 215 | 215
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 25 | 250 | 360 | 0
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 36 | 32 | 36 |  | 9 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 53 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 200 | 184 | 100 | 110 | 85 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 30 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 10 | 130 | 137 |  | 13 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 101 | 100 | 100 |  | 63 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 190 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 116 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 150 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 114 | 9 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 45 | 90 | 90 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1029 | 1426 | 1703 | 2136 | 623 | 118
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 138 | 130 | 150 | 150 | 52 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 110 | 185 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 103 | 103 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 447 | 461 | 528.6 | 507 | 52 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 110 | 110 | 110 | 220 |  | GT-1 S/D & Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 5 | 5 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 56 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 50 | 50 | 50 | 36 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 16 | 16 |  | 9 | Engine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 401 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 381 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1739 | 1735 | 1766 | 1807 | 357 | 237
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 922 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 91 | 85 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 35 | 40 |  | 14 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 41 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 275 | 252 | 285 | 270 | 140 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 24 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 53 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1494 | 1482 | 1815 | 1985 | 140 | 63
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 29 | 32 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 6 | 31 | 20 | 20 |  | 30 | Machine problem
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 88 | 88 | 88 | 106 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 840 | 700 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 50 | 210 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1025 | 1078 | 1445 | 1638 | 106 | 30
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 18 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 27 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 | 16 |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 186 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 419 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 15 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 52 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 65 | 65 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 165 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 80 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 76 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 766 | 1071 | 1132 | 1320 | 657 | 147
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 82 | 105 | 113 | 113
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 66 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 326 | 395 | 411 | 403 | 99 | 170
|  | Total |  |  |  |  | 22348 | 21584 | 10702 | 12348 | 13856.6 | 14964 | 3172 | 2670
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10410.8238 | 12012.04 | 13479.5945 | 14556.8648
| A. |  | 2022-05-28 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12348 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9098 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12348 | MW
| 3 | Day peak Generation : |  |  | 10702 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12012.04 | MW
| 4 | Evening peak Generation : |  |  | 12348 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 262.641 | MKWHr | By Solar | 1.1523 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 133.6993 | MKWHr |  | By Oil: | 76.9847 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 25.3077 | MKWHr |  | By Hydro: | 1.0498 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3172 | MW | Dhaka | 4822.24 | 4822.24 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2670 | MW | Chittagong | 1424 | 1424 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5842 | MW | Khulna | 1187 | 1187 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1023.6 | MMCFD |  |  | Rajshahi | 824.8 | 824.8 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151271873.7 | ii) Oil : | Taka | 1001300230.9 | Comilla | 1222 | 1222 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 212108589 | Total | Taka | 1364680693.6 | Mymensingh | 922 | 922 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.02 | MKWHr. | Sylhet | 540 | 540 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 784 | MW (E to W) at | 19:30 | hrs | Barisal | 257 | 257 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 56 | MW at | 1:00 | hrs | Rangpur | 813 | 813 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 12012.04 | 12012.04 |  | 0
| B. |  | 2022-05-29 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14964 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1164 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 293.5249 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9409 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1585 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2886 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.59 |  | (b) Today: | 74.58 |  | (c) Rule Curve: |  | 76.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 338 |  | 0 | 225 | 135 | 82 | 96 | 40 | 280 | 0 | 0 | 48 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 70 | 45 | 22 | 42 | 0 | 0 | 0 | 100 | 0 | 199 | 182 | 100 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 88 | 177 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 158 | 62 | 0 | 0 | 219 | 0 | 27 | 10 | 270 | 0 | 0 | 0 | 130 | 0 | 0 | 191 | 0 | 149 | 0 | 38 | 170 | 132 | 400 | 107 | 105 | 105 | 0 | 283 | 36 | 107 | 17 | 12 | 30 | 400 | 92 | 0 | 162 | 108 | 0 | 17 | 0 | 57 | 55 |  | 912 | 0 | 275 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 12 | 32 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 8 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 353 | 105 | 0 | 70 | 50 | 81 | 0 | 0 | 76 | 860 | 211 | 0 | 17 | 0 | 0 | 52 |  | 7469 | 3798 | 11267 | 3527 | 912 | 2172 | 0 | 3328 | 1035 | 38 | 0 | 167 | 88 | 0 | 0 | 74.6
2:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 338 |  | 0 | 225 | 140 | 81 | 96 | 40 | 280 | 0 | 0 | 37 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 72 | 50 | 22 | 42 | 0 | 0 | 0 | 0 | 0 | 214 | 184 | 100 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 0 | 33 | 20 | 86 | 181 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 159 | 62 | 0 | 0 | 219 | 0 | 27 | 10 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 191 | 0 | 149 | 0 | 38 | 120 | 140 | 400 | 106 | 105 | 105 | 0 | 284 | 36 | 93 | 17 | 9 | 25 | 400 | 91 | 0 | 162 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 285 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 11 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 350 | 105 | 0 | 70 | 32 | 81 | 0 | 0 | 76 | 850 | 218 | 0 | 17 | 0 | 0 | 34 |  | 7082 | 3640 | 10722 | 3452 | 912 | 2182 | 0 | 2978 | 1026 | 38 | 0 | 48 | 86 | 0 | 0 | 74.6
3:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 135 | 82 | 96 | 40 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 74 | 50 | 22 | 42 | 0 | 0 | 0 | 0 | 0 | 214 | 184 | 102 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 82 | 197 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 160 | 62 | 0 | 0 | 219 | 0 | 27 | 10 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 101 | 0 | 25 | 51 | 132 | 401 | 107 | 70 | 105 | 0 | 283 | 36 | 105 | 17 | 9 | 25 | 400 | 91 | 0 | 162 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 290 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 380 | 94 | 0 | 70 | 32 | 81 | 0 | 0 | 76 | 800 | 222 | 0 | 17 | 0 | 0 | 34 |  | 6898 | 3617 | 10515 | 3547 | 912 | 2234 | 0 | 2710 | 976 | 38 | 0 | 16 | 82 | 0 | 0 | 74.6
4:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 140 | 81 | 96 | 40 | 319 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 77 | 50 | 22 | 42 | 0 | 0 | 0 | 0 | 0 | 214 | 187 | 100 | 29 | 20 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 80 | 200 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 159 | 62 | 0 | 0 | 219 | 0 | 27 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 28 | 0 | 25 | 17 | 10 | 399 | 107 | 70 | 105 | 0 | 300 | 36 | 98 | 17 | 9 | 25 | 400 | 91 | 0 | 152 | 108 | 0 | 17 | 0 | 0 | 55 |  | 913 | 0 | 295 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 380 | 70 | 0 | 70 | 32 | 81 | 0 | 0 | 76 | 800 | 223 | 0 | 17 | 0 | 0 | 34 |  | 6559 | 3600 | 10159 | 3534 | 913 | 2252 | 0 | 2350 | 976 | 38 | 0 | 16 | 80 | 0 | 0 | 74.6
5:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 130 | 81 | 80 | 15 | 319 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 77 | 50 | 22 | 42 | 0 | 0 | 0 | 0 | 0 | 217 | 192 | 102 | 29 | 51 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 78 | 200 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 160 | 63 | 0 | 0 | 219 | 0 | 27 | 10 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 25 | 17 | 10 | 399 | 107 | 70 | 105 | 0 | 300 | 36 | 89 | 17 | 9 | 25 | 397 | 92 | 0 | 144 | 108 | 0 | 17 | 0 | 0 | 55 |  | 912 | 0 | 300 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 372 | 70 | 0 | 70 | 28 | 81 | 0 | 0 | 76 | 780 | 187 | 0 | 17 | 0 | 0 | 34 |  | 6470 | 3537 | 10007 | 3544 | 912 | 2220 | 0 | 2244 | 955 | 38 | 0 | 16 | 78 | 0 | 0 | 74.59
6:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 283 |  | 0 | 225 | 145 | 81 | 17 | 15 | 316 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 29 | 50 | 22 | 38 | 0 | 0 | 0 | 0 | 0 | 180 | 200 | 100 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 74 | 201 | 0 | 20 | 0 | 43 | 41 | 48 | 25 | 110 | 161 | 40 | 0 | 0 | 219 | 0 | 27 | 10 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 1 | 25 | 17 | 10 | 400 | 16 | 17 | 51 | 0 | 230 | 36 | 89 | 17 | 9 | 25 | 400 | 22 | 2 | 17 | 108 | 0 | 17 | 0 | 0 | 17 |  | 915 | 0 | 305 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 350 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 780 | 223 | 0 | 17 | 0 | 4 | 0 |  | 5737 | 3361 | 9098 | 3503 | 915 | 2203 | 0 | 1387 | 955 | 38 | 0 | 16 | 74 | 7 | 0 | 74.59
7:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 303 |  | 0 | 225 | 140 | 81 | 16 | 15 | 314 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 19 | 50 | 22 | 39 | 0 | 0 | 0 | 0 | 0 | 203 | 200 | 100 | 32 | 56 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 74 | 191 | 0 | 20 | 1 | 43 | 41 | 48 | 25 | 110 | 158 | 40 | 0 | 0 | 219 | 0 | 27 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 4 | 25 | 17 | 10 | 401 | 16 | 17 | 51 | 1 | 247 | 36 | 88 | 17 | 9 | 25 | 395 | 17 | 12 | 17 | 108 | 0 | 17 | 0 | 0 | 17 |  | 914 | 0 | 310 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 350 | 35 | 0 | 35 | 15 | 34 | 0 | 1 | 45 | 730 | 218 | 0 | 17 | 0 | 22 | 0 |  | 5828 | 3338 | 9166 | 3527 | 914 | 2255 | 0 | 1396 | 905 | 38 | 0 | 16 | 74 | 41 | 0 | 74.59
8:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 303 |  | 0 | 225 | 145 | 0 | 16 | 15 | 314 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 20 | 50 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 180 | 200 | 100 | 32 | 56 | 0 | 51 | 0 | 0 | 8 | 18 | 6 | 33 | 20 | 80 | 178 | 0 | 20 | 1 | 42 | 41 | 48 | 25 | 110 | 158 | 40 | 0 | 0 | 219 | 0 | 27 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 10 | 25 | 17 | 13 | 401 | 41 | 21 | 53 | 0 | 265 | 36 | 88 | 17 | 9 | 25 | 400 | 17 | 26 | 17 | 108 | 0 | 17 | 0 | 0 | 18 |  | 914 | 0 | 305 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 422 | 45 | 0 | 65 | 15 | 34 | 0 | 1 | 76 | 700 | 218 | 0 | 17 | 1 | 45 | 0 |  | 5769 | 3466 | 9235 | 3490 | 914 | 2297 | 0 | 1441 | 875 | 38 | 0 | 16 | 80 | 84 | 0 | 74.59
9:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 300 |  | 0 | 225 | 150 | 0 | 26 | 40 | 280 | 0 | 0 | 18 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 5 | 25 | 33 | 30 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 63 | 0 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 183 | 200 | 100 | 32 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 30 | 20 | 88 | 164 | 0 | 20 | 1 | 43 | 41 | 0 | 0 | 110 | 160 | 40 | 0 | 0 | 219 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 20 | 0 | 0 | 32 | 0 | 31 | 11 | 25 | 17 | 30 | 389 | 98 | 70 | 93 | 2 | 265 | 36 | 88 | 17 | 9 | 25 | 360 | 54 | 40 | 144 | 108 | 0 | 17 | 0 | 0 | 0 |  | 915 | 0 | 300 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 423 | 70 | 0 | 70 | 15 | 67 | 0 | 1 | 76 | 700 | 184 | 0 | 17 | 2 | 70 | 0 |  | 5965 | 3504 | 9469 | 3371 | 915 | 2122 | 0 | 1917 | 875 | 38 | 0 | 16 | 88 | 127 | 0 | 74.59
10:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 322 |  | 0 | 225 | 145 | 0 | 37 | 40 | 335 | 0 | 37 | 40 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 40 | 22 | 25 | 28 | 25 | 33 | 33 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 181 | 200 | 100 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 22 | 20 | 94 | 152 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 110 | 158 | 60 | 0 | 0 | 219 | 0 | 0 | 9 | 320 | 0 | 0 | 0 | 60 | 0 | 0 | 60 | 0 | 76 | 1 | 25 | 51 | 53 | 403 | 105 | 70 | 87 | 2 | 266 | 36 | 88 | 17 | 9 | 25 | 394 | 78 | 44 | 144 | 108 | 0 | 17 | 0 | 3 | 0 |  | 915 | 0 | 290 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 380 | 70 | 0 | 70 | 0 | 82 | 0 | 1 | 76 | 780 | 45 | 0 | 17 | 3 | 86 | 17 |  | 6491 | 3420 | 9911 | 3514 | 915 | 1994 | 0 | 2246 | 955 | 38 | 0 | 16 | 94 | 139 | 0 | 74.58
11:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 322 |  | 0 | 225 | 138 | 0 | 82 | 40 | 300 | 0 | 96 | 40 | 48 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 22 | 25 | 27 | 25 | 33 | 41 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 0 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 181 | 200 | 98 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 25 | 20 | 100 | 141 | 0 | 20 | 0 | 44 | 41 | 5 | 0 | 110 | 158 | 60 | 0 | 0 | 219 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 178 | 0 | 0 | 90 | 0 | 114 | 4 | 25 | 126 | 50 | 403 | 99 | 70 | 87 | 0 | 267 | 36 | 88 | 17 | 9 | 38 | 391 | 90 | 41 | 144 | 108 | 0 | 17 | 0 | 22 | 0 |  | 914 | 0 | 285 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 350 | 80 | 0 | 70 | 0 | 75 | 0 | 2 | 76 | 800 | 54 | 0 | 17 | 3 | 74 | 17 |  | 6866 | 3411 | 10277 | 3526 | 914 | 1948 | 0 | 2636 | 975 | 38 | 0 | 16 | 100 | 124 | 0 | 74.58
12:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 300 |  | 0 | 225 | 145 | 20 | 95 | 40 | 325 | 0 | 95 | 48 | 76 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 22 | 25 | 28 | 25 | 33 | 41 | 0 | 38 | 0 | 100 | 0 | 2 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 0 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 201 | 200 | 0 | 32 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 25 | 20 | 84 | 138 | 0 | 20 | 2 | 43 | 41 | 5 | 0 | 110 | 156 | 59 | 0 | 0 | 220 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 225 | 0 | 0 | 110 | 0 | 131 | 9 | 25 | 190 | 50 | 405 | 103 | 80 | 87 | 1 | 267 | 36 | 90 | 17 | 9 | 38 | 381 | 90 | 50 | 144 | 105 | 0 | 17 | 0 | 45 | 0 |  | 914 | 0 | 275 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 6 | 29 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 380 | 105 | 0 | 70 | 15 | 82 | 0 | 3 | 76 | 840 | 50 | 0 | 17 | 4 | 86 | 66 |  | 7091 | 3611 | 10702 | 3461 | 914 | 1975 | 0 | 3007 | 1015 | 38 | 0 | 53 | 84 | 155 | 0 | 74.58
13:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 322 |  | 0 | 225 | 140 | 62 | 96 | 40 | 330 | 0 | 94 | 78 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 73 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 180 | 199 | 0 | 32 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 25 | 20 | 96 | 110 | 0 | 20 | 2 | 44 | 41 | 5 | 0 | 110 | 156 | 61 | 0 | 0 | 219 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 243 | 52 | 40 | 135 | 25 | 149 | 9 | 25 | 196 | 73 | 404 | 103 | 90 | 100 | 3 | 267 | 36 | 105 | 17 | 9 | 38 | 394 | 90 | 54 | 144 | 90 | 0 | 17 | 0 | 99 | 0 |  | 914 | 0 | 270 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 24 | 86 | 6 | 32 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 8 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 105 | 0 | 70 | 15 | 83 | 0 | 5 | 76 | 870 | 50 | 0 | 17 | 4 | 74 | 96 |  | 7560 | 3715 | 11275 | 3423 | 914 | 2028 | 117 | 3341 | 1045 | 38 | 0 | 122 | 96 | 151 | 0 | 74.58
14:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 322 |  | 0 | 225 | 145 | 80 | 96 | 40 | 280 | 0 | 61 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 27 | 25 | 33 | 49 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 71 | 0 | 22 | 7 | 0 | 0 | 0 | 0 | 25 | 180 | 199 | 98 | 31 | 55 | 0 | 43 | 0 | 0 | 8 | 19 | 6 | 25 | 0 | 98 | 122 | 0 | 20 | 2 | 44 | 41 | 5 | 0 | 110 | 156 | 61 | 0 | 0 | 219 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 245 | 0 | 0 | 174 | 0 | 149 | 10 | 25 | 200 | 107 | 365 | 103 | 90 | 105 | 2 | 267 | 36 | 105 | 17 | 9 | 38 | 390 | 90 | 45 | 144 | 90 | 0 | 17 | 0 | 100 | 0 |  | 914 | 0 | 260 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 0 | 32 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 24 | 11 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 105 | 0 | 70 | 50 | 80 | 0 | 7 | 76 | 880 | 50 | 0 | 17 | 4 | 42 | 113 |  | 7537 | 3782 | 11319 | 3402 | 914 | 1994 | 0 | 3543 | 1055 | 38 | 0 | 163 | 98 | 112 | 0 | 74.58
15:00 | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 322 |  | 0 | 225 | 142 | 80 | 96 | 40 | 327 | 0 | 97 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 27 | 25 | 33 | 49 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 13 | 10 | 72 | 0 | 22 | 5 | 0 | 0 | 0 | 0 | 25 | 193 | 199 | 98 | 31 | 53 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 6 | 104 | 130 | 0 | 20 | 2 | 43 | 41 | 5 | 0 | 110 | 154 | 55 | 0 | 0 | 220 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 248 | 0 | 0 | 180 | 0 | 149 | 8 | 25 | 200 | 122 | 403 | 102 | 90 | 105 | 3 | 267 | 36 | 106 | 17 | 15 | 32 | 380 | 90 | 37 | 144 | 108 | 0 | 25 | 0 | 101 | 0 |  | 914 | 0 | 255 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 1 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 24 | 22 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 414 | 105 | 0 | 70 | 50 | 75 | 0 | 6 | 76 | 910 | 52 | 0 | 17 | 3 | 52 | 112 |  | 7758 | 3819 | 11577 | 3530 | 914 | 2018 | 0 | 3589 | 1085 | 38 | 0 | 188 | 104 | 111 | 0 | 74.57
16:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 290 |  | 0 | 225 | 140 | 80 | 96 | 40 | 332 | 0 | 94 | 91 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 27 | 25 | 33 | 33 | 0 | 38 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 17 | 10 | 72 | 0 | 22 | 4 | 0 | 0 | 0 | 0 | 25 | 180 | 195 | 100 | 32 | 51 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 17 | 104 | 138 | 0 | 20 | 1 | 44 | 41 | 5 | 0 | 110 | 105 | 62 | 0 | 0 | 220 | 0 | 0 | 10 | 275 | 0 | 0 | 0 | 248 | 0 | 0 | 171 | 0 | 149 | 6 | 25 | 155 | 80 | 403 | 102 | 70 | 105 | 2 | 267 | 36 | 110 | 17 | 60 | 25 | 393 | 90 | 26 | 144 | 108 | 0 | 35 | 0 | 75 | 0 |  | 914 | 0 | 255 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 9 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 8 | 32 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 415 | 105 | 0 | 70 | 50 | 72 | 0 | 4 | 76 | 880 | 45 | 0 | 17 | 2 | 22 | 111 |  | 7501 | 3768 | 11269 | 3512 | 914 | 1946 | 0 | 3449 | 1055 | 38 | 0 | 188 | 104 | 63 | 0 | 74.57
17:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 280 |  | 0 | 225 | 140 | 80 | 96 | 48 | 332 | 0 | 0 | 70 | 68 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 33 | 0 | 38 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 17 | 10 | 68 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 14 | 211 | 195 | 100 | 35 | 52 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 33 | 17 | 104 | 138 | 0 | 20 | 0 | 44 | 41 | 5 | 0 | 110 | 111 | 56 | 0 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 248 | 0 | 0 | 175 | 0 | 123 | 3 | 25 | 155 | 60 | 403 | 101 | 70 | 105 | 1 | 267 | 36 | 110 | 114 | 113 | 25 | 392 | 90 | 11 | 144 | 108 | 0 | 35 | 0 | 75 | 0 |  | 914 | 0 | 230 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 16 | 83 | 16 | 16 | 0 | 0 | 0 | 17 | 27 | 0 | 0 | 8 | 32 | 8 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 320 | 53 | 0 | 78 | 32 | 80 | 0 | 3 | 113 | 820 | 50 | 0 | 0 | 0 | 8 | 90 |  | 7507 | 3481 | 10988 | 3402 | 914 | 1877 | 0 | 3439 | 995 | 38 | 0 | 193 | 104 | 26 | 0 | 74.57
18:00 | 0 | 0 | 0 | 180 | 280 | 58 | 0 | 0 | 250 |  | 0 | 225 | 138 | 80 | 96 | 55 | 280 | 0 | 0 | 50 | 68 | 100 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 25 | 33 | 42 | 0 | 38 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 17 | 10 | 67 | 0 | 22 | 9 | 0 | 0 | 0 | 0 | 40 | 170 | 197 | 100 | 35 | 53 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 17 | 100 | 128 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 40 | 0 | 0 | 185 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 252 | 0 | 0 | 160 | 0 | 122 | 1 | 50 | 155 | 40 | 328 | 75 | 70 | 105 | 0 | 281 | 36 | 110 | 114 | 114 | 55 | 360 | 54 | 2 | 108 | 108 | 0 | 35 | 0 | 51 | 0 |  | 914 | 0 | 210 | 0 | 49 | 0 | 0 | 0 | 3 | 0 | 16 | 87 | 18 | 16 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 8 | 32 | 8 | 12 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 35 | 0 | 70 | 32 | 70 | 0 | 1 | 70 | 740 | 140 | 0 | 0 | 0 | 4 | 34 |  | 7029 | 3253 | 10282 | 3113 | 914 | 1852 | 0 | 3135 | 915 | 38 | 0 | 207 | 100 | 8 | 0 | 74.57
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 330 |  | 0 | 225 | 145 | 75 | 96 | 55 | 330 | 0 | 0 | 73 | 93 | 142 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 32 | 85 | 10 | 67 | 7 | 22 | 9 | 0 | 0 | 0 | 0 | 40 | 211 | 182 | 101 | 36 | 53 | 0 | 30 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 122 | 128 | 0 | 20 | 0 | 43 | 41 | 6 | 0 | 110 | 111 | 56 | 50 | 0 | 220 | 0 | 0 | 10 | 305 | 16 | 0 | 20 | 275 | 151 | 76 | 184 | 90 | 143 | 0 | 50 | 166 | 10 | 402 | 103 | 90 | 105 | 0 | 285 | 36 | 110 | 114 | 114 | 64 | 388 | 75 | 0 | 114 | 108 | 0 | 35 | 0 | 70 | 10 |  | 923 | 0 | 235 | 0 | 50 | 0 | 0 | 0 | 29 | 38 | 24 | 87 | 21 | 32 | 0 | 0 | 0 | 17 | 26 | 15 | 0 | 8 | 32 | 25 | 31 | 15 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 415 | 35 | 0 | 42 | 32 | 80 | 0 | 0 | 70 | 700 | 160 | 0 | 11 | 0 | 0 | 70 |  | 8273 | 3560 | 11833 | 3413 | 923 | 2172 | 337 | 3476 | 875 | 68 | 0 | 447 | 122 | 0 | 0 | 74.57
19:30 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 330 |  | 0 | 225 | 150 | 88 | 96 | 55 | 333 | 0 | 0 | 91 | 93 | 142 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 42 | 85 | 10 | 67 | 29 | 22 | 16 | 0 | 0 | 0 | 0 | 25 | 213 | 184 | 101 | 36 | 53 | 0 | 30 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 116 | 130 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 56 | 50 | 0 | 220 | 0 | 0 | 10 | 270 | 24 | 0 | 20 | 275 | 29 | 75 | 185 | 75 | 149 | 0 | 50 | 200 | 10 | 401 | 103 | 90 | 105 | 0 | 285 | 36 | 110 | 114 | 114 | 64 | 395 | 90 | 0 | 126 | 108 | 0 | 35 | 0 | 90 | 55 |  | 922 | 0 | 252 | 0 | 85 | 0 | 0 | 0 | 38 | 41 | 24 | 88 | 31 | 32 | 0 | 0 | 0 | 18 | 27 | 65 | 0 | 34 | 32 | 43 | 31 | 15 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 419 | 53 | 0 | 80 | 67 | 105 | 0 | 0 | 113 | 700 | 210 | 0 | 17 | 0 | 0 | 115 |  | 8322 | 4026 | 12348 | 3473 | 922 | 2214 | 199 | 3960 | 875 | 68 | 0 | 521 | 116 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 332 |  | 0 | 225 | 150 | 82 | 96 | 55 | 335 | 0 | 0 | 91 | 93 | 142 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 48 | 85 | 10 | 67 | 36 | 22 | 21 | 0 | 0 | 0 | 0 | 25 | 213 | 195 | 101 | 36 | 54 | 0 | 30 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 116 | 129 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 57 | 50 | 0 | 220 | 0 | 0 | 10 | 260 | 24 | 0 | 0 | 260 | 13 | 0 | 200 | 25 | 149 | 0 | 50 | 200 | 10 | 401 | 102 | 90 | 105 | 0 | 285 | 36 | 110 | 114 | 114 | 64 | 392 | 90 | 0 | 128 | 108 | 0 | 35 | 0 | 96 | 55 |  | 923 | 0 | 275 | 0 | 95 | 0 | 0 | 0 | 12 | 18 | 24 | 88 | 28 | 32 | 0 | 0 | 0 | 17 | 26 | 65 | 0 | 34 | 32 | 43 | 31 | 15 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 371 | 53 | 0 | 90 | 67 | 109 | 0 | 0 | 108 | 690 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8184 | 3969 | 12153 | 3498 | 923 | 2182 | 38 | 3987 | 865 | 68 | 0 | 476 | 116 | 0 | 0 | 74.57
21:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 332 |  | 0 | 225 | 150 | 88 | 96 | 55 | 335 | 0 | 0 | 83 | 93 | 145 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 85 | 10 | 68 | 48 | 22 | 19 | 0 | 0 | 0 | 0 | 18 | 187 | 185 | 101 | 36 | 54 | 0 | 44 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 116 | 129 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 111 | 57 | 50 | 0 | 219 | 0 | 0 | 10 | 290 | 24 | 0 | 0 | 280 | 0 | 0 | 140 | 0 | 149 | 0 | 50 | 200 | 16 | 402 | 104 | 90 | 105 | 0 | 287 | 36 | 110 | 114 | 115 | 64 | 396 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 924 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 31 | 32 | 0 | 0 | 0 | 8 | 0 | 65 | 0 | 34 | 32 | 43 | 32 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 420 | 53 | 0 | 106 | 50 | 109 | 0 | 0 | 113 | 760 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8143 | 4036 | 12179 | 3466 | 924 | 2273 | 0 | 3996 | 935 | 68 | 0 | 401 | 116 | 0 | 0 | 74.57
22:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 333 |  | 0 | 225 | 145 | 82 | 96 | 55 | 280 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 43 | 10 | 70 | 50 | 22 | 28 | 0 | 0 | 0 | 0 | 80 | 172 | 158 | 101 | 36 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 116 | 131 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 111 | 62 | 50 | 0 | 220 | 0 | 0 | 10 | 265 | 24 | 0 | 0 | 285 | 0 | 0 | 100 | 0 | 149 | 0 | 50 | 200 | 41 | 401 | 75 | 90 | 105 | 0 | 287 | 36 | 110 | 114 | 114 | 56 | 395 | 89 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 923 | 0 | 265 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 31 | 32 | 0 | 0 | 0 | 8 | 0 | 76 | 0 | 8 | 32 | 43 | 30 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 380 | 53 | 0 | 110 | 50 | 109 | 0 | 0 | 113 | 800 | 183 | 0 | 17 | 0 | 0 | 115 |  | 8022 | 3951 | 11973 | 3429 | 923 | 2157 | 0 | 3931 | 976 | 68 | 0 | 373 | 116 | 0 | 0 | 74.57
23:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 145 | 88 | 96 | 55 | 280 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 17 | 10 | 70 | 50 | 22 | 36 | 0 | 0 | 0 | 0 | 45 | 191 | 110 | 100 | 36 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 112 | 147 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 61 | 50 | 0 | 220 | 0 | 0 | 10 | 305 | 16 | 0 | 0 | 295 | 0 | 0 | 100 | 0 | 149 | 0 | 50 | 200 | 71 | 403 | 75 | 105 | 105 | 0 | 290 | 36 | 110 | 114 | 116 | 50 | 375 | 89 | 0 | 140 | 108 | 0 | 35 | 0 | 100 | 55 |  | 923 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 88 | 32 | 32 | 0 | 0 | 0 | 8 | 0 | 83 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 380 | 53 | 0 | 113 | 50 | 109 | 0 | 0 | 113 | 830 | 182 | 0 | 17 | 0 | 0 | 115 |  | 8004 | 3953 | 11957 | 3406 | 923 | 2160 | 0 | 3947 | 1005 | 68 | 0 | 336 | 112 | 0 | 0 | 74.57
24:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 135 | 89 | 96 | 55 | 335 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 0 | 10 | 74 | 50 | 22 | 40 | 0 | 0 | 0 | 0 | 55 | 193 | 110 | 100 | 36 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 5 | 33 | 20 | 112 | 142 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 61 | 50 | 0 | 219 | 0 | 0 | 10 | 310 | 16 | 0 | 0 | 290 | 0 | 0 | 110 | 0 | 149 | 0 | 38 | 200 | 80 | 401 | 83 | 90 | 105 | 0 | 288 | 36 | 103 | 17 | 34 | 38 | 398 | 90 | 0 | 130 | 108 | 0 | 35 | 0 | 99 | 55 |  | 924 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 88 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 420 | 60 | 0 | 70 | 50 | 84 | 0 | 0 | 76 | 860 | 221 | 0 | 17 | 0 | 0 | 115 |  | 7811 | 3966 | 11777 | 3479 | 924 | 2238 | 0 | 3640 | 1035 | 38 | 0 | 311 | 112 | 0 | 0 | 74.57
KWH | 0 | 0 | 0 | 4347000 | 6678582 | 2403500 | 0 | 0 | 7594000 |  | 0 | 5131150 | 3453178 | 1596480 | 1904664 | 1015129 | 7519121 | 0 | 572000 | 1248000 | 1232064 | 1764480 | 0 | 0 | 0 | 0 | 1289160 | 855095 | 1140419 | 369612 | 600000 | 622260 | 586440 | 807500 | 720000 | 0 | 905760 | 144000 | 2400000 | 0 | 257308 | 0 | 0 | 0 | 0 |  | 575040 | 196032 | 378495 | 259200 | 1577280 | 679200 | 531840 | 527520 | 0 | 0 | 0 | 243800 | 369000 | 4763000 | 4466181 | 2209360 | 734400 | 1128480 | 0 | 1150799 | 0 | 0 | 203597 | 430560 | 129600 | 755200 | 451850 | 2288640 | 3615360 | 0 | 406836 | 14350 | 1025000 | 962552 | 470400 | 248112 | 2659009 | 3147000 | 1329408 | 315840 | 0 | 5240970 | 0 | 0 | 237420 | 7140500 | 212665 | 0 | 18432 | 3926726 | 120566 | 89502 | 2904000 | 99535 | 2613170 | 82485 | 788160 | 3202080 | 1513818 | 9319000 | 2198400 | 1887600 | 2351007 | 23039 | 6601418 | 898948 | 2433808 | 1086420 | 1050840 | 878400 | 9322700 | 1903680 | 369390 | 3147840 | 2566800 | 0 | 617760 | 0 | 1297920 | 658440 |  | 22158545 | 0 | 6831072 | 0 | 2117760 | 0 | 0 | 0 | 45600 | 46848 | 369375 | 2085743 | 307727 | 699456 | 0 | 0 | 0 | 105632 | 177588 | 450744 | 0 | 196533 | 286200 | 313910 | 227840 | 467280 | 0 | 178020 | 0 | 0 | 4277900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4475473 | 0 | 9144800 | 1854720 | 0 | 1873728 | 846576 | 1888656 | 0 | 37035 | 1861344 | 21029800 | 3580473 | 0 | 394800 | 33480 | 592560 | 1480512 |  | 172203282 | 90437730 | 262641012 | 83272924 | 22158545 | 50426369 | 328035 | 72977241 | 25307700 | 1049760 | 0 | 3679459 | 2288640 | 1152339 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 7480011.84 | 3196655 | 0 | 0 | 8201520 |  | 0 | 5592953.5 | 3833027.58 | 17848646.4 | 25236798 | 13450459.25 | 8421415.52 | 0 | 1001000 | 18245760 | 17335140.48 | 28602220.8 | 0 | 0 | 0 | 0 | 16398115.2 | 11543782.5 | 15293018.79 | 277209 | 450000 | 0 | 0 | 0 | 12247200 | 0 | 244555.2 | 38880 | 4536000 | 0 | 4206985.8 | 0 | 0 | 0 | 0 |  | 7504272 | 3269813.76 | 6441984.9 | 3501792 | 19999910.4 | 7858344 | 675436.8 | 1756641.6 | 0 | 0 | 0 | 270618 | 402210 | 5525080 | 5761373.49 | 2695419.2 | 829872 | 1681435.2 | 0 | 1921834.33 | 0 | 0 | 2738379.65 | 589867.2 | 97200 | 1321600 | 338887.5 | 16432435.2 | 3940742.4 | 0 | 553296.96 | 228739 | 1404250 | 1270568.64 | 818496 | 429233.76 | 3057860.35 | 3367290 | 2579051.52 | 720115.2 | 0 | 5293379.7 | 0 | 0 | 470091.6 | 7140500 | 159498.75 | 0 | 386334.72 | 53599809.9 | 2527063.36 | 1850006.34 | 39145920 | 2057388.45 | 36192404.5 | 964249.65 | 8133811.2 | 43740412.8 | 20088364.86 | 8573480 | 26732544 | 27294696 | 29740238.55 | 0 | 77500647.32 | 9789543.72 | 25871379.04 | 14742719.4 | 13545327.6 | 10347552 | 8576884 | 24652656 | 5337685.5 | 39946089.6 | 29210184 | 0 | 8067945.6 | 0 | 19429862.4 | 8671654.8 |  | 66475635 | 0 | 7650800.64 | 0 | 22045881.6 | 0 | 0 | 0 | 821256 | 843264 | 5307918.75 | 2336032.16 | 596990.38 | 7624070.4 | 0 | 0 | 0 | 1771448.64 | 3106014.12 | 7049636.16 | 0 | 3254586.48 | 4839642 | 4278593.3 | 3843660.8 | 967269.6 | 0 | 134761.14 | 0 | 0 | 22630091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5191548.68 | 0 | 9053352 | 24927436.8 | 0 | 22166202.24 | 12233023.2 | 23985931.2 | 0 | 409236.75 | 22596716.16 | 189478498 | 3652082.46 | 0 | 2921520 | 378658.8 | 6950728.8 | 22696248.96 |  | 949922761.28 | 512218736.22 | 1462141497.5 | 92420441.65 | 66475635 | 58851432.05 | 6820792.87 | 933890496.85 | 212108589 | 283435.2 | 0 | 60588941.18 | 16432435.2 | 14269298.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 0 | 300 |  | 0 | 225 | 145 | 20 | 95 | 40 | 325 | 0 | 95 | 48 | 76 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 22 | 25 | 28 | 25 | 33 | 41 | 0 | 38 | 0 | 100 | 0 | 2 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 75 | 0 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 201 | 200 | 0 | 32 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 6 | 25 | 20 | 84 | 138 | 0 | 20 | 2 | 43 | 41 | 5 | 0 | 110 | 156 | 59 | 0 | 0 | 220 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 225 | 0 | 0 | 110 | 0 | 131 | 9 | 25 | 190 | 50 | 405 | 103 | 80 | 87 | 1 | 267 | 36 | 90 | 17 | 9 | 38 | 381 | 90 | 50 | 144 | 105 | 0 | 17 | 0 | 45 | 0 |  | 914 | 0 | 275 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 6 | 29 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 380 | 105 | 0 | 70 | 15 | 82 | 0 | 3 | 76 | 840 | 50 | 0 | 17 | 4 | 86 | 66 |  | 10702 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 330 | 0 | 0 | 225 | 150 | 88 | 96 | 55 | 333 | 0 | 0 | 91 | 93 | 142 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 23 | 42 | 85 | 10 | 67 | 29 | 22 | 16 | 0 | 0 | 0 | 0 | 25 | 213 | 184 | 101 | 36 | 53 | 0 | 30 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 116 | 130 | 0 | 20 | 0 | 43 | 41 | 5 | 0 | 110 | 110 | 56 | 50 | 0 | 220 | 0 | 0 | 10 | 270 | 24 | 0 | 20 | 275 | 29 | 75 | 185 | 75 | 149 | 0 | 50 | 200 | 10 | 401 | 103 | 90 | 105 | 0 | 285 | 36 | 110 | 114 | 114 | 64 | 395 | 90 | 0 | 126 | 108 | 0 | 35 | 0 | 90 | 55 |  | 922 | 0 | 252 | 0 | 85 | 0 | 0 | 0 | 38 | 41 | 24 | 88 | 31 | 32 | 0 | 0 | 0 | 18 | 27 | 65 | 0 | 34 | 32 | 43 | 31 | 15 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 419 | 53 | 0 | 80 | 67 | 105 | 0 | 0 | 113 | 700 | 210 | 0 | 17 | 0 | 0 | 115 |  | 12348 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 108 | 0 | 0 | 350 | 0 | 0 | 225 | 150 | 85 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 142 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 85 | 10 | 85 | 50 | 22 | 15 | 0 | 0 | 0 | 0 | 360 | 215 | 110 | 100 | 36 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 165 | 150 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 110 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 341 | 16 | 0 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 137 | 400 | 115 | 105 | 105 | 0 | 300 | 36 | 110 | 114 | 113 | 70 | 400 | 92 | 0 | 162 | 110 | 0 | 35 |  | 101 | 55 |  | 930 | 0 | 270 | 0 | 115 | 220 | 0 | 0 | 40 | 60 | 40 | 88 | 20 | 110 | 0 | 0 | 0 | 43 | 30 | 80 | 0 | 34 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 165 | 113 | 105 | 113 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 88 | 96 | 55 | 330 | 0 | 100 | 90 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 75 | 50 | 22 | 10 | 0 | 0 | 0 | 0 | 250 | 215 | 100 | 100 | 32 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 143 | 150 | 0 | 20 | 1.6 | 43 | 42 | 5 | 0 | 110 | 110 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 300 | 16 | 0 | 150 | 300 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 130 | 400 | 115 | 105 | 105 | 5 | 280 | 35 | 110 | 17 | 9 | 30 | 400 | 92 | 50 | 162 | 110 | 0 | 17 | 30 | 90 | 55 |  | 930 | 0 | 285 | 0 | 115 | 0 | 0 | 0 | 35 | 0 | 40 | 88 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 65 | 0 | 34 | 32 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 180 | 0 | 410 | 105 | 0 | 113 | 105 | 113 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 332 | 0 | 0 | 225 | 145 | 88 | 32 | 55 | 330 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 28 | 17 | 33 | 18 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 32 | 44 | 22 | 12 | 0 | 0 | 0 | 0 | 95 | 181 | 107 | 30 | 30 | 52 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 15 | 92 | 145 | 0 | 17 | 1 | 43 | 42 | 5 | 0 | 110 | 110 | 61 | 0 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 15 | 0 | 0 | 45 | 0 | 50 | 10 | 25 | 68 | 30 | 400 | 65 | 52 | 53 | 1 | 283 | 36 | 110 | 17 | 9 | 25 | 370 | 53 | 10 | 72 | 108 | 0 | 17 | 0 | 34 | 17 | 0 | 919 | 0 | 250 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 425 | 17 | 0 | 70 | 15 | 50 | 0 | 3 | 76 | 680 | 190 | 0 | 17 | 2 | 7 | 34 | 0 |  |  |  |  | 76984735 |  | 0
76984735
| Minimum Generation |  | 9098 | 6:00
| Highest Generation |  | 12348 | 19:30
| Day Peak Generation |  | 10702 | 12:00
| Evening Peak Generation |  | 12348 | 19:30
| HVDC Max Flow |  | 924 | 21:00
| HVDC EvPeak Flow |  | 922 | 19:30
| Load factor L.F |  | 88.62%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-29
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10702 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9409 | MW
Evening Peak Generation : |  | 12348 | MW Hour : | 19:30 | Available Max Generation : |  | 14964 | MW
E.P. Demand (at gen end) : |  | 12348 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 12348 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1164 | MW
Total Gen. (MKWH) : |  | 262.641 | System Load Factor : | 88.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 56 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-29
Actual : | 74.58 | Ft.(MSL) , | Rule curve : | 76.6 | Ft.( MSL )
Gas Consumed : | Total = | 1023.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151271873.7
: |  | Coal : | 212108589 | Oil : | 1001300230.9 | Total : | 1364680693.6
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4942.823 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1601.9385 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1563.2174 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1399.5409 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1276.4094 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1047.8272 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.754 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 315.7179 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 769.79 |  |  | 0 | 0%
Total | 0 |  | 13430.0183 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1,2
9) Ashuganj North
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rajshahi 132/33 kV T-2 transformer with 33 kV bus were under shut down from 08:28 to 11:35 due to
replacement bus isolator of 33 kV Hologram NESCO feeder.
b) Payra 132 kV bus-1 was under shut down from 08:50 to 19:35 for C/M.
c) Ashuganj-Shahjibazar 132 kV Ckt-3 was under shut down from 09:30 to 10:10 for C/M.
d) Chapainawabganj-Rohanpur 132 kV Ckt-1 was under shut down from 08:52 to 16:52 due to tapping
of 132 kV Ckt-2.
e) Siddhirganj-Maniknagar 230 kV Ckt-1 was switched on at 11:06.
f) Ashuganj-Ghorasal 132 kV Ckt-1 was under shut down from 10:17 to 11:38 for C/M.
g) Hathazari-Madunaghat 132 kV Ckt-1 was under shut down from 10:23 to 13:25 for telecom work.
h) Siddhirganj-Maniknagar 230 kV Ckt-2 was under shut down since at 11:14 for D/W.
i) Khagrachori 132/33 kV T-2 transformer with 132 kV bus-1 were under shut down from 11:24 to 13:22
due to red hot maintenance at 132 kV Y-phase bus isolator .
j) Mithapukur-Rangpur confidence 132 kV Ckt-1 was under shut down from 11:20 to 12:17 due to red hot
maintenance at Mithapukur end.
k) Mithapukur 132/33 kV T-1 transformer was under shut down from 12:57 to 13:30 for energy meter replacement work.
l) Bhola Nutun Biddut CCPP ST trip at 09:00 due to lube oil pressure low and was synchronized at 17:20.
m) Siddhirganj GT-1 was synchronized at 09:39 and was shut down 16:17.
n) Chandpur CCPP GT trip at 11:56 due to reignite primary flame failure and was synchronized at 13:19.
o) Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-1 was under shut down since at 09:33 for C/M.
p) Chattak 132/33 kV T-2 transformer was under shut down since at 12:59 for oil centrifuging.
q) Ashuganj(s) GT was synchronized at 13:15.
r) Hathazari-Madunaghat 132 kV Ckt-1 was under shut down from 13:32 to 15:03 for D/W.
s) Bagerhat-Mongla 132 kV Ckt-1 was under shut down from 16:03 to 17:32 for C/M.
t) Kabirpur 132/33 kV T-3 transformer was under shut down from 21:43 to 22:45 due to red hot maintenance | [5 empty] | About 60 MW power interruption occurred under
at 33 kV Radio feeder bus isolator. | [5 empty] | Kabirpur S/S area from 21:43 to 22:35.
u) Barisal(N) 132/33 kV T-4 transformer was under shut down from 20:25 to 22:23 due to red hot maintenance
at 33 kV Y-phase bus isolator.
w) Sherpur 132/33 kV T-3 transformer was under shut down from 01:41 to 02:50(29-05-22) due to red hot | [5 empty] | About 35 MW power interruption occurred under
maintenance at 33 kV bay isolator. | [5 empty] | Sherpur S/S area from 01:41 to 02:50.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6678582 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 106 | 2403500
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 330 | 7594000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5131150 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 88 | 1596480 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3453178 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 1904664
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1015129
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 369612
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 572000 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1248000 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7519121
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1232064 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1289160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 142 | 1764480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 855095
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1140419
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1222260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 586440 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 807500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 720000 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 3926726 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 29 | 120566 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 75 | 89502 | Low Demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 75 | 99535 | Low Demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2613170
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 1887600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1903680 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 3147840 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 658440
| Dhaka area Total |  |  |  | 5898 | 3478 | 67896893
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 257308
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 82485 | Reserve.
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 29 | 679200 | Low Demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1049760 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2351007
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 196032 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 378495 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 259200 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 788160 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 531840
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 527520
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 67 | 1577280 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 6601418
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 898948 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2433808
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 64 | 878400
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2566800
| Chattogram area Total |  |  |  | 2382 | 1222 | 24480700
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4763000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 243800
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 25 | 369000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 734400 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1128480
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 184 | 4466181
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 30 | 1150799 | Low Demand
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 1513818 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2209360 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3202080
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 430560 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 129600 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2288640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 755200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 203597 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 451850 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 18432 | Low Demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1086420
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 1050840
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 617760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1297920 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1426 | 28111737
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 130 | 3615360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 406836
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 185 | 2904000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 2198400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 369390
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 575040
| Mymensingh Area Total |  |  |  | 622 | 461 | 10083376
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1025000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 962552 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2659009 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 3147000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 470400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 248112 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1329408 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 315840 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5240970
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 212665
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7140500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9319000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237420
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9322700
| Sylhet Area Total |  |  |  | 2477 | 1735 | 41630576
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22158545
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 85 | 2117760 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 45600 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 41 | 46848 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 252 | 6831072 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 369375 | Low Demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 1854720 | Low Demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 846576 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 592560
| Khulna Area Total |  |  |  | 2384 | 1482 | 34863056
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 699456 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 31 | 307727 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2085743 | Gas shortage+ST under maintenance
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 700 | 21029800 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 210 | 3580473
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 394800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1078 | 28097999
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 18 | 105632 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 27 | 177588 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 196533 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 286200 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4475473 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 9144800
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 227840 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 15 | 467280 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178020 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 313910 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 65 | 450744 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 1873728 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1861344
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33480
| Rajshahi Area Total |  |  |  | 2129 | 1071 | 19792572
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4277900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1888656
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37035
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1480512
| Rangpur Area Total |  |  |  | 720 | 395 | 7684103
| Total |  |  |  | 21584 | 12348 | 262641012
| Eastern Grid Total |  |  |  | 14393 | 8322 | 172203282
| Western Grid Total |  |  |  | 7191 | 4026 | 90437730
| National Grid Total |  |  |  | 21584 | 12348 | 262641012
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-28
(a) ENTIRE EASTERN GRID : |  | 8930.24 | MW | (b) ENTIRE WESTERN GRID : |  | 3081.8 | MW
i) Dhaka area |  | 4822.24 | MW | i) Khulna area |  | 1187 | MW
ii) Chittagong area |  | 1424 | MW | ii) Rajshahi area |  | 824.8 | MW
iii) Comilla area |  | 1222 | MW | iii) Barisal area |  | 257 | MW
iv) Mymensingh area |  | 922 | MW | iv) Rangpur area |  | 813 | MW
v) Sylhet area |  | 540 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12012.04 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 30 | 13:00 | Hasnabad | 82 | 13:00 | Palashbari | 99 | 20:00
Agargaon | 83 | 13:00 | Hathazari | 100 | 19:30 | Panchagarh | 58 | 19:30
Agrabad | 86 | 19:00 | Ishurdi | 68 | 16:00 | Patuakhali | 95 | 22:00
AKS | 19 | 10:00 | Jaldhaka | 66 | 20:00 | PHP | 10 | 11:00
AKSML | 14 | 13:00 | Jamalpur | 132 | 00:00 | Purbachal | 19 | 15:00
Amnura | 38 | 00:00 | Jashore | 113 | 13:00 | Purbasadipur | 114 | 20:00
Ashuganj | 47 | 00:00 | Jhenaidah | 108 | 00:00 | Rahim | 21 | 09:00
Bagerhat | 86 | 19:30 | Joydebpur | 178 | 21:00 | Rajbari | 56 | 00:00
Bakulia | 123 | 19:30 | Joypurhat | 60 | 00:00 | Rajendrapur | 112 | 20:00
Banani | 50 | 13:00 | Juldah | 25 | 16:00 | Rajshahi | 153 | 00:00
Bangabhaban | 10 | 10:00 | Kabirpur | 284 | 16:00 | Rajshahi | 35 | 14:00
Barapukuria | 49 | 19:30 | Kachua | 82 | 19:30 | Ramganj | 98 | 22:00
Barguna | 16 | 22:00 | Kallyanpur | 105 | 19:00 | Rampur | 13 | 14:00
Barishal | 110 | 12:00 | Kalurghat | 5 | 18:00 | Rangamati | 12 | 18:00
Barishal | 44 | 19:30 | Kamrangirchar | 76 | 19:00 | Rangpur | 140 | 19:00
Baroaulia | 64 | 15:00 | Kaptai | 4.2 | 19:30 | Ruppur | 3 | 10:00
Baroirhat | 55 | 19:00 | Kazla | 91 | 13:00 | Saidpur | 99 | 19:30
Bashundhara | 171 | 15:00 | Keranigonj | 64 | 19:00 | Satkhira | 113 | 00:00
BashundharaCement | 13 | 00:00 | Khagrachori | 26 | 19:00 | Satmasjid | 91 | 19:00
Beanibazar | 67 | 19:30 | Khulna | 84 | 13:00 | Savar | 161 | 19:30
Benapole | 60 | 00:00 | Khulshi | 163 | 19:30 | Shahjadpur | 81 | 00:00
Bhaluka | 144 | 19:30 | Kishoreganj | 132 | 20:00 | Shahjibazar | 112 | 21:00
Bhandaria | 30 | 21:00 | Kodda | 315 | 19:30 | Shahmirpur | 44.4 | 19:00
Bhangura | 38 | 18:30 | KSRM | 22 | 01:00 | Shariatpur | 74 | 21:00
Bheramara(GK) | 58 | 00:00 | Kulaura | 46 | 20:00 | Sherpur | 114 | 19:00
Bhulta | 238 | 21:00 | Kurigram | 70 | 20:00 | Shikalbaha | 28 | 19:30
Bog-Sherpur | 54 | 00:00 | Kushtia | 120 | 00:00 | Shitalakhya | 117 | 12:00
Bogura | 151 | 00:00 | Lalbag | 94 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 35 | 22:00 | Lalmonirhat | 50 | 19:30 | Shyampur | 180 | 12:00
Brahmanbaria | 166 | 22:00 | Madanganj | 190 | 19:00 | Siddhirganj | 114 | 19:00
BSRM | 161 | 10:00 | Madaripur | 96 | 22:00 | Sirajganj | 83 | 21:00
Cantonment | 140 | 19:00 | Madartek | 80 | 19:00 | Sonargaon | 82 | 10:00
Chandpur | 72 | 22:00 | Madunaghat | 59 | 15:00 | Sreemongol | 57 | 20:00
Chandraghona | 30 | 21:00 | Magura | 48 | 00:00 | Srinagar | 43.25 | 21:00
Chapai | 74 | 00:00 | Mahasthangarh | 60 | 00:00 | SSM | 8 | 23:00
Charsaidpur | 28 | 10:00 | Manikganj | 71 | 22:00 | Sunamganj | 52 | 21:00
Chauddagram | 57 | 21:00 | Maniknagar | 65 | 13:00 | Sylhet | 149 | 21:00
Chhatak | 32 | 20:00 | Matarbari | 40 | 19:00 | Tangail | 171 | 00:00
Chowmuhani | 210 | 20:00 | Matuail | 65 | 12:00 | Thakurgaon | 87 | 00:00
Chuadanga | 107 | 00:00 | Millgate | 64 | 12:00 | TK | 28.8 | 21:00
Coxsbazar | 115 | 20:00 | Mirpur | 134 | 19:00 | Tongi | 142 | 15:00
Cumilla(N) | 129 | 23:00 | Mirsorai | N/A | N/A | Ullon | 40 | 19:00
Cumilla(S) | 153 | 19:00 | Mithapukur | 29 | 19:30 | Uttara | 86 | 19:00
Daudkandi | 148 | 20:00 | Modern | 0 | 00:00 | UttaraNew | 15 | 13:00
Dhaka | 34 | 13:00 | Mogbazar | 117 | 15:00 | Zigatola | 43 | 13:00
Dhamrai | 116 | 15:00 | Mongla | 44 | 14:00
Dhanmondi | 134 | 11:00 | Motijheel | 36 | 13:00
Dohazari | 104 | 21:00 | Munshiganj | 100 | 21:00
Faridpur | 118 | 21:00 | Mymensingh | 249 | 20:00
Fatullah | 67 | 12:00 | Naogaon | 112 | 00:00
Fenchuganj | 48 | 19:00 | Narail | 51 | 19:30
Feni | 130 | 21:00 | Narinda | 70 | 13:00
Ghorashal | 65 | 20:00 | Narshingdi | 179 | 22:00
Goalpara | 26 | 19:30 | Natore | 124 | 19:30
Gollamari | 61 | 13:00 | Nawabganj | 52.1 | 21:00
Gopalganj | 91 | 21:00 | Netrakona | 122 | 20:00
GPH | 89 | 17:00 | New | 83.4 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 2:00 | 401 | 16:00 | Kaliakoir | 396 | 0.77083 | 380 | 0.375
| Bheramara | 399 | 5:00 | 392 | 24:00 | Bhulta | 394 | 24:00 | 371 | 0.5
| Ashuganj(N) | 395 | 1:00 | 374 | 12:00 | Gopalganj | 421 | 0.625 | 410 | 0.083333
| Payra | 423 | 19:30 | 415 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 9:00 | Hathazari | 236 | 21:00 | 225 | 24:00
| Ishurdi | 238 | 20:00 | 226 | 15:00 | Megnaghat | 229 | 17:00 | 220 | 16:00
| Ashuganj | 240 | 1:00 | 230 | 8:00 | Fenchuganj | 241 | 1:00 | 236 | 9:00
| Serajganj | 236 | 19:30 | 229 | 2:00 | Siddhirganj | 230 | 1:00 | 220 | 11:00
| Baghabari | 234 | 19:30 | 227 | 12:00 | Maniknagar | 228 | 1:00 | 216 | 11:00
| Barapukuria | 228 | 10:00 | 220 | 7:00 | Agargaon | 227 | 18:00 | 215 | 15:00
| Bogra | 232 | 19:30 | 224 | 1:00 | Barisal | 245 | 18:00 | 238 | 24:00
| Rajshahi | 241 | 20:00 | 225 | 13:00 | Bhola 225 MW | 248 | 18:30 | 238 | 24:00
| Khulna South | 237 | 18:30 | 227 | 14:00 | AKSML | 236 | 5:00 | 227 | 15:00
| Rampura | 227 | 1:00 | 217 | 12:00 | BSRM | 235 | 21:00 | 225 | 15:00
| Haripur | 225 | 1:00 | 217 | 11:00 | Bibiyana | 240 | 2:00 | 234 | 8:00
| Hasnabad | 224 | 1:00 | 214 | 12:00 | Bhulta | 231 | 24:00 | 219 | 12:00
| Shyampur | 227 | 1:00 | 216 | 12:00 | Ashuganj (S) | 237 | 1:00 | 228 | 9:00
| Aminbazar | 228 | 1:00 | 215 | 2:00 | Kaliakoir | 229 | 1:00 | 217 | 9:00
| Tongi | 230 | 1:00 | 216 | 12:00 | GPH | 237 | 21:00 | 226 | 15:00
| Comilla (N) | 230 | 1:00 | 223 | 9:00 | Jhenaidah | 238 | 8:00 | 223 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 00:00 | 127 | 12:00 | Manikganj | 137 | 01:00 | 122 | 18:00
| Agargaon | 132 | 00:00 | 124 | 12:00 | Maniknagar | 134 | 00:00 | 126 | 11:00
| Agrabad | 140 | 21:00 | 130 | 15:00 | Matarbari | 131 | 21:00 | 118 | 19:00
| AKS | 137 | 21:00 | 130 | 15:00 | Matuail | 133 | 00:00 | 126.5 | 12:00
| Aminbazar | 134 | 01:00 | 126 | 09:00 | Millgate | 135 | 00:00 | 124 | 12:00
| Amnura | 134 | 18:00 | 119 | 12:00 | Mirpur | 133 | 00:00 | 125 | 12:00
| Ashuganj | 138 | 10:00 | 135 | 16:00 | Mithapukur | 134 | 18:00 | 126 | 07:00
| Bagerhat | 133 | 09:00 | 125 | 23:00 | Modern | 140 | 05:00 | 132 | 15:00
| Bakulia | 138 | 19:30 | 132 | 16:00 | Mogbazar | 137 | 05:00 | 128 | 12:00
| Banani | 135 | 01:00 | 123 | 13:00 | Mongla | 137 | 09:00 | 129 | 23:00
| Bangabhaban | 134 | 00:00 | 122 | 11:00 | Motijheel | 134 | 00:00 | 122 | 11:00
| Barapukuria | 136 | 10:00 | 130 | 07:00 | Munshiganj | 138 | 01:00 | 130 | 08:00
| Barguna | 138 | 16:00 | 130 | 11:00 | Mymensingh | 134 | 00:00 | 126 | 07:00
| Barishal | 143 | 18:30 | 127 | 11:00 | Naogaon | 136 | 18:00 | 123 | 00:00
| Barishal | 143 | 17:00 | 137 | 00:00 | Narail | 136 | 18:30 | 124 | 13:00
| Baroaulia | 142 | 21:00 | 133 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 135 | 17:00 | 128 | 04:00 | Narshingdi | 128 | 00:00 | 121 | 12:00
| Bashundhara | 134 | 00:00 | 123 | 16:00 | Natore | 136 | 18:00 | 126 | 00:00
| BashundharaCement | 136 | 06:00 | 129 | 07:00 | Nawabganj | 136 | 00:00 | 127 | 16:00
| Beanibazar | 132 | 06:00 | 127 | 19:00 | Netrakona | 132 | 21:00 | 122 | 18:30
| Benapole | 135 | 05:00 | 128 | 00:00 | New | 136 | 01:00 | 124 | 12:00
| Bhaluka | 131 | 04:00 | 117 | 19:00 | Niamatpur | 136 | 18:00 | 119 | 00:00
| Bhandaria | 144 | 18:30 | 138 | 12:00 | Noapara | 137 | 09:00 | 131 | 15:00
| Bhangura | 140 | 20:00 | 133 | 00:00 | Pabna | 137 | 18:00 | 130 | 16:00
| Bheramara | 137 | 18:00 | 132 | 16:00 | Palashbari | 131 | 17:00 | 123 | 07:00
| Bheramara(GK) | 139 | 05:00 | 134 | 15:00 | Panchagarh | 135 | 13:00 | 121 | 02:00
| Bhulta | 127 | 00:00 | 118 | 11:00 | Patuakhali | 137 | 05:00 | 131 | 11:00
| Bog-Sherpur | 139 | 20:00 | 129 | 00:00 | PHP | 136 | 18:30 | 127 | 04:00
| Bogura | 137 | 18:00 | 128 | 00:00 | Purbachal | 135 | 00:00 | 124 | 12:00
| Bogura | 137 | 19:30 | 130 | 00:00 | Purbasadipur | 134 | 10:00 | 125 | 07:00
| Brahmanbaria | 133 | 09:00 | 130 | 19:00 | Rahim | 134 | 00:00 | 127 | 11:00
| Cantonment | 132 | 01:00 | 122 | 15:00 | Rajbari | 139 | 18:30 | 131 | 00:00
| Chandpur | 141 | 16:00 | 128 | 09:00 | Rajendrapur | 136 | 02:00 | 124 | 09:00
| Chandraghona | 140 | 21:00 | 132 | 16:00 | Rajshahi | 133 | 18:00 | 122 | 15:00
| Chapai | 133 | 18:00 | 119 | 12:00 | Rajshahi | 132 | 20:00 | 121 | 12:00
| Charsaidpur | 137 | 00:00 | 127 | 09:00 | Ramganj | 137 | 17:00 | 123 | 04:00
| Chauddagram | 134 | 18:00 | 128 | 23:00 | Rampur | 139 | 21:00 | 130 | 15:00
| Chhatak | 133 | 06:00 | 127 | 12:00 | Rampura | 135 | 00:00 | 126 | 16:00
| Chowmuhani | 135 | 19:30 | 124 | 07:00 | Rangamati | 139 | 21:00 | 132 | 16:00
| Chuadanga | 136 | 19:30 | 117 | 13:00 | Rangpur | 132 | 10:00 | 124 | 07:00
| Coxsbazar | 131 | 21:00 | 118 | 19:30 | Ruppur | 139 | 17:00 | 132 | 00:00
| Cumilla(N) | 135 | 19:00 | 130 | 09:00 | Saidpur | 133 | 10:00 | 126 | 19:00
| Cumilla(S) | 136 | 17:00 | 129 | 20:00 | Satkhira | 137 | 20:00 | 128 | 00:00
| Daudkandi | 130 | 00:00 | 127 | 10:00 | Satmasjid | 132 | 00:00 | 123 | 15:00
| Dhaka | 136 | 00:00 | 127 | 12:00 | Savar | 135 | 01:00 | 126 | 08:00
| Dhamrai | 133 | 00:00 | 124 | 15:00 | Shahjadpur | 141 | 18:00 | 134 | 00:00
| Dhanmondi | 136 | 00:00 | 127 | 11:00 | Shahjibazar | 134 | 00:00 | 133 | 02:00
| Dohazari | 140 | 21:00 | 129 | 15:00 | Shahmirpur | 139 | 20:00 | 131 | 16:00
| Faridpur | 138 | 18:30 | 131 | 00:00 | Shariatpur | 138 | 09:00 | 133 | 23:00
| Fatullah | 134 | 00:00 | 126 | 12:00 | Sherpur | 139 | 00:00 | 124 | 06:00
| Fenchuganj | 136 | 06:00 | 133 | 19:30 | Shikalbaha | 141 | 05:00 | 133 | 15:00
| Feni | 136 | 17:00 | 129 | 02:00 | Shikalbaha | 140 | 22:00 | 134 | 15:00
| Ghorashal | 138 | 00:00 | 135 | 09:00 | Shitalakhya | 137 | 00:00 | 129 | 09:00
| Goalpara | 139 | 05:00 | 132 | 11:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 05:00 | 133 | 15:00 | Shyampur | 134 | 01:00 | 125 | 12:00
| Gopalganj | 139 | 18:00 | 134 | 16:00 | Shyampur | 134 | 00:00 | 126 | 12:00
| Gopalganj_I | 140 | 18:30 | 135 | 00:00 | Siddhirganj | 134 | 00:00 | 127 | 09:00
| Gulshan | 135 | 00:00 | 127 | 12:00 | Sirajganj | 137 | 19:00 | 130 | 00:00
| Halishahar | 140 | 21:00 | 130 | 15:00 | Sonargaon | 134 | 00:00 | 127 | 09:00
| Haripur | 134 | 00:00 | 127 | 11:00 | Sreemongol | 136 | 05:00 | 133 | 12:00
| HaripurSBU | 137 | 11:00 | 127 | 12:00 | Srinagar | 136 | 00:00 | 127 | 15:00
| Hasnabad | 137 | 00:00 | 130 | 10:00 | SSM | 142 | 21:00 | 132 | 10:00
| Hathazari | 140 | 21:00 | 132 | 15:00 | Sunamganj | 130 | 05:00 | 124 | 21:00
| Ishurdi | 138 | 18:00 | 132 | 12:00 | Sylhet | 133 | 00:00 | 130 | 16:00
| Jaldhaka | 131 | 10:00 | 122 | 01:00 | Tangail | 137 | 00:00 | 129 | 15:00
| Jamalpur | 141 | 21:00 | 123 | 07:00 | Thakurgaon | 136 | 13:00 | 122 | 02:00
| Jashore | 135 | 04:00 | 127 | 13:00 | TK | 140 | 21:00 | 132 | 15:00
| Jhenaidah | 138 | 20:00 | 129 | 15:00 | Tongi | 137 | 01:00 | 126 | 15:00
| Jhenaidah | 138 | 20:00 | 129 | 14:00 | Ullon | 136 | 00:00 | 127 | 11:00
| Joydebpur | 142 | 13:00 | 135 | 08:00 | Uttara | 134 | 02:00 | 126 | 15:00
| Joypurhat | 140 | 18:00 | 120 | 00:00 | UttaraNew | 133 | 00:00 | 125 | 11:00
| Juldah | 140 | 05:00 | 131 | 15:00 | Zigatola | 136 | 01:00 | 127 | 17:00
| Kabirpur | 136 | 00:00 | 120 | 12:00
| Kachua | 139 | 13:00 | 128 | 03:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 134 | 00:00 | 127 | 08:00
| Kalurghat | 141 | 21:00 | 130 | 00:00
| Kamrangirchar | 135 | 00:00 | 128 | 12:00
| Kaptai | 138 | 22:00 | 135 | 03:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 496 | 7811 | 3966 | 11777 |  |  |  | QF-LDC-11
0:30 | 276 | 7640 | 3882 | 11522 | Date: | 2022-05-28
1:00 | 56 | 7469 | 3798 | 11267
1:30 | 94 | 7275.5 | 3719 | 10994.5
2:00 | 132 | 7082 | 3640 | 10722
2:30 | 157 | 6990 | 3628.5 | 10618.5 | [5 empty] | Gen. at Eve. Peak | 12348 | 12348 MW (19:30 )
3:00 | 182 | 6898 | 3617 | 10515 | [6 empty] | 19:30
3:30 | 245 | 6728.5 | 3608.5 | 10337 | [5 empty] | Gen. at Day Peak | 10702 | 10702 MW (12:00 )
4:00 | 308 | 6559 | 3600 | 10159 | [6 empty] | 12:00
4:30 | 330 | 6514.5 | 3568.5 | 10083 | [5 empty] | Highest Generation | 12348
5:00 | 352 | 6470 | 3537 | 10007 | [6 empty] | 19:30
5:30 | 391 | 6103.5 | 3449 | 9552.5
6:00 | 430 | 5737 | 3361 | 9098
6:30 | 433 | 5782.5 | 3349.5 | 9132
7:00 | 436 | 5828 | 3338 | 9166
7:30 | 537 | 5798.5 | 3402 | 9200.5
8:00 | 638 | 5769 | 3466 | 9235
8:30 | 744 | 5867 | 3485 | 9352
9:00 | 850 | 5965 | 3504 | 9469
9:30 | 796 | 6228 | 3462 | 9690
10:00 | 742 | 6491 | 3420 | 9911
10:30 | 695 | 6678.5 | 3415.5 | 10094
11:00 | 648 | 6866 | 3411 | 10277
11:30 | 641 | 6978.5 | 3511 | 10489.5
12:00 | 634 | 7091 | 3611 | 10702
12:30 | 549 | 7325.5 | 3663 | 10988.5
13:00 | 464 | 7560 | 3715 | 11275
13:30 | 502 | 7548.5 | 3748.5 | 11297
14:00 | 540 | 7537 | 3782 | 11319
14:30 | 566 | 7647.5 | 3800.5 | 11448
15:00 | 592 | 7758 | 3819 | 11577
15:30 | 627 | 7629.5 | 3793.5 | 11423
16:00 | 662 | 7501 | 3768 | 11269
16:30 | 737 | 7504 | 3624.5 | 11128.5
17:00 | 812 | 7507 | 3481 | 10988
17:30 | 861 | 7268 | 3367 | 10635
18:00 | 910 | 7029 | 3253 | 10282
18:30 | 767 | 7651 | 3406.5 | 11057.5
19:00 | 624 | 8273 | 3560 | 11833
19:30 | 784 | 8322 | 4026 | 12348
20:00 | 614 | 8184 | 3969 | 12153 |  |  |  | Executive Engineer
20:30 | 614 | 8163.5 | 4002.5 | 12166 |  |  |  | Network Operation Division
21:00 | 614 | 8143 | 4036 | 12179
21:30 | 513 | 8082.5 | 3993.5 | 12076
22:00 | 412 | 8022 | 3951 | 11973 |  |  |  |  | Page 6 of 7
22:30 | 436 | 8013 | 3952 | 11965
23:00 | 460 | 8004 | 3953 | 11957
23:30 | 478 | 7907.5 | 3959.5 | 11867
24:00 | 496 | 7811 | 3966 | 11777
12348 MW (19:30 )
10702 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-28 |  | Energy |  | 262641012
[13 empty] | 2022-05-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3479 | 924 | 2238 | 0 | 3640 | 1035 | 38 | 0 | 311 | 112 | 0 | 0
0:30 | 3503 | 918 | 2205 | 0 | 3484 | 1035 | 38 | 0 | 239 | 100 | 0 | 0 | Date: | 2022-05-28
1:00 | 3527 | 912 | 2172 | 0 | 3328 | 1035 | 38 | 0 | 167 | 88 | 0 | 0
1:30 | 3489.5 | 912 | 2177 | 0 | 3153 | 1030.5 | 38 | 0 | 107.5 | 87 | 0 | 0 | [8 empty] | Total Energy | 262.641 | Total Energy Gen 262.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 262.641 MKWHr
2:00 | 3452 | 912 | 2182 | 0 | 2978 | 1026 | 38 | 0 | 48 | 86 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3499.5 | 912 | 2208 | 0 | 2844 | 1001 | 38 | 0 | 32 | 84 | 0 | 0 | [8 empty] | Energy Requirement | 262.641
3:00 | 3547 | 912 | 2234 | 0 | 2710 | 976 | 38 | 0 | 16 | 82 | 0 | 0
3:30 | 3540.5 | 912.5 | 2243 | 0 | 2530 | 976 | 38 | 0 | 16 | 81 | 0 | 0 | [6 empty] | Shortage
4:00 | 3534 | 913 | 2252 | 0 | 2350 | 976 | 38 | 0 | 16 | 80 | 0 | 0
4:30 | 3539 | 912.5 | 2236 | 0 | 2297 | 965.5 | 38 | 0 | 16 | 79 | 0 | 0
5:00 | 3544 | 912 | 2220 | 0 | 2244 | 955 | 38 | 0 | 16 | 78 | 0 | 0
5:30 | 3523.5 | 913.5 | 2211.5 | 0 | 1815.5 | 955 | 38 | 0 | 16 | 76 | 3.5 | 0
6:00 | 3503 | 915 | 2203 | 0 | 1387 | 955 | 38 | 0 | 16 | 74 | 7 | 0
6:30 | 3515 | 914.5 | 2229 | 0 | 1391.5 | 930 | 38 | 0 | 16 | 74 | 24 | 0 |  |  |  |  | Coal
7:00 | 3527 | 914 | 2255 | 0 | 1396 | 905 | 38 | 0 | 16 | 74 | 41 | 0
7:30 | 3508.5 | 914 | 2276 | 0 | 1418.5 | 890 | 38 | 0 | 16 | 77 | 62.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3490 | 914 | 2297 | 0 | 1441 | 875 | 38 | 0 | 16 | 80 | 84 | 0
8:30 | 3430.5 | 914.5 | 2209.5 | 0 | 1679 | 875 | 38 | 0 | 16 | 84 | 105.5 | 0
9:00 | 3371 | 915 | 2122 | 0 | 1917 | 875 | 38 | 0 | 16 | 88 | 127 | 0
9:30 | 3442.5 | 915 | 2058 | 0 | 2081.5 | 915 | 38 | 0 | 16 | 91 | 133 | 0
10:00 | 3514 | 915 | 1994 | 0 | 2246 | 955 | 38 | 0 | 16 | 94 | 139 | 0
10:30 | 3520 | 914.5 | 1971 | 0 | 2441 | 965 | 38 | 0 | 16 | 97 | 131.5 | 0
11:00 | 3526 | 914 | 1948 | 0 | 2636 | 975 | 38 | 0 | 16 | 100 | 124 | 0
11:30 | 3493.5 | 914 | 1961.5 | 0 | 2821.5 | 995 | 38 | 0 | 34.5 | 92 | 139.5 | 0
12:00 | 3461 | 914 | 1975 | 0 | 3007 | 1015 | 38 | 0 | 53 | 84 | 155 | 0
12:30 | 3442 | 914 | 2001.5 | 58.5 | 3174 | 1030 | 38 | 0 | 87.5 | 90 | 153 | 0
13:00 | 3423 | 914 | 2028 | 117 | 3341 | 1045 | 38 | 0 | 122 | 96 | 151 | 0
13:30 | 3423 | 914 | 2028 | 117 | 3341 | 1045 | 38 | 0 | 122 | 96 | 151 | 0
14:00 | 3423 | 914 | 2028 | 117 | 3341 | 1045 | 38 | 0 | 122 | 96 | 151 | 0
14:30 | 3476.5 | 914 | 2023 | 58.5 | 3465 | 1065 | 38 | 0 | 155 | 100 | 131 | 0
15:00 | 3530 | 914 | 2018 | 0 | 3589 | 1085 | 38 | 0 | 188 | 104 | 111 | 0
15:30 | 3521 | 914 | 1982 | 0 | 3519 | 1070 | 38 | 0 | 188 | 104 | 87 | 0
16:00 | 3512 | 914 | 1946 | 0 | 3449 | 1055 | 38 | 0 | 188 | 104 | 63 | 0
16:30 | 3402 | 914 | 1911.5 | 0 | 3444 | 1025 | 38 | 0 | 190.5 | 104 | 44.5 | 0
17:00 | 3402 | 914 | 1877 | 0 | 3439 | 995 | 38 | 0 | 193 | 104 | 26 | 0
17:30 | 3257.5 | 914 | 1864.5 | 0 | 3287 | 955 | 38 | 0 | 200 | 102 | 17 | 0
18:00 | 3113 | 914 | 1852 | 0 | 3135 | 915 | 38 | 0 | 207 | 100 | 8 | 0
18:30 | 3263 | 918.5 | 2012 | 168.5 | 3305.5 | 895 | 53 | 0 | 327 | 111 | 4 | 0
19:00 | 3413 | 923 | 2172 | 337 | 3476 | 875 | 68 | 0 | 447 | 122 | 0 | 0
19:30 | 3473 | 922 | 2214 | 199 | 3960 | 875 | 68 | 0 | 521 | 116 | 0 | 0
20:00 | 3498 | 923 | 2182 | 38 | 3987 | 865 | 68 | 0 | 476 | 116 | 0 | 0
20:30 | 3482 | 923.5 | 2227.5 | 19 | 3991.5 | 900 | 68 | 0 | 438.5 | 116 | 0 | 0
21:00 | 3466 | 924 | 2273 | 0 | 3996 | 935 | 68 | 0 | 401 | 116 | 0 | 0
21:30 | 3447.5 | 923.5 | 2215 | 0 | 3963.5 | 955.5 | 68 | 0 | 387 | 116 | 0 | 0
22:00 | 3429 | 923 | 2157 | 0 | 3931 | 976 | 68 | 0 | 373 | 116 | 0 | 0
22:30 | 3417.5 | 923 | 2158.5 | 0 | 3939 | 990.5 | 68 | 0 | 354.5 | 114 | 0 | 0
23:00 | 3406 | 923 | 2160 | 0 | 3947 | 1005 | 68 | 0 | 336 | 112 | 0 | 0
23:30 | 3442.5 | 923.5 | 2199 | 0 | 3793.5 | 1020 | 53 | 0 | 323.5 | 112 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.0° C
24:00 | 3479 | 924 | 2238 | 0 | 3640 | 1035 | 38 | 0 | 311 | 112 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 262.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 262.641 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 905760
2 | Karnaphuli Hydro PP Unit-4 & 5 | [17 empty] | 0 |  | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 144000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 2 | 25 | 25 | 25 | 8 | 8 | 8 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 257308
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 10 | 11 | 1 | 4 | 9 | 9 | 10 | 8 | 6 | 3 | 1 | [8 empty] | 82485
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 13 | 17 | 17 | 17 |  | 85 | 85 | 85 | 85 | 43 | 17 | 0 | 378495
12 | Hathazari 100 MW peaking PP | [19 empty] | 32 | 42 | 48 | 34 | 34 | 34 | 34 | 196032
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 51 | 51 | 53 | 93 | 87 | 87 | 87 | 100 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2351007
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 20 | 20 | [5 empty] | 18432
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [9 empty] | 37 | 96 | 95 | 94 | 61 | 97 | 94 | 0 | [9 empty] | 572000
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 335 | 319 | 319 | 316 | 314 | 314 | 280 | 335 | 300 | 325 | 330 | 280 | 327 | 332 | 332 | 280 |  | 330 | 333 | 335 | 335 | 280 | 280 | 335 | 7519121
18 | Kodda 300 MW PP Unit-2 (Summit) | 130 | 15 | 0 | [5 empty] | 20 | 60 | 178 | 225 | 243 | 245 | 248 | 248 | 248 | 252 |  | 275 | 275 | 260 | 280 | 285 | 295 | 290 | 3926726
19 | Ashuganj 195MW PP (APSCL-United) | 182 | 184 | 184 | 187 | 192 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 195 | 195 | 197 |  | 182 | 184 | 195 | 185 | 158 | 110 | 110 | 4466181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6678582
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 29 | 29 | 29 | 29 | 32 | 32 | 32 | 33 | 33 | 32 | 32 | 31 | 31 | 32 | 35 | 35 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 734400
33 | Ashuganj 225 MW CCPP | 199 | 214 | 214 | 214 | 217 | 180 | 203 | 180 | 183 | 181 | 181 | 201 | 180 | 180 | 193 | 180 | 211 | 170 |  | 211 | 213 | 213 | 187 | 172 | 191 | 193 | 4763000
34 | Ashuganj 450 MW CCPP(South) | [13 empty] | 25 | 25 | 25 | 14 | 40 |  | 40 | 25 | 25 | 18 | 80 | 45 | 55 | 369000
| Ashuganj 450 MW CCPP(North) | 100 | [25 empty] | 243800
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 20 | 51 | 55 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 53 | 51 | 52 | 53 |  | 53 | 53 | 54 | 54 | 55 | 54 | 55 | 1128480
36 | Chandpur 150 MW CCPP | 100 | 100 | 102 | 100 | 102 | 100 | 100 | 100 | 100 | 100 | 98 | 0 |  | 98 | 98 | 100 | 100 | 100 |  | 101 | 101 | 101 | 101 | 101 | 100 | 100 | 2209360
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5131150
41 | Haripur 360MW CCPP(HPL) | 338 | 338 | 337 | 337 | 337 | 283 | 303 | 303 | 300 | 322 | 322 | 300 | 322 | 322 | 322 | 290 | 280 | 250 |  | 330 | 330 | 332 | 332 | 333 | 337 | 337 | 7594000
42 | RPCL 210MW CCPP | 177 | 181 | 197 | 200 | 200 | 201 | 191 | 178 | 164 | 152 | 141 | 138 | 110 | 122 | 130 | 138 | 138 | 128 |  | 128 | 130 | 129 | 129 | 131 | 147 | 142 | 3615360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 12 | 26 | 40 | 44 | 41 | 50 | 54 | 45 | 37 | 26 | 11 | 2 | [8 empty] | 369390
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 44 | 43 | 44 | 44 | 43 | 44 | 44 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 962552
46 | Shajibazar 330 MW CCPP | 158 | 159 | 160 | 159 | 160 | 161 | 158 | 158 | 160 | 158 | 158 | 156 | 156 | 156 | 154 | 105 | 111 | 110 |  | 111 | 110 | 110 | 111 | 111 | 110 | 110 | 3147000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 63 | 40 | 40 | 40 | 40 | 60 | 60 | 59 | 61 | 61 | 55 | 62 | 56 | 40 |  | 56 | 56 | 57 | 57 | 62 | 61 | 61 | 1329408
48 | Shahjibazar 86MW PP (Shahjibazar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 315840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 219 | 219 | 220 | 220 | 220 | 185 |  | 220 | 220 | 220 | 219 | 220 | 220 | 219 | 5240970
51 | Sylhet 20 MW GTPP | [9 empty] | 0
52 | Sylhet 50MW PP (EPL) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237420
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 0 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 470400
56 | Shahjahanulla 25 MW PP | [19 empty] | 16 | 24 | 24 | 24 | 24 | 16 | 16 | 212665
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 270 | 295 | 290 | 275 | 275 | 315 | 310 | 280 | 320 | 290 | 310 | 310 | 290 | 310 | 275 | 290 | 270 |  | 305 | 270 | 260 | 290 | 265 | 305 | 310 | 7140500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 397 | 400 | 395 | 400 | 360 | 394 | 391 | 381 | 394 | 390 | 380 | 393 | 392 | 360 |  | 388 | 395 | 392 | 396 | 395 | 375 | 398 | 9322700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 40 | 53 | 53 | 53 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1140419
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 575040
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531840
61 | Narshingdi 22 MW PP (Doreen) | [5 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 369612
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 406836
63 | Impoprt (Tripura) | 88 | 86 | 82 | 80 | 78 | 74 | 74 | 80 | 88 | 94 | 100 | 84 | 96 | 98 | 104 | 104 | 104 | 100 |  | 122 | 116 | 116 | 116 | 116 | 112 | 112 | 2288640
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 39 | 11 | 6 | 2 | 6 | 6 | 11 | 7 | 5 | 4 | 11 | 9 |  | 9 | 16 | 21 | 19 | 28 | 36 | 40 | 527520
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 430560
66 | Feni 11 MW PP (Doreen) | 6 | 0 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 129600
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 22 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 755200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 6 | 17 | 17 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 451850
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 5 | 28 | 27 | 28 | 28 | 27 | 27 | 27 | 27 | 27 |  | 22 | 27 | 28 | 28 | 28 | 28 | 28 | 622260
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 586440
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807500
73 | Ghorashal 108MW PP (Regent) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 99 | 99 | 102 | 102 | 102 | 102 | 102 | 103 | 103 | 58 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2403500
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 1086420
| Chowmuhani 113 MW | 12 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 60 | 113 | 114 |  | 114 | 114 | 114 | 115 | 114 | 116 | 34 | 1050840
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 152 | 144 | 17 | 17 | 17 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 108 |  | 114 | 126 | 128 | 144 | 144 | 140 | 130 | 3147840
77 | Siddhirganj 100 PP(Dutch Bangla) | 48 | 37 | [6 empty] | 18 | 40 | 40 | 48 | 78 | 90 | 91 | 91 | 70 | 50 |  | 73 | 91 | 91 | 83 | 91 | 91 | 91 | 1248000
78 | Gazipur 52 MW PP | [8 empty] | 30 | 33 | 41 | 41 | 49 | 49 | 49 | 33 | 33 | 42 |  | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 720000
79 | Kodda 150MW PP | 64 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 115 | 132 | 132 | 100 | 100 | 100 |  | 142 | 142 | 142 | 145 | 150 | 132 | 132 | 1764480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 203597
| Gazipur 100 MW PP | 105 | 105 | 70 | 70 | 70 | 17 | 17 | 21 | 70 | 70 | 70 | 80 | 90 | 90 | 90 | 70 | 70 | 70 |  | 90 | 90 | 90 | 90 | 90 | 105 | 90 | 1887600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 |  | 2 | 2 | 0 | 1 | 3 | 2 | 3 | 2 | 1 | [9 empty] | 23039
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 898948
| Karnaphuli Power Ltd. | 107 | 93 | 105 | 98 | 89 | 89 | 88 | 88 | 88 | 88 | 88 | 90 | 105 | 105 | 106 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 103 | 2433808
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 80 | 17 | 16 | 16 | 26 | 37 | 82 | 95 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1904664
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 135 | 140 | 135 | 140 | 130 | 145 | 140 | 145 | 150 | 145 | 138 | 145 | 140 | 145 | 142 | 140 | 140 | 138 |  | 145 | 150 | 150 | 150 | 145 | 145 | 135 | 3453178
87 | Meghnaghat 100 MW(IEL) | 82 | 81 | 82 | 81 | 81 | 81 | 81 | 0 |  |  |  | 20 | 62 | 80 | 80 | 80 | 80 | 80 |  | 75 | 88 | 82 | 88 | 82 | 88 | 89 | 1596480
| Meghnaghat 104 MW PP (OPCL) | 92 | 91 | 91 | 91 | 92 | 22 | 17 | 17 | 54 | 78 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 54 |  | 75 | 90 | 90 | 90 | 89 | 89 | 90 | 1903680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 259200
92 | Fenchuganj 44MW (Energyprima) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [17 empty] | 248112
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 |  | 30 | 30 | 30 | 44 | 51 | 51 | 51 | 1150799
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 0 | [7 empty] | 24 | 48 | 76 | 84 | 93 | 93 | 93 | 68 | 68 |  | 93 | 93 | 93 | 93 | 93 | 93 | 94 | 1232064
95 | Patenga 50MW PP (Baraka) | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | [10 empty] | 7 | 29 | 36 | 48 | 50 | 50 | 50 | 679200
96 | Chattogram 108 MW PP (ECPV) | 70 | 72 | 74 | 77 | 77 | 29 | 19 | 20 | 63 | 75 | 75 | 75 | 73 | 71 | 72 | 72 | 68 | 67 |  | 67 | 67 | 67 | 68 | 70 | 70 | 74 | 1577280
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 15 | 15 | 15 | 15 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 48 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1015129
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 855095
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2659009
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 0 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1289160
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 52 | [6 empty] | 151 | 29 | 13 |  |  |  |  | 120566
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 40 | [6 empty] | 76 | 75 | [5 empty] | 89502
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 160 | 50 | 16 | 16 | 16 | 19 | 32 | 60 | 90 | 110 | 135 | 174 | 180 | 171 | 175 | 160 |  | 184 | 185 | 200 | 140 | 100 | 100 | 110 | 2904000
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 25 | [6 empty] | 90 | 75 | 25 |  |  |  |  | 99535
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 101 | 28 | 17 | 17 | 17 | 17 | 31 | 76 | 114 | 131 | 149 | 149 | 149 | 149 | 123 | 122 |  | 143 | 149 | 149 | 149 | 149 | 149 | 149 | 2613170
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 38 | 788160
116 | Chandpur 200MW (Desh energy) | 170 | 120 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 126 | 190 | 196 | 200 | 200 | 155 | 155 | 155 |  | 166 | 200 | 200 | 200 | 200 | 200 | 200 | 3202080
117 | Ashuganj 150MW PP (Midland) | 132 | 140 | 132 | 10 | 10 | 10 | 10 | 13 | 30 | 53 | 50 | 50 | 73 | 107 | 122 | 80 | 60 | 40 |  | 10 | 10 | 10 | 16 | 41 | 71 | 80 | 1513818
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 401 | 399 | 399 | 400 | 401 | 401 | 389 | 403 | 403 | 405 | 404 | 365 | 403 | 403 | 403 | 328 |  | 402 | 401 | 401 | 402 | 401 | 403 | 401 | 9319000
| Jamalpur 115 MW PP (United) | 107 | 106 | 107 | 107 | 107 | 16 | 16 | 41 | 98 | 105 | 99 | 103 | 103 | 103 | 102 | 102 | 101 | 75 |  | 103 | 103 | 102 | 104 | 75 | 75 | 83 | 2198400
| Anwara 300 MW PP (United) | 283 | 284 | 283 | 300 | 300 | 230 | 247 | 265 | 265 | 266 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 281 |  | 285 | 285 | 285 | 287 | 287 | 290 | 288 | 6601418
| Juldah unit-2 (Acorn) | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 32 | 25 | 25 | 55 |  | 64 | 64 | 64 | 64 | 56 | 50 | 38 | 878400
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 105 | 90 | 90 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2566800
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 617760
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 57 | [8 empty] | 3 | 22 | 45 | 99 | 100 | 101 | 75 | 75 | 51 |  | 70 | 90 | 96 | 100 | 100 | 100 | 99 | 1297920
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 18 | 0 | 0 | [9 empty] | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 658440
120 | Eastern Zone Total | 7469 | 7082 | 6898 | 6559 | 6470 | 5737 | 5828 | 5769 | 5965 | 6491 | 6866 | 7091 | 7560 | 7537 | 7758 | 7501 | 7507 | 7029 |  | 8273 | 8322 | 8184 | 8143 | 8022 | 8004 | 7811 | 172203282
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 81 | 97 | 97 | 98 | 98 | 98 | 97 | 95 | 92 | 92 | 92 | 91 | 90 | 87 | 87 | 90 | 90 | 49 |  | 50 | 85 | 95 | 96 | 96 | 96 | 96 | 2117760
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 3 |  | 29 | 38 | 12 |  |  |  |  | 45600
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 94 | 70 | 70 | 35 | 35 | 45 | 70 | 70 | 80 | 105 | 105 | 105 | 105 | 105 | 53 | 35 |  | 35 | 53 | 53 | 53 | 53 | 53 | 60 | 1854720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 22 | 45 | 70 | 86 | 74 | 86 | 74 | 42 | 52 | 22 | 8 | 4 | [8 empty] | 592560
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 394800
133 | Bhola Nutan Biddut BD LTD (GAS) | 211 | 218 | 222 | 223 | 187 | 223 | 218 | 218 | 184 | 45 | 54 | 50 | 50 | 50 | 52 | 45 | 50 | 140 |  | 160 | 210 | 220 | 220 | 183 | 182 | 221 | 3580473
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 29 | 32 | 32 | 32 | 32 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 699456
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 88 | 88 | 88 | 87 | 88 | 85 | 85 | 85 | 84 | 83 | 83 | 86 | 87 | 86 | 87 | 83 | 87 |  | 87 | 88 | 88 | 87 | 87 | 88 | 88 | 2085743
140 | Bhola 33 MW PP (Venture) | 12 | 11 | 10 | 9 | 10 | 10 | 10 | 8 | 8 | 10 | 10 | 6 | 6 | 0 | 1 | 9 | 16 | 18 |  | 21 | 31 | 28 | 31 | 31 | 32 | 31 | 307727
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | [10 empty] | 8 | 24 | 40 | 40 | 40 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 369375
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 38 | 41 | 18 |  |  |  |  | 46848
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 50 | 32 | 32 | 32 | 28 | 15 | 15 | 15 | 15 | 0 |  | 15 | 15 | 50 | 50 | 50 | 32 | 32 |  | 32 | 67 | 67 | 50 | 50 | 50 | 50 | 846576
146 | Bheramara HVDC | 912 | 912 | 912 | 913 | 912 | 915 | 914 | 914 | 915 | 915 | 914 | 914 | 914 | 914 | 914 | 914 | 914 | 914 |  | 923 | 922 | 923 | 924 | 923 | 923 | 924 | 22158545
147 | Bheramara 410 MW CCPP | 275 | 285 | 290 | 295 | 300 | 305 | 310 | 305 | 300 | 290 | 285 | 275 | 270 | 260 | 255 | 255 | 230 | 210 |  | 235 | 252 | 275 | 270 | 265 | 270 | 270 | 6831072
148 | Payra 1320 MW | 860 | 850 | 800 | 800 | 780 | 780 | 730 | 700 | 700 | 780 | 800 | 840 | 870 | 880 | 910 | 880 | 820 | 740 |  | 700 | 700 | 690 | 760 | 800 | 830 | 860 | 21029800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 176 | 176 | 176 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 176 | 175 | 175 | 4277900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 17 | 17 | 17 |  | 17 | 18 | 17 | 8 | 8 | 8 | 0 | 105632
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 33480
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 168 | 168 | 168 | 168 | 170 | 172 | 175 | 175 | 180 | 174 | 181 | 194 | 189 | 190 | 186 | 184 | 175 | 140 |  | 154 | 186 | 188 | 190 | 160 | 160 | 170 | 4475473
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 353 | 350 | 380 | 380 | 372 | 350 | 350 | 422 | 423 | 380 | 350 | 380 | 414 | 414 | 414 | 415 | 320 | 300 |  | 415 | 419 | 371 | 420 | 380 | 380 | 420 | 9144800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 5 | 7 | 20 | 21 | 22 | 27 | 26 |  | 26 | 27 | 26 | 0 |  |  |  | 177588
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 19 | 18 | 18 | 18 | 19 | 18 |  | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 467280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178020
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 8 | 24 | 24 | 8 | 8 | 8 |  | 8 | 34 | 34 | 34 | 8 | 0 |  | 196533
167 | Katakhali 50 MW Peaking PP | [13 empty] | 11 | 22 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 286200
168 | Santahar 50 MW Peaking PP | 38 | [16 empty] | 12 |  | 31 | 31 | 31 | 32 | 30 | 30 | 30 | 227840
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 43 | 43 | 43 | 43 | 8 | 8 | 313910
170 | Chapainawabganj 100 MW Peaking PP | 65 | [18 empty] | 15 | 65 | 65 | 65 | 76 | 83 | 83 | 450744
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 78 | 70 |  | 42 | 80 | 90 | 106 | 110 | 113 | 70 | 1873728
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 35 | 45 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 113 | 70 |  | 70 | 113 | 108 | 113 | 113 | 113 | 76 | 1861344
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [15 empty] | 0
176 | Rangpur 113 MW PP (Confidence) | 81 | 81 | 81 | 81 | 81 | 34 | 34 | 34 | 67 | 82 | 75 | 82 | 83 | 80 | 75 | 72 | 80 | 70 |  | 80 | 105 | 109 | 109 | 109 | 109 | 84 | 1888656
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 1 | 2 | 3 | 5 | 7 | 6 | 4 | 3 | 1 | [8 empty] | 37035
178 | Energypac Power Venture Thakurgaon Ltd. | 52 | 34 | 34 | 34 | 34 |  |  |  |  | 17 | 17 | 66 | 96 | 113 | 112 | 111 | 90 | 34 |  | 70 | 115 | 115 | 115 | 115 | 115 | 115 | 1480512
178