## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-05-30 | Monday
|  |  | Date (day): | 2022-05-30 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13830.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14808 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-05-29 | 2022-05-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 280 | 280 | 280 |  | 85 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 103 | 105 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 337 | 340 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-2 S/D due to Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 88 | 81 | 88 | 85 |  | 15 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 140 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 96 | 96 | 96 | 96 |  |  | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M, Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 91 | 90 | 91 |  | 9 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 330 | 330 | 330
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 150 | 150 |  | -1
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 53 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 218 | 286 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 76 | 202 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 97 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 60 | 98 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 72 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 90 | 92 | 92
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 3294 | 3721 | 3922 | 3903 | 671 | 1244
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 68 | 68 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 46 | 0 | 60 |  | 38 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 0 | 102 | 0 |  | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 57 | 25 | 50 | 50 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 27 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 72 | 76 | 75 | 85 |  | 23 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 265 | 300 | 280 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 35 | 36 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 65 | 30 | 70 | 50 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 962 | 1287 | 1082 | 1330 | 450 | 615
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 203 | 215 | 215
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 345 | 300 | 360 | 0
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 35 | 32 | 36 |  | 9 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 30 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 110 | 8 | 16 | 16 | 179 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 123 | 130 | 137 |  | 13 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 12 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 54 | 152 | 152 |  | 11
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 112 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 20 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 150 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 0 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 115 | 9 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 102 | 100 | 90 | 101 |  | 14 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1399 | 1650 | 1721 | 1980 | 717 | 66
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 117 | 128 | 150 | 150 | 52 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 178 | 187 | 170 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 104 | 103 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 495 | 459 | 528.6 | 507 | 52 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 42 | 42 |  | 48 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 11 | 5 | 5 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 41 | 56 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 81 | 81 | 81 | 5 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 11 | 0 | 11 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 16 | 16 |  | 9 | Engine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 401 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1557 | 1736 | 1718 | 1770 | 436 | 237
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 920 | 938 | 938
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 98 | 115 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 35 | 40 |  | 14 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 67 | 0 | 67 |  | 42 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 235 | 285 | 270 | 140 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 30 | 100 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 21 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1244 | 1633 | 1823 | 2000 | 140 | 56
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 50 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 12 | 30 | 20 | 20 |  | 30 | Machine problem
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 87 | 88 | 88 | 106 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 900 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 163 | 223 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 955 | 1289 | 1445 | 1638 | 106 | 30
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 18 | 30 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 | 16 |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 174 | 195 | 200 | 20 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 417 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 65 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 56 | 100 | 165 |  | 40 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 94 | 90 | 94
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 76 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 766 | 1128 | 1180 | 1277 | 637 | 147
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 9 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 79 | 101 | 113 | 113
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 90 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 351 | 400 | 411 | 403 | 99 | 170
|  | Total |  |  |  |  | 22348 | 21584 | 11023 | 13303 | 13830.6 | 14808 | 3308 | 2573
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10623.0548 | 12820.33 | 13328.7872 | 14270.7244
| A. |  | 2022-05-29 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13303 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9409 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13303 | MW
| 3 | Day peak Generation : |  |  | 11023 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12820.33 | MW
| 4 | Evening peak Generation : |  |  | 13303 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 272.5444 | MKWHr | By Solar | 0.84103 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 132.9994 | MKWHr |  | By Oil: | 88.2874 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 24.4777 | MKWHr |  | By Hydro: | 1.3494 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3308 | MW | Dhaka | 4763.16 | 4763.16 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2573 | MW | Chittagong | 1221.17 | 1221.17 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5881 | MW | Khulna | 1540.4 | 1540.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1009.57 | MMCFD |  |  | Rajshahi | 1391.6 | 1391.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 149491835.778 | ii) Oil : | Taka | 1187510549.57 | Comilla | 1079 | 1079 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 204575605 | Total | Taka | 1541577990.348 | Mymensingh | 1064 | 1064 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.022 | MKWHr. | Sylhet | 526 | 526 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 96 | MW (E to W) at | 21:00 | hrs | Barisal | 343 | 343 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 56 | MW at | 24:00 | hrs | Rangpur | 892 | 892 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 12820.33 | 12820.33 |  | 0
| B. |  | 2022-05-30 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14808 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
| 4 | Reserve(Generation end) |  |  |  | 808 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 286.8242 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9847 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2567 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3328 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.58 |  | (b) Today: | 74.7 |  | (c) Rule Curve: |  | 76.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-05-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 337 |  | 0 | 225 | 140 | 89 | 96 | 55 | 335 | 0 | 0 | 91 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 0 | 10 | 74 | 45 | 22 | 38 | 0 | 0 | 0 | 0 | 55 | 201 | 110 | 102 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 104 | 144 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 110 | 56 | 0 | 0 | 219 | 0 | 0 | 10 | 280 | 16 | 0 | 0 | 293 | 0 | 0 | 120 | 0 | 149 | 0 | 38 | 200 | 80 | 401 | 106 | 90 | 105 | 0 | 297 | 36 | 103 | 17 | 8 | 25 | 383 | 89 | 0 | 131 | 108 | 0 | 35 | 0 | 100 | 55 |  | 924 | 0 | 265 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 416 | 70 | 0 | 70 | 50 | 80 | 0 | 0 | 76 | 830 | 221 | 0 | 17 | 0 | 0 | 115 |  | 7736 | 3779 | 11515 | 3479 | 924 | 2156 | 0 | 3643 | 1005 | 38 | 0 | 166 | 104 | 0 | 0 | 74.58
2:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 336 |  | 0 | 225 | 145 | 89 | 92 | 55 | 335 | 0 | 0 | 68 | 93 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 25 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 74 | 49 | 22 | 38 | 0 | 0 | 0 | 0 | 55 | 180 | 78 | 100 | 33 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 102 | 145 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 110 | 55 | 0 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 293 | 0 | 0 | 120 | 0 | 149 | 0 | 38 | 200 | 80 | 402 | 106 | 90 | 105 | 0 | 281 | 36 | 102 | 17 | 9 | 25 | 389 | 89 | 0 | 144 | 108 | 0 | 35 | 0 | 90 | 55 |  | 920 | 0 | 265 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 70 | 0 | 70 | 50 | 80 | 0 | 0 | 76 | 820 | 222 | 0 | 17 | 0 | 0 | 34 |  | 7485 | 3670 | 11155 | 3447 | 920 | 2125 | 0 | 3464 | 995 | 38 | 0 | 64 | 102 | 0 | 0 | 74.58
3:00 | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 337 |  | 0 | 225 | 145 | 89 | 80 | 55 | 325 | 0 | 0 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 25 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 74 | 50 | 22 | 38 | 0 | 0 | 0 | 0 | 35 | 180 | 78 | 102 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 100 | 151 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 111 | 55 | 0 | 0 | 219 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 240 | 0 | 0 | 120 | 0 | 149 | 0 | 25 | 200 | 80 | 401 | 105 | 90 | 105 | 0 | 282 | 36 | 110 | 17 | 9 | 25 | 371 | 89 | 0 | 138 | 108 | 0 | 35 | 0 | 50 | 55 |  | 919 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 70 | 0 | 70 | 32 | 82 | 0 | 0 | 76 | 800 | 221 | 0 | 17 | 0 | 0 | 0 |  | 7202 | 3580 | 10782 | 3412 | 919 | 2136 | 0 | 3138 | 975 | 38 | 0 | 64 | 100 | 0 | 0 | 74.58
4:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 337 |  | 0 | 225 | 135 | 88 | 92 | 55 | 325 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 25 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 74 | 45 | 22 | 38 | 0 | 0 | 0 | 0 | 60 | 180 | 78 | 100 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 98 | 150 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 111 | 55 | 0 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 190 | 0 | 0 | 120 | 0 | 132 | 0 | 25 | 200 | 80 | 401 | 105 | 90 | 95 | 0 | 283 | 36 | 110 | 17 | 9 | 25 | 365 | 90 | 0 | 126 | 108 | 0 | 35 | 0 | 17 | 55 |  | 920 | 0 | 265 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 70 | 0 | 70 | 15 | 82 | 0 | 0 | 76 | 770 | 222 | 0 | 17 | 0 | 0 | 0 |  | 7062 | 3529 | 10591 | 3424 | 920 | 2114 | 0 | 2988 | 945 | 38 | 0 | 64 | 98 | 0 | 0 | 74.58
5:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 342 |  | 0 | 225 | 140 | 89 | 96 | 55 | 325 | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 74 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 55 | 180 | 78 | 102 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 96 | 154 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 111 | 56 | 0 | 0 | 219 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 45 | 0 | 0 | 68 | 0 | 92 | 0 | 25 | 155 | 80 | 401 | 105 | 70 | 87 | 0 | 282 | 36 | 110 | 17 | 9 | 25 | 365 | 89 | 0 | 126 | 108 | 0 | 35 | 0 | 17 | 55 |  | 920 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 35 | 0 | 70 | 15 | 82 | 0 | 0 | 76 | 750 | 205 | 0 | 17 | 0 | 0 | 0 |  | 6682 | 3461 | 10143 | 3430 | 920 | 2096 | 0 | 2590 | 925 | 38 | 0 | 48 | 96 | 0 | 0 | 74.58
6:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 342 |  | 0 | 225 | 150 | 89 | 52 | 55 | 331 | 0 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 47 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 55 | 192 | 78 | 30 | 33 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 88 | 155 | 0 | 17 | 0 | 43 | 42 | 5 | 0 | 110 | 110 | 61 | 0 | 0 | 219 | 0 | 0 | 10 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 50 | 2 | 25 | 68 | 30 | 401 | 65 | 50 | 51 | 0 | 282 | 36 | 110 | 17 | 9 | 25 | 365 | 67 | 2 | 72 | 108 | 0 | 24 | 0 | 17 | 17 |  | 920 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 415 | 35 | 0 | 70 | 15 | 49 | 0 | 0 | 76 | 730 | 221 | 0 | 17 | 0 | 5 | 0 |  | 6013 | 3396 | 9409 | 3326 | 920 | 2118 | 0 | 1973 | 905 | 38 | 0 | 32 | 88 | 9 | 0 | 74.58
7:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 342 |  | 0 | 225 | 140 | 86 | 32 | 55 | 330 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 31 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 70 | 181 | 107 | 30 | 33 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 84 | 154 | 0 | 17 | 1 | 44 | 42 | 5 | 0 | 110 | 110 | 61 | 0 | 0 | 219 | 0 | 0 | 10 | 320 | 0 | 0 | 0 | 15 | 0 | 0 | 45 | 0 | 50 | 3 | 25 | 68 | 30 | 401 | 65 | 50 | 51 | 1 | 282 | 36 | 102 | 17 | 9 | 25 | 365 | 53 | 13 | 72 | 108 | 0 | 17 | 0 | 24 | 17 |  | 919 | 0 | 270 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 415 | 35 | 0 | 70 | 32 | 49 | 0 | 1 | 76 | 720 | 219 | 0 | 17 | 0 | 32 | 13 |  | 6062 | 3468 | 9530 | 3359 | 919 | 2180 | 0 | 1972 | 895 | 38 | 0 | 32 | 84 | 51 | 0 | 74.58
8:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 332 |  | 0 | 225 | 145 | 88 | 32 | 55 | 330 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 28 | 17 | 33 | 18 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 32 | 44 | 22 | 12 | 0 | 0 | 0 | 0 | 95 | 181 | 107 | 30 | 30 | 52 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 15 | 92 | 145 | 0 | 17 | 1 | 43 | 42 | 5 | 0 | 110 | 110 | 61 | 0 | 0 | 219 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 15 | 0 | 0 | 45 | 0 | 50 | 10 | 25 | 68 | 30 | 400 | 65 | 52 | 53 | 1 | 283 | 36 | 110 | 17 | 9 | 25 | 370 | 53 | 10 | 72 | 108 | 0 | 17 | 0 | 34 | 17 |  | 919 | 0 | 250 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 425 | 17 | 0 | 70 | 15 | 50 | 0 | 3 | 76 | 680 | 190 | 0 | 17 | 2 | 7 | 34 |  | 6060 | 3366 | 9426 | 3384 | 919 | 2085 | 0 | 1987 | 855 | 38 | 0 | 32 | 92 | 34 | 0 | 74.59
9:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 330 |  | 0 | 225 | 140 | 88 | 32 | 55 | 332 | 0 | 0 | 10 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 25 | 25 | 22 | 25 | 28 | 17 | 33 | 37 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 43 | 44 | 22 | 5 | 0 | 0 | 0 | 0 | 79 | 183 | 110 | 31 | 36 | 53 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 15 | 102 | 130 | 0 | 17 | 2 | 43 | 42 | 5 | 0 | 110 | 110 | 61 | 0 | 0 | 219 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 26 | 0 | 0 | 75 | 0 | 76 | 15 | 25 | 91 | 38 | 401 | 90 | 66 | 79 | 0 | 283 | 36 | 110 | 17 | 9 | 25 | 370 | 56 | 41 | 126 | 108 | 0 | 17 | 0 | 40 | 48 |  | 919 | 0 | 220 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 421 | 17 | 0 | 70 | 15 | 55 | 0 | 4 | 76 | 700 | 165 | 0 | 17 | 1 | 10 | 68 |  | 6448 | 3351 | 9799 | 3335 | 919 | 2073 | 0 | 2336 | 875 | 38 | 0 | 48 | 102 | 73 | 0 | 74.59
10:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 338 |  | 0 | 225 | 140 | 88 | 79 | 55 | 326 | 0 | 0 | 60 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 5 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 70 | 0 | 22 | 5 | 0 | 0 | 0 | 0 | 135 | 203 | 110 | 30 | 35 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 25 | 15 | 104 | 117 | 0 | 17 | 2 | 43 | 42 | 5 | 0 | 110 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 128 | 0 | 0 | 113 | 0 | 101 | 13 | 25 | 163 | 108 | 401 | 104 | 72 | 87 | 1 | 267 | 36 | 110 | 17 | 9 | 25 | 370 | 75 | 47 | 126 | 108 | 0 | 17 | 0 | 70 | 55 |  | 920 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 414 | 17 | 0 | 70 | 15 | 81 | 0 | 5 | 76 | 680 | 164 | 0 | 17 | 3 | 27 | 72 |  | 6911 | 3368 | 10279 | 3284 | 920 | 2053 | 0 | 2879 | 855 | 38 | 0 | 48 | 104 | 98 | 0 | 74.6
11:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 317 |  | 0 | 225 | 138 | 88 | 96 | 55 | 326 | 0 | 0 | 67 | 85 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 14 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 70 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 170 | 186 | 110 | 30 | 35 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 25 | 15 | 108 | 118 | 0 | 20 | 1 | 43 | 42 | 5 | 0 | 110 | 0 | 40 | 0 | 0 | 219 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 190 | 27 | 90 | 170 | 25 | 140 | 19 | 25 | 200 | 127 | 401 | 104 | 72 | 87 | 1 | 265 | 36 | 110 | 17 | 9 | 25 | 370 | 72 | 25 | 145 | 92 | 0 | 26 | 0 | 94 | 55 |  | 919 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 416 | 17 | 0 | 70 | 15 | 82 | 0 | 7 | 76 | 650 | 164 | 0 | 17 | 3 | 44 | 72 |  | 7380 | 3321 | 10701 | 3293 | 919 | 2020 | 142 | 3178 | 825 | 68 | 0 | 48 | 108 | 100 | 0 | 74.6
12:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 320 |  | 0 | 225 | 145 | 88 | 96 | 55 | 326 | 0 | 0 | 70 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 42 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 72 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 250 | 201 | 110 | 30 | 35 | 53 | 0 | 51 | 0 | 12 | 8 | 19 | 5 | 20 | 15 | 102 | 117 | 0 | 20 | 2 | 43 | 42 | 5 | 0 | 110 | 0 | 41 | 0 | 0 | 219 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 218 | 76 | 97 | 178 | 60 | 149 | 19 | 25 | 200 | 125 | 403 | 104 | 72 | 87 | 5 | 265 | 36 | 110 | 17 | 9 | 25 | 385 | 70 | 51 | 144 | 90 | 0 | 35 | 0 | 102 | 55 |  | 919 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 414 | 17 | 0 | 70 | 15 | 79 | 0 | 7 | 76 | 660 | 163 | 0 | 17 | 4 | 21 | 90 |  | 7707 | 3316 | 11023 | 3386 | 919 | 2037 | 233 | 3274 | 835 | 68 | 0 | 60 | 102 | 109 | 0 | 74.61
13:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 323 |  | 0 | 225 | 120 | 88 | 96 | 55 | 332 | 0 | 0 | 84 | 85 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 42 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 72 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 350 | 182 | 110 | 30 | 35 | 52 | 0 | 51 | 0 | 50 | 8 | 19 | 0 | 16 | 15 | 60 | 106 | 0 | 17 | 2 | 43 | 41 | 5 | 0 | 110 | 0 | 51 | 0 | 0 | 219 | 0 | 0 | 10 | 300 | 0 | 11 | 30 | 230 | 72 | 99 | 178 | 97 | 149 | 13 | 25 | 200 | 118 | 402 | 103 | 72 | 87 | 3 | 265 | 36 | 110 | 17 | 9 | 25 | 392 | 71 | 18 | 126 | 90 | 0 | 35 | 0 | 100 | 55 |  | 921 | 0 | 235 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 7 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 17 | 0 | 70 | 15 | 79 | 0 | 7 | 76 | 700 | 163 | 0 | 17 | 4 | 26 | 108 |  | 7825 | 3457 | 11282 | 3466 | 921 | 2018 | 298 | 3325 | 875 | 68 | 0 | 178 | 60 | 73 | 0 | 74.61
14:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 327 |  | 0 | 225 | 130 | 88 | 96 | 55 | 330 | 0 | 0 | 92 | 85 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 28 | 25 | 33 | 44 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 49 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 305 | 155 | 68 | 30 | 33 | 52 | 0 | 51 | 0 | 50 | 8 | 19 | 0 | 25 | 0 | 62 | 104 | 0 | 17 | 2 | 44 | 41 | 5 | 0 | 110 | 0 | 57 | 0 | 0 | 219 | 0 | 0 | 10 | 310 | 0 | 11 | 10 | 253 | 13 | 25 | 186 | 25 | 149 | 15 | 25 | 200 | 118 | 403 | 104 | 70 | 34 | 0 | 210 | 36 | 110 | 17 | 9 | 25 | 390 | 72 | 22 | 144 | 90 | 0 | 34 | 0 | 102 | 55 |  | 919 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 16 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 388 | 17 | 0 | 70 | 15 | 79 | 0 | 7 | 76 | 700 | 185 | 0 | 17 | 4 | 31 | 108 |  | 7360 | 3455 | 10815 | 3376 | 919 | 1996 | 73 | 3174 | 875 | 68 | 0 | 191 | 62 | 81 | 0 | 74.62
15:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 332 |  | 0 | 225 | 135 | 82 | 96 | 55 | 334 | 0 | 0 | 91 | 93 | 90 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 49 | 0 | 37 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 52 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 360 | 158 | 8 | 28 | 33 | 50 | 0 | 51 | 0 | 50 | 8 | 19 | 0 | 25 | 12 | 82 | 108 | 0 | 0 | 1 | 44 | 41 | 5 | 0 | 110 | 0 | 56 | 0 | 0 | 220 | 0 | 0 | 10 | 320 | 0 | 11 | 80 | 278 | 183 | 97 | 186 | 98 | 149 | 8 | 25 | 200 | 120 | 402 | 102 | 70 | 38 | 0 | 264 | 36 | 110 | 17 | 15 | 25 | 394 | 90 | 30 | 126 | 90 | 0 | 26 | 0 | 100 | 55 |  | 919 | 0 | 220 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 16 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 17 | 0 | 70 | 15 | 79 | 0 | 5 | 76 | 730 | 186 | 0 | 17 | 2 | 36 | 108 |  | 7927 | 3505 | 11432 | 3423 | 919 | 1981 | 458 | 3316 | 905 | 67 | 0 | 199 | 82 | 82 | 0 | 74.62
16:00 | 0 | 0 | 0 | 180 | 280 | 89 | 0 | 0 | 330 |  | 0 | 225 | 140 | 82 | 96 | 55 | 332 | 0 | 0 | 91 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 49 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 75 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 355 | 186 | 8 | 30 | 33 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 25 | 12 | 80 | 123 | 0 | 17 | 1 | 44 | 41 | 5 | 0 | 110 | 0 | 61 | 78 | 0 | 220 | 0 | 0 | 9 | 280 | 0 | 11 | 0 | 275 | 28 | 50 | 176 | 65 | 149 | 3 | 25 | 200 | 125 | 402 | 102 | 76 | 72 | 0 | 289 | 36 | 110 | 17 | 68 | 25 | 387 | 91 | 24 | 126 | 90 | 0 | 17 | 0 | 101 | 55 |  | 918 | 0 | 220 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 16 | 8 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 414 | 35 | 0 | 70 | 15 | 79 | 0 | 3 | 76 | 740 | 185 | 0 | 17 | 1 | 28 | 108 |  | 7811 | 3532 | 11343 | 3501 | 918 | 1991 | 143 | 3460 | 915 | 68 | 0 | 207 | 80 | 60 | 0 | 74.63
17:00 | 0 | 0 | 0 | 180 | 280 | 100 | 0 | 0 | 330 |  | 0 | 225 | 130 | 72 | 96 | 55 | 333 | 0 | 0 | 91 | 93 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 49 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 74 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 350 | 187 | 8 | 35 | 34 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 25 | 14 | 78 | 132 | 0 | 17 | 1 | 44 | 41 | 5 | 0 | 110 | 0 | 61 | 81 | 0 | 220 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 278 | 0 | 0 | 150 | 0 | 145 | 3 | 28 | 200 | 123 | 402 | 101 | 70 | 85 | 0 | 284 | 36 | 110 | 17 | 113 | 37 | 397 | 90 | 12 | 126 | 108 | 0 | 17 | 0 | 78 | 55 |  | 920 | 0 | 215 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 16 | 88 | 18 | 16 | 0 | 0 | 0 | 0 | 5 | 43 | 0 | 0 | 16 | 8 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 35 | 0 | 70 | 15 | 82 | 0 | 2 | 70 | 740 | 185 | 0 | 17 | 0 | 22 | 90 |  | 7751 | 3521 | 11272 | 3552 | 920 | 2017 | 0 | 3470 | 915 | 68 | 0 | 212 | 78 | 40 | 0 | 74.63
18:00 | 0 | 0 | 0 | 180 | 280 | 106 | 0 | 0 | 250 |  | 0 | 225 | 130 | 78 | 91 | 55 | 250 | 0 | 0 | 91 | 93 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 1 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 75 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 310 | 194 | 8 | 56 | 34 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 0 | 33 | 14 | 96 | 128 | 0 | 17 | 0 | 44 | 41 | 5 | 0 | 110 | 0 | 61 | 81 | 0 | 220 | 18 | 0 | 9 | 270 | 24 | 0 | 0 | 283 | 0 | 0 | 150 | 0 | 133 | 0 | 54 | 155 | 122 | 362 | 101 | 70 | 87 | 0 | 284 | 36 | 110 | 17 | 114 | 38 | 396 | 90 | 2 | 126 | 108 | 0 | 17 | 0 | 58 | 55 |  | 920 | 0 | 215 | 0 | 64 | 0 | 0 | 0 | 8 | 5 | 16 | 88 | 18 | 16 | 0 | 0 | 0 | 32 | 5 | 43 | 0 | 8 | 32 | 8 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 322 | 35 | 0 | 70 | 15 | 70 | 0 | 0 | 70 | 680 | 165 | 0 | 17 | 0 | 3 | 52 |  | 7457 | 3348 | 10805 | 3415 | 920 | 1802 | 0 | 3387 | 855 | 68 | 0 | 257 | 96 | 5 | 0 | 74.64
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 312 |  | 0 | 225 | 145 | 80 | 96 | 55 | 329 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 18 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 13 | 0 | 0 | 0 | 0 |  | 24 | 20 | 102 | 10 | 75 | 0 | 22 | 4 | 0 | 0 | 0 | 0 | 320 | 207 | 8 | 56 | 35 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 5 | 33 | 17 | 112 | 128 | 0 | 17 | 0 | 44 | 41 | 11 | 0 | 110 | 0 | 60 | 81 | 0 | 220 | 18 | 0 | 9 | 290 | 24 | 0 | 50 | 283 | 103 | 100 | 170 | 70 | 142 | 0 | 55 | 170 | 123 | 402 | 101 | 80 | 89 | 0 | 300 | 36 | 110 | 17 | 114 | 65 | 385 | 90 | 0 | 132 | 108 | 0 | 24 | 0 | 82 | 55 |  | 920 | 0 | 225 | 0 | 85 | 0 | 0 | 0 | 45 | 55 | 40 | 88 | 26 | 32 | 0 | 0 | 0 | 43 | 20 | 80 | 0 | 34 | 32 | 8 | 31 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 383 | 58 | 5 | 78 | 75 | 101 | 0 | 0 | 100 | 730 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8373 | 4023 | 12396 | 3560 | 920 | 2028 | 328 | 3847 | 905 | 68 | 0 | 628 | 112 | 0 | 0 | 74.65
19:30 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 332 |  | 0 | 225 | 140 | 82 | 96 | 55 | 331 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 18 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 42 | 102 | 10 | 75 | 0 | 22 | 4 | 0 | 0 | 0 | 0 | 330 | 210 | 8 | 56 | 35 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 20 | 118 | 129 | 0 | 17 | 0 | 44 | 41 | 11 | 0 | 110 | 0 | 56 | 81 | 0 | 220 | 18 | 0 | 9 | 300 | 24 | 0 | 150 | 283 | 203 | 100 | 187 | 98 | 149 | 0 | 55 | 200 | 122 | 401 | 101 | 90 | 95 | 0 | 300 | 36 | 110 | 17 | 114 | 65 | 390 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 921 | 0 | 235 | 0 | 96 | 0 | 0 | 0 | 38 | 63 | 40 | 88 | 28 | 32 | 0 | 0 | 0 | 43 | 22 | 80 | 0 | 34 | 32 | 8 | 31 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 174 | 0 | 416 | 105 | 42 | 94 | 105 | 101 | 0 | 0 | 113 | 900 | 222 | 0 | 17 | 0 | 0 | 115 |  | 8803 | 4420 | 13223 | 3587 | 921 | 2090 | 623 | 4088 | 1075 | 68 | 0 | 653 | 118 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 101 | 0 | 0 | 335 |  | 0 | 225 | 135 | 82 | 96 | 55 | 329 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 42 | 102 | 10 | 75 | 1 | 22 | 7 | 0 | 0 | 0 | 0 | 345 | 212 | 8 | 55 | 35 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 116 | 128 | 0 | 17 | 0 | 44 | 41 | 11 | 0 | 110 | 0 | 57 | 81 | 0 | 220 | 18 | 0 | 9 | 280 | 24 | 11 | 150 | 283 | 203 | 100 | 187 | 98 | 149 | 0 | 56 | 200 | 122 | 401 | 103 | 90 | 98 | 0 | 300 | 36 | 110 | 17 | 115 | 65 | 400 | 89 | 0 | 144 | 108 | 0 | 35 | 0 | 99 | 55 |  | 920 | 0 | 235 | 0 | 97 | 0 | 0 | 0 | 37 | 70 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 43 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 174 | 0 | 417 | 105 | 57 | 94 | 105 | 101 | 0 | 0 | 113 | 900 | 222 | 0 | 17 | 0 | 0 | 115 |  | 8832 | 4433 | 13265 | 3632 | 920 | 2072 | 633 | 4095 | 1075 | 68 | 0 | 654 | 116 | 0 | 0 | 74.65
21:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 337 |  | 0 | 225 | 140 | 81 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 46 | 102 | 10 | 76 | 30 | 22 | 27 | 0 | 0 | 0 | 0 | 345 | 203 | 8 | 54 | 35 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 112 | 128 | 0 | 17 | 0 | 44 | 41 | 11 | 0 | 110 | 0 | 56 | 81 | 0 | 219 | 18 | 11 | 9 | 300 | 24 | 11 | 80 | 286 | 202 | 100 | 187 | 98 | 149 | 0 | 57 | 200 | 123 | 401 | 103 | 90 | 105 | 0 | 300 | 36 | 110 | 17 | 115 | 65 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 920 | 0 | 235 | 0 | 98 | 0 | 0 | 0 | 33 | 67 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 43 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 174 | 0 | 417 | 105 | 56 | 94 | 105 | 101 | 0 | 0 | 113 | 900 | 223 | 0 | 17 | 0 | 0 | 115 |  | 8853 | 4450 | 13303 | 3629 | 920 | 2134 | 566 | 4139 | 1075 | 68 | 9 | 651 | 112 | 0 | 0 | 74.65
22:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 343 |  | 0 | 225 | 145 | 80 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 102 | 10 | 76 | 0 | 22 | 3 | 0 | 0 | 0 | 0 | 330 | 196 | 8 | 86 | 36 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 112 | 128 | 0 | 17 | 0 | 44 | 42 | 11 | 0 | 110 | 0 | 57 | 81 | 0 | 219 | 18 | 11 | 9 | 265 | 24 | 11 | 80 | 283 | 84 | 100 | 188 | 97 | 149 | 0 | 59 | 200 | 130 | 400 | 104 | 90 | 93 | 0 | 282 | 36 | 110 | 17 | 117 | 65 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 921 | 0 | 235 | 0 | 97 | 0 | 0 | 0 | 33 | 67 | 40 | 87 | 29 | 32 | 0 | 0 | 0 | 34 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 178 | 0 | 418 | 105 | 70 | 94 | 105 | 101 | 0 | 0 | 113 | 900 | 191 | 0 | 17 | 0 | 0 | 115 |  | 8653 | 4427 | 13080 | 3645 | 921 | 2054 | 461 | 4087 | 1075 | 68 | 9 | 648 | 112 | 0 | 0 | 74.66
23:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 342 |  | 0 | 225 | 140 | 79 | 96 | 55 | 318 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 59 | 102 | 10 | 76 | 0 | 22 | 30 | 0 | 0 | 0 | 0 | 160 | 212 | 8 | 85 | 36 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 112 | 127 | 0 | 17 | 0 | 44 | 41 | 11 | 10 | 110 | 0 | 56 | 81 | 0 | 219 | 18 | 11 | 9 | 285 | 24 | 11 | 0 | 285 | 122 | 100 | 188 | 99 | 149 | 0 | 60 | 200 | 130 | 402 | 104 | 90 | 90 | 0 | 300 | 36 | 110 | 17 | 115 | 65 | 397 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 922 | 0 | 235 | 0 | 97 | 0 | 0 | 0 | 33 | 60 | 24 | 87 | 32 | 32 | 0 | 0 | 0 | 34 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 415 | 105 | 0 | 94 | 105 | 101 | 0 | 0 | 113 | 910 | 220 | 0 | 17 | 0 | 0 | 115 |  | 8515 | 4340 | 12855 | 3478 | 922 | 2135 | 321 | 4086 | 1085 | 68 | 0 | 648 | 112 | 0 | 0 | 74.66
24:00 | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 341 |  | 0 | 225 | 135 | 80 | 95 | 55 | 315 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 9 | 25 | 17 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 59 | 102 | 10 | 75 | 23 | 22 | 30 | 0 | 0 | 0 | 0 | 115 | 180 | 8 | 151 | 36 | 30 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 21 | 110 | 127 | 0 | 20 | 0 | 44 | 41 | 5 | 0 | 110 | 0 | 57 | 81 | 0 | 219 | 19 | 11 | 9 | 290 | 24 | 11 | 0 | 282 | 221 | 70 | 188 | 98 | 149 | 0 | 37 | 200 | 120 | 400 | 95 | 90 | 87 | 0 | 300 | 36 | 110 | 17 | 23 | 38 | 401 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 922 | 0 | 235 | 0 | 101 | 0 | 0 | 0 | 30 | 60 | 24 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 424 | 105 | 0 | 70 | 105 | 88 | 0 | 0 | 76 | 890 | 222 | 0 | 17 | 0 | 0 | 115 |  | 8375 | 4256 | 12631 | 3436 | 922 | 2127 | 389 | 3871 | 1065 | 68 | 0 | 643 | 110 | 0 | 0 | 74.67
KWH | 0 | 0 | 0 | 4347000 | 6723255 | 2357500 | 0 | 0 | 7892000 |  | 0 | 5175250 | 3442473 | 2037120 | 2026272 | 1331745 | 7823976 | 0 | 0 | 1478035 | 1657296 | 2064480 | 0 | 0 | 0 | 0 | 1199880 | 1104119 | 1189973 | 455544 | 600000 | 627120 | 606200 | 784800 | 951360 | 0 | 941400 | 408000 | 2400000 | 0 | 263822 | 0 | 0 | 0 | 0 |  | 570240 | 289872 | 546424 | 258960 | 1599360 | 512160 | 502848 | 414240 | 0 | 0 | 0 | 0 | 4823000 | 4630000 | 1438545 | 1417090 | 806760 | 1092000 | 0 | 1197536 | 0 | 577744 | 204350 | 428472 | 128700 | 724500 | 416120 | 2332800 | 3079680 | 0 | 362700 | 14100 | 1030000 | 958136 | 157800 | 18288 | 2675945 | 993000 | 1436992 | 711360 | 0 | 5266690 | 127000 | 33200 | 229860 | 7157500 | 252685 | 99100 | 441984 | 5133598 | 1224040 | 930000 | 3391200 | 821323 | 3081312 | 111915 | 824640 | 4212480 | 2435490 | 9597000 | 2350800 | 1909200 | 2029845 | 14279 | 6671673 | 912105 | 2656279 | 429780 | 1050000 | 833280 | 9192200 | 1941120 | 326660 | 3081600 | 2489018 | 0 | 710640 | 0 | 1848000 | 1233720 |  | 22256727 | 0 | 6017184 | 0 | 1856640 | 0 | 0 | 0 | 186720 | 337792 | 250875 | 2093743 | 542995 | 526944 | 0 | 0 | 0 | 238170 | 109697 | 743224 | 0 | 185783 | 252900 | 196565 | 165360 | 488640 | 0 | 109044 | 0 | 0 | 4292600 | 0 | 18000 | 0 | 0 | 0 | 0 | 0 | 102720 | 4439927 | 0 | 9855709 | 1345440 | 208338 | 1909920 | 1021968 | 1939305 | 0 | 53435 | 2003520 | 20185100 | 4818082 | 0 | 442800 | 29040 | 291600 | 1738368 |  | 181289558 | 91254875 | 272544433 | 83300466 | 22256727 | 49698923 | 3728405 | 79028600 | 24477700 | 1349400 | 18000 | 5512383 | 2332800 | 841029 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 7530045.6 | 3135475 | 0 | 0 | 8523360 |  | 0 | 5641022.5 | 3821145.03 | 22775001.6 | 26848104 | 17645621.25 | 8762853.12 | 0 | 0 | 21608871.7 | 23318154.72 | 33465220.8 | 0 | 0 | 0 | 0 | 15262473.6 | 14905606.5 | 15957537.93 | 341658 | 450000 | 0 | 0 | 0 | 16182633.6 | 0 | 254178 | 110160 | 4536000 | 0 | 4313489.7 | 0 | 0 | 0 | 0 |  | 7441632 | 4835064.96 | 9300136.48 | 3498549.6 | 20279884.8 | 5925691.2 | 638616.96 | 1379419.2 | 0 | 0 | 0 | 0 | 5257070 | 5370800 | 1855723.05 | 1728849.8 | 911638.8 | 1627080 | 0 | 1999885.12 | 0 | 9977638.88 | 2748507.5 | 587006.64 | 96525 | 1267875 | 312090 | 16749504 | 3356851.2 | 0 | 493272 | 224754 | 1411100 | 1264739.52 | 274572 | 31638.24 | 3077336.75 | 1062510 | 2787764.48 | 1621900.8 | 0 | 5319356.9 | 273050 | 49468 | 455122.8 | 7157500 | 189513.75 | 75316 | 9263984.64 | 70073612.7 | 25655878.4 | 19223100 | 45713376 | 16976746.41 | 42676171.2 | 1308286.35 | 8510284.8 | 57542476.8 | 32318952.3 | 8829240 | 28585728 | 27607032 | 25677539.25 | 0 | 78325441.02 | 9932823.45 | 28236245.77 | 5832114.6 | 13534500 | 9816038.4 | 8456824 | 25137504 | 4720237 | 39105504 | 28325024.84 | 0 | 9280958.4 | 0 | 27664560 | 16248092.4 |  | 66770181 | 0 | 6739246.08 | 0 | 19327622.4 | 0 | 0 | 0 | 3362827.2 | 6080256 | 3605073.75 | 2344992.16 | 1053410.3 | 5743689.6 | 0 | 0 | 0 | 3994110.9 | 1918600.53 | 11624023.36 | 0 | 3076566.48 | 4276539 | 2679180.95 | 2789623.2 | 1011484.8 | 0 | 82546.308 | 0 | 0 | 22707854 | 0 | 632700 | 0 | 0 | 0 | 0 | 0 | 2155065.6 | 5150315.32 | 0 | 9757151.91 | 18082713.6 | 4368847.86 | 22594353.6 | 14767437.6 | 24629173.5 | 0 | 590456.75 | 24322732.8 | 181867751 | 4914443.64 | 0 | 3276720 | 328442.4 | 3420468 | 26649181.44 |  | 1119358874.81 | 516695783.038 | 1636054657.848 | 92104696.638 | 66770181 | 57387139.14 | 77643622.91 | 1017610185.35 | 204575605 | 364338 | 632700 | 91624041.31 | 16749504 | 10592644.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 0 | 320 |  | 0 | 225 | 145 | 88 | 96 | 55 | 326 | 0 | 0 | 70 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 42 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 72 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 250 | 201 | 110 | 30 | 35 | 53 | 0 | 51 | 0 | 12 | 8 | 19 | 5 | 20 | 15 | 102 | 117 | 0 | 20 | 2 | 43 | 42 | 5 | 0 | 110 | 0 | 41 | 0 | 0 | 219 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 218 | 76 | 97 | 178 | 60 | 149 | 19 | 25 | 200 | 125 | 403 | 104 | 72 | 87 | 5 | 265 | 36 | 110 | 17 | 9 | 25 | 385 | 70 | 51 | 144 | 90 | 0 | 35 | 0 | 102 | 55 |  | 919 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 414 | 17 | 0 | 70 | 15 | 79 | 0 | 7 | 76 | 660 | 163 | 0 | 17 | 4 | 21 | 90 |  | 11023 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 103 | 0 | 0 | 337 | 0 | 0 | 225 | 140 | 81 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 46 | 102 | 10 | 76 | 30 | 22 | 27 | 0 | 0 | 0 | 0 | 345 | 203 | 8 | 54 | 35 | 30 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 112 | 128 | 0 | 17 | 0 | 44 | 41 | 11 | 0 | 110 | 0 | 56 | 81 | 0 | 219 | 18 | 11 | 9 | 300 | 24 | 11 | 80 | 286 | 202 | 100 | 187 | 98 | 149 | 0 | 57 | 200 | 123 | 401 | 103 | 90 | 105 | 0 | 300 | 36 | 110 | 17 | 115 | 65 | 400 | 90 | 0 | 144 | 108 | 0 | 35 | 0 | 100 | 55 |  | 920 | 0 | 235 | 0 | 98 | 0 | 0 | 0 | 33 | 67 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 43 | 18 | 80 | 0 | 34 | 32 | 8 | 30 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 174 | 0 | 417 | 105 | 56 | 94 | 105 | 101 | 0 | 0 | 113 | 900 | 223 | 0 | 17 | 0 | 0 | 115 |  | 13303 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 108 | 0 | 0 | 350 | 0 | 0 | 225 | 150 | 85 | 96 | 55 | 330 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 102 | 10 | 85 | 50 | 22 | 25 | 0 | 0 | 0 | 0 | 360 | 215 | 16 | 152 | 36 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 165 | 150 | 0 | 20 | 0 | 43 | 42 | 5 | 0 | 110 | 0 | 60 | 81 | 0 | 220 | 20 | 11 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 50 | 200 | 137 | 400 | 115 | 105 | 105 | 0 | 300 | 36 | 110 | 0 | 113 | 70 | 400 | 92 | 0 | 162 | 110 | 0 | 35 |  | 101 | 55 |  | 938 | 0 | 270 | 0 | 115 | 220 | 0 | 0 | 40 | 67 | 40 | 88 | 20 | 110 | 0 | 0 | 0 | 43 | 30 | 80 | 0 | 34 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 200 | 0 | 410 | 105 | 165 | 94 | 105 | 113 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 105 | 0 | 0 | 340 | 0 | 0 | 225 | 150 | 88 | 96 | 55 | 330 | 0 | 0 | 90 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 75 | 50 | 22 | 10 | 0 | 0 | 0 | 0 | 300 | 215 | 16 | 152 | 32 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 143 | 150 | 0 | 20 | 1.6 | 43 | 42 | 5 | 0 | 110 | 0 | 60 | 81 | 0 | 220 | 20 | 0 | 10 | 300 | 16 | 11 | 150 | 300 | 300 | 100 | 170 | 100 | 149 | 20 | 25 | 200 | 130 | 400 | 115 | 105 | 105 | 5 | 280 | 35 | 110 | 17 | 9 | 30 | 400 | 92 | 50 | 162 | 110 | 0 | 17 | 30 | 90 | 55 |  | 938 | 0 | 285 | 0 | 115 | 0 | 0 | 0 | 35 | 0 | 40 | 88 | 20 | 50 | 0 | 0 | 0 | 34 | 30 | 65 | 0 | 34 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 195 | 0 | 410 | 105 | 100 | 90 | 105 | 113 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 0 | 333 | 0 | 0 | 225 | 140 | 72 | 65 | 42 | 315 | 0 | 0 | 2 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 28 | 25 | 33 | 15 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 70 | 23 | 22 | 12 | 0 | 0 | 0 | 0 | 135 | 214 | 102 | 152 | 33 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 25 | 19 | 94 | 117 | 0 | 20 | 1 | 43 | 42 | 5 | 0 | 110 | 0 | 62 | 81 | 0 | 220 | 19 | 0 | 9 | 270 | 0 | 11 | 0 | 115 | 0 | 0 | 150 | 0 | 100 | 9 | 13 | 155 | 90 | 388 | 107 | 17 | 105 | 2 | 264 | 36 | 110 | 17 | 9 | 25 | 360 | 70 | 24 | 144 | 108 | 0 | 17 | 0 | 6 | 55 | 0 | 921 | 0 | 180 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 357 | 53 | 0 | 70 | 0 | 80 | 0 | 0 | 76 | 680 | 160 | 0 | 17 | 1 | 17 | 16 | 0 |  |  |  |  | 88287388 |  | 0
88287388
| Minimum Generation |  | 9409 | 6:00
| Highest Generation |  | 13303 | 21:00
| Day Peak Generation |  | 11023 | 12:00
| Evening Peak Generation |  | 13303 | 21:00
| HVDC Max Flow |  | 924 | 1:00
| HVDC EvPeak Flow |  | 920 | 21:00
| Load factor L.F |  | 85.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-05-30
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-05-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11023 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9847 | MW
Evening Peak Generation : |  | 13303 | MW Hour : | 21:00 | Available Max Generation : |  | 14808 | MW
E.P. Demand (at gen end) : |  | 13303 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13303 | MW Hour : | 21:00 | Reserve(Generation end) |  | 808 | MW
Total Gen. (MKWH) : |  | 272.5444 | System Load Factor : | 85.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 56 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-05-30
Actual : | 74.7 | Ft.(MSL) , | Rule curve : | 76.4 | Ft.( MSL )
Gas Consumed : | Total = | 1009.57 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 149491835.778
: |  | Coal : | 204575605 | Oil : | 1187510549.57 | Total : | 1541577990.348
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4968.4584 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1610.8418 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1571.2276 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1406.7905 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1282.9543 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1053.1091 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 515.4682 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 317.0716 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 773.8649 |  |  | 0 | 0%
Total | 0 |  | 13499.7865 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1,2
9) Ashuganj North
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari-Madunaghat 132 kV Ckt-1 was under shut down from 08:38 to 15:48 for C/M.
b) Shahjibazar 330MW GT-2 tripped at 09:43 due to fire at unit transformer.
c) Bibiyana-Shahjibazar 230 kV Ckt-1,2 tripped at 09:43 showing dist Z1,67N at Bibiyana end.
d) Cumilla(N)-Shahjibazar 230 kV Ckt-1,2 tripped at 09:43 showing dist Z1 at Ckt-1 & dist Z2,Y-phase at
Ckt-2.
f) Bibiyana-Fenchuganj 230 kV Ckt-1 tripped at 09:43 showing dist 3-phase,O/C relay Fenchuganj end
g) Manikganj-Kabirpur 132 kV Ckt-2 was under shut down from 10:31 to 11:59 for C/M.
h) Jhenaidah 132/33 kV T-1 transformer was under shut down from 08:11 to 09:50 for C/M.
i) Rajbari 132/33 kV T-1 transformer was under shut down from 08:26 to 19:03 for C/M.
j) Payra-Patuakhali 132 kV Ckt-2 was under shut down from 08:48 to 14:44 for C/M.
k) Gopalganj S/S-Gopalganj P/S 132 kV Ckt was under shut down from 09:04 to 12:43 for C/M.
l) Dohazari-Cox's bazar 132 kV Ckt-2 tripped at 13:03 showing dist Z1,3 phase at Dohazari end and was
switched on at 13:30.
m) Chandpur CCPP STG was synchronized at 16:55.
n) Ashuganj(S) GT & ST were synchronized at 23:18,00:30(30-5-22) respectively.
o) Noapara 132/33 kV T-1 transformer was under shut down from 23:17 to 00:58 for red hot maint.
p) Bhulta 132/33 kV T-2 transformer was under shut down from 23:40 to 08:35 due to flashing at 33 kV bushing.
q) Ashuganj(S) ST was shut down at 01:33(30-5-22)due to generator bearing problem and was
synchronized at 02:28 and ST S/D at 03:40 & GT S/D at 04:13 again synchronized at 04:53.
r) Sherpur-Sirajganj 132 kV Ckt-2 was under shut down from 05:48 to 08:53 due to red hot maintenance
at R-phase CT point at Sherpur end.
s) Cumilla(N)-BSRM 230 kV Ckt-2 tripped at 06:44 from Cumilla (N) end showing dist S-phase,Z1 and
was switched on at 07:12(30-05-2022).
t) Chandraghona 132/33 kV T-1 transformer was under shut down at 07:24(30-05-22) for D/W.
u) Cumilla(N)-BSRM 230 kV Ckt-2 tripped at 07:25 from Cumilla (N) end showing dist S-phase, Z1 and
was switched on at 07:34(30-05-2022).
v) Ashuganj(S) GT & ST were synchronized at 06:24,07:29(30-5-22) respectively.
w) Naogaon 132/33 kV T-1,2 transformer tripped at 00:50 showing E/F relay and were switched on at 00:58. | [5 empty] | About 122 MW power interruption occurred under
Naogaon S/S area from 00:50 to 00:58.
x) Bogura(O) 132/33 kV T-4 transformer was under shut down at 07:36 to 08:28(30-05-22) for red hot maint.
y) Rajbari 132/33 kV T-1 transformer was under shut down at 07:46(30-05-22) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-05-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6723255 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2357500
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7892000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5175250 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 81 | 2037120 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3442473 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 96 | 2026272
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1331745
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 455544
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1478035 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7823976
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1657296 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1199880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2064480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1104119
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1189973
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1227120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 606200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 951360 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 5133598 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 202 | 1224040 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 930000
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 821323
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3081312
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 1909200 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1941120 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3081600 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1233720
| Dhaka area Total |  |  |  | 5898 | 3721 | 75231311
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 263822
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 111915
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 512160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1349400 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2029845
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 289872 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 546424
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 57 | 824640 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502848
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 414240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 76 | 1599360 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 14279
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6671673
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 912105 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2656279
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 65 | 833280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2489018
| Chattogram area Total |  |  |  | 2382 | 1287 | 24680120
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4630000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 4823000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 806760 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 1092000 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1438545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1197536
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 2435490 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 577744
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 54 | 1417090 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4212480
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 428472 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 128700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 2332800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 724500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 204350 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 416120 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 80 | 441984 | Low Demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 429780 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1050000
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 710640 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 1848000 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1650 | 31345991
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 128 | 3079680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 362700
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 187 | 3391200 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 2350800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 326660
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 570240
| Mymensingh Area Total |  |  |  | 622 | 459 | 10095380
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1030000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 958136 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2675945 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 993000
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 157800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 0 | 18288 | Machine problem
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 99100
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1436992
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 711360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5266690
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 127000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 11 | 33200 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 252685
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7157500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9597000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 229860
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9192200
| Sylhet Area Total |  |  |  | 2477 | 1736 | 39936756
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 22256727
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 98 | 1856640 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 186720 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 67 | 337792 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 6017184 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 250875
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 30 | 102720 | Low Demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1345440
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1021968
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 291600
| Khulna Area Total |  |  |  | 2384 | 1633 | 33667666
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 526944 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 30 | 542995 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2093743 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 20185100 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 4818082
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 442800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1289 | 28609664
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 238170 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 18 | 109697 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 185783 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 252900 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 174 | 4439927 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 417 | 9855709
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 165360 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 488640
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 109044 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 196565 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 743224 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 56 | 208338 | Low Demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1909920 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2003520
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29040
| Rajshahi Area Total |  |  |  | 2129 | 1128 | 20935837
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4292600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 9 | 18000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 1939305 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53435
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1738368
| Rangpur Area Total |  |  |  | 720 | 400 | 8041708
| Total |  |  |  | 21584 | 13303 | 272544433
| Eastern Grid Total |  |  |  | 14393 | 8853 | 181289558
| Western Grid Total |  |  |  | 7191 | 4450 | 91254875
| National Grid Total |  |  |  | 21584 | 13303 | 272544433
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-05-29
(a) ENTIRE EASTERN GRID : |  | 8653.33 | MW | (b) ENTIRE WESTERN GRID : |  | 4167 | MW
i) Dhaka area |  | 4763.16 | MW | i) Khulna area |  | 1540.4 | MW
ii) Chittagong area |  | 1221.17 | MW | ii) Rajshahi area |  | 1391.6 | MW
iii) Comilla area |  | 1079 | MW | iii) Barisal area |  | 343 | MW
iv) Mymensingh area |  | 1064 | MW | iv) Rangpur area |  | 892 | MW
v) Sylhet area |  | 526 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12820.33 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 30 | 19:00 | Hasnabad | 78 | 00:00 | Palashbari | 127 | 20:00
Agargaon | 87 | 13:00 | Hathazari | 94 | 21:00 | Panchagarh | 59 | 19:30
Agrabad | 84 | 12:00 | Ishurdi | 76 | 20:00 | Patuakhali | 104 | 23:00
AKS | 0 | 00:00 | Jaldhaka | 68 | 19:30 | PHP | 10 | 05:00
AKSML | 13 | 05:00 | Jamalpur | 164 | 22:00 | Purbachal | 18 | 15:00
Amnura | 41 | 23:00 | Jashore | 107 | 21:00 | Purbasadipur | 126 | 21:00
Ashuganj | 39 | 05:00 | Jhenaidah | 114 | 19:30 | Rahim | 28 | 17:00
Bagerhat | 90 | 19:00 | Joydebpur | 186 | 19:00 | Rajbari | 66 | 20:00
Bakulia | 120 | 12:00 | Joypurhat | 58 | 19:30 | Rajendrapur | 118 | 19:30
Banani | 52 | 10:00 | Juldah | 29 | 14:00 | Rajshahi | 172 | 21:00
Bangabhaban | 22 | 10:00 | Kabirpur | 289 | 16:00 | Rajshahi | 22 | 23:00
Barapukuria | 52 | 19:30 | Kachua | 74 | 00:00 | Ramganj | 88 | 00:00
Barguna | 16 | 21:00 | Kallyanpur | 99 | 22:00 | Rampur | 12.5 | 21:00
Barishal | 105 | 21:00 | Kalurghat | 5 | 09:00 | Rangamati | 12 | 19:00
Barishal | 44 | 19:00 | Kamrangirchar | 74 | 19:00 | Rangpur | 153 | 19:30
Baroaulia | 62 | 01:00 | Kaptai | 4 | 19:00 | Ruppur | 4.2 | 11:00
Baroirhat | 47 | 19:00 | Kazla | 84 | 12:00 | Saidpur | 110 | 21:00
Bashundhara | 172 | 15:00 | Keranigonj | 66 | 19:30 | Satkhira | 111 | 22:00
BashundharaCement | 12 | 07:00 | Khagrachori | 24 | 19:00 | Satmasjid | 87 | 13:00
Beanibazar | 62 | 22:00 | Khulna | 84 | 19:00 | Savar | 191 | 15:00
Benapole | 60 | 19:30 | Khulshi | 160 | 10:00 | Shahjadpur | 93 | 23:00
Bhaluka | 138 | 19:00 | Kishoreganj | 134 | 00:00 | Shahjibazar | 112 | 22:00
Bhandaria | 49 | 21:00 | Kodda | 321 | 18:30 | Shahmirpur | 45 | 19:30
Bhangura | 35 | 21:00 | KSRM | 22.82 | 16:00 | Shariatpur | 66 | 00:00
Bheramara(GK) | 55 | 21:00 | Kulaura | 42 | 19:00 | Sherpur | 116 | 23:00
Bhulta | 236 | 17:00 | Kurigram | 66 | 20:00 | Shikalbaha | 28 | 19:30
Bog-Sherpur | 64 | 21:00 | Kushtia | 138 | 20:00 | Shitalakhya | 111 | 12:00
Bogura | 166 | 20:00 | Lalbag | 97 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 40 | 01:00 | Lalmonirhat | 48 | 21:00 | Shyampur | 170 | 12:00
Brahmanbaria | 160 | 00:00 | Madanganj | 186 | 00:00 | Siddhirganj | 110 | 11:00
BSRM | 166 | 06:00 | Madaripur | 86 | 22:00 | Sirajganj | 110 | 20:00
Cantonment | 144 | 13:00 | Madartek | 78 | 22:00 | Sonargaon | 80 | 19:30
Chandpur | 64 | 00:00 | Madunaghat | 55 | 11:00 | Sreemongol | 53 | 20:00
Chandraghona | 28 | 19:00 | Magura | 56 | 19:30 | Srinagar | 38.55 | 00:00
Chapai | 75 | 22:00 | Mahasthangarh | 70 | 21:00 | SSM | 14 | 00:00
Charsaidpur | 39 | 20:00 | Manikganj | 81 | 20:00 | Sunamganj | 52 | 22:00
Chauddagram | 51 | 00:00 | Maniknagar | 72 | 13:00 | Sylhet | 147 | 19:00
Chhatak | 31 | 20:00 | Matarbari | 37 | 22:00 | Tangail | 206 | 20:00
Chowmuhani | 184 | 01:00 | Matuail | 124 | 19:30 | Thakurgaon | 91 | 23:00
Chuadanga | 104 | 21:00 | Millgate | 59 | 18:00 | TK | 27.7 | 22:00
Coxsbazar | 111 | 20:00 | Mirpur | 129 | 15:00 | Tongi | 138 | 11:00
Cumilla(N) | 136 | 22:00 | Mirsorai | N/A | N/A | Ullon | 39 | 00:00
Cumilla(S) | 143 | 19:30 | Mithapukur | 32 | 21:00 | Uttara | 90 | 19:00
Daudkandi | 142 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 30 | 14:00
Dhaka | 38 | 12:00 | Mogbazar | 125 | 15:00 | Zigatola | 42 | 13:00
Dhamrai | 118 | 15:00 | Mongla | 42 | 10:00
Dhanmondi | 151 | 12:00 | Motijheel | 36 | 13:00
Dohazari | 88 | 00:00 | Munshiganj | 98 | 00:00
Faridpur | 132 | 22:00 | Mymensingh | 234 | 22:00
Fatullah | 69 | 09:00 | Naogaon | 130 | 21:00
Fenchuganj | 46 | 19:30 | Narail | 48 | 20:00
Feni | 126 | 01:00 | Narinda | 69 | 12:00
Ghorashal | 64 | 00:00 | Narshingdi | 180 | 21:00
Goalpara | 26 | 00:00 | Natore | 135 | 21:00
Gollamari | 60 | 00:00 | Nawabganj | 51.1 | 22:00
Gopalganj | 90.4 | 20:00 | Netrakona | 117 | 22:00
GPH | 87 | 05:00 | New | 86 | 11:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-05-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 3:00 | 400 | 16:00 | Kaliakoir | 394 | 0.375 | 377 | 0.41667
| Bheramara | 401 | 7:00 | 392 | 22:00 | Bhulta | 386 | 0.20833 | 367 | 0.41667
| Ashuganj(N) | 388 | 4:00 | 371 | 10:00 | Gopalganj | 420 | 0.625 | 410 | 0.625
| Payra | 421 | 9:00 | 417 | 16:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 238 | 21:00 | 227 | 10:00
| Ishurdi | 235 | 5:00 | 225 | 19:30 | Megnaghat | 228 | 24:00 | 221 | 11:00
| Ashuganj | 240 | 13:00 | 232 | 17:00 | Fenchuganj | 241 | 21:00 | 235 | 10:00
| Serajganj | 234 | 18:00 | 227 | 23:00 | Siddhirganj | 228 | 22:00 | 219 | 11:00
| Baghabari | 231 | 4:00 | 224 | 23:00 | Maniknagar | 226 | 22:00 | 215 | 10:00
| Barapukuria | 225 | 6:00 | 210 | 20:00 | Agargaon | 226 | 10:00 | 213 | 10:00
| Bogra | 230 | 18:30 | 217 | 20:00 | Barisal | 245 | 10:00 | 238 | 21:00
| Rajshahi | 236 | 18:30 | 224 | 23:00 | Bhola 225 MW | 248 | 10:00 | 238 | 21:00
| Khulna South | 237 | 8:00 | 225 | 19:30 | AKSML | 235 | 22:00 | 228 | 10:00
| Rampura | 226 | 24:00 | 215 | 10:00 | BSRM | 238 | 22:00 | 225 | 10:00
| Haripur | 226 | 22:00 | 217 | 11:00 | Bibiyana | 240 | 4:00 | 234 | 8:00
| Hasnabad | 227 | 24:00 | 213 | 10:00 | Bhulta | 231 | 22:00 | 217 | 10:00
| Shyampur | 227 | 22:00 | 213 | 11:00 | Ashuganj (S) | 236 | 22:00 | 225 | 10:00
| Aminbazar | 227 | 1:00 | 215 | 2:00 | Kaliakoir | 228 | 22:00 | 216 | 10:00
| Tongi | 226 | 22:00 | 212 | 10:00 | GPH | 239 | 22:00 | 227 | 10:00
| Comilla (N) | 231 | 21:00 | 219 | 10:00 | Jhenaidah | 233 | 8:00 | 219 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 03:00 | 126 | 10:00 | Manikganj | 134 | 05:00 | 124 | 08:00
| Agargaon | 131 | 02:00 | 122 | 10:00 | Maniknagar | 133 | 22:00 | 125 | 10:00
| Agrabad | 141 | 13:00 | 131 | 10:00 | Matarbari | 133 | 14:00 | 115 | 04:00
| AKS | 140 | 22:00 | 130 | 00:00 | Matuail | 134 | 22:00 | 126 | 10:00
| Aminbazar | 134 | 21:00 | 125 | 10:00 | Millgate | 134 | 00:00 | 124 | 11:00
| Amnura | 130 | 18:00 | 121 | 23:00 | Mirpur | 133 | 22:00 | 128 | 08:00
| Ashuganj | 138 | 18:00 | 134 | 10:00 | Mithapukur | 131 | 04:00 | 118 | 19:30
| Bagerhat | 132 | 09:00 | 122 | 19:00 | Modern | 140 | 21:00 | 133 | 00:00
| Bakulia | 143 | 22:00 | 132 | 00:00 | Mogbazar | 135 | 02:00 | 126 | 11:00
| Banani | 132 | 04:00 | 122 | 10:00 | Mongla | 137 | 09:00 | 125 | 19:00
| Bangabhaban | 133 | 22:00 | 125 | 09:00 | Motijheel | 133 | 22:00 | 125 | 11:00
| Barapukuria | 134 | 08:00 | 123 | 20:00 | Munshiganj | 138 | 22:00 | 129 | 10:00
| Barguna | 138 | 10:00 | 131 | 18:00 | Mymensingh | 133 | 06:00 | 116 | 22:00
| Barishal | 143 | 07:00 | 130 | 07:00 | Naogaon | 130 | 18:00 | 117 | 20:00
| Barishal | 143 | 09:00 | 137 | 00:00 | Narail | 134 | 05:00 | 123 | 19:30
| Baroaulia | 142 | 13:00 | 134 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 138 | 13:00 | 125 | 00:00 | Narshingdi | 127 | 18:30 | 122 | 10:00
| Bashundhara | 132 | 02:00 | 123 | 09:00 | Natore | 132 | 05:00 | 123 | 21:00
| BashundharaCement | 138 | 22:00 | 129 | 10:00 | Nawabganj | 137 | 22:00 | 127 | 10:00
| Beanibazar | 132 | 06:00 | 127 | 19:30 | Netrakona | 132 | 06:00 | 116 | 22:00
| Benapole | 136 | 08:00 | 124 | 19:30 | New | 132 | 00:00 | 124 | 10:00
| Bhaluka | 133 | 06:00 | 115 | 19:00 | Niamatpur | 130 | 04:00 | 112 | 20:00
| Bhandaria | 145 | 10:00 | 135 | 21:00 | Noapara | 138 | 09:00 | 130 | 15:00
| Bhangura | 138 | 05:00 | 131 | 20:00 | Pabna | 136 | 05:00 | 128 | 19:30
| Bheramara | 136 | 04:00 | 131 | 19:30 | Palashbari | 131 | 05:00 | 117 | 20:00
| Bheramara(GK) | 138 | 05:00 | 135 | 10:00 | Panchagarh | 134 | 12:00 | 115 | 19:30
| Bhulta | 126 | 05:00 | 119 | 16:00 | Patuakhali | 137 | 10:00 | 132 | 21:00
| Bog-Sherpur | 135 | 05:00 | 124 | 20:00 | PHP | 136 | 13:00 | 124 | 00:00
| Bogura | 135 | 05:00 | 124 | 23:00 | Purbachal | 133 | 03:00 | 123 | 09:00
| Bogura | 135 | 05:00 | 125 | 23:00 | Purbasadipur | 132 | 12:00 | 117 | 20:00
| Brahmanbaria | 133 | 06:00 | 127 | 21:00 | Rahim | 134 | 22:00 | 128 | 11:00
| Cantonment | 131 | 04:00 | 121 | 10:00 | Rajbari | 136 | 05:00 | 130 | 19:30
| Chandpur | 141 | 11:00 | 133 | 00:00 | Rajendrapur | 132 | 03:00 | 121 | 09:00
| Chandraghona | 142 | 22:00 | 133 | 01:00 | Rajshahi | 130 | 18:00 | 121 | 21:00
| Chapai | 132 | 18:30 | 122 | 21:00 | Rajshahi | 129 | 18:30 | 121 | 21:00
| Charsaidpur | 137 | 03:00 | 130 | 10:00 | Ramganj | 136 | 13:00 | 124 | 00:00
| Chauddagram | 135 | 21:00 | 128 | 00:00 | Rampur | 139 | 21:00 | 130 | 05:00
| Chhatak | 132 | 10:00 | 127 | 20:00 | Rampura | 133 | 03:00 | 126 | 10:00
| Chowmuhani | 135 | 12:00 | 120 | 00:00 | Rangamati | 140 | 22:00 | 134 | 11:00
| Chuadanga | 132 | 09:00 | 119 | 19:30 | Rangpur | 129 | 09:00 | 115 | 19:30
| Coxsbazar | 130 | 18:00 | 116 | 00:00 | Ruppur | 136 | 01:00 | 130 | 19:30
| Cumilla(N) | 136 | 21:00 | 129 | 10:00 | Saidpur | 131 | 03:00 | 117 | 19:30
| Cumilla(S) | 137 | 22:00 | 129 | 00:00 | Satkhira | 138 | 08:00 | 127 | 19:00
| Daudkandi | 135 | 19:00 | 125 | 10:00 | Satmasjid | 131 | 22:00 | 123 | 10:00
| Dhaka | 134 | 02:00 | 126 | 10:00 | Savar | 134 | 22:00 | 124 | 10:00
| Dhamrai | 132 | 04:00 | 123 | 10:00 | Shahjadpur | 140 | 05:00 | 132 | 20:00
| Dhanmondi | 134 | 22:00 | 127 | 10:00 | Shahjibazar | 136 | 18:00 | 131 | 15:00
| Dohazari | 136 | 13:00 | 128 | 00:00 | Shahmirpur | 141 | 22:00 | 132 | 00:00
| Faridpur | 135 | 03:00 | 130 | 19:30 | Shariatpur | 138 | 07:00 | 133 | 00:00
| Fatullah | 136 | 22:00 | 125 | 10:00 | Sherpur | 138 | 02:00 | 120 | 23:00
| Fenchuganj | 136 | 06:00 | 133 | 01:00 | Shikalbaha | 143 | 13:00 | 134 | 10:00
| Feni | 136 | 13:00 | 123 | 00:00 | Shikalbaha | 141 | 22:00 | 133 | 11:00
| Ghorashal | 138 | 00:00 | 135 | 11:00 | Shitalakhya | 138 | 22:00 | 129 | 10:00
| Goalpara | 139 | 09:00 | 131 | 19:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 08:00 | 131 | 19:00 | Shyampur | 133 | 20:00 | 127 | 09:00
| Gopalganj | 139 | 18:30 | 134 | 02:00 | Shyampur | 132 | 02:00 | 125 | 10:00
| Gopalganj_I | 141 | 09:00 | 135 | 00:00 | Siddhirganj | 133 | 21:00 | 126 | 10:00
| Gulshan | 133 | 03:00 | 125 | 10:00 | Sirajganj | 134 | 05:00 | 125 | 20:00
| Halishahar | 141 | 22:00 | 132 | 00:00 | Sonargaon | 135 | 21:00 | 129 | 12:00
| Haripur | 134 | 22:00 | 128 | 11:00 | Sreemongol | 137 | 18:00 | 133 | 01:00
| HaripurSBU | 138 | 05:00 | 127 | 10:00 | Srinagar | 136 | 21:00 | 128 | 10:00
| Hasnabad | 138 | 21:00 | 131 | 09:00 | SSM | 142 | 13:00 | 136 | 15:00
| Hathazari | 140 | 21:00 | 134 | 01:00 | Sunamganj | 131 | 00:00 | 125 | 20:00
| Ishurdi | 136 | 04:00 | 131 | 19:30 | Sylhet | 133 | 09:00 | 131 | 14:00
| Jaldhaka | 129 | 14:00 | 114 | 19:30 | Tangail | 134 | 03:00 | 121 | 21:00
| Jamalpur | 139 | 11:00 | 123 | 22:00 | Thakurgaon | 135 | 12:00 | 117 | 03:00
| Jashore | 136 | 09:00 | 125 | 18:30 | TK | 141 | 13:00 | 132 | 10:00
| Jhenaidah | 139 | 19:00 | 127 | 19:30 | Tongi | 137 | 14:00 | 135 | 14:00
| Jhenaidah | 136 | 05:00 | 134 | 18:00 | Ullon | 134 | 22:00 | 126 | 12:00
| Joydebpur | 139 | 00:00 | 130 | 12:00 | Uttara | 132 | 22:00 | 125 | 10:00
| Joypurhat | 130 | 05:00 | 114 | 20:00 | UttaraNew | 133 | 22:00 | 124 | 10:00
| Juldah | 142 | 22:00 | 133 | 00:00 | Zigatola | 137 | 22:00 | 128 | 11:00
| Kabirpur | 132 | 13:00 | 120 | 10:00
| Kachua | 137 | 21:00 | 129 | 00:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 135 | 23:00 | 125 | 10:00
| Kalurghat | 142 | 22:00 | 133 | 02:00
| Kamrangirchar | 137 | 22:00 | 129 | 16:00
| Kaptai | 140 | 22:00 | 135 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-05-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 56 | 8375 | 4256 | 12631 |  |  |  | QF-LDC-11
0:30 | 298 | 8055.5 | 4017.5 | 12073 | Date: | 2022-05-29
1:00 | 540 | 7736 | 3779 | 11515
1:30 | 495 | 7610.5 | 3724.5 | 11335
2:00 | 450 | 7485 | 3670 | 11155
2:30 | 456 | 7343.5 | 3625 | 10968.5 | [5 empty] | Gen. at Eve. Peak | 13303 | 13303 MW (21:00 )
3:00 | 462 | 7202 | 3580 | 10782 | [6 empty] | 21:00
3:30 | 474 | 7132 | 3554.5 | 10686.5 | [5 empty] | Gen. at Day Peak | 11023 | 11023 MW (12:00 )
4:00 | 486 | 7062 | 3529 | 10591 | [6 empty] | 12:00
4:30 | 541 | 6872 | 3495 | 10367 | [5 empty] | Highest Generation | 13303
5:00 | 596 | 6682 | 3461 | 10143 | [6 empty] | 21:00
5:30 | 646 | 6347.5 | 3428.5 | 9776
6:00 | 696 | 6013 | 3396 | 9409
6:30 | 675 | 6037.5 | 3432 | 9469.5
7:00 | 654 | 6062 | 3468 | 9530
7:30 | 729 | 6061 | 3417 | 9478
8:00 | 804 | 6060 | 3366 | 9426
8:30 | 719 | 6254 | 3358.5 | 9612.5
9:00 | 634 | 6448 | 3351 | 9799
9:30 | 638 | 6679.5 | 3359.5 | 10039
10:00 | 642 | 6911 | 3368 | 10279
10:30 | 636 | 7145.5 | 3344.5 | 10490
11:00 | 630 | 7380 | 3321 | 10701
11:30 | 529 | 7543.5 | 3318.5 | 10862
12:00 | 428 | 7707 | 3316 | 11023
12:30 | 365 | 7766 | 3386.5 | 11152.5
13:00 | 302 | 7825 | 3457 | 11282
13:30 | 317 | 7592.5 | 3456 | 11048.5
14:00 | 332 | 7360 | 3455 | 10815
14:30 | 340 | 7643.5 | 3480 | 11123.5
15:00 | 348 | 7927 | 3505 | 11432
15:30 | 388 | 7869 | 3518.5 | 11387.5
16:00 | 428 | 7811 | 3532 | 11343
16:30 | 439 | 7781 | 3526.5 | 11307.5
17:00 | 450 | 7751 | 3521 | 11272
17:30 | 403 | 7604 | 3434.5 | 11038.5
18:00 | 356 | 7457 | 3348 | 10805
18:30 | 338 | 7915 | 3685.5 | 11600.5
19:00 | 320 | 8373 | 4023 | 12396
19:30 | 192 | 8803 | 4420 | 13223
20:00 | 122 | 8832 | 4433 | 13265 |  |  |  | Executive Engineer
20:30 | 109 | 8842.5 | 4441.5 | 13284 |  |  |  | Network Operation Division
21:00 | 96 | 8853 | 4450 | 13303
21:30 | 91 | 8753 | 4438.5 | 13191.5
22:00 | 86 | 8653 | 4427 | 13080 |  |  |  |  | Page 6 of 7
22:30 | 96 | 8584 | 4383.5 | 12967.5
23:00 | 106 | 8515 | 4340 | 12855
23:30 | 81 | 8445 | 4298 | 12743
24:00 | 56 | 8375 | 4256 | 12631
13303 MW (21:00 )
11023 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-05-29 |  | Energy |  | 272544433
[13 empty] | 2022-05-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3436 | 922 | 2127 | 389 | 3871 | 1065 | 68 | 0 | 643 | 110 | 0 | 0
0:30 | 3457.5 | 923 | 2141.5 | 194.5 | 3757 | 1035 | 53 | 0 | 404.5 | 107 | 0 | 0 | Date: | 2022-05-29
1:00 | 3479 | 924 | 2156 | 0 | 3643 | 1005 | 38 | 0 | 166 | 104 | 0 | 0
1:30 | 3463 | 922 | 2140.5 | 0 | 3553.5 | 1000 | 38 | 0 | 115 | 103 | 0 | 0 | [8 empty] | Total Energy | 272.5444 | Total Energy Gen 272.544 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.544 MKWHr
2:00 | 3447 | 920 | 2125 | 0 | 3464 | 995 | 38 | 0 | 64 | 102 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3429.5 | 919.5 | 2130.5 | 0 | 3301 | 985 | 38 | 0 | 64 | 101 | 0 | 0 | [8 empty] | Energy Requirement | 272.5444
3:00 | 3412 | 919 | 2136 | 0 | 3138 | 975 | 38 | 0 | 64 | 100 | 0 | 0
3:30 | 3418 | 919.5 | 2125 | 0 | 3063 | 960 | 38 | 0 | 64 | 99 | 0 | 0 | [6 empty] | Shortage
4:00 | 3424 | 920 | 2114 | 0 | 2988 | 945 | 38 | 0 | 64 | 98 | 0 | 0
4:30 | 3427 | 920 | 2105 | 0 | 2789 | 935 | 38 | 0 | 56 | 97 | 0 | 0
5:00 | 3430 | 920 | 2096 | 0 | 2590 | 925 | 38 | 0 | 48 | 96 | 0 | 0
5:30 | 3378 | 920 | 2107 | 0 | 2281.5 | 915 | 38 | 0 | 40 | 92 | 4.5 | 0
6:00 | 3326 | 920 | 2118 | 0 | 1973 | 905 | 38 | 0 | 32 | 88 | 9 | 0
6:30 | 3342.5 | 919.5 | 2149 | 0 | 1972.5 | 900 | 38 | 0 | 32 | 86 | 30 | 0 |  |  |  |  | Coal
7:00 | 3359 | 919 | 2180 | 0 | 1972 | 895 | 38 | 0 | 32 | 84 | 51 | 0
7:30 | 3371.5 | 919 | 2132.5 | 0 | 1979.5 | 875 | 38 | 0 | 32 | 88 | 42.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3384 | 919 | 2085 | 0 | 1987 | 855 | 38 | 0 | 32 | 92 | 34 | 0
8:30 | 3359.5 | 919 | 2079 | 0 | 2161.5 | 865 | 38 | 0 | 40 | 97 | 53.5 | 0
9:00 | 3335 | 919 | 2073 | 0 | 2336 | 875 | 38 | 0 | 48 | 102 | 73 | 0
9:30 | 3309.5 | 919.5 | 2063 | 0 | 2607.5 | 865 | 38 | 0 | 48 | 103 | 85.5 | 0
10:00 | 3284 | 920 | 2053 | 0 | 2879 | 855 | 38 | 0 | 48 | 104 | 98 | 0
10:30 | 3288.5 | 919.5 | 2036.5 | 71 | 3028.5 | 840 | 53 | 0 | 48 | 106 | 99 | 0
11:00 | 3293 | 919 | 2020 | 142 | 3178 | 825 | 68 | 0 | 48 | 108 | 100 | 0
11:30 | 3339.5 | 919 | 2028.5 | 187.5 | 3226 | 830 | 68 | 0 | 54 | 105 | 104.5 | 0
12:00 | 3386 | 919 | 2037 | 233 | 3274 | 835 | 68 | 0 | 60 | 102 | 109 | 0
12:30 | 3426 | 920 | 2027.5 | 265.5 | 3299.5 | 855 | 68 | 0 | 119 | 81 | 91 | 0
13:00 | 3466 | 921 | 2018 | 298 | 3325 | 875 | 68 | 0 | 178 | 60 | 73 | 0
13:30 | 3466 | 921 | 2018 | 298 | 3325 | 875 | 68 | 0 | 178 | 60 | 73 | 0
14:00 | 3466 | 921 | 2018 | 298 | 3325 | 875 | 68 | 0 | 178 | 60 | 73 | 0
14:30 | 3444.5 | 920 | 1999.5 | 378 | 3320.5 | 890 | 67.5 | 0 | 188.5 | 71 | 77.5 | 0
15:00 | 3423 | 919 | 1981 | 458 | 3316 | 905 | 67 | 0 | 199 | 82 | 82 | 0
15:30 | 3462 | 918.5 | 1986 | 300.5 | 3388 | 910 | 67.5 | 0 | 203 | 81 | 71 | 0
16:00 | 3501 | 918 | 1991 | 143 | 3460 | 915 | 68 | 0 | 207 | 80 | 60 | 0
16:30 | 3552 | 919 | 2004 | 71.5 | 3465 | 915 | 68 | 0 | 209.5 | 79 | 50 | 0
17:00 | 3552 | 920 | 2017 | 0 | 3470 | 915 | 68 | 0 | 212 | 78 | 40 | 0
17:30 | 3483.5 | 920 | 1909.5 | 0 | 3428.5 | 885 | 68 | 0 | 234.5 | 87 | 22.5 | 0
18:00 | 3415 | 920 | 1802 | 0 | 3387 | 855 | 68 | 0 | 257 | 96 | 5 | 0
18:30 | 3487.5 | 920 | 1915 | 164 | 3617 | 880 | 68 | 0 | 442.5 | 104 | 2.5 | 0
19:00 | 3560 | 920 | 2028 | 328 | 3847 | 905 | 68 | 0 | 628 | 112 | 0 | 0
19:30 | 3587 | 921 | 2090 | 623 | 4088 | 1075 | 68 | 0 | 653 | 118 | 0 | 0
20:00 | 3632 | 920 | 2072 | 633 | 4095 | 1075 | 68 | 0 | 654 | 116 | 0 | 0
20:30 | 3630.5 | 920 | 2103 | 599.5 | 4117 | 1075 | 68 | 4.5 | 652.5 | 114 | 0 | 0
21:00 | 3629 | 920 | 2134 | 566 | 4139 | 1075 | 68 | 9 | 651 | 112 | 0 | 0
21:30 | 3637 | 920.5 | 2094 | 513.5 | 4113 | 1075 | 68 | 9 | 649.5 | 112 | 0 | 0
22:00 | 3645 | 921 | 2054 | 461 | 4087 | 1075 | 68 | 9 | 648 | 112 | 0 | 0
22:30 | 3561.5 | 921.5 | 2094.5 | 391 | 4086.5 | 1080 | 68 | 4.5 | 648 | 112 | 0 | 0
23:00 | 3478 | 922 | 2135 | 321 | 4086 | 1085 | 68 | 0 | 648 | 112 | 0 | 0
23:30 | 3457 | 922 | 2131 | 355 | 3978.5 | 1075 | 68 | 0 | 645.5 | 111 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.6° C
24:00 | 3436 | 922 | 2127 | 389 | 3871 | 1065 | 68 | 0 | 643 | 110 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 272.544 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.544 MKWHr
Note on W13: Author:

## Generation
g | 2022-05-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 941400
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 408000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [7 empty] | 5 | 14 | 25 | 25 | 0 |  |  |  | 1 |  | 13 | 25 | 25 | 25 | 25 | 25 | 25 | 263822
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 2 | 3 | 10 | 15 | 13 | 19 | 19 | 13 | 15 | 8 | 3 | 3 | 0 | [8 empty] | 111915
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 546424
12 | Hathazari 100 MW peaking PP | 34 | 0 | [17 empty] | 20 | 42 | 42 | 46 | 52 | 59 | 59 | 289872
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 95 | 87 | 51 | 51 | 53 | 79 | 87 | 87 | 87 | 87 | 34 | 38 | 72 | 85 | 87 |  | 89 | 95 | 98 | 105 | 93 | 90 | 87 | 2029845
| Daudkandi 200 MW PP (B.Trac) | [12 empty] | 30 | 10 | 80 |  |  |  |  | 50 | 150 | 150 | 80 | 80 |  |  | 441984
14 | Titas 50 MW Peaking PP | [11 empty] | 12 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 577744
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 325 | 325 | 325 | 331 | 330 | 330 | 332 | 326 | 326 | 326 | 332 | 330 | 334 | 332 | 333 | 250 |  | 329 | 331 | 329 | 330 | 330 | 318 | 315 | 7823976
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 293 | 240 | 190 | 45 | 15 | 15 | 15 | 26 | 128 | 190 | 218 | 230 | 253 | 278 | 275 | 278 | 283 |  | 283 | 283 | 283 | 286 | 283 | 285 | 282 | 5133598
19 | Ashuganj 195MW PP (APSCL-United) | 110 | 78 | 78 | 78 | 78 | 78 | 107 | 107 | 110 | 110 | 110 | 110 | 110 | 68 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1438545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6723255
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 36 | 35 | 35 | 35 | 35 | 33 | 33 | 33 | 34 | 34 |  | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 806760
33 | Ashuganj 225 MW CCPP | 201 | 180 | 180 | 180 | 180 | 192 | 181 | 181 | 183 | 203 | 186 | 201 | 182 | 155 | 158 | 186 | 187 | 194 |  | 207 | 210 | 212 | 203 | 196 | 212 | 180 | 4630000
34 | Ashuganj 450 MW CCPP(South) | 55 | 55 | 35 | 60 | 55 | 55 | 70 | 95 | 79 | 135 | 170 | 250 | 350 | 305 | 360 | 355 | 350 | 310 |  | 320 | 330 | 345 | 345 | 330 | 160 | 115 | 4823000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 54 | 55 | 55 | 55 | 54 | 54 | 52 | 53 | 52 | 53 | 53 | 52 | 52 | 50 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1092000
36 | Chandpur 150 MW CCPP | 102 | 100 | 102 | 100 | 102 | 30 | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 35 | 56 |  | 56 | 56 | 55 | 54 | 86 | 85 | 151 | 1417090
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5175250
41 | Haripur 360MW CCPP(HPL) | 337 | 336 | 337 | 337 | 342 | 342 | 342 | 332 | 330 | 338 | 317 | 320 | 323 | 327 | 332 | 330 | 330 | 250 |  | 312 | 332 | 335 | 337 | 343 | 342 | 341 | 7892000
42 | RPCL 210MW CCPP | 144 | 145 | 151 | 150 | 154 | 155 | 154 | 145 | 130 | 117 | 118 | 117 | 106 | 104 | 108 | 123 | 132 | 128 |  | 128 | 129 | 128 | 128 | 128 | 127 | 127 | 3079680
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 13 | 10 | 41 | 47 | 25 | 51 | 18 | 22 | 30 | 24 | 12 | 2 | [8 empty] | 326660
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1030000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 42 | 41 | 41 | 958136
46 | Shajibazar 330 MW CCPP | 110 | 110 | 111 | 111 | 111 | 110 | 110 | 110 | 110 | 0 | [16 empty] | 993000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 55 | 55 | 55 | 56 | 61 | 61 | 61 | 61 | 50 | 40 | 41 | 51 | 57 | 56 | 61 | 61 | 61 |  | 60 | 56 | 57 | 56 | 57 | 56 | 57 | 1436992
48 | Shahjibazar 86MW PP (Shahjibazar) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 711360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 220 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 219 | 219 | 219 | 219 | 5266690
51 | Sylhet 20 MW GTPP | [16 empty] | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 127000
52 | Sylhet 50MW PP (EPL) | [22 empty] | 11 | 11 | 11 | 11 | 33200
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 229860
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 99100
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 157800
56 | Shahjahanulla 25 MW PP | 16 | 0 | [13 empty] | 0 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 252685
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 280 | 270 | 270 | 320 | 280 | 310 | 300 | 310 | 300 | 300 | 310 | 320 | 280 | 300 | 270 |  | 290 | 300 | 280 | 300 | 265 | 285 | 290 | 7157500
| Bibiyana South 400 MW | 383 | 389 | 371 | 365 | 365 | 365 | 365 | 370 | 370 | 370 | 370 | 385 | 392 | 390 | 394 | 387 | 397 | 396 |  | 385 | 390 | 400 | 400 | 400 | 397 | 401 | 9192200
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1189973
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 570240
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502848
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 455544
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 17 | 17 | 0 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 362700
63 | Impoprt (Tripura) | 104 | 102 | 100 | 98 | 96 | 88 | 84 | 92 | 102 | 104 | 108 | 102 | 60 | 62 | 82 | 80 | 78 | 96 |  | 112 | 118 | 116 | 112 | 112 | 112 | 110 | 2332800
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 36 | 12 | 5 | 5 | 2 | 5 | 2 | 2 | 2 | 2 | 2 | 2 |  | 4 | 4 | 7 | 27 | 3 | 30 | 30 | 414240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 428472
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  | 0 | 11 | 11 | 0 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 128700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 20 | 16 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 724500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 12 | 12 | 14 | 14 |  | 17 | 20 | 21 | 21 | 21 | 21 | 21 | 416120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 18 | 18 | 28 | 28 | 28 | 28 | 9 | 627120
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 606200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 784800
73 | Ghorashal 108MW PP (Regent) | 106 | 106 | 105 | 103 | 103 | 103 | 103 | 99 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 89 | 100 | 106 |  | 103 | 103 | 101 | 103 | 103 | 103 | 103 | 2357500
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 429780
| Chowmuhani 113 MW | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 68 | 113 | 114 |  | 114 | 114 | 115 | 115 | 117 | 115 | 23 | 1050000
| Manikgonj 162MW PP(MPGL) | 131 | 144 | 138 | 126 | 126 | 72 | 72 | 72 | 126 | 126 | 145 | 144 | 126 | 144 | 126 | 126 | 126 | 126 |  | 132 | 144 | 144 | 144 | 144 | 144 | 144 | 3081600
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 68 | 0 | [5 empty] | 10 | 60 | 67 | 70 | 84 | 92 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 1478035
78 | Gazipur 52 MW PP | 50 | 25 | 25 | 25 | 8 | 8 | 8 | 18 | 37 | 50 | 50 | 42 | 42 | 44 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 951360
79 | Kodda 150MW PP | 132 | 64 | 64 | 64 | 48 | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 82 | 82 | 90 | 98 | 98 | 82 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2064480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 204350
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 70 | 50 | 50 | 52 | 66 | 72 | 72 | 72 | 72 | 70 | 70 | 76 | 70 | 70 |  | 80 | 90 | 90 | 90 | 90 | 90 | 90 | 1909200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 |  | 1 | 1 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 14279
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 912105
| Karnaphuli Power Ltd. | 103 | 102 | 110 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2656279
82 | Madanganj 102 PP(Summit) | 96 | 92 | 80 | 92 | 96 | 52 | 32 | 32 | 32 | 79 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 91 |  | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 2026272
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 140 | 145 | 145 | 135 | 140 | 150 | 140 | 145 | 140 | 140 | 138 | 145 | 120 | 130 | 135 | 140 | 130 | 130 |  | 145 | 140 | 135 | 140 | 145 | 140 | 135 | 3442473
87 | Meghnaghat 100 MW(IEL) | 89 | 89 | 89 | 88 | 89 | 89 | 86 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 82 | 82 | 72 | 78 |  | 80 | 82 | 82 | 81 | 80 | 79 | 80 | 2037120
| Meghnaghat 104 MW PP (OPCL) | 89 | 89 | 89 | 90 | 89 | 67 | 53 | 53 | 56 | 75 | 72 | 70 | 71 | 72 | 90 | 91 | 90 | 90 |  | 90 | 90 | 89 | 90 | 90 | 90 | 90 | 1941120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258960
92 | Fenchuganj 44MW (Energyprima) | [24 empty] | 10 |  | 18288
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1197536
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 24 | 7 | 7 | 7 | 32 | 32 | 48 | 48 | 85 | 85 | 85 | 85 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1657296
95 | Patenga 50MW PP (Baraka) | 45 | 49 | 50 | 45 | 44 | 44 | 44 | 44 | 44 | 0 | [11 empty] | 1 | 30 |  |  | 23 | 512160
96 | Chattogram 108 MW PP (ECPV) | 74 | 74 | 74 | 74 | 74 | 47 | 31 | 32 | 43 | 70 | 70 | 72 | 72 | 49 | 52 | 75 | 74 | 75 |  | 75 | 75 | 75 | 76 | 76 | 76 | 75 | 1599360
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1331745
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 25 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1104119
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2675945
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | [9 empty] | 14100
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1199880
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 27 | 76 | 72 | 13 | 183 | 28 |  |  |  | 103 | 203 | 203 | 202 | 84 | 122 | 221 | 1224040
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 90 | 97 | 99 | 25 | 97 | 50 |  |  |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 930000
106 | Mymensingh 200 MW PP (United) | 120 | 120 | 120 | 120 | 68 | 40 | 45 | 45 | 75 | 113 | 170 | 178 | 178 | 186 | 186 | 176 | 150 | 150 |  | 170 | 187 | 187 | 187 | 188 | 188 | 188 | 3391200
112 | Aurahati 100MW PP (Aggreko) | [10 empty] | 25 | 60 | 97 | 25 | 98 | 65 |  |  |  | 70 | 98 | 98 | 98 | 97 | 99 | 98 | 821323
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 132 | 92 | 50 | 50 | 50 | 76 | 101 | 140 | 149 | 149 | 149 | 149 | 149 | 145 | 133 |  | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 3081312
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 54 |  | 55 | 55 | 56 | 57 | 59 | 60 | 37 | 824640
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 155 | 68 | 68 | 68 | 91 | 163 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 155 |  | 170 | 200 | 200 | 200 | 200 | 200 | 200 | 4212480
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 80 | 80 | 80 | 30 | 30 | 30 | 38 | 108 | 127 | 125 | 118 | 118 | 120 | 125 | 123 | 122 |  | 123 | 122 | 122 | 123 | 130 | 130 | 120 | 2435490
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 401 | 401 | 401 | 401 | 401 | 400 | 401 | 401 | 401 | 403 | 402 | 403 | 402 | 402 | 402 | 362 |  | 402 | 401 | 401 | 401 | 400 | 402 | 400 | 9597000
| Jamalpur 115 MW PP (United) | 106 | 106 | 105 | 105 | 105 | 65 | 65 | 65 | 90 | 104 | 104 | 104 | 103 | 104 | 102 | 102 | 101 | 101 |  | 101 | 101 | 103 | 103 | 104 | 104 | 95 | 2350800
| Anwara 300 MW PP (United) | 297 | 281 | 282 | 283 | 282 | 282 | 282 | 283 | 283 | 267 | 265 | 265 | 265 | 210 | 264 | 289 | 284 | 284 |  | 300 | 300 | 300 | 300 | 282 | 300 | 300 | 6671673
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 38 |  | 65 | 65 | 65 | 65 | 65 | 65 | 38 | 833280
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 92 | 90 | 90 | 90 | 90 | 90 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2489018
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 24 | 17 | 17 | 17 | 17 | 26 | 35 | 35 | 34 | 26 | 17 | 17 | 17 |  | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 710640
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 100 | 90 | 50 | 17 | 17 | 17 | 24 | 34 | 40 | 70 | 94 | 102 | 100 | 102 | 100 | 101 | 78 | 58 |  | 82 | 100 | 99 | 100 | 100 | 100 | 100 | 1848000
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1233720
120 | Eastern Zone Total | 7736 | 7485 | 7202 | 7062 | 6682 | 6013 | 6062 | 6060 | 6448 | 6911 | 7380 | 7707 | 7825 | 7360 | 7927 | 7811 | 7751 | 7457 |  | 8373 | 8803 | 8832 | 8853 | 8653 | 8515 | 8375 | 181289558
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 92 | 96 | 96 | 96 | 96 | 96 | 96 | 88 | 69 | 49 | 32 | 32 | 66 | 66 | 65 | 65 | 65 | 64 |  | 85 | 96 | 97 | 98 | 97 | 97 | 101 | 1856640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 8 |  | 45 | 38 | 37 | 33 | 33 | 33 | 30 | 186720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 58 | 105 | 105 | 105 | 105 | 105 | 105 | 1345440
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 5 | 32 | 7 | 10 | 27 | 44 | 21 | 26 | 31 | 36 | 28 | 22 | 3 | [8 empty] | 291600
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 442800
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 222 | 221 | 222 | 205 | 221 | 219 | 190 | 165 | 164 | 164 | 163 | 163 | 185 | 186 | 185 | 185 | 165 |  | 220 | 222 | 222 | 223 | 191 | 220 | 222 | 4818082
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 526944
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 84 | 82 | 86 | 87 | 87 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 2093743
140 | Bhola 33 MW PP (Venture) | 30 | 28 | 29 | 28 | 27 | 24 | 21 | 20 | 21 | 21 | 1 | 12 | 18 | 18 | 18 | 16 | 18 | 18 |  | 26 | 28 | 30 | 30 | 29 | 32 | 30 | 542995
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [10 empty] | 30 | 25 | 30 | 30 |  |  | 102720
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | 8 | 0 | [13 empty] | 16 | 16 |  | 40 | 40 | 40 | 40 | 40 | 24 | 24 | 250875
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 5 |  | 55 | 63 | 70 | 67 | 67 | 60 | 60 | 337792
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 50 | 50 | 32 | 15 | 15 | 15 | 32 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 75 | 105 | 105 | 105 | 105 | 105 | 105 | 1021968
146 | Bheramara HVDC | 924 | 920 | 919 | 920 | 920 | 920 | 919 | 919 | 919 | 920 | 919 | 919 | 921 | 919 | 919 | 918 | 920 | 920 |  | 920 | 921 | 920 | 920 | 921 | 922 | 922 | 22256727
147 | Bheramara 410 MW CCPP | 265 | 265 | 270 | 265 | 270 | 270 | 270 | 250 | 220 | 240 | 240 | 240 | 235 | 225 | 220 | 220 | 215 | 215 |  | 225 | 235 | 235 | 235 | 235 | 235 | 235 | 6017184
148 | Payra 1320 MW | 830 | 820 | 800 | 770 | 750 | 730 | 720 | 680 | 700 | 680 | 650 | 660 | 700 | 700 | 730 | 740 | 740 | 680 |  | 730 | 900 | 900 | 900 | 900 | 910 | 890 | 20185100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4292600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 32 |  | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 238170
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 3 | 3 | 4 | 4 | 4 | 2 | 1 | 0 | 0 | [8 empty] | 29040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 170 | 170 | 170 | 170 | 140 | 168 | 188 | 190 | 187 | 182 | 175 | 170 | 165 | 163 | 172 | 170 | 171 |  | 174 | 174 | 174 | 174 | 178 | 182 | 182 | 4439927
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 416 | 415 | 415 | 415 | 415 | 415 | 415 | 425 | 421 | 414 | 416 | 414 | 414 | 388 | 414 | 414 | 414 | 322 |  | 383 | 416 | 417 | 417 | 418 | 415 | 424 | 9855709
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 0 | 5 | 5 |  | 20 | 22 | 18 | 18 | 18 | 18 | 18 | 109697
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 20 |  | 20 | 20 | 20 | 21 | 21 | 22 | 22 | 488640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 0 |  |  | 5 | 5 | 5 |  | 8 | 0 |  | 8 | 8 | 8 | 8 | 109044
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 185783
167 | Katakhali 50 MW Peaking PP | [12 empty] | 7 | 16 | 16 | 16 | 16 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 252900
168 | Santahar 50 MW Peaking PP | [19 empty] | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 165360
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196565
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 39 | 43 | 43 | 43 | 43 | 43 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 743224
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 5 | 42 | 57 | 56 | 70 |  |  | 208338
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 78 | 94 | 94 | 94 | 94 | 94 | 70 | 1909920
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 76 | 2003520
173 | Rangpur 20 MW GTPP | [21 empty] | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [22 empty] | 9 | 9 | 0 | 0 | 18000
176 | Rangpur 113 MW PP (Confidence) | 80 | 80 | 82 | 82 | 82 | 49 | 49 | 50 | 55 | 81 | 82 | 79 | 79 | 79 | 79 | 79 | 82 | 70 |  | 101 | 101 | 101 | 101 | 101 | 101 | 88 | 1939305
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 | 5 | 7 | 7 | 7 | 7 | 5 | 3 | 2 | 0 | [8 empty] | 53435
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 34 | 0 |  |  |  | 13 | 34 | 68 | 72 | 72 | 90 | 108 | 108 | 108 | 108 | 90 | 52 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1738368
178