## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-04 | Saturday
|  |  | Date (day): | 2022-06-04 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14234.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15274 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-03 | 2022-06-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 280 | 280 | 280 |  | 85 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 98 | 102 | 102
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 396 | 390 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 327 | 330 | 340
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-2 S/D due to Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 72 | 85 | 88 | 88 |  | 12 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 133 | 150 | 150 | 185 |  | FGMO & Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 70 | 92 | 96 | 96 |  |  | Engine problem
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 18 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M & gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 8 | 92 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 170 | 250 | 170 | 170 | 165 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 94 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 42 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 72 | 291 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 114 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 37 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5898 | 2620 | 3484 | 4161 | 4163 | 836 | 821
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 44 | 43 | 43 |  | 7 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 68 | 68 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 43 | 17 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 77 | 90 | 90 | 90 | 10 |  | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 22 | 39 | 25 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 80 | 85 |  | 23 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 115 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 38 | 54 | 54 | 54 |  | 19
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 86 | 98 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 110 | 110
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 758 | 1072 | 1286 | 1350 | 411 | 632
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 165 | 194 | 215 | 215
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 340 | 340
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 38 | 32 | 36 |  | 9 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 40 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 81 | 122 | 130 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 150 | 149 | 150 | 150 |  | 13
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 77 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 110 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 114 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 105 | 9 | 105 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 77 | 83 | 90 | 101 |  | 14
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1200 | 1529 | 1769 | 2076 | 708 | 65
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 136 | 150 | 160 | 42 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 140 | 200 | 170 | 187 |  | 13 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 96 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 5 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 293 | 476 | 528.6 | 504 | 42 | 21
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 0 | 0 | 0 |  | 70 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 42 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 55 | 53 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 5 | 45 | 30 | 45 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 60 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81 | 5 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 191 | 178 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 32 | 40 | 40 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 401 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1669 | 1727 | 1812 | 1856 | 431 | 272
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 905 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 94 | 109 | 100 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 35 | 40 |  | 14 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 72 | 0 | 72 |  | 37 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 260 | 285 | 285 | 125 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 2 | 93 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 89 | 105 | 105
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1317 | 1608 | 1700 | 2012 | 125 | 51
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 32 | 48 | 110
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 17 | 27 | 20 | 27 |  | 30 | Machine problem
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 85 | 88 | 88 | 106 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 970 | 1050 | 1050
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 207 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1100 | 1351 | 1443 | 1645 | 106 | 30
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 34 | 43 |  | 9 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 30 | 35 |  | 36 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 190 | 170 | 170 | 50 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 410 | 410
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 30 | 40 |  | 10 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 65 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 160 |  | 30 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 41 | 94 | 94 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 95 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 730 | 1115 | 1157 | 1278 | 695 | 136
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 37 | 98 | 80 | 100 |  | 13 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 252 | 363 | 378 | 390 | 99 | 183
|  | Total |  |  |  |  | 22348 | 21584 | 9939 | 12725 | 14234.6 | 15274 | 3453 | 2211
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9610.3296 | 12304.2 | 13763.8794 | 14768.9077
| A. |  | 2022-06-03 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12725 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9394 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12725 | MW
| 3 | Day peak Generation : |  |  | 9939 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12304.2 | MW
| 4 | Evening peak Generation : |  |  | 12725 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 262.0653 | MKWHr | By Solar | 0.66712 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 140.1888 | MKWHr |  | By Oil: | 69.0739 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 26.0601 | MKWHr |  | By Hydro: | 1.5636 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3453 | MW | Dhaka | 4146 | 4146 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2211 | MW | Chittagong | 1171.4 | 1171.4 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5664 | MW | Khulna | 1655.2 | 1655.2 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1061.32 | MMCFD |  |  | Rajshahi | 1403.6 | 1403.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160054933.136 | ii) Oil : | Taka | 897115330.8 | Comilla | 1159 | 1159 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 218670465 | Total | Taka | 1275840728.936 | Mymensingh | 1074 | 1074 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.327 | MKWHr. | Sylhet | 466 | 466 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -62 | MW (E to W) at | 21:00 | hrs | Barisal | 356 | 356 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -102 | MW at | 20:00 | hrs | Rangpur | 873 | 873 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 12304.2 | 12304.2 |  | 0
| B. |  | 2022-06-04 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 37.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15274 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1174 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 290.3827 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9265 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0531 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4586 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.9 |  | (b) Today: | 0 |  | (c) Rule Curve: |  | 76.52
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 399 | 332 |  | 0 | 225 | 148 | 81 | 92 | 40 | 170 | 0 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 38 | 22 | 30 | 0 | 0 | 0 | 0 | 99 | 202 | 55 | 150 | 31 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 21 | 120 | 139 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 219 | 19 | 7 | 10 | 285 | 24 | 0 | 0 | 293 | 0 | 0 | 186 | 0 | 142 | 0 | 88 | 200 | 132 | 401 | 105 | 105 | 105 | 0 | 300 | 36 | 109 | 114 | 13 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 100 | 55 |  | 908 | 0 | 220 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 40 | 84 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 415 | 105 | 0 | 70 | 105 | 79 | 0 | 0 | 76 | 990 | 220 | 0 | 17 | 0 | 0 | 109 |  | 8110 | 4081 | 12191 | 3617 | 908 | 2183 | 0 | 3995 | 1164 | 68 | 0 | 136 | 120 | 0 | 0 | 73.92
2:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 399 | 332 |  | 0 | 225 | 140 | 80 | 92 | 30 | 170 | 0 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 38 | 22 | 30 | 0 | 0 | 0 | 0 | 165 | 181 | 55 | 151 | 31 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 21 | 118 | 137 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 219 | 19 | 7 | 10 | 295 | 24 | 0 | 0 | 293 | 0 | 0 | 186 | 0 | 147 | 0 | 88 | 200 | 127 | 401 | 105 | 105 | 105 | 0 | 260 | 36 | 109 | 34 | 9 | 92 | 400 | 104 | 0 | 162 | 108 | 0 | 20 | 0 | 100 | 55 |  | 908 | 0 | 220 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 105 | 0 | 70 | 89 | 81 | 0 | 0 | 76 | 970 | 221 | 0 | 17 | 0 | 0 | 109 |  | 7996 | 4034 | 12030 | 3664 | 908 | 2186 | 0 | 3832 | 1145 | 68 | 0 | 109 | 118 | 0 | 0 | 73.92
3:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 398 | 332 |  | 0 | 225 | 138 | 80 | 92 | 40 | 170 | 0 | 0 | 100 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 24 | 25 | 33 | 16 | 0 | 37 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 22 | 40 | 0 | 0 | 0 | 0 | 220 | 181 | 55 | 150 | 31 | 56 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 20 | 116 | 139 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 219 | 18 | 7 | 10 | 280 | 24 | 0 | 0 | 293 | 0 | 0 | 186 | 0 | 132 | 0 | 88 | 200 | 135 | 400 | 105 | 105 | 105 | 0 | 120 | 36 | 110 | 17 | 8 | 90 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 82 | 55 |  | 909 | 0 | 235 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 414 | 105 | 0 | 70 | 89 | 81 | 0 | 0 | 76 | 920 | 220 | 0 | 17 | 0 | 0 | 109 |  | 7828 | 3938 | 11766 | 3759 | 909 | 2178 | 0 | 3588 | 1095 | 67 | 0 | 54 | 116 | 0 | 0 | 73.91
4:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 398 | 332 |  | 0 | 225 | 138 | 80 | 92 | 40 | 170 | 0 | 0 | 96 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 25 | 33 | 16 | 0 | 37 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 22 | 40 | 0 | 0 | 0 | 0 | 325 | 180 | 55 | 151 | 31 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 20 | 114 | 139 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 178 | 17 | 7 | 10 | 270 | 24 | 0 | 0 | 296 | 0 | 0 | 200 | 0 | 132 | 0 | 88 | 200 | 132 | 400 | 70 | 90 | 105 | 0 | 45 | 36 | 110 | 17 | 9 | 90 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 88 | 55 |  | 909 | 0 | 236 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 70 | 0 | 70 | 50 | 81 | 0 | 0 | 76 | 890 | 221 | 0 | 17 | 0 | 0 | 109 |  | 7746 | 3829 | 11575 | 3833 | 909 | 2166 | 0 | 3397 | 1065 | 67 | 0 | 24 | 114 | 0 | 0 | 73.91
5:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 398 | 332 |  | 0 | 225 | 138 | 72 | 92 | 40 | 170 | 0 | 0 | 54 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 14 | 25 | 33 | 16 | 0 | 37 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 22 | 40 | 0 | 0 | 0 | 0 | 356 | 180 | 55 | 150 | 31 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 20 | 106 | 140 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 178 | 19 | 7 | 10 | 275 | 24 | 0 | 0 | 195 | 0 | 0 | 200 | 0 | 133 | 0 | 89 | 200 | 138 | 400 | 8 | 90 | 105 | 0 | 0 | 36 | 110 | 17 | 9 | 90 | 400 | 104 | 0 | 17 | 108 | 0 | 17 | 0 | 97 | 55 |  | 906 | 0 | 240 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 414 | 35 | 0 | 70 | 50 | 81 | 0 | 0 | 76 | 870 | 221 | 0 | 17 | 0 | 0 | 109 |  | 7363 | 3742 | 11105 | 3862 | 906 | 2166 | 0 | 2928 | 1046 | 67 | 0 | 24 | 106 | 0 | 0 | 73.91
6:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 377 | 332 |  | 0 | 225 | 140 | 72 | 92 | 15 | 170 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 14 | 25 | 32 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 22 | 40 | 0 | 0 | 0 | 0 | 356 | 180 | 55 | 151 | 31 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 20 | 104 | 139 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 61 | 81 | 0 | 178 | 19 | 7 | 10 | 265 | 24 | 0 | 0 | 30 | 0 | 0 | 100 | 0 | 0 | 2 | 89 | 100 | 50 | 399 | 8 | 90 | 105 | 0 | 0 | 17 | 96 | 17 | 9 | 90 | 360 | 104 | 1 | 17 | 95 | 0 | 17 | 0 | 100 | 54 |  | 905 | 0 | 240 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 364 | 35 | 0 | 70 | 50 | 81 | 0 | 0 | 76 | 830 | 221 | 0 | 17 | 0 | 3 | 72 |  | 6479 | 3591 | 10070 | 3783 | 905 | 2110 | 0 | 2065 | 1005 | 68 | 0 | 24 | 104 | 6 | 0 | 73.9
7:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 366 | 331 |  | 0 | 225 | 127 | 75 | 50 | 15 | 170 | 0 | 0 | 8 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 14 | 25 | 33 | 18 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 22 | 30 | 0 | 0 | 0 | 0 | 356 | 180 | 55 | 149 | 31 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 20 | 94 | 139 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 62 | 81 | 0 | 178 | 19 | 7 | 10 | 275 | 24 | 0 | 0 | 30 | 0 | 0 | 100 | 0 | 6 | 3 | 89 | 100 | 50 | 376 | 8 | 90 | 105 | 2 | 0 | 17 | 93 | 17 | 9 | 90 | 361 | 100 | 4 | 17 | 108 | 0 | 17 | 0 | 84 | 35 |  | 905 | 0 | 240 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 365 | 35 | 0 | 70 | 50 | 81 | 0 | 1 | 76 | 780 | 221 | 0 | 17 | 0 | 11 | 72 |  | 6384 | 3547 | 9931 | 3754 | 905 | 2089 | 0 | 2005 | 955 | 68 | 0 | 40 | 94 | 21 | 0 | 73.9
8:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 366 | 282 |  | 0 | 225 | 140 | 79 | 48 | 15 | 170 | 0 | 0 | 8 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 14 | 25 | 32 | 32 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 38 | 22 | 30 | 0 | 0 | 0 | 0 | 330 | 181 | 55 | 150 | 31 | 56 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 21 | 92 | 137 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 40 | 81 | 0 | 178 | 19 | 7 | 10 | 265 | 24 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 70 | 11 | 89 | 68 | 50 | 352 | 8 | 90 | 105 | 3 | 0 | 17 | 65 | 17 | 9 | 90 | 360 | 93 | 6 | 17 | 108 | 0 | 17 | 0 | 75 | 35 |  | 905 | 0 | 240 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 309 | 0 | 0 | 50 | 32 | 50 | 0 | 1 | 76 | 740 | 187 | 0 | 17 | 1 | 28 | 72 |  | 6250 | 3324 | 9574 | 3683 | 905 | 1954 | 0 | 1867 | 915 | 68 | 0 | 40 | 92 | 50 | 0 | 73.9
9:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 367 | 282 |  | 0 | 225 | 140 | 71 | 48 | 15 | 170 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 14 | 25 | 32 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 38 | 22 | 20 | 0 | 0 | 0 | 0 | 312 | 181 | 55 | 150 | 31 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 21 | 90 | 130 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 40 | 81 | 0 | 178 | 18 | 7 | 10 | 280 | 24 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 70 | 16 | 89 | 68 | 20 | 352 | 8 | 90 | 105 | 4 | 0 | 17 | 51 | 17 | 9 | 90 | 360 | 104 | 15 | 17 | 108 | 0 | 0 | 0 | 67 | 35 |  | 906 | 0 | 245 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 300 | 0 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 740 | 173 | 0 | 17 | 3 | 72 | 34 |  | 6165 | 3229 | 9394 | 3689 | 906 | 1933 | 0 | 1658 | 915 | 68 | 0 | 24 | 90 | 111 | 0 | 73.89
10:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 369 | 281 |  | 0 | 225 | 135 | 72 | 48 | 15 | 170 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 14 | 25 | 32 | 16 | 0 | 38 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 38 | 0 | 20 | 0 | 0 | 0 | 0 | 312 | 182 | 55 | 150 | 32 | 49 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 33 | 20 | 86 | 120 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 40 | 78 | 0 | 178 | 19 | 7 | 10 | 295 | 24 | 0 | 0 | 18 | 0 | 0 | 100 | 0 | 70 | 11 | 77 | 68 | 20 | 401 | 8 | 90 | 105 | 3 | 0 | 17 | 51 | 17 | 9 | 90 | 397 | 104 | 13 | 17 | 108 | 0 | 6 | 0 | 77 | 35 |  | 905 | 0 | 245 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 352 | 0 | 0 | 35 | 0 | 38 | 0 | 0 | 35 | 750 | 176 | 0 | 17 | 4 | 64 | 34 |  | 6195 | 3269 | 9464 | 3743 | 905 | 1983 | 0 | 1672 | 925 | 38 | 0 | 16 | 86 | 96 | 0 | 73.89
11:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 398 | 332 |  | 0 | 225 | 135 | 72 | 63 | 22 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 16 | 25 | 32 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 37 | 22 | 20 | 0 | 0 | 0 | 0 | 310 | 180 | 55 | 150 | 32 | 48 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 33 | 20 | 84 | 120 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 60 | 81 | 0 | 184 | 19 | 7 | 10 | 290 | 8 | 0 | 0 | 60 | 0 | 0 | 123 | 0 | 70 | 17 | 77 | 68 | 30 | 402 | 8 | 90 | 105 | 5 | 0 | 25 | 65 | 17 | 9 | 90 | 400 | 104 | 1 | 17 | 108 | 0 | 17 | 0 | 77 | 35 |  | 906 | 0 | 245 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 350 | 0 | 0 | 35 | 0 | 37 | 0 | 0 | 35 | 750 | 175 | 0 | 17 | 4 | 37 | 34 |  | 6440 | 3230 | 9670 | 3807 | 906 | 2023 | 0 | 1792 | 925 | 68 | 0 | 0 | 84 | 65 | 0 | 73.88
12:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 405 | 332 |  | 0 | 225 | 140 | 72 | 70 | 30 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 25 | 35 | 0 | 25 | 11 | 25 | 32 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 11 | 22 | 22 | 0 | 0 | 0 | 0 | 310 | 165 | 26 | 150 | 32 | 51 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 25 | 20 | 92 | 109 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 61 | 78 | 0 | 191 | 19 | 7 | 10 | 280 | 16 | 0 | 0 | 72 | 0 | 0 | 140 | 0 | 70 | 20 | 77 | 77 | 81 | 402 | 8 | 90 | 105 | 1 | 0 | 38 | 86 | 17 | 9 | 90 | 400 | 104 | 5 | 17 | 108 | 0 | 17 | 0 | 77 | 37 |  | 906 | 0 | 240 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 2 | 0 | 41 | 0 | 37 | 0 | 6 | 70 | 740 | 207 | 0 | 17 | 2 | 67 | 34 |  | 6540 | 3399 | 9939 | 3766 | 906 | 2086 | 0 | 2004 | 915 | 68 | 0 | 0 | 92 | 102 | 0 | 73.86
13:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 400 | 328 |  | 0 | 225 | 140 | 73 | 79 | 30 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 11 | 25 | 33 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 37 | 22 | 36 | 0 | 0 | 0 | 0 | 310 | 178 | 8 | 150 | 33 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 17 | 20 | 102 | 109 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 61 | 10 | 0 | 191 | 19 | 7 | 10 | 290 | 24 | 0 | 0 | 75 | 0 | 0 | 151 | 0 | 70 | 16 | 77 | 120 | 110 | 402 | 8 | 90 | 105 | 0 | 0 | 54 | 87 | 17 | 9 | 100 | 391 | 104 | 8 | 17 | 108 | 0 | 17 | 0 | 77 | 37 |  | 905 | 0 | 230 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 19 | 0 | 68 | 0 | 68 | 0 | 7 | 76 | 760 | 217 | 0 | 17 | 2 | 32 | 34 |  | 6646 | 3471 | 10117 | 3759 | 905 | 2028 | 0 | 2254 | 935 | 68 | 0 | 0 | 102 | 66 | 0 | 73.84
14:00 | 0 | 0 | 0 | 180 | 280 | 94 | 0 | 391 | 282 |  | 0 | 225 | 140 | 79 | 78 | 30 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 11 | 0 | 32 | 0 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 10 | 0 | 37 | 22 | 30 | 0 | 0 | 0 | 0 | 310 | 189 | 8 | 150 | 30 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 26 | 20 | 100 | 109 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 61 | 75 | 0 | 192 | 18 | 7 | 10 | 260 | 24 | 0 | 0 | 75 | 0 | 0 | 160 | 0 | 70 | 7 | 77 | 120 | 118 | 351 | 8 | 50 | 105 | 0 | 0 | 54 | 87 | 17 | 9 | 100 | 360 | 104 | 7 | 17 | 108 | 0 | 17 | 0 | 17 | 54 |  | 905 | 0 | 230 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 24 | 83 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 350 | 35 | 0 | 70 | 0 | 78 | 0 | 7 | 76 | 770 | 213 | 0 | 17 | 2 | 29 | 52 |  | 6449 | 3466 | 9915 | 3653 | 905 | 1943 | 0 | 2248 | 945 | 68 | 0 | 0 | 100 | 53 | 0 | 73.82
15:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 389 | 322 |  | 0 | 225 | 140 | 79 | 78 | 30 | 170 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 40 | 0 | 25 | 11 | 25 | 32 | 0 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 31 | 22 | 19 | 0 | 0 | 0 | 0 | 310 | 192 | 8 | 148 | 30 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 14 | 102 | 109 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 60 | 75 | 0 | 191 | 19 | 7 | 10 | 300 | 16 | 0 | 0 | 75 | 0 | 0 | 160 | 0 | 70 | 6 | 77 | 142 | 118 | 400 | 8 | 50 | 105 | 0 | 0 | 54 | 88 | 17 | 9 | 100 | 400 | 104 | 10 | 17 | 108 | 0 | 17 | 0 | 26 | 55 |  | 905 | 0 | 225 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 35 | 0 | 70 | 0 | 77 | 0 | 5 | 76 | 770 | 203 | 0 | 17 | 1 | 41 | 52 |  | 6671 | 3529 | 10200 | 3757 | 905 | 2070 | 0 | 2289 | 945 | 68 | 0 | 0 | 102 | 64 | 0 | 73.8
16:00 | 0 | 0 | 0 | 180 | 280 | 90 | 0 | 396 | 272 |  | 0 | 225 | 140 | 73 | 78 | 30 | 170 | 0 | 0 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 11 | 25 | 32 | 0 | 0 | 37 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 34 | 22 | 31 | 0 | 0 | 0 | 0 | 310 | 189 | 8 | 150 | 33 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 33 | 14 | 112 | 124 | 0 | 20 | 1 | 43 | 41 | 5 | 5 | 110 | 0 | 40 | 10 | 0 | 191 | 19 | 7 | 10 | 270 | 20 | 0 | 0 | 110 | 0 | 0 | 200 | 0 | 70 | 0 | 77 | 164 | 125 | 400 | 8 | 50 | 105 | 1 | 0 | 54 | 88 | 17 | 37 | 100 | 390 | 104 | 9 | 17 | 108 | 0 | 17 | 0 | 46 | 54 |  | 905 | 0 | 220 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 270 | 17 | 0 | 70 | 15 | 76 | 0 | 4 | 76 | 720 | 186 | 0 | 17 | 1 | 21 | 52 |  | 6730 | 3280 | 10010 | 3763 | 905 | 1766 | 0 | 2465 | 895 | 67 | 0 | 0 | 112 | 37 | 0 | 73.78
17:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 395 | 272 |  | 0 | 225 | 145 | 71 | 83 | 30 | 170 | 0 | 0 | 8 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 12 | 25 | 32 | 40 | 0 | 37 | 28 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 44 | 22 | 27 | 0 | 0 | 0 | 0 | 310 | 193 | 8 | 150 | 33 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 7 | 25 | 20 | 94 | 136 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 40 | 81 | 0 | 192 | 19 | 7 | 10 | 260 | 0 | 0 | 0 | 30 | 0 | 0 | 200 | 0 | 0 | 0 | 30 | 85 | 132 | 363 | 8 | 95 | 105 | 1 | 0 | 17 | 51 | 17 | 76 | 94 | 350 | 73 | 6 | 17 | 108 | 0 | 17 | 0 | 59 | 55 |  | 906 | 0 | 230 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0 | 70 | 15 | 76 | 0 | 2 | 113 | 680 | 186 | 0 | 17 | 0 | 12 | 52 |  | 6492 | 3212 | 9704 | 3659 | 906 | 1814 | 0 | 2242 | 855 | 65 | 0 | 48 | 94 | 21 | 0 | 73.76
18:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 396 | 273 |  | 0 | 225 | 140 | 76 | 92 | 30 | 170 | 0 | 0 | 8 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 12 | 25 | 32 | 8 | 0 | 37 | 28 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 44 | 22 | 30 | 0 | 0 | 0 | 0 | 310 | 191 | 8 | 150 | 38 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 25 | 20 | 84 | 131 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 38 | 81 | 0 | 192 | 19 | 7 | 10 | 270 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 0 | 30 | 0 | 30 | 85 | 133 | 364 | 8 | 50 | 34 | 0 | 0 | 17 | 17 | 17 | 46 | 100 | 350 | 17 | 2 | 17 | 92 | 0 | 17 | 0 | 63 | 55 |  | 905 | 0 | 240 | 0 | 108 | 0 | 0 | 0 | 5 | 25 | 8 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0 | 50 | 15 | 54 | 0 | 0 | 50 | 650 | 186 | 0 | 17 | 0 | 3 | 52 |  | 6139 | 3102 | 9241 | 3660 | 905 | 1828 | 0 | 1796 | 825 | 65 | 0 | 73 | 84 | 5 | 0 | 73.74
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 100 | 0 | 397 | 295 |  | 0 | 225 | 143 | 75 | 92 | 30 | 170 | 0 | 0 | 17 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 12 | 25 | 33 | 8 | 0 | 37 | 30 | 100 | 0 | 4 | 0 | 0 | 0 | 0 |  | 24 | 4 | 51 | 10 | 5 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 310 | 194 | 8 | 148 | 34 | 40 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 33 | 20 | 108 | 134 | 0 | 20 | 0 | 43 | 41 | 5 | 5 | 110 | 0 | 60 | 81 | 0 | 192 | 19 | 7 | 10 | 300 | 16 | 0 | 0 | 95 | 0 | 0 | 150 | 0 | 42 | 0 | 70 | 115 | 133 | 384 | 24 | 90 | 73 | 0 | 135 | 30 | 54 | 17 | 78 | 100 | 380 | 36 | 0 | 32 | 90 | 0 | 17 | 0 | 81 | 55 |  | 905 | 0 | 260 | 0 | 115 | 0 | 0 | 0 | 45 | 72 | 40 | 83 | 23 | 32 | 0 | 0 | 0 | 40 | 4 | 63 | 0 | 0 | 6 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 350 | 19 | 0 | 73 | 88 | 86 | 0 | 0 | 113 | 720 | 210 | 0 | 17 | 0 | 0 | 90 |  | 7047 | 3834 | 10881 | 3774 | 905 | 2023 | 0 | 2722 | 895 | 67 | 0 | 387 | 108 | 0 | 0 | 73.68
19:30 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 395 | 342 |  | 0 | 225 | 145 | 81 | 92 | 30 | 170 | 0 | 0 | 92 | 84 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 19 | 25 | 33 | 24 | 0 | 37 | 30 | 100 | 0 | 9 | 0 | 0 | 0 | 0 |  | 24 | 33 | 51 | 10 | 8 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 310 | 195 | 8 | 149 | 40 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 108 | 134 | 0 | 20 | 0 | 0 | 42 | 42 | 25 | 110 | 0 | 60 | 81 | 0 | 192 | 19 | 7 | 10 | 260 | 16 | 0 | 0 | 245 | 0 | 0 | 200 | 0 | 115 | 0 | 90 | 200 | 128 | 400 | 91 | 90 | 105 | 0 | 150 | 54 | 88 | 17 | 106 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 83 | 55 |  | 905 | 0 | 260 | 0 | 109 | 0 | 0 | 0 | 40 | 72 | 40 | 87 | 25 | 32 | 0 | 0 | 0 | 42 | 12 | 80 | 0 | 0 | 24 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 419 | 90 | 0 | 94 | 89 | 97 | 0 | 0 | 113 | 890 | 210 | 0 | 17 | 0 | 0 | 90 |  | 8085 | 4275 | 12360 | 3847 | 905 | 2158 | 0 | 3754 | 1065 | 67 | 0 | 456 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 395 | 341 |  | 0 | 225 | 147 | 80 | 92 | 40 | 250 | 0 | 0 | 82 | 85 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 19 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 15 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 10 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 310 | 192 | 8 | 149 | 37 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 108 | 136 | 0 | 20 | 0 | 0 | 42 | 53 | 42 | 110 | 0 | 60 | 81 | 0 | 192 | 19 | 22 | 10 | 270 | 16 | 0 | 0 | 273 | 0 | 0 | 200 | 0 | 110 | 0 | 90 | 189 | 123 | 400 | 91 | 90 | 105 | 0 | 150 | 54 | 89 | 17 | 105 | 100 | 400 | 104 | 0 | 135 | 108 | 0 | 17 | 0 | 83 | 55 |  | 906 | 0 | 260 | 0 | 109 | 0 | 0 | 0 | 40 | 72 | 40 | 87 | 26 | 32 | 0 | 0 | 0 | 43 | 26 | 80 | 0 | 8 | 32 | 8 | 40 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 419 | 93 | 0 | 94 | 89 | 99 | 0 | 0 | 113 | 890 | 210 | 0 | 17 | 0 | 0 | 90 |  | 8230 | 4323 | 12553 | 3931 | 906 | 2213 | 0 | 3771 | 1065 | 68 | 0 | 491 | 108 | 0 | 0 | 73.7
21:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 396 | 327 |  | 0 | 225 | 133 | 85 | 92 | 40 | 250 | 0 | 0 | 92 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 17 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 10 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 310 | 194 | 8 | 149 | 38 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 110 | 136 | 0 | 20 | 0 | 0 | 42 | 53 | 45 | 110 | 0 | 60 | 81 | 0 | 178 | 19 | 32 | 10 | 280 | 16 | 0 | 0 | 291 | 0 | 0 | 200 | 0 | 114 | 0 | 90 | 200 | 122 | 401 | 96 | 90 | 105 | 0 | 115 | 54 | 98 | 17 | 105 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 83 | 55 |  | 905 | 0 | 260 | 0 | 109 | 0 | 0 | 0 | 40 | 72 | 40 | 85 | 27 | 32 | 0 | 0 | 0 | 43 | 28 | 80 | 0 | 43 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 93 | 0 | 94 | 89 | 98 | 0 | 0 | 113 | 970 | 220 | 0 | 17 | 0 | 0 | 90 |  | 8288 | 4437 | 12725 | 3915 | 905 | 2214 | 0 | 3877 | 1145 | 68 | 0 | 491 | 110 | 0 | 0 | 73.68
22:00 | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 396 | 302 |  | 0 | 225 | 137 | 89 | 70 | 40 | 250 | 0 | 0 | 76 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 20 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 10 | 0 | 44 | 22 | 37 | 0 | 0 | 0 | 0 | 310 | 200 | 8 | 150 | 38 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 114 | 135 | 0 | 20 | 0 | 0 | 41 | 53 | 50 | 110 | 0 | 60 | 81 | 0 | 179 | 18 | 38 | 10 | 290 | 16 | 0 | 0 | 296 | 0 | 0 | 200 | 0 | 128 | 0 | 90 | 200 | 122 | 401 | 96 | 90 | 105 | 0 | 115 | 54 | 110 | 17 | 105 | 100 | 400 | 104 | 0 | 108 | 108 | 0 | 17 | 0 | 83 | 55 |  | 906 | 0 | 260 | 0 | 109 | 0 | 0 | 0 | 40 | 66 | 40 | 87 | 28 | 32 | 0 | 0 | 0 | 43 | 25 | 80 | 0 | 43 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 380 | 105 | 0 | 94 | 89 | 98 | 0 | 0 | 113 | 990 | 220 | 0 | 17 | 0 | 0 | 90 |  | 8241 | 4434 | 12675 | 3929 | 906 | 2179 | 0 | 3832 | 1165 | 68 | 0 | 482 | 114 | 0 | 0 | 73.66
23:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 397 | 301 |  | 0 | 225 | 140 | 89 | 71 | 40 | 250 | 0 | 0 | 51 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 20 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 17 | 10 | 0 | 44 | 22 | 40 | 0 | 0 | 0 | 0 | 310 | 203 | 8 | 150 | 38 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 114 | 151 | 0 | 20 | 0 | 0 | 41 | 53 | 50 | 110 | 0 | 61 | 81 | 0 | 179 | 18 | 39 | 10 | 300 | 16 | 0 | 0 | 293 | 0 | 0 | 191 | 0 | 131 | 0 | 90 | 200 | 128 | 401 | 96 | 90 | 105 | 0 | 115 | 54 | 110 | 0 | 105 | 100 | 400 | 104 | 0 | 108 | 108 | 0 | 17 | 0 | 83 | 55 |  | 906 | 0 | 260 | 0 | 110 | 0 | 0 | 0 | 26 | 66 | 40 | 85 | 28 | 32 | 0 | 0 | 0 | 43 | 25 | 80 | 0 | 43 | 32 | 0 | 32 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 382 | 105 | 0 | 94 | 89 | 98 | 0 | 0 | 113 | 990 | 221 | 0 | 17 | 0 | 0 | 90 |  | 8201 | 4406 | 12607 | 3945 | 906 | 2200 | 0 | 3781 | 1165 | 68 | 0 | 428 | 114 | 0 | 0 | 73.64
24:00 | 0 | 0 | 0 | 180 | 280 | 99 | 0 | 397 | 331 |  | 0 | 225 | 125 | 89 | 80 | 40 | 170 | 0 | 0 | 73 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 20 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 0 | 44 | 22 | 42 | 0 | 0 | 0 | 0 | 310 | 202 | 8 | 150 | 38 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 21 | 108 | 151 | 0 | 20 | 0 | 0 | 41 | 22 | 20 | 110 | 0 | 62 | 81 | 0 | 179 | 19 | 40 | 10 | 300 | 16 | 0 | 0 | 291 | 0 | 0 | 188 | 0 | 135 | 0 | 90 | 200 | 135 | 401 | 96 | 90 | 105 | 0 | 170 | 54 | 110 | 0 | 44 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 82 | 55 |  | 897 | 0 | 260 | 0 | 110 | 0 | 0 | 0 | 34 | 66 | 40 | 86 | 28 | 32 | 0 | 0 | 0 | 34 | 25 | 80 | 0 | 43 | 32 | 0 | 32 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 417 | 105 | 0 | 70 | 89 | 79 | 0 | 0 | 76 | 990 | 223 | 0 | 17 | 0 | 0 | 38 |  | 8141 | 4300 | 12441 | 3866 | 897 | 2194 | 0 | 3733 | 1165 | 68 | 0 | 410 | 108 | 0 | 0 | 73.62
KWH | 0 | 0 | 0 | 4347000 | 6698018 | 2270727 | 0 | 9515010 | 7500000 |  | 0 | 5107500 | 3390284 | 1876800 | 1873872 | 758467 | 4468693 | 0 | 0 | 948480 | 862848 | 607200 | 0 | 0 | 0 | 0 | 1113840 | 724286 | 1066583 | 318492 | 600000 | 394560 | 606900 | 774800 | 514560 | 0 | 899640 | 664000 | 2300000 | 0 | 126248 | 0 | 0 | 0 | 0 |  | 518160 | 224176 | 224188 | 252480 | 24960 | 793440 | 496752 | 793920 | 0 | 0 | 0 | 0 | 7178000 | 4541000 | 769454 | 3570910 | 780624 | 1132800 | 0 | 1187958 | 0 | 52184 | 299170 | 0 | 123120 | 751500 | 47600 | 2458560 | 3059520 | 0 | 426888 | 9150 | 824000 | 966325 | 319200 | 318024 | 2706055 | 0 | 1320000 | 1788480 | 0 | 4535620 | 439000 | 274120 | 254520 | 6968000 | 459792 | 0 | 0 | 3843926 | 2704 | 0 | 3952800 | 0 | 2139552 | 112725 | 1898880 | 3603360 | 2577672 | 9387000 | 1044000 | 2095200 | 2461418 | 18959 | 1628400 | 968897 | 2141081 | 541500 | 852600 | 2298240 | 9276100 | 236160 | 90770 | 1743840 | 2554255 | 0 | 451080 | 0 | 1816320 | 1199520 |  | 22053090 | 0 | 5893920 | 0 | 2446080 | 0 | 0 | 0 | 208800 | 403584 | 546000 | 2079708 | 534800 | 900960 | 0 | 0 | 0 | 239696 | 113587 | 660024 | 0 | 157104 | 134184 | 114240 | 300505 | 479760 | 0 | 258858 | 0 | 0 | 4336300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4157491 | 0 | 8866291 | 1220160 | 0 | 1746720 | 1146384 | 1779168 | 0 | 27758 | 1869408 | 21723800 | 4929736 | 0 | 454800 | 26160 | 381600 | 1719168 |  | 170155417 | 91909844 | 262065261 | 90597201 | 22053090 | 49591629 | 2704 | 65903087 | 26060100 | 1563640 | 0 | 3168128 | 2458560 | 667122 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 7501780.16 | 3020066.91 | 0 | 9990760.5 | 8100000 |  | 0 | 5567175 | 3763215.24 | 20982624 | 24828804 | 10049687.75 | 5004936.16 | 0 | 0 | 13866777.6 | 12140271.36 | 9842712 | 0 | 0 | 0 | 0 | 14168044.8 | 9777861 | 14302878.03 | 238869 | 450000 | 0 | 0 | 0 | 8752665.6 | 0 | 242902.8 | 179280 | 4347000 | 0 | 2064154.8 | 0 | 0 | 0 | 0 |  | 6761988 | 3739255.68 | 3815679.76 | 3411004.8 | 316492.8 | 9180100.8 | 630875.04 | 2643753.6 | 0 | 0 | 0 | 0 | 7824020 | 5267560 | 992595.66 | 4356510.2 | 882105.12 | 1687872 | 0 | 1983889.86 | 0 | 901217.68 | 4023836.5 | 0 | 92340 | 1315125 | 35700 | 17652460.8 | 3334876.8 | 0 | 580567.68 | 145851 | 1128880 | 1275549 | 555408 | 550181.52 | 3111963.25 | 0 | 2560800 | 4077734.4 | 0 | 4580976.2 | 943850 | 408438.8 | 503949.6 | 6968000 | 344844 | 0 | 0 | 52469589.9 | 56675.84 | 0 | 53283744 | 0 | 29632795.2 | 1317755.25 | 19596441.6 | 49221897.6 | 34205707.44 | 8636040 | 12695040 | 30296592 | 31136937.7 | 0 | 19117416 | 10551288.33 | 22759691.03 | 7348155 | 10990014 | 27073267.2 | 8534012 | 3058272 | 1311626.5 | 22129329.6 | 29067421.9 | 0 | 5891104.8 | 0 | 27190310.4 | 15797678.4 |  | 66159270 | 0 | 6601190.4 | 0 | 25463692.8 | 0 | 0 | 0 | 3760488 | 7264512 | 7846020 | 2329272.96 | 1037512 | 9820464 | 0 | 0 | 0 | 4019701.92 | 1986636.63 | 10322775.36 | 0 | 2601642.24 | 2269051.44 | 1557091.2 | 5069519.35 | 993103.2 | 0 | 195955.506 | 0 | 0 | 22939027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822689.56 | 0 | 8777628.09 | 16398950.4 | 0 | 20663697.6 | 16565248.8 | 22595433.6 | 0 | 306725.9 | 22694613.12 | 195731438 | 5028330.72 | 0 | 3365520 | 295869.6 | 4476168 | 26354845.44 |  | 837614553.95 | 530314084.836 | 1367928638.786 | 100284115.286 | 66159270 | 59770817.85 | 56675.84 | 844067105.14 | 218670465 | 422182.8 | 0 | 52991549.82 | 17652460.8 | 7853996.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 405 | 332 |  | 0 | 225 | 140 | 72 | 70 | 30 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 25 | 35 | 0 | 25 | 11 | 25 | 32 | 16 | 0 | 38 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 11 | 22 | 22 | 0 | 0 | 0 | 0 | 310 | 165 | 26 | 150 | 32 | 51 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 25 | 20 | 92 | 109 | 0 | 20 | 1 | 44 | 41 | 5 | 5 | 110 | 0 | 61 | 78 | 0 | 191 | 19 | 7 | 10 | 280 | 16 | 0 | 0 | 72 | 0 | 0 | 140 | 0 | 70 | 20 | 77 | 77 | 81 | 402 | 8 | 90 | 105 | 1 | 0 | 38 | 86 | 17 | 9 | 90 | 400 | 104 | 5 | 17 | 108 | 0 | 17 | 0 | 77 | 37 |  | 906 | 0 | 240 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 2 | 0 | 41 | 0 | 37 | 0 | 6 | 70 | 740 | 207 | 0 | 17 | 2 | 67 | 34 |  | 9939 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 396 | 327 | 0 | 0 | 225 | 133 | 85 | 92 | 40 | 250 | 0 | 0 | 92 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 17 | 25 | 33 | 50 | 0 | 38 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 43 | 51 | 10 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 310 | 194 | 8 | 149 | 38 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 7 | 33 | 20 | 110 | 136 | 0 | 20 | 0 | 0 | 42 | 53 | 45 | 110 | 0 | 60 | 81 | 0 | 178 | 19 | 32 | 10 | 280 | 16 | 0 | 0 | 291 | 0 | 0 | 200 | 0 | 114 | 0 | 90 | 200 | 122 | 401 | 96 | 90 | 105 | 0 | 115 | 54 | 98 | 17 | 105 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 17 | 0 | 83 | 55 |  | 905 | 0 | 260 | 0 | 109 | 0 | 0 | 0 | 40 | 72 | 40 | 85 | 27 | 32 | 0 | 0 | 0 | 43 | 28 | 80 | 0 | 43 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 93 | 0 | 94 | 89 | 98 | 0 | 0 | 113 | 970 | 220 | 0 | 17 | 0 | 0 | 90 |  | 12725 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 412 | 340 | 0 | 0 | 225 | 150 | 88 | 96 | 55 | 170 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 10 | 85 | 43 | 22 | 25 | 0 | 0 | 0 | 0 | 340 | 215 | 8 | 150 | 36 | 55 | 0 | 51 | 0 | 50 | 25 | 22 | 11 | 33 | 20 | 165 | 160 | 0 | 20 | 0 | 0 | 41 | 53 | 45 | 110 | 0 | 60 | 81 | 0 | 220 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 187 | 100 | 149 | 0 | 90 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 105 | 100 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 101 | 55 |  | 930 | 0 | 285 | 0 | 115 | 220 | 0 | 0 | 40 | 72 | 40 | 88 | 27 | 110 | 0 | 0 | 0 | 43 | 35 | 90 | 0 | 50 | 32 | 8 | 40 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 170 | 0 | 410 | 105 | 160 | 94 | 105 | 100 | 0 | 0 | 113 | 1050 | 220 |  | 150 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 102 | 0 | 390 | 330 | 0 | 0 | 225 | 150 | 88 | 96 | 55 | 170 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 40 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 10 | 80 | 43 | 22 | 25 | 0 | 0 | 0 | 0 | 340 | 215 | 8 | 150 | 32 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 143 | 150 | 0 | 20 | 1.6 | 0 | 41 | 55 | 30 | 110 | 0 | 60 | 81 | 0 | 220 | 20 | 40 | 10 | 310 | 24 | 11 | 150 | 300 | 300 | 100 | 170 | 100 | 149 | 20 | 90 | 200 | 130 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 17 | 9 | 100 | 400 | 104 | 50 | 162 | 110 | 0 | 35 | 30 | 90 | 55 |  | 930 | 0 | 285 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 40 | 88 | 20 | 48 | 0 | 0 | 0 | 34 | 30 | 65 | 0 | 50 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 410 | 105 | 100 | 94 | 105 | 80 | 0 | 8 | 95 | 1050 | 220 |  | 17 | 6 | 100 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 361 | 302 | 0 | 0 | 225 | 148 | 84 | 62 | 15 | 170 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 10 | 0 | 45 | 20 | 7 | 0 | 0 | 0 | 0 | 265 | 180 | 8 | 150 | 34 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 33 | 21 | 96 | 159 | 0 | 17 | 0 | 0 | 41 | 22 | 20 | 110 | 0 | 61 | 78 | 0 | 178 | 19 | 40 | 10 | 270 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 32 | 1 | 90 | 155 | 30 | 370 | 0 | 35 | 87 | 1 | 0 | 34 | 110 | 0 | 9 | 100 | 370 | 104 | 2 | 17 | 108 | 0 | 17 | 0 | 83 | 34 | 0 | 896 | 0 | 285 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 300 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 690 | 167 | 0 | 17 | 0 | 23 | 34 | 0 |  |  |  |  | 69073919 |  | 0
69073919
| Minimum Generation |  | 9394 | 9:00
| Highest Generation |  | 12725 | 21:00
| Day Peak Generation |  | 9939 | 12:00
| Evening Peak Generation |  | 12725 | 21:00
| HVDC Max Flow |  | 909 | 3:00
| HVDC EvPeak Flow |  | 905 | 21:00
| Load factor L.F |  | 85.81%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-04
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9939 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9265 | MW
Evening Peak Generation : |  | 12725 | MW Hour : | 21:00 | Available Max Generation : |  | 15274 | MW
E.P. Demand (at gen end) : |  | 12725 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14100 | MW
Maximum Generation : |  | 12725 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1174 | MW
Total Gen. (MKWH) : |  | 262.0653 | System Load Factor : | 85.81% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -102 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-04
Actual : | 0 | Ft.(MSL) , | Rule curve : | 76.52 | Ft.( MSL )
Gas Consumed : | Total = | 1061.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160054933.136
: |  | Coal : | 218670465 | Oil : | 897115330.8 | Total : | 1275840728.936
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5020.2199 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1628.8189 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1587.4013 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1421.4286 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1296.1694 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1063.7742 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 520.9487 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 319.8048 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 782.0927 |  |  | 0 | 0%
Total | 0 |  | 13640.6584 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1,2
9) Ashuganj North
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shahjibazar 132/33 kV T-4 transformers was under shut down from 08:46 to 12:42 for C/M.
b) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 09:24 to 20:49 for C/M.
c) Maniknagar 230/132 kV T0-2 transformers was under shut down from 09:40 to 16:56 for C/M.
d) Faridpur 132/33 kV T-1 transformer with 132 kV bus was under shut down since at 08:03 for D/W.
e) Gallamari 132/33 kV T-2 transformer was under shut down from 08:14 to 17:41 for D/W.
f) Rajbari 132/33 kV T-1 transformer was under shut down from 08:56 to 16:07 for protection test.
g) Bagerhat 132/33 kV T-3 transformer was under shut down from 07:38 to 10:14 for C/M.
h) Halishahar-Juldah 132 kv Ckt tripped at 11:06 showing dist Z1,3-phase and was switched on at 11:24.
i) Sikalbaha-Madunaghat 132 kv Ckt-1 tripped at 11:06 showing O/C,E/F,dist Z1,3-phase relay and was
switched on at 11:24.
j) Kulshi-Madunaghat 132 kv Ckt-2 tripped at 11:06 showing dist L/O relay and was switched on at 11:25.
k) Barisal-Bhola 230 kV Ckt-1 was under shut down from 10:36 to 11:18 for C/M.
l) Rampur 230 kV T0-2 transformer tripped at 11:06 showing Buchholz relay and was switched on at 15:17.
m) Shahjibazar 132/33 kV T-2 & T-4 transformer tripped at 12:50 due to 33 kV PDB side jumper tear off | [5 empty] | About 50 MW power interruption occurred under
and was switched on at 19:12. | [5 empty] | Shahjibazar S/S area from 12:50 to 19:12.
n) Barisal(N)-Faridpur 230 kV Ckt-1 was under shut down from 15:00 to 15:10 for jumpering with Ckt-2.
o) Shahjibazar 132/33 kV T-2 transformer was under shut down from 17:16 to 18:02 for loop maintenance work.
p) Fenchuganj 90 MW #01 ST & GT were under shut down since at 19:10,19:19 respectively due to
control system problem.
q) Sonargaon 132/33 kV T1 & T2 transformer tripped at 23:56 from 33 kV side due to bird fall in auxiliary | [5 empty] | About 60 MW power interruption occurred under
transformer and were switched on at 00:13(04-06-2022). | [5 empty] | Sonargaon S/S area from 23:56 to 00:13.
r) Sherpur 132/33 kV T3 transformer tripped at 05:43 due to bad weather and were switched on at 06:49. | [5 empty] | About 12 MW power interruption occurred under
Sherpur S/S area from 05:43 to 06:49.
s) Dohazari 132/33 kV T-2 transformer with 33 kV bus-2 was under shut down since at 07:20(04-06-2022) | [5 empty] | About 22 MW power interruption occurred under
to red hot maintenance work. | [5 empty] | Dohazari S/S area from 07:20 to 08:18.
t) Gallamari 132/33 kV T-2 transformer was under shut down since at 07:08(04-06-2022) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6698018 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2270727
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 396 | 9515010
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 7500000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5107500 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 85 | 1876800 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 133 | 3390284 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 92 | 1873872 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 758467 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 318492 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 92 | 948480 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 4468693 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 862848 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1113840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 607200 | Low Demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 724286 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1066583
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 994560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 606900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 774800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 514560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 291 | 3843926
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 2704 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 2139552 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2095200 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 236160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1743840
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1199520
| Dhaka area Total |  |  |  | 5898 | 3484 | 67599822
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 126248
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 112725
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 793440 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1563640 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2461418
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 224176 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 224188 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 252480 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1898880 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496752
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 39 | 793920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 24960 | Under maint.
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18959
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 115 | 1628400 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 968897
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 98 | 2141081 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2298240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2554255 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1072 | 20882659
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 4541000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7178000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 780624 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 40 | 1132800 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 769454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1187958
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 122 | 2577672 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 52184
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 149 | 3570910
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3603360
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 123120 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2458560
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 751500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 299170 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 47600 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 541500 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 852600 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 451080 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 1816320 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1529 | 32735412
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 136 | 3059520 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 426888
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9150
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 3952800
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1044000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 90770
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 518160
| Mymensingh Area Total |  |  |  | 622 | 476 | 9101288
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 824000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 966325 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2706055 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 319200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 45 | 318024
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1320000
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1788480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 178 | 4535620 | DP high
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 439000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 32 | 274120 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 459792
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6968000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9387000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 254520
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9276100
| Sylhet Area Total |  |  |  | 2477 | 1727 | 39836236
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 22053090
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 109 | 2446080 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 208800 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 72 | 403584 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 5893920 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 546000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1220160 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 1146384 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 381600
| Khulna Area Total |  |  |  | 2384 | 1608 | 34299618
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 900960 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 27 | 534800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2079708 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 970 | 21723800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4929736
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 454800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1351 | 30623804
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 239696 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 113587 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 157104 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 134184 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4157491 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8866291
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 300505 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 479760
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 258858
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 114240 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 660024 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1746720 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1869408
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26160
| Rajshahi Area Total |  |  |  | 2129 | 1115 | 19124028
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4336300 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1779168 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27758
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1719168 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 363 | 7862394
| Total |  |  |  | 21584 | 12725 | 262065261
| Eastern Grid Total |  |  |  | 14393 | 8288 | 170155417
| Western Grid Total |  |  |  | 7191 | 4437 | 91909844
| National Grid Total |  |  |  | 21584 | 12725 | 262065261
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-03
(a) ENTIRE EASTERN GRID : |  | 8016.4 | MW | (b) ENTIRE WESTERN GRID : |  | 4287.8 | MW
i) Dhaka area |  | 4146 | MW | i) Khulna area |  | 1655.2 | MW
ii) Chittagong area |  | 1171.4 | MW | ii) Rajshahi area |  | 1403.6 | MW
iii) Comilla area |  | 1159 | MW | iii) Barisal area |  | 356 | MW
iv) Mymensingh area |  | 1074 | MW | iv) Rangpur area |  | 873 | MW
v) Sylhet area |  | 466 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12304.2 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 30 | 00:00 | Hasnabad | 77 | 15:00 | Palashbari | 118 | 21:00
Agargaon | 76 | 19:00 | Hathazari | 84 | 19:30 | Panchagarh | 61 | 20:00
Agrabad | 72 | 00:00 | Ishurdi | 75 | 21:00 | Patuakhali | 116 | 00:00
AKS | 8 | 00:00 | Jaldhaka | 64 | 20:00 | PHP | 5 | 03:00
AKSML | 4 | 08:00 | Jamalpur | 152 | 00:00 | Purbachal | 17 | 00:00
Amnura | 45 | 21:00 | Jashore | 124 | 21:00 | Purbasadipur | 126 | 00:00
Ashuganj | 45 | 23:00 | Jhenaidah | 125 | 20:00 | Rahim | 18 | 00:00
Bagerhat | 99 | 00:00 | Joydebpur | 167 | 22:00 | Rajbari | 70 | 21:00
Bakulia | 106 | 00:00 | Joypurhat | 66 | 21:00 | Rajendrapur | 90 | 22:00
Banani | 36 | 15:00 | Juldah | 24 | 00:00 | Rajshahi | 163 | 21:00
Bangabhaban | 6 | 13:00 | Kabirpur | 209 | 11:00 | Rajshahi | 123 | 23:00
Barapukuria | 55 | 20:00 | Kachua | 76 | 00:00 | Ramganj | 100 | 00:00
Barguna | 20 | 01:00 | Kallyanpur | 96 | 00:00 | Rampur | 13 | 00:00
Barishal | 113 | 00:00 | Kalurghat | 3 | 00:00 | Rangamati | 12 | 19:00
Barishal | 45 | 22:00 | Kamrangirchar | 67 | 00:00 | Rangpur | 144 | 00:00
Baroaulia | 79 | 07:00 | Kaptai | 4 | 18:30 | Ruppur | 4.2 | 11:00
Baroirhat | 60 | 02:00 | Kazla | 81 | 00:00 | Saidpur | 101 | 00:00
Bashundhara | 149 | 19:00 | Keranigonj | 66 | 00:00 | Satkhira | 118 | 21:00
BashundharaCement | 13 | 00:00 | Khagrachori | 28 | 20:00 | Satmasjid | 89 | 19:00
Beanibazar | 61 | 00:00 | Khulna | 96 | 13:00 | Savar | 161 | 12:00
Benapole | 64 | 20:00 | Khulshi | 156 | 20:00 | Shahjadpur | 104 | 20:00
Bhaluka | 118 | 00:00 | Kishoreganj | 140 | 21:00 | Shahjibazar | 93 | 21:00
Bhandaria | 56 | 00:00 | Kodda | 234 | 17:00 | Shahmirpur | 35.5 | 23:00
Bhangura | 36 | 20:00 | KSRM | 23.5 | 06:00 | Shariatpur | 72 | 21:00
Bheramara(GK) | 62 | 21:00 | Kulaura | 44 | 22:00 | Sherpur | 138 | 00:00
Bhulta | 234 | 00:00 | Kurigram | 60 | 00:00 | Shikalbaha | 35 | 00:00
Bog-Sherpur | 58 | 20:00 | Kushtia | 126 | 21:00 | Shitalakhya | 95 | 00:00
Bogura | 167 | 21:00 | Lalbag | 79 | 00:00 | Sholosohor | N/A | N/A
Borhanuddin | 44 | 20:00 | Lalmonirhat | 43 | 00:00 | Shyampur | 164 | 01:00
Brahmanbaria | 160 | 00:00 | Madanganj | 163 | 00:00 | Siddhirganj | 106 | 01:00
BSRM | 165 | 01:00 | Madaripur | 96 | 21:00 | Sirajganj | 101 | 22:00
Cantonment | 134 | 19:00 | Madartek | 81 | 00:00 | Sonargaon | 88 | 00:00
Chandpur | 68.5 | 00:00 | Madunaghat | 50 | 19:30 | Sreemongol | 70 | 19:00
Chandraghona | 32 | 19:00 | Magura | 60 | 19:30 | Srinagar | 44.89 | 21:00
Chapai | 78 | 22:00 | Mahasthangarh | 68 | 23:00 | SSM | 2 | 00:00
Charsaidpur | 27 | 15:00 | Manikganj | 80 | 20:00 | Sunamganj | 50 | 00:00
Chauddagram | 62 | 00:00 | Maniknagar | 52 | 19:00 | Sylhet | 125 | 00:00
Chhatak | 29 | 00:00 | Matarbari | 36 | 00:00 | Tangail | 219 | 21:00
Chowmuhani | 204 | 00:00 | Matuail | 61 | 00:00 | Thakurgaon | 95 | 23:00
Chuadanga | 108 | 22:00 | Millgate | 48 | 00:00 | TK | 26.1 | 19:30
Coxsbazar | 98 | 00:00 | Mirpur | 120 | 19:30 | Tongi | 118 | 15:00
Cumilla(N) | 148 | 00:00 | Mirsorai | N/A | N/A | Ullon | 48 | 00:00
Cumilla(S) | 154 | 00:00 | Mithapukur | 31 | 01:00 | Uttara | 88 | 19:30
Daudkandi | 142 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 15 | 23:00
Dhaka | 25 | 12:00 | Mogbazar | 96 | 19:00 | Zigatola | 42 | 20:00
Dhamrai | 98 | 21:00 | Mongla | 34 | 00:00
Dhanmondi | 123 | 12:00 | Motijheel | 28 | 18:00
Dohazari | 90 | 00:00 | Munshiganj | 106 | 00:00
Faridpur | 146 | 21:00 | Mymensingh | 228 | 00:00
Fatullah | 62 | 00:00 | Naogaon | 118 | 21:00
Fenchuganj | 42 | 00:00 | Narail | 54 | 19:30
Feni | 102 | 19:30 | Narinda | 41 | 20:00
Ghorashal | 52 | 02:00 | Narshingdi | 175 | 23:00
Goalpara | 27 | 00:00 | Natore | 128 | 21:00
Gollamari | 52 | 00:00 | Nawabganj | 55.9 | 22:00
Gopalganj | 100.2 | 21:00 | Netrakona | 119 | 00:00
GPH | 91 | 04:00 | New | 59.4 | 11:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 20:00 | 404 | 15:00 | Kaliakoir | 393 | 0.75 | 384 | 0.66667
| Bheramara | 399 | 6:00 | 388 | 16:00 | Bhulta | 389 | 0.125 | 379 | 0.625
| Ashuganj(N) | 393 | 4:00 | 383 | 15:00 | Gopalganj | 421 | 0.625 | 402 | 0.041667
| Payra | 423 | 18:30 | 414 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 7:00 | Hathazari | 238 | 19:30 | 225 | 10:00
| Ishurdi | 234 | 7:00 | 225 | 1:00 | Megnaghat | 231 | 9:00 | 226 | 17:00
| Ashuganj | 243 | 6:00 | 235 | 15:00 | Fenchuganj | 244 | 4:00 | 238 | 1:00
| Serajganj | 235 | 17:00 | 228 | 1:00 | Siddhirganj | 229 | 5:00 | 225 | 14:00
| Baghabari | 231 | 17:00 | 223 | 23:00 | Maniknagar | 228 | 5:00 | 222 | 15:00
| Barapukuria | 226 | 17:00 | 209 | 24:00 | Agargaon | 227 | 9:00 | 219 | 15:00
| Bogra | 231 | 19:00 | 216 | 24:00 | Barisal | 243 | 9:00 | 235 | 1:00
| Rajshahi | 233 | 18:30 | 220 | 19:30 | Bhola 225 MW | 246 | 8:00 | 235 | 1:00
| Khulna South | 237 | 7:00 | 221 | 22:00 | AKSML | 236 | 20:00 | 224 | 10:00
| Rampura | 228 | 3:00 | 223 | 10:00 | BSRM | 235 | 19:30 | 226 | 6:00
| Haripur | 228 | 20:00 | 222 | 12:00 | Bibiyana | 239 | 5:00 | 235 | 15:00
| Hasnabad | 226 | 19:30 | 221 | 3:00 | Bhulta | 230 | 4:00 | 224 | 15:00
| Shyampur | 226 | 3:00 | 220 | 13:00 | Ashuganj (S) | 238 | 4:00 | 232 | 15:00
| Aminbazar | 228 | 1:00 | 221 | 2:00 | Kaliakoir | 229 | 4:00 | 222 | 15:00
| Tongi | 230 | 1:00 | 221 | 15:00 | GPH | 236 | 19:30 | 225 | 10:00
| Comilla (N) | 231 | 20:00 | 226 | 15:00 | Jhenaidah | 232 | 7:00 | 219 | 19:30
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 02:00 | 131 | 14:00 | Manikganj | 134 | 00:00 | 129 | 06:00
| Agargaon | 132 | 02:00 | 126 | 15:00 | Maniknagar | 134 | 03:00 | 129 | 12:00
| Agrabad | 139 | 19:00 | 131 | 10:00 | Matarbari | 134 | 16:00 | 122 | 02:00
| AKS | 137 | 14:00 | 131 | 04:00 | Matuail | 134 | 19:00 | 132 | 00:00
| Aminbazar | 133 | 19:30 | 128 | 18:00 | Millgate | 135 | 00:00 | 129 | 14:00
| Amnura | 130 | 18:00 | 122 | 15:00 | Mirpur | 132 | 19:30 | 127 | 11:00
| Ashuganj | 140 | 08:00 | 135 | 00:00 | Mithapukur | 133 | 17:00 | 121 | 00:00
| Bagerhat | 131 | 18:30 | 122 | 19:00 | Modern | 139 | 19:30 | 133 | 09:00
| Bakulia | 139 | 01:00 | 131 | 05:00 | Mogbazar | 135 | 00:00 | 131 | 15:00
| Banani | 135 | 03:00 | 129 | 11:00 | Mongla | 135 | 08:00 | 126 | 21:00
| Bangabhaban | 134 | 08:00 | 128 | 13:00 | Motijheel | 134 | 08:00 | 128 | 13:00
| Barapukuria | 135 | 17:00 | 124 | 22:00 | Munshiganj | 138 | 19:30 | 133 | 10:00
| Barguna | 139 | 09:00 | 128 | 22:00 | Mymensingh | 130 | 17:00 | 120 | 00:00
| Barishal | 140 | 07:00 | 127 | 22:00 | Naogaon | 130 | 17:00 | 117 | 22:00
| Barishal | 142 | 18:00 | 132 | 01:00 | Narail | 132 | 06:00 | 121 | 21:00
| Baroaulia | 140 | 19:30 | 134 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 19:30 | 127 | 03:00 | Narshingdi | 131 | 11:00 | 125 | 00:00
| Bashundhara | 135 | 03:00 | 129 | 14:00 | Natore | 133 | 18:30 | 124 | 23:00
| BashundharaCement | 137 | 19:30 | 132 | 09:00 | Nawabganj | 137 | 03:00 | 135 | 05:00
| Beanibazar | 135 | 07:00 | 128 | 00:00 | Netrakona | 129 | 07:00 | 119 | 00:00
| Benapole | 133 | 05:00 | 123 | 19:30 | New | 136 | 03:00 | 130 | 09:00
| Bhaluka | 129 | 20:00 | 118 | 00:00 | Niamatpur | 129 | 18:00 | 112 | 22:00
| Bhandaria | 141 | 18:00 | 130 | 00:00 | Noapara | 136 | 05:00 | 128 | 22:00
| Bhangura | 138 | 06:00 | 131 | 21:00 | Pabna | 135 | 17:00 | 128 | 22:00
| Bheramara | 136 | 07:00 | 131 | 01:00 | Palashbari | 134 | 06:00 | 117 | 23:00
| Bheramara(GK) | 139 | 18:00 | 134 | 19:30 | Panchagarh | 138 | 06:00 | 114 | 21:00
| Bhulta | 125 | 04:00 | 124 | 00:00 | Patuakhali | 138 | 07:00 | 130 | 22:00
| Bog-Sherpur | 135 | 06:00 | 125 | 00:00 | PHP | 134 | 16:00 | 126 | 03:00
| Bogura | 136 | 17:00 | 124 | 23:00 | Purbachal | 135 | 00:00 | 128 | 15:00
| Bogura | 136 | 19:00 | 126 | 00:00 | Purbasadipur | 135 | 06:00 | 115 | 23:00
| Brahmanbaria | 136 | 10:00 | 130 | 00:00 | Rahim | 134 | 18:30 | 132 | 15:00
| Cantonment | 132 | 04:00 | 125 | 15:00 | Rajbari | 135 | 07:00 | 120 | 23:00
| Chandpur | 139 | 20:00 | 135 | 13:00 | Rajendrapur | 138 | 04:00 | 130 | 15:00
| Chandraghona | 139 | 20:00 | 132 | 10:00 | Rajshahi | 130 | 17:00 | 123 | 19:30
| Chapai | 131 | 18:30 | 123 | 15:00 | Rajshahi | 129 | 07:00 | 122 | 13:00
| Charsaidpur | 137 | 19:30 | 133 | 07:00 | Ramganj | 135 | 16:00 | 128 | 02:00
| Chauddagram | 134 | 19:00 | 128 | 02:00 | Rampur | 139 | 20:00 | 132 | 04:00
| Chhatak | 135 | 02:00 | 128 | 00:00 | Rampura | 135 | 06:00 | 128 | 06:00
| Chowmuhani | 132 | 15:00 | 123 | 01:00 | Rangamati | 138 | 19:30 | 132 | 10:00
| Chuadanga | 130 | 08:00 | 116 | 22:00 | Rangpur | 131 | 17:00 | 118 | 21:00
| Coxsbazar | 134 | 16:00 | 117 | 04:00 | Ruppur | 135 | 06:00 | 130 | 21:00
| Cumilla(N) | 136 | 19:00 | 131 | 05:00 | Saidpur | 134 | 05:00 | 121 | 22:00
| Cumilla(S) | 136 | 20:00 | 130 | 00:00 | Satkhira | 138 | 18:30 | 124 | 21:00
| Daudkandi | 133 | 08:00 | 129 | 22:00 | Satmasjid | 132 | 04:00 | 126 | 15:00
| Dhaka | 135 | 02:00 | 131 | 14:00 | Savar | 134 | 02:00 | 125 | 15:00
| Dhamrai | 134 | 04:00 | 129 | 15:00 | Shahjadpur | 140 | 07:00 | 134 | 20:00
| Dhanmondi | 136 | 15:00 | 132 | 11:00 | Shahjibazar | 138 | 11:00 | 133 | 00:00
| Dohazari | 138 | 16:00 | 130 | 04:00 | Shahmirpur | 141 | 20:00 | 132 | 09:00
| Faridpur | 137 | 18:30 | 129 | 00:00 | Shariatpur | 137 | 09:00 | 129 | 22:00
| Fatullah | 134 | 04:00 | 131 | 10:00 | Sherpur | 132 | 17:00 | 122 | 00:00
| Fenchuganj | 138 | 08:00 | 135 | 00:00 | Shikalbaha | 141 | 19:30 | 133 | 05:00
| Feni | 135 | 16:00 | 128 | 04:00 | Shikalbaha | 140 | 19:30 | 133 | 04:00
| Ghorashal | 140 | 09:00 | 136 | 00:00 | Shitalakhya | 138 | 19:30 | 132 | 09:00
| Goalpara | 138 | 06:00 | 131 | 22:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 07:00 | 130 | 01:00 | Shyampur | 135 | 21:00 | 131 | 05:00
| Gopalganj | 141 | 18:30 | 132 | 01:00 | Shyampur | 134 | 20:00 | 130 | 15:00
| Gopalganj_I | 140 | 18:30 | 133 | 01:00 | Siddhirganj | 134 | 19:30 | 131 | 14:00
| Gulshan | 135 | 04:00 | 130 | 15:00 | Sirajganj | 135 | 05:00 | 126 | 22:00
| Halishahar | 140 | 19:30 | 131 | 10:00 | Sonargaon | 135 | 08:00 | 133 | 15:00
| Haripur | 134 | 18:30 | 132 | 14:00 | Sreemongol | 140 | 07:00 | 135 | 00:00
| HaripurSBU | 135 | 19:30 | 133 | 00:00 | Srinagar | 136 | 03:00 | 131 | 15:00
| Hasnabad | 137 | 19:00 | 133 | 09:00 | SSM | 140 | 00:00 | 132 | 18:00
| Hathazari | 140 | 00:00 | 133 | 10:00 | Sunamganj | 135 | 02:00 | 126 | 00:00
| Ishurdi | 136 | 06:00 | 131 | 01:00 | Sylhet | 134 | 05:00 | 131 | 00:00
| Jaldhaka | 131 | 06:00 | 115 | 21:00 | Tangail | 135 | 07:00 | 132 | 00:00
| Jamalpur | 135 | 17:00 | 125 | 00:00 | Thakurgaon | 135 | 06:00 | 115 | 22:00
| Jashore | 134 | 06:00 | 124 | 19:30 | TK | 140 | 19:30 | 133 | 09:00
| Jhenaidah | 135 | 08:00 | 125 | 22:00 | Tongi | 136 | 21:00 | 130 | 15:00
| Jhenaidah | 136 | 07:00 | 126 | 19:30 | Ullon | 135 | 07:00 | 130 | 15:00
| Joydebpur | 142 | 00:00 | 135 | 15:00 | Uttara | 133 | 04:00 | 126 | 09:00
| Joypurhat | 129 | 17:00 | 113 | 22:00 | UttaraNew | 134 | 03:00 | 132 | 01:00
| Juldah | 141 | 19:30 | 133 | 10:00 | Zigatola | 136 | 04:00 | 131 | 13:00
| Kabirpur | 137 | 02:00 | 127 | 10:00
| Kachua | 136 | 16:00 | 132 | 03:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 134 | 03:00 | 128 | 10:00
| Kalurghat | 138 | 00:00 | 132 | 10:00
| Kamrangirchar | 136 | 03:00 | 131 | 13:00
| Kaptai | 138 | 00:00 | 132 | 18:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 42 | 8141 | 4300 | 12441 |  |  |  | QF-LDC-11
0:30 | 32 | 8125.5 | 4190.5 | 12316 | Date: | 2022-06-03
1:00 | 22 | 8110 | 4081 | 12191
1:30 | 17 | 8053 | 4057.5 | 12110.5
2:00 | 12 | 7996 | 4034 | 12030
2:30 | 16 | 7912 | 3986 | 11898 | [5 empty] | Gen. at Eve. Peak | 12725 | 12725 MW (21:00 )
3:00 | 20 | 7828 | 3938 | 11766 | [6 empty] | 21:00
3:30 | 32 | 7787 | 3883.5 | 11670.5 | [5 empty] | Gen. at Day Peak | 9939 | 9939 MW (12:00 )
4:00 | 44 | 7746 | 3829 | 11575 | [6 empty] | 12:00
4:30 | 74 | 7554.5 | 3785.5 | 11340 | [5 empty] | Highest Generation | 12725
5:00 | 104 | 7363 | 3742 | 11105 | [6 empty] | 21:00
5:30 | 277 | 6921 | 3666.5 | 10587.5
6:00 | 450 | 6479 | 3591 | 10070
6:30 | 413 | 6431.5 | 3569 | 10000.5
7:00 | 376 | 6384 | 3547 | 9931
7:30 | 367 | 6317 | 3435.5 | 9752.5
8:00 | 358 | 6250 | 3324 | 9574
8:30 | 354 | 6207.5 | 3276.5 | 9484
9:00 | 350 | 6165 | 3229 | 9394
9:30 | 364 | 6180 | 3249 | 9429
10:00 | 378 | 6195 | 3269 | 9464
10:30 | 303 | 6317.5 | 3249.5 | 9567
11:00 | 228 | 6440 | 3230 | 9670
11:30 | 216 | 6490 | 3314.5 | 9804.5
12:00 | 204 | 6540 | 3399 | 9939
12:30 | 192 | 6593 | 3435 | 10028
13:00 | 180 | 6646 | 3471 | 10117
13:30 | 212 | 6547.5 | 3468.5 | 10016
14:00 | 244 | 6449 | 3466 | 9915
14:30 | 253 | 6560 | 3497.5 | 10057.5
15:00 | 262 | 6671 | 3529 | 10200
15:30 | 176 | 6700.5 | 3404.5 | 10105
16:00 | 90 | 6730 | 3280 | 10010
16:30 | 170 | 6611 | 3246 | 9857
17:00 | 250 | 6492 | 3212 | 9704
17:30 | 266 | 6315.5 | 3157 | 9472.5
18:00 | 282 | 6139 | 3102 | 9241
18:30 | 242 | 6593 | 3468 | 10061
19:00 | 202 | 7047 | 3834 | 10881
19:30 | 26 | 8085 | 4275 | 12360
20:00 | 102 | 8230 | 4323 | 12553 |  |  |  | Executive Engineer
20:30 | 82 | 8259 | 4380 | 12639 |  |  |  | Network Operation Division
21:00 | 62 | 8288 | 4437 | 12725
21:30 | 73 | 8264.5 | 4435.5 | 12700
22:00 | 84 | 8241 | 4434 | 12675 |  |  |  |  | Page 6 of 7
22:30 | 64 | 8221 | 4420 | 12641
23:00 | 44 | 8201 | 4406 | 12607
23:30 | 43 | 8171 | 4353 | 12524
24:00 | 42 | 8141 | 4300 | 12441
12725 MW (21:00 )
9939 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-03 |  | Energy |  | 262065261
[13 empty] | 2022-06-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3866 | 897 | 2194 | 0 | 3733 | 1165 | 68 | 0 | 410 | 108 | 0 | 0
0:30 | 3741.5 | 902.5 | 2188.5 | 0 | 3864 | 1164.5 | 68 | 0 | 273 | 114 | 0 | 0 | Date: | 2022-06-03
1:00 | 3617 | 908 | 2183 | 0 | 3995 | 1164 | 68 | 0 | 136 | 120 | 0 | 0
1:30 | 3640.5 | 908 | 2184.5 | 0 | 3913.5 | 1154.5 | 68 | 0 | 122.5 | 119 | 0 | 0 | [8 empty] | Total Energy | 262.0653 | Total Energy Gen 262.065 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 262.065 MKWHr
2:00 | 3664 | 908 | 2186 | 0 | 3832 | 1145 | 68 | 0 | 109 | 118 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3711.5 | 908.5 | 2182 | 0 | 3710 | 1120 | 67.5 | 0 | 81.5 | 117 | 0 | 0 | [8 empty] | Energy Requirement | 262.0653
3:00 | 3759 | 909 | 2178 | 0 | 3588 | 1095 | 67 | 0 | 54 | 116 | 0 | 0
3:30 | 3796 | 909 | 2172 | 0 | 3492.5 | 1080 | 67 | 0 | 39 | 115 | 0 | 0 | [6 empty] | Shortage
4:00 | 3833 | 909 | 2166 | 0 | 3397 | 1065 | 67 | 0 | 24 | 114 | 0 | 0
4:30 | 3847.5 | 907.5 | 2166 | 0 | 3162.5 | 1055.5 | 67 | 0 | 24 | 110 | 0 | 0
5:00 | 3862 | 906 | 2166 | 0 | 2928 | 1046 | 67 | 0 | 24 | 106 | 0 | 0
5:30 | 3822.5 | 905.5 | 2138 | 0 | 2496.5 | 1025.5 | 67.5 | 0 | 24 | 105 | 3 | 0
6:00 | 3783 | 905 | 2110 | 0 | 2065 | 1005 | 68 | 0 | 24 | 104 | 6 | 0
6:30 | 3768.5 | 905 | 2099.5 | 0 | 2035 | 980 | 68 | 0 | 32 | 99 | 13.5 | 0 |  |  |  |  | Coal
7:00 | 3754 | 905 | 2089 | 0 | 2005 | 955 | 68 | 0 | 40 | 94 | 21 | 0
7:30 | 3718.5 | 905 | 2021.5 | 0 | 1936 | 935 | 68 | 0 | 40 | 93 | 35.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3683 | 905 | 1954 | 0 | 1867 | 915 | 68 | 0 | 40 | 92 | 50 | 0
8:30 | 3686 | 905.5 | 1943.5 | 0 | 1762.5 | 915 | 68 | 0 | 32 | 91 | 80.5 | 0
9:00 | 3689 | 906 | 1933 | 0 | 1658 | 915 | 68 | 0 | 24 | 90 | 111 | 0
9:30 | 3716 | 905.5 | 1958 | 0 | 1665 | 920 | 53 | 0 | 20 | 88 | 103.5 | 0
10:00 | 3743 | 905 | 1983 | 0 | 1672 | 925 | 38 | 0 | 16 | 86 | 96 | 0
10:30 | 3775 | 905.5 | 2003 | 0 | 1732 | 925 | 53 | 0 | 8 | 85 | 80.5 | 0
11:00 | 3807 | 906 | 2023 | 0 | 1792 | 925 | 68 | 0 | 0 | 84 | 65 | 0
11:30 | 3786.5 | 906 | 2054.5 | 0 | 1898 | 920 | 68 | 0 | 0 | 88 | 83.5 | 0
12:00 | 3766 | 906 | 2086 | 0 | 2004 | 915 | 68 | 0 | 0 | 92 | 102 | 0
12:30 | 3762.5 | 905.5 | 2057 | 0 | 2129 | 925 | 68 | 0 | 0 | 97 | 84 | 0
13:00 | 3759 | 905 | 2028 | 0 | 2254 | 935 | 68 | 0 | 0 | 102 | 66 | 0
13:30 | 3759 | 905 | 2028 | 0 | 2254 | 935 | 68 | 0 | 0 | 102 | 66 | 0
14:00 | 3759 | 905 | 2028 | 0 | 2254 | 935 | 68 | 0 | 0 | 102 | 66 | 0
14:30 | 3758 | 905 | 2049 | 0 | 2271.5 | 940 | 68 | 0 | 0 | 102 | 65 | 0
15:00 | 3757 | 905 | 2070 | 0 | 2289 | 945 | 68 | 0 | 0 | 102 | 64 | 0
15:30 | 3760 | 905 | 1918 | 0 | 2377 | 920 | 67.5 | 0 | 0 | 107 | 50.5 | 0
16:00 | 3763 | 905 | 1766 | 0 | 2465 | 895 | 67 | 0 | 0 | 112 | 37 | 0
16:30 | 3659 | 905.5 | 1790 | 0 | 2353.5 | 875 | 66 | 0 | 24 | 103 | 29 | 0
17:00 | 3659 | 906 | 1814 | 0 | 2242 | 855 | 65 | 0 | 48 | 94 | 21 | 0
17:30 | 3659.5 | 905.5 | 1821 | 0 | 2019 | 840 | 65 | 0 | 60.5 | 89 | 13 | 0
18:00 | 3660 | 905 | 1828 | 0 | 1796 | 825 | 65 | 0 | 73 | 84 | 5 | 0
18:30 | 3717 | 905 | 1925.5 | 0 | 2259 | 860 | 66 | 0 | 230 | 96 | 2.5 | 0
19:00 | 3774 | 905 | 2023 | 0 | 2722 | 895 | 67 | 0 | 387 | 108 | 0 | 0
19:30 | 3847 | 905 | 2158 | 0 | 3754 | 1065 | 67 | 0 | 456 | 108 | 0 | 0
20:00 | 3931 | 906 | 2213 | 0 | 3771 | 1065 | 68 | 0 | 491 | 108 | 0 | 0
20:30 | 3923 | 905.5 | 2213.5 | 0 | 3824 | 1105 | 68 | 0 | 491 | 109 | 0 | 0
21:00 | 3915 | 905 | 2214 | 0 | 3877 | 1145 | 68 | 0 | 491 | 110 | 0 | 0
21:30 | 3922 | 905.5 | 2196.5 | 0 | 3854.5 | 1155 | 68 | 0 | 486.5 | 112 | 0 | 0
22:00 | 3929 | 906 | 2179 | 0 | 3832 | 1165 | 68 | 0 | 482 | 114 | 0 | 0
22:30 | 3937 | 906 | 2189.5 | 0 | 3806.5 | 1165 | 68 | 0 | 455 | 114 | 0 | 0
23:00 | 3945 | 906 | 2200 | 0 | 3781 | 1165 | 68 | 0 | 428 | 114 | 0 | 0
23:30 | 3905.5 | 901.5 | 2197 | 0 | 3757 | 1165 | 68 | 0 | 419 | 111 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.2° C
24:00 | 3866 | 897 | 2194 | 0 | 3733 | 1165 | 68 | 0 | 410 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 262.065 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 262.065 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 38 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 37 |  | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 899640
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 664000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 4 | 9 | 15 | 25 | 25 | 25 | 25 | 126248
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 2 | 3 | 11 | 16 | 11 | 17 | 20 | 16 | 7 | 6 |  | 0 | 0 | [8 empty] | 112725
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 17 |  | 224188
12 | Hathazari 100 MW peaking PP | [19 empty] | 4 | 33 | 43 | 43 | 43 | 43 | 43 | 224176
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 34 |  | 73 | 105 | 105 | 105 | 105 | 105 | 105 | 2461418
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 35 | 0 | [5 empty] | 52184
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 250 | 250 | 250 | 250 | 170 | 4468693
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 293 | 293 | 296 | 195 | 30 | 30 | 15 | 15 | 18 | 60 | 72 | 75 | 75 | 75 | 110 | 30 | 30 |  | 95 | 245 | 273 | 291 | 296 | 293 | 291 | 3843926
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 26 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 769454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6698018
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 33 | 30 | 30 | 33 | 33 | 38 |  | 34 | 40 | 37 | 38 | 38 | 38 | 38 | 780624
33 | Ashuganj 225 MW CCPP | 202 | 181 | 181 | 180 | 180 | 180 | 180 | 181 | 181 | 182 | 180 | 165 | 178 | 189 | 192 | 189 | 193 | 191 |  | 194 | 195 | 192 | 194 | 200 | 203 | 202 | 4541000
34 | Ashuganj 450 MW CCPP(South) | 99 | 165 | 220 | 325 | 356 | 356 | 356 | 330 | 312 | 312 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7178000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 56 | 54 | 54 | 55 | 55 | 56 | 52 | 49 | 48 | 51 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1132800
36 | Chandpur 150 MW CCPP | 150 | 151 | 150 | 151 | 150 | 151 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 148 | 150 | 150 | 150 |  | 148 | 149 | 149 | 149 | 150 | 150 | 150 | 3570910
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 399 | 399 | 398 | 398 | 398 | 377 | 366 | 366 | 367 | 369 | 398 | 405 | 400 | 391 | 389 | 396 | 395 | 396 |  | 397 | 395 | 395 | 396 | 396 | 397 | 397 | 9515010
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5107500
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 332 | 332 | 332 | 332 | 331 | 282 | 282 | 281 | 332 | 332 | 328 | 282 | 322 | 272 | 272 | 273 |  | 295 | 342 | 341 | 327 | 302 | 301 | 331 | 7500000
42 | RPCL 210MW CCPP | 139 | 137 | 139 | 139 | 140 | 139 | 139 | 137 | 130 | 120 | 120 | 109 | 109 | 109 | 109 | 124 | 136 | 131 |  | 134 | 134 | 136 | 136 | 135 | 151 | 151 | 3059520
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 4 | 6 | 15 | 13 | 1 | 5 | 8 | 7 | 10 | 9 | 6 | 2 | [8 empty] | 90770
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 |  | 43 | 0 | [5 empty] | 824000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 42 | 42 | 42 | 41 | 41 | 41 | 966325
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 61 | 61 | 62 | 40 | 40 | 40 | 60 | 61 | 61 | 61 | 60 | 40 | 40 | 38 |  | 60 | 60 | 60 | 60 | 60 | 61 | 62 | 1320000
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 81 | 78 | 10 | 75 | 75 | 10 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1788480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 184 | 191 | 191 | 192 | 191 | 191 | 192 | 192 |  | 192 | 192 | 192 | 178 | 179 | 179 | 179 | 4535620
51 | Sylhet 20 MW GTPP | 19 | 19 | 18 | 17 | 19 | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 439000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 22 | 32 | 38 | 39 | 40 | 274120
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 254520
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 42 | 53 | 53 | 53 | 53 | 22 | 319200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 16 | 24 | 24 | 16 | 20 |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 459792
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 295 | 280 | 270 | 275 | 265 | 275 | 265 | 280 | 295 | 290 | 280 | 290 | 260 | 300 | 270 | 260 | 270 |  | 300 | 260 | 270 | 280 | 290 | 300 | 300 | 6968000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 360 | 361 | 360 | 360 | 397 | 400 | 400 | 391 | 360 | 400 | 390 | 350 | 350 |  | 380 | 400 | 400 | 400 | 400 | 400 | 400 | 9276100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 40 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1066583
59 | Tangail Palli Power Gen 22 MW | 23 | 22 | 24 | 24 | 24 | 24 | 24 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 23 | 23 | 23 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 518160
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496752
61 | Narshingdi 22 MW PP (Doreen) |  | 0 | 22 | 22 | 22 | 0 |  |  | 22 | 22 | 22 | 0 |  |  | 0 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 318492
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 426888
63 | Impoprt (Tripura) | 120 | 118 | 116 | 114 | 106 | 104 | 94 | 92 | 90 | 86 | 84 | 92 | 102 | 100 | 102 | 112 | 94 | 84 |  | 108 | 108 | 108 | 110 | 114 | 114 | 108 | 2458560
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 40 | 40 | 40 | 40 | 30 | 30 | 20 | 20 | 20 | 22 | 36 | 30 | 19 | 31 | 27 | 30 |  | 39 | 39 | 39 | 39 | 37 | 40 | 42 | 793920
65 | Feni 22MW PP (Doreen) | [26 empty] | 0
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 |  |  | 7 | 7 | 7 | 7 | 7 |  |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 123120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 17 | 26 | 33 | 33 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 751500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 14 | 14 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 47600
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 24 | 25 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 11 | 11 | 11 | 11 | 11 | 12 | 12 |  | 12 | 19 | 19 | 17 | 20 | 20 | 20 | 394560
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 606900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 32 | 32 | 32 | 32 | 32 | 33 | 32 | 32 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 774800
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 95 | 95 | 95 | 94 | 98 | 90 | 95 | 99 |  | 100 | 98 | 98 | 98 | 98 | 99 | 99 | 2270727
| Feni Lanka Power | 114 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 541500
| Chowmuhani 113 MW | 13 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 37 | 76 | 46 |  | 78 | 106 | 105 | 105 | 105 | 105 | 44 | 852600
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 32 | 162 | 135 | 162 | 108 | 108 | 162 | 1743840
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 96 | 54 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 92 | 82 | 92 | 76 | 51 | 73 | 948480
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 32 | 16 | 16 | 16 | 16 | 16 |  |  |  | 40 | 8 |  | 8 | 24 | 50 | 50 | 50 | 50 | 50 | 514560
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 16 | 16 | 0 | [5 empty] | 48 | 32 |  | 32 | 64 | 64 | 64 | 64 | 64 | 64 | 607200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 299170
| Gazipur 100 MW PP | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 95 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2095200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 3 | 5 | 1 | 0 | 0 | 0 | 1 | 1 | [9 empty] | 18959
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 25 | 38 | 54 | 54 | 54 | 54 | 17 | 17 |  | 30 | 54 | 54 | 54 | 54 | 54 | 54 | 968897
| Karnaphuli Power Ltd. | 109 | 109 | 110 | 110 | 110 | 96 | 93 | 65 | 51 | 51 | 65 | 86 | 87 | 87 | 88 | 88 | 51 | 17 |  | 54 | 88 | 89 | 98 | 110 | 110 | 110 | 2141081
82 | Madanganj 102 PP(Summit) | 92 | 92 | 92 | 92 | 92 | 92 | 50 | 48 | 48 | 48 | 63 | 70 | 79 | 78 | 78 | 78 | 83 | 92 |  | 92 | 92 | 92 | 92 | 70 | 71 | 80 | 1873872
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 148 | 140 | 138 | 138 | 138 | 140 | 127 | 140 | 140 | 135 | 135 | 140 | 140 | 140 | 140 | 140 | 145 | 140 |  | 143 | 145 | 147 | 133 | 137 | 140 | 125 | 3390284
87 | Meghnaghat 100 MW(IEL) | 81 | 80 | 80 | 80 | 72 | 72 | 75 | 79 | 71 | 72 | 72 | 72 | 73 | 79 | 79 | 73 | 71 | 76 |  | 75 | 81 | 80 | 85 | 89 | 89 | 89 | 1876800
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 100 | 93 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 73 | 17 |  | 36 | 104 | 104 | 104 | 104 | 104 | 104 | 236160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252480
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 25 | 42 | 45 | 50 | 50 | 20 | 318024
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1187958
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 40 | 16 | 0 | [9 empty] | 5 | 24 | 24 | 7 |  | 64 | 84 | 85 | 94 | 94 | 94 | 94 | 862848
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 11 | 37 | 37 | 31 | 34 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 793440
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 5 | 8 | [5 empty] | 24960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 30 | 40 | 40 | 40 | 15 | 15 | 15 | 15 | 15 | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 758467
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 17 | 17 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 724286
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2706055
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 9150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1113840
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 2704
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 186 | 186 | 186 | 200 | 200 | 100 | 100 | 100 | 100 | 100 | 123 | 140 | 151 | 160 | 160 | 200 | 200 | 120 |  | 150 | 200 | 200 | 200 | 200 | 191 | 188 | 3952800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 142 | 147 | 132 | 132 | 133 | 0 | 6 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 30 |  | 42 | 115 | 110 | 114 | 128 | 131 | 135 | 2139552
115 | Juldah 100 MW PP Unit-3 (Acorn) | 88 | 88 | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 30 | 30 |  | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 1898880
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 100 | 100 | 68 | 68 | 68 | 68 | 77 | 120 | 120 | 142 | 164 | 85 | 85 |  | 115 | 200 | 189 | 200 | 200 | 200 | 200 | 3603360
117 | Ashuganj 150MW PP (Midland) | 132 | 127 | 135 | 132 | 138 | 50 | 50 | 50 | 20 | 20 | 30 | 81 | 110 | 118 | 118 | 125 | 132 | 133 |  | 133 | 128 | 123 | 122 | 122 | 128 | 135 | 2577672
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 400 | 400 | 400 | 399 | 376 | 352 | 352 | 401 | 402 | 402 | 402 | 351 | 400 | 400 | 363 | 364 |  | 384 | 400 | 400 | 401 | 401 | 401 | 401 | 9387000
| Jamalpur 115 MW PP (United) | 105 | 105 | 105 | 70 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 91 | 91 | 96 | 96 | 96 | 96 | 1044000
| Anwara 300 MW PP (United) | 300 | 260 | 120 | 45 | 0 | [14 empty] | 135 | 150 | 150 | 115 | 115 | 115 | 170 | 1628400
| Juldah unit-2 (Acorn) | 100 | 92 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 94 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2298240
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 95 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 92 |  | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 2554255
| Bhairob 54.5 MW | 35 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 451080
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 100 | 100 | 82 | 88 | 97 | 100 | 84 | 75 | 67 | 77 | 77 | 77 | 77 | 17 | 26 | 46 | 59 | 63 |  | 81 | 83 | 83 | 83 | 83 | 83 | 82 | 1816320
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 54 | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 54 | 55 | 54 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1199520
120 | Eastern Zone Total | 8110 | 7996 | 7828 | 7746 | 7363 | 6479 | 6384 | 6250 | 6165 | 6195 | 6440 | 6540 | 6646 | 6449 | 6671 | 6730 | 6492 | 6139 |  | 7047 | 8085 | 8230 | 8288 | 8241 | 8201 | 8141 | 170155417
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 100 | 110 | 95 | 110 | 110 | 94 | 94 | 93 | 93 | 92 | 92 | 94 | 104 | 103 | 105 | 103 | 107 | 108 |  | 115 | 109 | 109 | 109 | 109 | 110 | 110 | 2446080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 5 |  | 45 | 40 | 40 | 40 | 40 | 26 | 34 | 208800
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 35 | 35 | 35 | 0 |  |  |  | 2 | 19 | 35 | 35 | 17 |  |  |  | 19 | 90 | 93 | 93 | 105 | 105 | 105 | 1220160
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 11 | 28 | 72 | 64 | 37 | 67 | 32 | 29 | 41 | 21 | 12 | 3 | [8 empty] | 381600
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 454800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 221 | 220 | 221 | 221 | 221 | 221 | 187 | 173 | 176 | 175 | 207 | 217 | 213 | 203 | 186 | 186 | 186 |  | 210 | 210 | 210 | 220 | 220 | 221 | 223 | 4929736
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 900960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 84 | 87 | 86 | 86 | 87 | 87 | 85 | 87 | 87 | 87 | 87 | 87 | 85 | 83 | 87 | 87 | 87 | 87 |  | 83 | 87 | 87 | 85 | 87 | 85 | 86 | 2079708
140 | Bhola 33 MW PP (Venture) | 30 | 30 | 29 | 28 | 23 | 24 | 16 | 16 | 17 | 17 | 17 | 17 | 19 | 20 | 20 | 18 | 17 | 17 |  | 23 | 25 | 26 | 27 | 28 | 28 | 28 | 534800
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 0 |  |  |  | 8 | 8 | 24 | 24 | 24 | 24 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 546000
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 25 |  | 72 | 72 | 72 | 72 | 66 | 66 | 66 | 403584
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 89 | 89 | 50 | 50 | 50 | 50 | 32 | 15 | 0 | [5 empty] | 15 | 15 | 15 |  | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 1146384
146 | Bheramara HVDC | 908 | 908 | 909 | 909 | 906 | 905 | 905 | 905 | 906 | 905 | 906 | 906 | 905 | 905 | 905 | 905 | 906 | 905 |  | 905 | 905 | 906 | 905 | 906 | 906 | 897 | 22053090
147 | Bheramara 410 MW CCPP | 220 | 220 | 235 | 236 | 240 | 240 | 240 | 240 | 245 | 245 | 245 | 240 | 230 | 230 | 225 | 220 | 230 | 240 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5893920
148 | Payra 1320 MW | 990 | 970 | 920 | 890 | 870 | 830 | 780 | 740 | 740 | 750 | 750 | 740 | 760 | 770 | 770 | 720 | 680 | 650 |  | 720 | 890 | 890 | 970 | 990 | 990 | 990 | 21723800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 174 | 175 | 175 | 175 | 176 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4336300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 0 | [18 empty] | 40 | 42 | 43 | 43 | 43 | 43 | 34 | 239696
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 4 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 26160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 141 | 150 | 152 | 158 | 164 | 164 | 167 | 170 | 171 | 173 | 170 | 166 | 166 | 162 | 130 | 130 |  | 130 | 185 | 193 | 190 | 194 | 191 | 189 | 4157491
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 414 | 414 | 414 | 414 | 364 | 365 | 309 | 300 | 352 | 350 | 414 | 414 | 350 | 414 | 270 | 250 | 250 |  | 350 | 419 | 419 | 414 | 380 | 382 | 417 | 8866291
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 4 | 12 | 26 | 28 | 25 | 25 | 25 | 113587
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 18 | 18 | 18 | 18 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 479760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 258858
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 0 | [20 empty] | 8 | 43 | 43 | 43 | 43 | 157104
167 | Katakhali 50 MW Peaking PP | 0 | [18 empty] | 6 | 24 | 32 | 32 | 32 | 32 | 32 | 134184
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 0 | [15 empty] | 35 | 38 | 40 | 38 | 38 | 32 | 32 | 300505
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [8 empty] | 8 | 8 | 8 | 8 | 8 | 0 |  | 114240
170 | Chapainawabganj 100 MW Peaking PP | 90 | 63 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [7 empty] | 7 |  | 63 | 80 | 80 | 80 | 80 | 80 | 80 | 660024
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 35 | 35 | 35 | 41 | 68 | 70 | 70 | 70 | 70 | 50 |  | 73 | 94 | 94 | 94 | 94 | 94 | 70 | 1746720
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 35 | 35 | 35 | 70 | 76 | 76 | 76 | 76 | 113 | 50 |  | 113 | 113 | 113 | 113 | 113 | 113 | 76 | 1869408
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 79 | 81 | 81 | 81 | 81 | 81 | 81 | 50 | 34 | 38 | 37 | 37 | 68 | 78 | 77 | 76 | 76 | 54 |  | 86 | 97 | 99 | 98 | 98 | 98 | 79 | 1779168
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 0 |  |  | 6 | 7 | 7 | 5 | 4 | 2 | 0 | [8 empty] | 27758
178 | Energypac Power Venture Thakurgaon Ltd. | 109 | 109 | 109 | 109 | 109 | 72 | 72 | 72 | 34 | 34 | 34 | 34 | 34 | 52 | 52 | 52 | 52 | 52 |  | 90 | 90 | 90 | 90 | 90 | 90 | 38 | 1719168
178