## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-04-01 |  | 2022-03-01 |  | 2021-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14782 | 2022-04-16 | 13662 | 2022-03-31 | 13792 | 44313 | 14782 | 2022-04-16
|  |  | 21:00 |  | 19:30 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 4262 | 2022-04-20 | 6823 | 2022-03-05 | 4853 | 2021-04-17 | - | -
|  |  | 6:00 |  | 6:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14782 | 2022-04-16 | 13662 | 2022-03-31 | 13792 | 2021-04-27 | 14782 | 2022-04-16
|  |  | 21:00 |  | 19:30 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12895 | 2022-04-26 | 12116 | 2022-03-27 | 11773 | 2021-04-28 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14782 | 2022-04-16 | 13662 | 2022-03-31 | 14097 | 2021-04-27 | 14782 | 2022-04-16
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 13536.3333 |  | 12057.9032 |  | 12676.7 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 11233.4 |  | 10564 |  | 10379.6667 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 935 | 2022-04-10 | 938 | 2022-03-29 | 933 | 2021-04-29 18:00 | 956 | 27/3/2019
|  |  | 21:30 |  | 10:30 |  | 18:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 2022-04-03 | 182 | 2022-03-23 | 187 | 2021-04-18 | 194 | 12/06/19
|  |  | 2:00 |  | 18:30 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 350 | 2022-04-07 | - | - | 275 | 2021-04-27 | 1459 | 04/05/2010
|  |  | 22:00 |  | - |  | 20:00 |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14008 | 2022-04-07 | - | - | 13792 | 2021-04-27 | 13792 | 2021-04-27
|  | - | 22:00 | - | - |  | 20:00 |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 1 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1929.4341 |  | 1551.2856 |  | 1830.3371 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 88.2498 |  | 80.4189 |  | 184.6566
22 | Net Generation of BPDB (MKWH) | 1841.1843 |  | 1470.8667 |  | 1645.6805
23 | Net Generation of IPP (MKWH) | 5255.3957 |  | 4916.0698 |  | 4706.4414
24 | Net Generation of REB (MKWH) | 131.5194 |  | 144.2163 |  | 133.246
24 | Net Generation of Rental Power Plant (MKWH) | 614.893 |  | 498.1914 |  | 587.4025
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7842.9924 |  | 7029.3442 |  | 7072.7704 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4240.1479 |  | 3806.7453 |  | 4613.3508 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 633.9729 |  | 475.2564 |  | 295.1848 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 2365.7466 |  | 2203.7804 |  | 1657.9757 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 45.2279 |  | 43.3314 |  | 41.547 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 36.5217 |  | 40.5844 |  | 21.9287 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 609.6252 |  | 540.0652 |  | 627.4399 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 754.5062 |  | 644.0891 |  | 658.1569 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 87.447 |  | 84.4682 |  | 77.1406 |  | 87.45 | April'22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14782 | 2022-04-16 | 21:00
Generation Period
| Dhaka | MW | 4928.95
| Chattogram | MW | 1396.3
| Cumilla | MW | 1392
| Mymensingh | MW | 1150
| Sylhet | MW | 514
a) | Total supply in East zone | MW | 9381.25
| Khulna | MW | 1843
| Barisal | MW | 419
| Rajshahi | MW | 1635.2
| Rangpur | MW | 908
b) | Total supply in West zone | MW | 4805.2
c) | Total supply in both zone ( a+b) | MW | 14186.45
Ref: | 27.21.0000.603.16.087.20.505 | Date: 18/05/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1080 | 2022-04-01 | 18:00
| b) Ishurdi end | MW | 434 | 2022-04-10 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1500 | 2022-04-10 | 9:00
| b) Ishurdi end | MW | 210 | 2022-04-21 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 8.16
| b) Ishurdi end | MKWH | 101.3
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2022-04-21 | 20:00
| b)Serajganj end | MW | 1260 | 2022-04-22 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 520 | 2022-04-10 | 9:00
| b)Sirajganj end | MW | 288 | 2022-04-21 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 12.306
| b)Sirajganj end | MKWH | 10.387
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 99.876
| b)Sirajganj end | MKWH | 12.546
30 | Transmission loss of EWI /NO-2 | % | 3.24
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
2nd East-West Interconnector Loss:
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062
| Difference (-) : | 3516000
| Loss : | 1.432%

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 33 kV Bus-B | 2022-04-01 09:45 | 2022-04-01 10:55 | 1:10 | T | Due to red-hot maint | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-04-02 18:55 | 2022-04-02 19:29 | 0:34 | T | Due to 33 kV feeder fault | 100 | 56.6667 | Power interruption
Kishoreganj | 230/33 kV transformers T-1 & T2 | 2022-04-10 20:18 | 2022-04-10 20:29 | 0:11 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-11 09:54 | 2022-04-11 11:17 | 1:23 | T | Due to red-hot maint | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-04-12 21:36 | 2022-04-12 22:30 | 0:54 | T | Due to red-hot maint by PBS | 26 | 23.4 | Power interruption
Aminbazar | 230/132 kV transformer T-02 | 2022-04-14 21:26 | 2022-04-14 22:28 | 1:02 | E/O | Due to heavy flashing at132 bushing of all transformer | 0 | 0 | No interruption
| 230/132 kV transformer T-03 | 2022-04-14 21:26 | 2022-04-14 22:34 | 1:08 | E/O |  | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-1 | 2022-04-20 01:42 | 2022-04-20 02:05 | 0:23 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformers T-2 | 2022-04-20 01:42 | 2022-04-20 02:49 | 1:07 | T |  | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformers T-1 & T3 | 2022-04-21 09:41 | 2022-04-21 10:07 | 0:26 | T | Due to 33 kV feeder fault | 200 | 86.6667 | Power interruption
Savar | 132/33 kV transformer T-3 | 2022-04-23 10:57 | 2022-04-23 12:40 | 1:43 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 | 2022-04-24 06:18 | 2022-04-24 09:52 | 3:34 | T | Due to red-hot maint | 30 | 107 | Power interruption
|  |  | Total : | 13:35 |  | Unserved Energy: |  | 273.7333
Dhaka (South) Grid Circle :
Nawabganj | 132/33 kV transformer T-2 | 2022-04-01 08:33 | 2022-04-01 11:03 | 2:30 | T | Due to red-hot maint.of 33 kV Bus-2 | 9 | 22.5 | Power interruption
| 132/33 kV transformers T-1 | 2022-04-01 10:21 | 2022-04-01 18:22 | 2:30 | T | Due to red-hot maint | 0 | 0 | No interruption
Gulshan | 132/33 kV transformers T-1 | 2022-04-03 15:50 | 2022-04-03 16:43 | 0:53 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2022-04-11 06:22 | 2022-04-11 07:07 | 0:53 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T-2 | 2022-04-20 11:22 | 2022-04-20 13:48 | 2:26 | T | Tripped showing Oil surge relay | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T-1 | 2022-04-21 20:50 | 2022-04-21 20:50 | 0:00 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-3 & 33 kV Bus | 2022-04-23 11:15 | 2022-04-23 15:50 | 0:00 | T | Due to red-hot maint | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-2 | 2022-04-28 12:42 | 2022-04-28 14:55 | 4:35 | T | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 13:47 |  | Unserved Energy: |  | 22.5
Chattogram Grid Circle :
Madunaghat | 132/33 kV transformer T1 | 2022-04-05 06:45 | 2022-04-05 06:45 | 0:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-04-11 15:13 | 2022-04-11 15:30 | 0:17 | T | Tripped showing O/C relay | 55 | 15.5833 | Power interruption
| 132/33 kV transformer T3 | 2022-04-13 20:15 | 2022-04-13 20:26 | 0:11 | T | Tripped showing O/C relay | 62 | 11.3667 | Power interruption
Halishahar | 132 kV Bus | 2022-04-16 05:53 | 2022-04-16 09:03 | 0:11 | T | Due to red-hot maint at 33 kV side | 50 | 9.1667 | Power interruption
Dohazari | 132/33 kV transformer T-2 | 2022-04-18 18:32 | 2022-04-18 18:50 | 3:10 | T | Due to 33 kV feeder fault | 80 | 253.3333 | Power interruption
| 132/33 kV transformer T1 | 2022-04-18 18:32 | 2022-04-18 22:54 | 4:22 | T | Tripped showing Diff. relay | 30 | 131 | Power interruption
Baroierhat | 132/33 kV transformer T1 | 2022-04-22 10:40 | 2022-04-22 12:05 | 4:22 | T | Due to red-hot maint at 33 kV side | 12 | 52.4 | Power interruption
Halishahar | 132/33 kV transformer T-3 | 2022-04-22 10:58 | 2022-04-22 11:18 | 1:25 | T |  | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer MT-1 & MT3 | 2022-04-24 09:33 | 2022-04-24 10:00 | 0:20 | T | Due to 132 Bus fault | 0 | 0 | No interruption
| 132/33 kV transformer MT-4 | 2022-04-24 09:33 | 2022-04-24 10:05 | 0:27 | T |  | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T4 | 2022-04-25 12:35 | 2022-04-25 14:02 | 1:27 | T | Tripped showing O/C relay | 15 | 21.75 | Power interruption
|  |  | Total : | 16:12 |  | Unserved Energy: |  | 494.6
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla (N) | 132/33 kV transformers T3 & T4 | 2022-04-04 10:10 | 2022-04-04 10:29 | 0:19 | T | Tripped showing O/C relay | 52 | 16.4667 | Power interruption
Sylhet | 132/33 kV transformer T2 | 2022-04-10 08:34 | 2022-04-10 09:42 | 1:08 | E/O | Due to CB burst of 33 kV feeder | 14 | 15.8667 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-04-14 06:12 | 2022-04-14 07:32 | 1:20 | T | Due to red-hot maint at 33 kV side | 34 | 45.3333 | Power interruption
| 132/33 kV transformer T2 | 2022-04-14 06:12 | 2022-04-14 08:53 | 2:41 | T | Due to red-hot maint at 33 kV side | 29 | 77.8167 | Power interruption
Sylhet | 132/33 kV transformer T2 | 2022-04-17 02:55 | 2022-04-17 03:21 | 0:26 | T | Tripped showing E/F relay | 47 | 39.1667 | Power interruption 02:55 to 3:45
| 132/33 kV transformer T2 | 2022-04-17 03:31 | 2022-04-17 03:45 | 0:14 | T
Ashuganj | 132/33 kV transformer OAT12 | 2022-04-21 03:08 | 2022-04-21 03:08 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformers T1 & T2 | 2022-04-22 19:32 | 2022-04-22 19:55 | 0:23 | T | Due to 33 kV feeder fault | 20 | 7.6667 | Power interruption
Sreemongal | 132/33 kV transformer T2 | 2022-04-26 02:54 | 2022-04-26 02:58 | 0:04 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Ashuganj | 132/33 kV transformer T3 | 2022-04-26 07:38 | 2022-04-26 08:06 | 0:28 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 with 33 kV Bus | 2022-04-26 08:34 | 2022-04-26 13:37 | 5:03 | T | Due to red-hot maint at 33 kV side | 20 | 101 | Power interruption
Ramganj | 132/33 kV transformer T1 | 2022-04-28 08:11 | 2022-04-28 09:51 | 1:40 | T | Due to red-hot maint at 33 kV side | 30 | 50 | Power interruption
Kachua | 132 kV Bus-2 | 2022-04-28 16:45 | 2022-04-28 17:31 | 0:46 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T3 | 2022-04-30 14:51 | 2022-04-30 15:14 | 0:23 | E/O | Due to CB gas filling | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T1 | 2022-04-30 20:25 | 2022-04-30 20:30 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 15:00
Khulna Grid Circle :
Madaripur | 132/33 kV transformer T2 | 2022-04-13 10:08 | 2022-04-13 11:15 | 1:07 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Chuadanga | 132/33 kV transformers T1 & T2 | 2022-04-14 19:46 | 2022-04-14 20:10 | 0:24 | T | Due to high voltage | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T1 | 2022-04-15 15:39 | 2022-04-15 16:24 | 0:45 | T | Due to red-hot maint at 33 kV side | 26 | 19.5 | Power interruption
Narail | 132/33 kV transformer T2 | 2022-04-16 07:14 | 2022-04-16 08:57 | 1:43 | T |  | 12 | 20.6 | Power interruption
Barisal(N) | 132/33 kV transformers T4 | 2022-04-19 11:46 | 2022-04-19 13:04 | 1:18 | T | Due to 33 kV feeder fault | 60 | 78 | Power interruption
| 132/33 kV transformer T3 | 2022-04-19 11:46 | 2022-04-19 15:06 | 3:20 | T
Magura | 132/33 kV transformers T1 & T2 | 2022-04-22 18:17 | 2022-04-22 18:50 | 0:33 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Gopalganj | 400/132 kV transformer T01 | 2022-04-25 10:40 | 2022-04-25 11:32 | 0:52 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T1 | 2022-04-25 16:25 | 2022-04-25 17:38 | 1:13 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-04-26 14:26 | 2022-04-26 17:30 | 3:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T1 | 2022-04-28 07:04 | 2022-04-28 07:43 | 0:39 | E/O | Due to red-hot maint by PBS | 24 | 15.6 | Power interruption
Bhandaria | 132/33 kV transformersT1 | 2022-04-29 09:54 | 2022-04-29 10:27 | 0:33 | T | Tripped showing Directional & E/F relay | 40 | 22 | Power interruption
| 132/33 kV transformersT2 | 2022-04-29 09:54 | 2022-04-29 10:28 | 0:34 | T
| 132/33 kV transformerT1 | 2022-04-29 15:05 | 2022-04-29 16:22 | 1:17 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 17:22 |  | Unserved Energy: |  | 155.7
HVDC Grid Circle :
Baghabari | 132 kV Bus | 2022-04-02 15:40 | 2022-04-02 16:17 | 0:37 | E/O | Due to bursting of CT | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformerT1 | 2022-04-22 19:06 | 2022-04-22 19:38 | 0:32 | T | Tripped showing Gen.trip & self protection relay | 25 | 13.3333 | Power interruption
| 132/33 kV transformerT1 | 2022-04-22 19:38 | 2022-04-23 01:20 | 5:42 | T |  | 0 | 0 | No interruption
Bottail | 132/33 kV transformerT1 | 2022-04-22 20:58 | 2022-04-22 21:07 | 0:09 | T | Due to 33 kV feeder fault | 34 | 5.1 | Power interruption
HVDC | 400 kV filter | 2022-04-23 14:04 | 2022-04-23 14:56 | 0:52 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 400 kV 10CF26 | 2022-04-24 00:16 | 2022-04-24 00:16 | 0:00 | T |  | 0 | 0 | No interruption
Jhenaidah(O) | 132/33 kV transformerT2 | 2022-04-27 08:56 | 2022-04-27 12:27 | 3:31 | E/O | Due to red-hot maint | 19 | 66.8167 | Power interruption
|  |  | Total : | 11:23 |  |  |  | 85.25
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Panchugarth | 132/33 kV transformer T3 | 2022-04-02 08:13 | 2022-04-02 11:57 | 3:44 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformerT2 | 2022-04-02 15:34 | 2022-04-02 15:43 | 0:09 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Mohasthangarh | 132/33 kV transformers T1 & T2 | 2022-04-03 08:26 | 2022-04-03 09:25 | 0:59 | T |  | 12 | 11.8 | Power interruption
Rajshahi | 132/33 kV transformer T3 | 2022-04-03 12:45 | 2022-04-03 13:33 | 0:48 | E/O | Due to red-hot maint | 63 | 50.4 | Power interruption
Naogaon | 132/33 kV transformer T3 with 33 kV Bus | 2022-04-04 20:35 | 2022-04-04 21:27 | 0:52 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 | 2022-04-07 23:15 | 2022-04-08 00:26 | 1:11 | E/O | Due to red-hot maint at 33 kV Bus | 20 | 23.6667 | Power interruption
Bogura | 132/33 kV transformers T3 & T4 | 2022-04-10 10:12 | 2022-04-10 12:33 | 2:21 | E/O | Due to bursting of 33 kV breaker | 60 | 141 | Power interruption
| 132/33 kV transformer T2 | 2022-04-15 11:31 | 2022-04-15 11:57 | 0:26 | T | Tripped showing O/C relay at 33 kV side | 50 | 21.6667 | Power interruption
Barapukuria | 132/11 kV transformer T4 | 2022-04-21 07:24 | 2022-04-21 08:47 | 1:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2022-04-21 10:05 | 2022-04-21 11:05 | 1:00 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Bogura | 132/33 kV transformers T1 & T2 | 2022-04-22 19:47 | 2022-04-22 20:15 | 0:28 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2022-04-25 09:15 | 2022-04-25 10:03 | 0:48 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T4 | 2022-04-25 08:51 | 2022-04-25 09:54 | 1:03 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T2 | 2022-04-27 15:25 | 2022-04-27 16:28 | 1:03 | E/O | Due to red-hot maint at | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-04-27 19:24 | 2022-04-27 20:41 | 1:17 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Panchugarth | 132/33 kV transformer T1 | 2022-04-30 01:04 | 2022-04-30 02:01 | 0:57 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T3 | 2022-04-30 03:10 | 2022-04-30 03:22 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 18:41 |  |  |  | 248.5333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 106:00 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 | 2022-04-03 12:36 | 2022-04-03 13:26 | 0:00 | T | Due to red-hot maint | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-04-06 06:09 | 2022-04-06 06:09 | 0:50 | T | Due to red-hot maint | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-1 | 2022-04-08 01:32 | 2022-04-08 01:49 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-04-11 02:02 | 2022-04-11 03:09 | 1:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-04-11 08:48 | 2022-04-11 12:55 | 4:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-Sutiakhali Solar 132 kV Ckt | 2022-04-12 02:35 | 2022-04-12 02:35 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-04-18 08:00 | 2022-04-18 08:07 | 0:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-04-22 11:18 | 2022-04-22 12:07 | 0:49 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-1 | 2022-04-22 14:40 | 2022-04-22 15:17 | 0:37 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 7:54 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Maniknagar | Maniknagar-Motijheel 132 kV Ckt-1 | 2022-04-01 09:14 | 2022-04-01 12:11 | 0:00 | T | Due to red-hot maint | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuil 132 kV Ckt | 2022-04-02 08:36 | 2022-04-02 08:47 | 0:11 | T | Tripped showing Dist.& E/F. relay | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2022-04-06 14:13 | 2022-04-06 15:18 | 0:11 | T | Due to red-hot maint | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-1 & 2 | 2022-04-07 12:48 | 2022-04-07 13:12 | 0:24 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV Ckt-1 | 2022-04-09 15:18 | 2022-04-09 15:41 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ghorashal-Bhulta 230 kV Ckt-2 | 2022-04-10 20:39 | 2022-04-10 20:39 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2022-04-11 16:11 | 2022-04-11 16:33 | 0:22 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Shyampur-Shyampur (O) 132 kV Ckt-1 | 2022-04-11 16:13 | 2022-04-11 17:08 | 0:55 | T |  |  | 0
| Shyampur-Shyampur (O) 132 kV Ckt-2 | 2022-04-11 16:13 | 2022-04-11 16:50 | 0:37 | T |  | 150 | 92.5 | Power interruption 16:13 to 16:50
Narsinghdi | Narsinghdi-Bhulta 132 kV Ckt | 2022-04-18 11:10 | 2022-04-18 12:34 | 0:37 | T | Due to red-hot maint | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt-1 | 2022-04-18 13:18 | 2022-04-18 13:46 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-04-19 05:48 | 2022-04-19 05:56 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-04-21 00:13 | 2022-04-21 00:42 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt | 2022-04-22 15:45 | 2022-04-22 15:52 | 0:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Fatullah 132 kV Ckt-1 | 2022-04-22 15:53 | 2022-04-22 16:13 | 0:20 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Shyampur(N)-Shyampur(O) 132 kV Ckt-1 | 2022-04-22 15:53 | 2022-04-22 16:05 | 0:12 | T | Tripped showing Dist.& E/F relay | 0 | 0 | No interruption
| Shyampur(N)-Shyampur(O) 132 kV Ckt-2 | 2022-04-22 15:53 | 2022-04-22 16:15 | 0:22 | T |  | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-04-22 16:28 | 2022-04-22 16:56 | 0:28 | T | Tripped showing Dist.& E/F relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-04-22 15:39 | 2022-04-22 15:44 | 0:05 | T | Tripped showing O/C & E/F. relay | 58 | 4.8333 | Power interruption
Rampura | Rampura-Ullon 132 kV U/G cable -1 | 2022-04-23 13:25 | 2022-04-23 14:08 | 0:05 | T | Due to red-hot maint | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj peaking 132 kV Ckt-1 & 2 | 2022-04-25 19:32 | 2022-04-25 20:06 | 0:34 | T | Tripped showing master trip relay | 0 | 0 | No interruption
| Siddhirganj S/S-siddhirganj Dutch Bangla 132 kV Ckt-1 & 2 | 2022-04-25 19:32 | 2022-04-26 06:37 | 11:05 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-04-26 20:11 | 2022-04-26 20:20 | 0:09 | T | Tripped showing Dist. relay. | 210 | 31.5 | Power interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-1 | 2022-04-27 18:17 | 2022-04-27 18:53 | 0:36 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2022-04-29 16:20 | 2022-04-29 17:20 | 1:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV Ckt | 2022-04-29 23:41 | 2022-04-30 00:15 | 0:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV Ckt-2 | 2022-04-29 23:44 | 2022-04-30 00:27 | 0:43 | T | Tripped showing gen.trip & inter trip relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-1 | 2022-04-30 18:31 | 2022-04-30 19:10 | 0:39 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 21:44 |  | Unserved Energy: |  | 128.8333
Page: 2/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-03 05:03 | 2022-04-03 05:33 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-1 | 2022-04-03 12:00 | 2022-04-03 12:41 | 0:41 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-06 04:32 | 2022-04-06 04:32 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-07 01:13 | 2022-04-07 01:13 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-04-07 04:29 | 2022-04-07 07:41 | 3:12 | T |  | 123 | 393.6 | Power interruption
| Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-07 00:05 | 2022-04-07 04:56 | 4:51 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-2 | 2022-04-13 20:05 | 2022-04-13 20:05 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV Ckt | 2022-04-14 11:26 | 2022-04-14 11:48 | 0:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Khulshi | Khulshi-Sholoshahar 132 kV Ckt | 2022-04-15 19:20 | 2022-04-15 20:05 | 0:45 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2022-04-16 04:53 | 2022-04-16 07:53 | 3:00 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
BSRM | BSRM-Cumilla(N) 230 kV Ckt-1 | 2022-04-20 06:52 | 2022-04-20 08:56 | 2:04 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2022-04-20 09:26 | 2022-04-20 10:02 | 0:36 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bakulia | Bakulia- Modern steel 132 kV Ckt | 2022-04-20 09:30 | 2022-04-20 10:14 | 0:44 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kalurghat 132 kV Ckt-2 | 2022-04-20 09:26 | 2022-04-20 11:55 | 2:29 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-1 | 2022-04-20 09:26 | 2022-04-20 11:02 | 1:36 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV Ckt-3 | 2022-04-20 10:44 | 2022-04-20 17:18 | 6:34 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-1 | 2022-04-20 15:30 | 2022-04-20 15:39 | 0:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-04-22 18:27 | 2022-04-22 18:37 | 0:10 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Baraulia | Baraulia-KSRM 132 kV Ckt | 2022-04-24 12:11 | 2022-04-24 12:33 | 0:22 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 28:05 |  | Unserved Energy: |  | 393.6
Cumilla Grid Circle :
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2022-03-04 06:27 | 2022-03-04 06:58 | 0:31 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-03-04 11:33 | 2022-03-04 12:12 | 0:39 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-03-04 17:18 | 2022-03-04 17:51 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV Ckt | 2022-03-06 09:12 | 2022-03-06 09:35 | 0:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-03-07 12:18 | 2022-03-07 13:06 | 0:48 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV Ckt-2 | 2022-03-10 11:55 | 2022-03-10 12:24 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-03-10 21:20 | 2022-03-10 21:54 | 0:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-11 03:32 | 2022-03-11 03:32 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-1 & 2 | 2022-03-11 03:36 | 2022-03-11 04:45 | 1:09 | T |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-(Beanibazar)-Sylhet 132 kV Ckt | 2022-03-12 23:09 | 2022-03-12 23:26 | 0:17 | T | Tripped showing Dist. relay | 45 | 12.75 | Power interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-2 | 2022-03-14 03:40 | 2022-03-14 03:48 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV Ckt | 2022-03-19 00:52 | 2022-03-19 01:34 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 230 kV Ckt-1 | 2022-03-20 02:52 | 2022-03-20 03:06 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV Ckt-2 | 2022-03-20 02:27 | 2022-03-20 03:08 | 0:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 | 2022-03-20 09:24 | 2022-03-20 09:52 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Kachua 132 kV Ckt | 2022-03-20 09:00 | 2022-03-20 09:16 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Shahjibazar 86 P/P 132 kV Ckt | 2022-03-20 15:06 | 2022-03-20 15:38 | 0:32 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Shahjibazar-Cumilla(N) 230 kV Ckt-2 | 2022-03-20 16:00 | 2022-03-20 16:23 | 0:23 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajagnj 230 kV Ckt-2 | 2022-03-21 10:28 | 2022-03-21 15:28 | 5:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 230 kV Ckt-1 | 2022-03-22 02:11 | 2022-03-22 02:21 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV Ckt-2 | 2022-03-22 03:08 | 2022-03-22 03:08 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2022-03-24 00:14 | 2022-03-24 00:23 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-2 | 2022-03-24 09:54 | 2022-03-24 10:12 | 0:18 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-1 | 2022-03-24 10:14 | 2022-03-24 12:23 | 2:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-2 | 2022-03-24 10:14 | 2022-03-24 18:21 | 8:07 | T |  | 0 | 0 | No interruption
Choddagram | Choddagram-Feni 132 kV Ckt-2 | 2022-03-24 14:47 | 2022-03-24 15:10 | 0:23 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Bibiyana-Fenchuganj 132 kV Ckt | 2022-03-25 01:21 | 2022-03-25 01:42 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-25 05:36 | 2022-03-25 06:29 | 0:53 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2022-03-26 01:52 | 2022-03-26 02:04 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV Ckt-2 | 2022-03-27 00:29 | 2022-03-27 01:17 | 0:48 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV Ckt-1 | 2022-03-27 01:07 | 2022-03-27 01:22 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV Ckt-1 | 2022-03-27 02:05 | 2022-03-27 09:20 | 7:15 | T |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt-1 | 2022-03-27 02:00 | 2022-03-27 02:10 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Chattak | Chattak-Sunamganj 132 kV Ckt | 2022-03-29 21:55 | 2022-03-30 00:33 | 2:38 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 37:35 |  | Unserved Energy: |  | 12.75
Khulna Grid Circle :
Gopalganj(N) | Gopalganj(N)-Rampal 400 kV Ckt-1 | 2022-04-02 14:20 | 2022-04-02 17:28 | 3:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Payra P/P | Payra-Gopalganj (N) 400 kV Ckt-1 | 2022-04-02 22:25 | 2022-04-02 22:25 | 0:00 | E/O | Due to flashing from CVT | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 | 2022-04-07 17:45 | 2022-04-07 21:45 | 4:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-1 | 2022-04-08 03:58 | 2022-04-08 03:58 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-2 | 2022-04-12 02:42 | 2022-04-12 02:42 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-2 | 2022-04-17 23:57 | 2022-04-18 00:40 | 0:43 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-1 | 2022-04-18 00:07 | 2022-04-18 00:07 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-2 | 2022-04-18 03:12 | 2022-04-18 03:12 | 0:00 | T |  | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Bhandaria 132 kV Ckt | 2022-04-22 19:55 | 2022-04-22 20:01 | 0:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj 132 kV Ckt-2 | 2022-04-22 20:36 | 2022-04-22 21:42 | 1:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Gopalganj(O)-Gallamari 132 kV Ckt-1 & 2 | 2022-04-23 10:49 | 2022-04-23 12:19 | 1:30 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| Gopalganj-Rampal 400 kV Ckt | 2022-04-27 10:45 | 2022-04-27 13:15 | 2:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Payra S/S | Payra S/S-Payra P/P 400 kV Ckt-3 | 2022-04-27 10:45 | 2022-04-27 14:28 | 3:43 | T | Due to Over flux | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal 400 kV Ckt | 2022-04-29 20:42 | 2022-04-30 00:48 | 4:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Gopalganj(N)-Payra coal P/S 400 kV Ckt-1 | 2022-04-29 20:42 | 2022-04-30 00:30 | 3:48 | T | Tripped showing Dist.& E/F. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2022-04-30 15:59 | 2022-04-30 16:22 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 25:03 |  | Unserved Energy: |  | 0
Page: 4/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Baghabari | Baghabari-Shahjadpur 132 kV Ckt-2 | 2022-04-02 15:40 | 2022-04-02 22:28 | 6:48 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-1 | 2022-04-14 21:08 | 2022-04-15 11:15 | 14:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 | 2022-04-14 21:08 | 2022-04-15 11:16 | 14:08 | T |  | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj 132 kV Ckt | 2022-04-20 05:20 | 2022-04-20 09:43 | 4:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV Ckt | 2022-04-23 11:35 | 2022-04-23 17:58 | 6:23 | T | Tripped showing Dist.& E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 45:49 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura(N) | Bogura(N)-Naogaon 132 kV Ckt-1 | 2022-04-02 09:10 | 2022-04-02 09:35 | 0:25 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt | 2022-04-02 15:40 | 2022-04-02 16:27 | 0:47 | T | Due to Bus fault | 27 | 21.15 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2022-04-10 02:29 | 2022-04-10 02:43 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV Ckt-1 | 2022-04-10 03:12 | 2022-04-10 04:22 | 1:10 |  |  | 0 | 0 | No interruption
| Bogura-Barapukuria 230 kV Ckt-2 | 2022-04-10 03:12 | 2022-04-10 04:30 | 1:18 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2022-04-10 04:12 | 2022-04-10 04:46 | 0:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Barapukuria P/S 230 kV Ckt-1 & 2 | 2022-04-10 03:12 | 2022-04-10 04:22 | 1:10 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 & 2 | 2022-04-10 06:21 | 2022-04-10 06:42 | 0:21 | T | Tripped showing Dist. relay | 100 | 35 | Power interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-2 | 2022-04-10 06:51 | 2022-04-10 07:20 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Rangpur 132 kV Ckt-1 & 2 | 2022-04-10 08:20 | 2022-04-10 08:50 | 0:30 | T | Tripped showing Dist. relay | 90 | 45 | Power interruption
Rangpur | Rangpur-Rangpur Confidence 132 kV Ckt-1 & 2 | 2022-04-10 08:20 | 2022-04-10 08:53 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV Ckt-1 & 2 | 2022-04-10 08:20 | 2022-04-10 08:56 | 0:36 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-1 | 2022-04-14 18:25 | 2022-04-14 18:30 | 0:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV Ckt-2 | 2022-04-21 02:35 | 2022-04-21 10:15 | 7:40 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 Ckt-1 | 2022-04-21 04:04 | 2022-04-21 10:15 | 6:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rasjshahi 132 kV Ckt-1 | 2022-04-22 15:04 | 2022-04-22 15:23 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mohastanghor | Mohastanghor-Polashbari 132 kV Ckt-2 | 2022-04-24 12:40 | 2022-04-24 13:11 | 0:31 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Rangpur 132 kV Ckt-1 | 2022-04-26 21:17 | 2022-04-26 21:44 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2022-04-29 21:38 | 2022-04-29 22:42 | 1:04 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-1 | 2022-04-29 21:45 | 2022-04-29 23:10 | 1:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 25:49 |  | Unserved Energy: |  | 101.15
Others :
Ullon | Ullon-Dhanmondi 132 kV Ckt-1 | 2022-04-06 09:51 | 2022-04-06 10:48 | 0:57 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV Ckt-2 | 2022-04-18 13:18 | 2022-04-18 13:44 | 0:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:23 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 193:22 | Hours
T = Tripping | [6 empty] | Executive Engineer
E/O = Emergency Outage | [6 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV transformer T-1 with 33 kV Bus | 2022-04-01 06:30 | 2022-04-01 06:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2022-04-01 07:54 | 2022-04-01 08:51 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 with 33 kV Bus | 2022-04-02 08:11 | 2022-04-02 11:53 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-02 | 2022-04-03 11:34 | 2022-04-03 12:31 | 0:57 | S/O | Due to PBS work | 0 | 0 | No interruption
Aminbazar | 132 kV main Bus | 2022-04-05 09:16 | 2022-04-05 13:08 | 3:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132 kV Bus-1 | 2022-04-08 11:59 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-04-09 08:22 | 2022-04-09 17:20 | 8:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 33 kV capacitor bank-1 | 2022-04-09 09:05 | 2022-04-09 17:50 | 8:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132 kV Bus-2 | 2022-04-09 08:34 | 2022-04-09 08:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-10 06:05 | 2022-04-10 11:36 | 5:31 | S/O | Due to C/M work | 10 | 55.1667 | Power interruption
Mymensingh | 132/33 kV transformer T-1 | 2022-04-10 06:45 | 2022-04-10 09:15 | 2:30 | S/O | Due to C/M work | 25 | 62.5 | Power interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-04-10 09:10 | 2022-04-10 11:36 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-04-10 09:23 | 2022-04-10 17:01 | 7:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer GT-1 | 2022-04-11 09:22 | 2022-04-11 17:25 | 8:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-04-11 12:11 | 2022-04-11 13:11 | 1:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-3 | 2022-04-12 07:07 | 2022-04-12 07:07 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Dhamrai | 132 kV Bus-2 | 2022-04-12 08:34 | 2022-04-12 12:18 | 3:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-04-12 09:23 | 2022-04-12 17:25 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-1 | 2022-04-13 06:26 | 2022-04-13 08:41 | 2:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT-1 | 2022-04-13 09:25 | 2022-04-13 17:22 | 7:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 33 kV capacitor Bank-1 | 2022-04-14 08:58 | 2022-04-14 18:12 | 9:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT-1 | 2022-04-14 09:30 | 2022-04-14 17:02 | 7:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-2 | 2022-04-15 07:14 | 2022-04-15 08:55 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-04-15 09:03 | 2022-04-15 10:20 | 1:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-04-15 12:54 | 2022-04-15 13:12 | 0:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirur | 132/33 kV transformer T-2 | 2022-04-16 09:37 | 2022-04-16 11:59 | 2:22 | S/O | Due to C/M work | 20 | 47.3333 | Power interruption
| 132/33 kV transformer T-1 | 2022-04-16 12:03 | 2022-04-16 13:27 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV transformer T-2 | 2022-04-17 05:49 | 2022-04-17 08:32 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-1 |  | 2022-04-17 16:40 |  |  | After.maint work | 0 | 0 | No interruption
Kabirur | 132/33 kV transformer T-2 | 2022-04-21 06:09 | 2022-04-21 06:11 | 0:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-04-21 06:32 | 2022-04-21 06:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformers T-1 | 2022-04-21 11:10 | 2022-04-21 12:17 | 1:07 | S/O | Due to maint.work | 200 | 223.3333 | Power interruption
| 132/33 kV transformers T-3 | 2022-04-21 11:10 | 2022-04-21 13:56 | 2:46 | S/O
Aminbazar | 230/132 kV transformer T-1 | 2022-04-24 10:08 | 2022-04-24 18:03 | 7:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-04-24 10:09 | 2022-04-24 18:01 | 7:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-04-24 12:21 | 2022-04-24 13:07 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus-2 | 2022-04-24 13:22 | 2022-04-24 19:08 | 5:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 with 33 kV Bus | 2022-04-26 06:16 | 2022-04-26 08:25 | 2:09 | S/O | Due to C/M work | 12 | 25.8 | Power interruption
Joydevpur | 132/33 kV transformers T-2 & T3 with 33 kV Bus | 2022-04-26 05:28 | 2022-04-26 06:50 | 1:22 | S/O | Due to C/M work | 20 | 27.3333 | Power interruption
Page:2/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 230/132 kV transformer T-1 | 2022-04-26 09:51 | 2022-04-26 14:25 | 4:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2022-04-26 11:51 | 2022-04-26 12:51 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sholoshahar | 132/33 kV transformer T-2 | 2022-04-26 13:20 | 2022-04-26 15:34 | 2:14 | S/O | Due to D/W work | 55 | 122.8333 | Power interruption
| 132/33 kV transformer T-1 | 2022-04-26 16:02 | 2022-04-26 17:49 | 1:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-04-26 07:07 | 2022-04-26 09:13 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-27 09:15 | 2022-04-27 10:41 | 1:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-04-27 09:59 | 2022-04-27 10:46 | 0:47 | S/O | Due to C/M work by PBS | 90 | 70.5 | Power interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-04-27 09:59 | 2022-04-27 09:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2022-04-27 09:42 | 2022-04-27 11:16 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-04-28 09:32 | 2022-04-28 11:16 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2022-04-30 07:14 | 2022-04-30 07:14 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-30 07:32 | 2022-04-30 11:58 | 4:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 | 2022-04-30 09:54 | 2022-04-30 13:00 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-04-30 11:59 | 2022-04-30 16:28 | 4:29 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 161:46 |  | Unserved Energy: |  | 634.8
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV transformer T-1 with 33 kv Bus | 2022-04-01 09:06 | 2022-04-01 16:22 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-5 | 2022-04-01 16:27 | 2022-04-01 20:31 | 4:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2022-04-03 09:40 | 2022-04-03 16:39 | 6:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-04-03 09:31 | 2022-04-03 15:46 | 6:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer ATR-2 | 2022-04-03 10:02 | 2022-04-03 15:40 | 5:38 | S/O | Due to DFDR connection | 0 | 0 | No interruption
| 230/132 kV transformer ATR-3 | 2022-04-05 10:00 | 2022-04-05 15:39 | 5:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-04-05 10:27 | 2022-04-05 12:05 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230 kV Bus coupler | 2022-04-06 10:03 | 2022-04-06 14:56 | 4:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-10 09:09 | 2022-04-10 12:07 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2022-04-11 07:20 | 2022-04-11 08:18 | 0:58 | S/O |  | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-04-20 11:15 | 2022-04-20 13:53 | 2:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 33 kV Bus | 2022-04-21 11:58 | 2022-04-21 13:12 | 1:14 | S/O | Due to loop changing | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-04-23 10:17 | 2022-04-23 11:07 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-04-24 13:40 | 2022-04-24 15:09 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-04-26 07:26 | 2022-04-26 09:59 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2022-04-26 07:59 | 2022-04-26 12:50 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-04-26 10:17 | 2022-04-26 12:07 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-04-29 09:20 | 2022-04-29 11:04 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2022-04-30 09:30 | 2022-04-30 10:50 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-5 | 2022-04-30 10:15 | 2022-04-30 12:41 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer T02 | 2022-04-30 13:28 | 2022-04-30 13:36 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 67:21 |  | Unserved Energy: |  | 0
Page:3/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Shahmirpur | 132/33 kV transformer T1 | 2022-04-01 08:07 | 2022-04-01 20:39 | 12:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-04-01 08:53 | 2022-04-01 13:27 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
GPH ispat | 132/33 kV transformer T1 | 2022-04-01 11:56 | 2022-04-01 11:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T2 | 2022-04-01 16:56 | 2022-04-01 17:33 | 0:37 | S/O | Due to D/W work | 0 | 0 | No interruption
BSRM | 230/132 kV transformer T02 | 2022-04-02 09:30 | 2022-04-02 09:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV transformer T2 | 2022-04-02 14:50 | 2022-04-02 17:16 | 2:26 | S/O | Due to C/M work | 20 | 48.6667 | Power interruption
Cox'sbazar | 132/33 kV transformers T1,& T2 | 2022-04-02 22:40 | 2022-04-03 00:12 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-04-02 22:40 | 2022-04-03 00:21 | 1:41 | S/O | Due to C/M work | 100 | 168.3333 | Power interruption
Shahmirpur | 132/33 kV transformer T1 | 2022-04-03 11:38 | 2022-04-03 14:35 | 2:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsharai | 230/132 kV transformer T02 | 2022-04-05 10:01 | 2022-04-05 13:48 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T2 | 2022-04-06 11:35 | 2022-04-06 13:20 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2022-04-07 09:42 | 2022-04-07 12:49 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T1 |  | 2022-04-09 17:18 |  |  | Due to C/M work | 0 | 0 | No interruption
GK project | 132/33 kV transformer T2 | 2022-04-11 11:57 | 2022-04-11 12:48 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T1 | 2022-04-13 06:15 | 2022-04-13 08:25 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
GPH ispat | 132/33 kV transformer T1 |  | 2022-04-13 13:20 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T1 | 2022-04-18 11:31 | 2022-04-18 14:35 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T2 | 2022-04-19 12:48 | 2022-04-19 13:43 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kalurghat | 132/33 kV transformers T1 |  | 2022-04-19 15:43 |  |  | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformers T2 |  | 2022-04-19 16:06 |  |  |  | 0 | 0 | No interruption
Halishahar | 132/33 kV transformersT1, T2 & T3 | 2022-04-20 12:20 | 2022-04-20 12:32 | 0:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-04-22 10:58 | 2022-04-22 11:18 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T-3 | 2022-04-24 09:25 | 2022-04-24 10:29 | 1:04 | S/O | Due to C/M work | 20 | 21.3333 | No interruption
GPH ispat | 230/132 kV transformer T01 | 2022-04-25 11:14 | 2022-04-25 11:56 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 44:16 |  | Unserved Energy : |  | 238.3333
Cumilla Grid Circle :
Ashuganj | 132 kV bus-2 | 2022-04-06 07:05 | 2022-04-06 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132 kV full Bus | 2022-04-09 09:21 | 2022-04-09 11:33 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T1 | 2022-04-10 17:10 | 2022-04-10 18:01 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2022-04-13 06:15 | 2022-04-13 09:37 | 3:22 | S/O | Due to C/M work | 60 | 202 | Power interruption
Ashuganj(N) | 400 kV Bus-1 & 2 | 2022-04-15 10:33 | 2022-04-15 10:33 | 0:00 | S/O | Due to protection test | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2022-04-16 10:15 | 2022-04-16 11:01 | 0:46 | S/O | Due to C/M work | 34 | 26.0667 | Power interruption
Kachua | 132/33 kV transformer T1 | 2022-04-19 10:08 | 2022-04-19 13:37 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132/33 kV transformer OAT12 | 2022-04-21 03:08 | 2022-04-21 03:08 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T2 | 2022-04-23 06:07 | 2022-04-23 06:07 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-04-24 11:36 | 2022-04-24 12:32 | 0:56 | S/O | Due to C/M work | 35 | 32.6667 | Power interruption
Sylhet | 132/33 kV transformer T2 | 2022-04-26 08:24 | 2022-04-26 08:45 | 0:21 | S/O | Due to 33 kV feeder fault | 21 | 7.35 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-04-26 15:53 | 2022-04-26 16:08 | 0:15 | S/O | Due to replacement work by PDB | 30 | 7.5 | Power interruption
Chowmuhani | 132/33 kV transformer T1 | 2022-04-27 00:15 | 2022-04-27 01:10 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T2 | 2022-04-27 10:25 | 2022-04-27 10:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2022-04-27 19:56 | 2022-04-27 20:22 | 0:26 | S/O | Due to maint.work by PBD | 40 | 17.3333 | Power interruption
Daudkandi | 132/33 kV transformer T1 | 2022-04-29 07:16 | 2022-04-29 09:21 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2022-04-30 08:09 | 2022-04-30 10:18 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 17:47 |  | Unserved Energy : |  | 292.9167
Page:4/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barishal | 230/132 kV transformer ATR-2 | 2022-04-02 11:20 | 2022-04-02 14:52 | 3:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T3 | 2022-04-02 14:11 | 2022-04-02 17:43 | 3:32 | S/O | Due to C/M work | 20 | 70.6667 | Power interruption
Bhandaria | 132/33 kV transformer T1 | 2022-04-07 11:22 | 2022-04-07 12:02 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-04-09 10:55 | 2022-04-09 12:23 | 1:28 | S/O | Due to C/M work | 10 | 14.6667 | No interruption
Barisal(N) | 132/33 kV transformer T4 | 2022-04-13 08:04 | 2022-04-13 13:40 | 5:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | 400/230 kV transformer ICT-1 | 2022-04-15 12:26 | 2022-04-15 12:38 | 0:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T1 | 2022-04-17 04:50 | 2022-04-17 04:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | 400 kV Bus | 2022-04-18 12:45 | 2022-04-18 19:30 | 6:45 | S/O | Due to poject work | 0 | 0 | No interruption
Noapara | 132 kV Bus-A | 2022-04-19 08:32 | 2022-04-19 10:17 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 | 2022-04-20 10:55 | 2022-04-20 12:30 | 1:35 | S/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-2 | 2022-04-21 08:10 | 2022-04-21 09:18 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 33 kV Bus | 2022-04-21 08:43 | 2022-04-21 10:37 | 1:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-1 | 2022-04-21 09:24 | 2022-04-21 12:16 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformer T-2 | 2022-04-21 09:53 | 2022-04-21 16:35 | 6:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T-1 | 2022-04-21 10:30 | 2022-04-21 15:29 | 4:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer T-1 | 2022-04-22 07:03 | 2022-04-22 07:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-1 | 2022-04-23 11:04 | 2022-04-23 12:26 | 1:22 | S/O | Due to 33 kV feeder problem | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-3 | 2022-04-24 00:13 | 2022-04-24 01:20 | 1:07 | S/O | Due to 33 kV feeder maint.work | 50 | 55.8333 | Power interruption
Madaripur | 132/33 kV transformer T-2 | 2022-04-24 11:15 | 2022-04-24 12:49 | 1:34 | S/O | Due to C/M work | 17 | 26.6333 | Power interruption
Barapukuria | 230/132 kV transformer T01 | 2022-04-26 05:43 | 2022-04-26 09:57 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T-1 | 2022-04-28 08:15 | 2022-04-28 10:09 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-04-29 07:12 | 2022-04-29 09:39 | 2:27 | S/O | Due to C/M work | 15 | 36.75 | Power interruption
Faridpur | 132/33 kV transformer T2 | 2022-04-29 07:47 | 2022-04-29 09:49 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-3 | 2022-04-29 08:31 | 2022-04-29 10:17 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 | 2022-04-30 07:16 | 2022-04-30 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 59:06 |  | Unserved Energy : |  | 204.55
HVDC Grid Circle
HVDC | HVDC block-1 | 2022-04-15 06:13 | 2022-04-15 09:59 | 3:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | 132 kV Bus coupler | 2022-04-28 08:24 | 2022-04-28 13:32 | 5:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T2 | 2022-04-28 14:11 | 2022-04-28 14:55 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T2 with 33 kV Bus | 2022-04-28 07:00 | 2022-04-28 10:01 | 3:01 | S/O | Due to C/M work | 48 | 144.8 | Power interruption
Benapole | 132/33 kV transformer T1 | 2022-04-30 08:23 | 2022-04-30 10:09 | 1:46 | S/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 14:25 |  | Unserved Energy : |  | 144.8
Bogura Grid Circle:
Mohastanghor | 132/33 kV transformer T2 | 2022-04-06 07:43 | 2022-04-06 10:37 | 2:54 | S/O | Due to C/M work | 20 | 58 | Power interruption
Niyamatpur | 132/33 kV transformer T3 | 2022-04-06 08:59 | 2022-04-06 13:30 | 4:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformerT2 | 2022-04-06 15:48 | 2022-04-06 17:30 | 1:42 | S/O | Due to 33 kV loop maint. | 50 | 85 | Power interruption
Jaldhaka | 132/11 kV transformer T1 | 2022-04-07 09:36 | 2022-04-07 14:20 | 4:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T-6 | 2022-04-10 05:25 | 2022-04-10 05:25 | 0:00 | S/O |  | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformerT2 | 2022-04-10 09:43 | 2022-04-10 10:32 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T-2 | 2022-04-11 08:25 | 2022-04-11 10:47 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 33 kV Bus section-3 | 2022-04-11 15:38 | 2022-04-11 16:50 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformerT1 | 2022-04-15 06:15 | 2022-04-15 09:05 | 2:50 | S/O | Due to C/M work | 40 | 113.3333 | Power interruption
Page:5/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Palashbari | 132/33 kV transformerT1 | 2022-04-16 09:25 | 2022-04-16 11:08 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/11 kV transformer T1 | 2022-04-16 11:55 | 2022-04-16 14:24 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Joypurhat | 132/11 kV transformer T3 | 2022-04-16 12:15 | 2022-04-16 15:26 | 3:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/11 kV transformer T2 | 2022-04-16 12:14 | 2022-04-16 13:25 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformerT2 | 2022-04-21 10:45 | 2022-04-21 11:50 | 1:05 | S/O | Due to CB maint.work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformerT2 | 2022-04-24 06:10 | 2022-04-24 06:10 | 0:00 | S/O | Due to 33 kV Bus connection | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformerT3 | 2022-04-24 08:10 | 2022-04-24 10:29 | 2:19 | S/O | Due to C/M work | 25 | 57.9167 | Power interruption
| 132/33 kV transformerT2 | 2022-04-24 11:17 | 2022-04-24 12:28 | 1:11 | S/O | Due to C/M work | 20 | 23.6667 | Power interruption
Barapukuria | 132 kV Bus-1 | 2022-04-26 05:51 | 2022-04-26 09:58 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformerT2 with 33 kV Bus | 2022-04-26 11:10 | 2022-04-26 11:43 | 0:33 | S/O | Due to C/M work | 12 | 6.6 | Power interruption
Natore | 132/11 kV transformer T1 | 2022-04-29 09:54 | 2022-04-29 11:12 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/11 kV transformer T1 | 2022-04-29 09:47 | 2022-04-29 11:55 | 2:08 | S/O | Due to C/M work | 37 | 78.9333 | Power interruption
Jaldhaka | 132/11 kV transformer T2 | 2022-04-29 07:53 | 2022-04-29 10:30 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/11 kV transformer T3 |  | 2022-04-30 12:50 |  |  | After maint.work | 0 | 0 | No interruption
Natore | 132/11 kV transformer T3 | 2022-04-30 08:15 | 2022-04-30 10:30 | 2:15 | S/O | Due to C/M work | 20 | 45 | Power interruption
Mithapukur | 132/33 kV transformerT1 | 2022-04-30 10:55 | 2022-04-30 12:01 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 48:17 |  | Unserved Energy : |  | 468.45
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 412:58 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-04-02 08:43 | 2022-04-02 11:28 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV Ckt-2 | 2022-04-02 11:31 | 2022-04-02 13:46 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-04-05 06:18 | 2022-04-05 07:21 | 1:03 | S/O | Due to C/M work | 20 | 21 | Power interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-04-05 06:34 | 2022-04-05 12:40 | 6:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-04-07 10:46 | 2022-04-07 16:26 | 5:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-04-09 08:40 | 2022-04-09 15:56 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-04-11 08:38 | 2022-04-11 13:28 | 4:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur 132 kV Ckt-1 & 2 |  | 2022-04-14 22:34 |  |  | After maint.work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV Ckt-2 | 2022-04-15 08:17 | 2022-04-15 09:43 | 1:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-04-15 08:44 | 2022-04-15 15:33 | 6:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV Ckt-2 | 2022-04-18 11:40 | 2022-04-18 12:10 | 0:30 | S/O | Due to removing kite | 0 | 0 | No interruption
| Mymensingh -Jamalpur 132 kV Ckt-2 | 2022-04-19 09:26 | 2022-04-19 14:52 | 5:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2022-04-19 12:54 | 2022-04-19 15:55 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV Ckt-2 | 2022-04-22 15:08 | 2022-04-22 15:08 | 0:00 | S/O | Due to kite removal | 0 | 0 | No interruption
| Mymensingh -Kishoreganj 132 kV Ckt-2 | 2022-04-26 12:45 | 2022-04-26 13:05 | 0:20 | S/O | Due to C/M work | 55 | 18.3333 | Power interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-2 | 2022-04-27 06:59 | 2022-04-27 06:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-04-28 06:47 | 2022-04-28 06:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Jamalpur 132 kV Ckt-1 | 2022-04-28 09:07 | 2022-04-28 18:04 | 8:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh -Kishoreganj 132 kV Ckt-2 | 2022-04-29 13:55 | 2022-04-29 14:52 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-1 & 2 | 2022-04-30 06:48 | 2022-04-30 06:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Jamalpur 132 kV Ckt-2 | 2022-04-30 11:29 | 2022-04-30 13:13 | 1:44 | S/O | Due to tree trimming | 0 | 0 | No interruption
|  |  | Total : | 59:05 |  | Unserved Energy: |  | 39.3333
Dhaka (South) Grid Circle :
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 & 2 | 2022-04-01 06:06 | 2022-04-01 06:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Peaking 132 kV Ckt | 2022-04-04 10:53 | 2022-04-04 15:32 | 4:39 | S/O | Due to maint.work | 0 | 0 | No interruption
| Siddhirganj-Haripur 230 kV Ckt-2 | 2022-04-04 13:21 | 2022-04-04 14:54 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Bramongaon 132 kV Ckt | 2022-04-05 14:12 | 2022-04-05 14:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Madanganj 132 kV Ckt |  | 2022-04-05 16:45 |  | S/O | After maint.work | 0 | 0 | No interruption
| Hasnabad-Shyampur 230 kV Ckt | 2022-04-07 06:54 | 2022-04-07 06:54 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Keraniganj 230 kV Ckt-2 | 2022-04-07 11:44 | 2022-04-07 13:41 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Kamrangirchar 132 kV Ckt | 2022-04-09 08:50 | 2022-04-09 12:49 | 3:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV Ckt | 2022-04-09 09:46 | 2022-04-09 11:30 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-2 | 2022-04-10 08:30 | 2022-04-10 08:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-04-10 12:14 | 2022-04-10 16:14 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Keraniganj-Srinagar 132 kV Ckt-2 | 2022-04-11 14:26 | 2022-04-11 15:48 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV Ckt-2 | 2022-04-11 14:32 | 2022-04-11 15:16 | 0:44 | S/O | Due to protection test | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aurahati 132 kV Ckt | 2022-04-11 15:56 | 2022-04-11 17:01 | 1:05 | S/O |  | 0 | 0 | No interruption
| Keraniganj-Nawabganj 132 kV Ckt-1 | 2022-04-12 10:12 | 2022-04-12 12:30 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| Keraniganj-Hasnabad 230 kV Ckt-1 | 2022-04-12 12:48 | 2022-04-12 15:48 | 3:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt | 2022-04-14 06:46 | 2022-04-14 06:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2022-04-18 08:23 | 2022-04-18 10:15 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV Ckt-1 | 2022-04-19 06:55 | 2022-04-19 06:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Purbachal 132 kV Ckt-1 |  | 2022-04-19 11:04 |  |  | new connection | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Maniknagar 230 kV Ckt-2 |  | 2022-04-22 11:52 |  |  | After maint.work | 0 | 0 | No interruption
| Siddhirganj -Maniknagar 230 kV Ckt-1 | 2022-04-22 12:15 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-04-23 08:53 | 2022-04-23 14:15 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV Ckt-2 | 2022-04-24 00:13 | 2022-04-24 01:20 | 1:07 | S/O | Due to bird nest removal | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-1 |  | 2022-04-29 10:17 |  |  | After maint.work | 0 | 0 | No interruption
Harpur | Harpur-Meghnaghat 230 kV Ckt-1 | 2022-04-30 06:35 | 2022-04-30 10:15 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 38:22 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khulshi | Khulshi-Halishahar 132 kV Ckt-1 | 2022-04-01 07:35 | 2022-04-01 07:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2022-04-01 10:10 | 2022-04-01 12:24 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur 132 kV Ckt-1 |  | 2022-04-01 13:22 |  | S/O | After maint.work | 0 | 0 | No interruption
Khulshi | Khulshi-Rampur 132 kV Ckt-1 |  | 2022-04-01 13:23 |  | S/O |  | 0 | 0 | No interruption
| Khulshi-Sholoshahar 132 kV Ckt | 2022-04-02 09:03 | 2022-04-02 15:35 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Sholoshahar | Sholoshahar-Madunaghat 132 kV Ckt | 2022-04-02 09:20 | 2022-04-02 15:19 | 5:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-04-07 11:32 | 2022-04-07 14:24 | 2:52 | S/O | Due to C/M work | 30 | 86 | Power interruption
Hathazari | Hathazari-Abul khair 230 kV Ckt | 2022-04-08 08:22 | 2022-04-08 08:22 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Abul khair | Abul khair-BSRM 230 kV Ckt | 2022-04-08 08:57 | 2022-04-08 08:57 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-09 07:25 | 2022-04-09 07:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-04-10 06:57 | 2022-04-10 12:32 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramgamati | Ramgamati-Khagrachori 132 kV Ckt-1 | 2022-04-10 10:04 | 2022-04-10 13:07 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-04-11 07:52 | 2022-04-11 07:52 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt | 2022-04-12 06:36 | 2022-04-12 06:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kalurghat 132 kV Ckt-1 & 2 | 2022-04-12 10:42 | 2022-04-12 10:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Solashahar 132 kV Ckt-1 | 2022-04-13 08:41 | 2022-04-13 10:53 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV Ckt | 2022-04-16 08:12 | 2022-04-16 15:10 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV Ckt-2 | 2022-04-17 06:37 | 2022-04-17 06:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kalurghat 132 kV Ckt- | 2022-04-19 13:43 | 2022-04-19 15:05 | 1:22 | S/O | Due to project work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV Ckt-2 | 2022-04-21 07:21 | 2022-04-21 07:21 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 & 2 | 2022-04-22 08:20 | 2022-04-22 17:37 | 9:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Chandraghona 132 kV Ckt-1 & 2 | 2022-04-22 20:01 | 2022-04-23 00:40 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV Ckt | 2022-04-23 08:24 | 2022-04-23 11:17 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt | 2022-04-23 08:24 | 2022-04-23 15:54 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2022-04-24 06:56 | 2022-04-24 06:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-04-24 08:55 | 2022-04-24 15:10 | 6:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2022-04-25 12:30 | 2022-04-25 12:43 | 0:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 & 2 | 2022-04-27 08:40 | 2022-04-27 08:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2022-04-27 10:49 | 2022-04-27 12:35 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 69:20 |  | Unserved Energy: |  | 86
Page: 3/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj P/S | B.Baria-Narsingdi 132 kV Ckt-2 | 2022-03-01 08:32 | 2022-03-01 18:06 | 9:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2022-03-11 11:34 | 2022-03-11 14:09 | 2:35 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-1 | 2022-03-11 12:31 | 2022-03-11 12:31 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 |  | 2022-03-12 17:44 |  | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj(N)-Bhulta 400 kV Ckt-1 & 2 | 2022-03-15 10:33 | 2022-03-15 10:33 | 0:00 | S/O | Due to protcetion test | 0 | 0 | No interruption
Lakdhanvi | Lakdhanvi-Cumilla(S) 132 kV Ckt | 2022-03-22 09:35 | 2022-03-22 17:44 | 8:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-03-24 11:15 | 2022-03-24 17:47 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 26:50 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Rajbari | Rajbari-Faridpur 132 kV Ckt-1 | 2022-04-01 09:08 | 2022-04-01 16:54 | 7:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra P/P | Payra P/P-Gopalganj (N) 400 kV Ckt-1 |  | 2022-04-02 12:07 |  |  | new connection | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal 400 kV Ckt-1 |  | 2022-04-02 14:05 |  |  |  | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-04-04 11:22 | 2022-04-04 17:13 | 5:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra -Gopalganj (P) 132 kV Ckt-1 |  | 2022-04-05 09:01 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 230 kV Ckt-1 | 2022-04-06 13:21 | 2022-04-06 16:28 | 3:07 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Ramgaj 400 kV Ckt-1 | 2022-04-07 15:34 | 2022-04-07 22:23 | 6:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra P/P | Payra P/P-Gopalganj (N) 400 kV Ckt-1 | 2022-04-08 08:52 | 2022-04-09 00:30 | 15:38 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gallamari 132 kV Ckt-2 | 2022-04-09 08:26 | 2022-04-09 10:58 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Gallamari 132 kV Ckt-1 |  | 2022-04-09 08:49 |  | S/O | After maint.work | 0 | 0 | No interruption
| Khulna©-Gallamari 132 kV Ckt-2 |  | 2022-04-09 08:51 |  | S/O |  | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV Ckt-2 | 2022-04-10 11:04 | 2022-04-10 18:11 | 7:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj-Gopalganj P/S 132 kV Ckt | 2022-04-11 14:52 | 2022-04-11 15:58 | 1:06 | S/O | Due to protection test | 0 | 0 | No interruption
Payra P/P | Payra P/P-Gopalganj (N) 400 kV Ckt-2 |  | 2022-04-12 23:59 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gallamari 132 kV Ckt-1 & 2 | 2022-04-13 10:04 | 2022-04-13 14:17 | 4:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj-Payra 400 kV Ckt-1 | 2022-04-15 12:06 | 2022-04-15 17:59 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-2 | 2022-04-16 06:13 | 2022-04-16 08:43 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV Ckt | 2022-04-18 12:50 | 2022-04-18 21:31 | 8:41 | S/O | Due to maint.work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-2 |  | 2022-04-19 03:23 |  | S/O | After maint.work | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV Ckt-1 | 2022-04-19 07:00 | 2022-04-19 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gopalganj P/S 132 kV Ckt | 2022-04-19 10:15 | 2022-04-19 11:36 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt | 2022-04-20 00:28 | 2022-04-20 11:28 | 11:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-2 | 2022-04-20 00:56 | 2022-04-20 03:41 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Payra-Payra 400 kV Ckt-3 & 4 |  | 2022-04-20 11:50 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Payra 400 kV Ckt-1 | 2022-04-22 07:00 | 2022-04-22 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Bhandaria 132 kV Ckt | 2022-04-22 19:55 | 2022-04-22 19:55 | 0:00 | S/O |  | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Payra 400 kV Ckt-2 | 2022-04-24 13:27 | 2022-04-25 14:57 | 25:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV Ckt-1 & 2 | 2022-04-25 08:05 | 2022-04-25 15:56 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur-Rajbari 132 kV Ckt-1 | 2022-04-26 07:16 | 2022-04-26 10:22 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 122:46 |  | Unserved Energy: |  | 0
Page: 4/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bhangura | Bhangura-Baghabari 132 kV Ckt-1 | 2022-04-01 08:25 | 2022-04-01 16:11 | 7:46 | S/O | Due to D/W work | 5 | 38.8333 | Power interruption
Jhenaidah | Jhenaidah-Chuadanga(O) 132 kV Ckt | 2022-04-02 07:06 | 2022-04-02 09:42 | 2:36 | S/O | Due to D/W work | 57 | 148.2 | Power interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt-2 |  | 2022-04-05 09:59 |  | S/O | After maint.work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV Ckt | 2022-04-08 07:52 | 2022-04-08 07:52 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Pabna-Shahjadpur 132 kV Ckt | 2022-04-09 07:24 | 2022-04-09 07:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Pabna-Shahjadpur 132 kV Ckt | 2022-04-10 09:11 | 2022-04-10 17:08 | 7:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Pabna-Shahjadpur 132 kV Ckt | 2022-04-14 08:17 | 2022-04-14 17:40 | 9:23 | S/O | Due to project work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV Ckt-1 & 2 | 2022-04-14 08:30 | 2022-04-14 17:35 | 9:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Jhenaidah 132 kV Ckt-1 & 2 |  | 2022-04-15 11:15 |  | S/O | After maint.work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-2 | 2022-04-15 11:18 | 2022-04-15 12:39 | 1:21 | S/O | Due to tree trimming | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV Ckt | 2022-04-20 09:39 | 2022-04-20 18:11 | 8:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV Ckt-3 | 2022-04-23 12:00 | 2022-04-23 18:17 | 6:17 | S/O | Due to maint.work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV Ckt-1 & 2 | 2022-04-24 07:11 | 2022-04-24 07:11 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-3 | 2022-04-25 10:32 | 2022-04-25 10:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt | 2022-04-25 14:21 | 2022-04-25 19:34 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah-Jashore 132 kV Ckt-2 |  | 2022-04-25 17:35 |  | S/O | After maint.work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-1 | 2022-04-27 08:22 | 2022-04-27 17:15 | 8:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-1 | 2022-04-29 08:18 | 2022-04-29 13:16 | 4:58 | S/O | Due to SAS work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 | 2022-04-29 13:17 | 2022-04-29 17:22 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 76:06 |  | Unserved Energy: |  | 187.0333
Bogura Grid Circle :
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2022-04-06 09:19 | 2022-04-06 13:36 | 4:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-1 | 2022-04-07 08:31 | 2022-04-07 11:46 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rangpur 132 kV Ckt | 2022-04-07 12:18 | 2022-04-07 13:12 | 0:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria S/S | Barapukuria S/S-Barapukuria P/S 230 kV Ckt-2 |  | 2022-04-10 11:11 |  |  | After maint.work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-2 | 2022-04-12 12:48 | 2022-04-12 13:55 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV Ckt | 2022-04-14 08:30 | 2022-04-14 17:45 | 9:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV Ckt | 2022-04-16 11:52 | 2022-04-16 14:54 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-1 |  | 2022-04-18 16:08 |  |  | After maint.work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rahonpur 132 kV Ckt-1 | 2022-04-19 11:46 | 2022-04-19 19:01 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| C.nawabganj-Rahonpur 132 kV Ckt | 2022-04-20 12:15 | 2022-04-20 16:05 | 3:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Thaurgaon P/S 132 kV Ckt-1 & 2 | 2022-04-22 06:18 | 2022-04-22 06:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | Power interruption
|  |  | Total : | 32:55 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 425:24 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
b) Ullon-Dhanmondi 132 kV Ckt-3 was under shut down from 08:33 to 08:47 for protection test.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April 2022
| Area | Previous Month (March' 2022) |  |  |  | Current Month (April '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 19 | 2 | 89 | 110 | 19 | 2 | 75 | 96
2 | Dhaka (South) Grid Circle. | 28 | 1 | 68 | 97 | 36 |  | 46 | 82
3 | Chattogram Grid Circle. | 12 | 1 | 42 | 55 | 29 | 1 | 51 | 81
4 | Cumilla Grid Circle. | 19 | 3 | 73 | 95 | 46 | 3 | 24 | 73
5 | Khulna Grid Circle. | 7 | 3 | 45 | 55 | 24 |  | 52 | 76
6 | HVDC Grid Circle | 8 | - | 36 | 44 | 9 | 3 | 24 | 36
7 | Bogura Grid Circle. | 7 | 10 | 26 | 43 | 28 | 10 | 37 | 75
8 | Others |  | 1 | 1 | 2 | 1 | 1 |  | 2
9 | Total | 100 | 21 | 380 | 501 | 192 | 20 | 309 | 521
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April 2022
| Area | Previous Month (March' 2022) |  |  |  | Current Month (April '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 544.4133 |  | 845.92 | 1390.3333 | 273.7333 |  | 674.1333 | 947.8667
2 | Dhaka (South) Grid Circle. | 113.7333 |  | 37.9167 | 151.65 | 151.33 |  |  | 151.33
3 | Chattogram Grid Circle. | 135.1167 |  | 557.9167 | 693.0333 | 888.2 |  | 324.33 | 1212.53
4 | Cumilla Grid Circle. | 251.2167 |  | 310.7167 | 561.9333 | 350.2 | 15.87 | 292.92 | 658.99
5 | Khulna Grid Circle. | 38.3333 | 31.73 | 546.02 | 616.0833 | 140.1 | 15.6 | 204.55 | 360.25
6 | HVDC Grid Circle |  |  | 11.47 | 11.47 | 18.43 | 66.82 | 331.83 | 417.08
7 | Bogura Grid Circle. | 72.08 | 270.32 | 2205.7833 | 2548.1833 | 134.62 | 215.07 | 468.45 | 818.14
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1154.8933 | 302.05 | 4515.7433 | 5972.6867 | 1956.6133 | 313.36 | 2296.2133 | 4566.1867
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 4 | 8 | 12 | 1 | 3 | 8 | 908.53
2 | Dhaka (South) | 5031.6 | 1 |  | 1 |  |  | 1 | 22.5
3 | Chattogram | 2042 | 7 | 3 | 10 | 3 |  | 7 | 732.93
4 | Khulna | 2434 | 5 | 5 | 10 |  | 3 | 7 | 360.25
5 | HVDC | 5954.3 | 2 | 1 | 2 | 1 | 1 | 1 | 230.05
6 | Bogura | 3145.6 | 5 | 8 | 13 | 1 | 3 | 9 | 716.98
7 | Cumilla | 2981 | 8 | 6 | 14 | 6 | 1 | 7 | 646.24
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3617.48
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.91%
4 | Khulna | 99.91%
5 | HVDC | 99.97% | [6 empty] | Executive Engineer
6 | Bogura | 99.92% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - |  | 2 | 2 | 1 | - | 1 | 39.33
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 | 1 |  | 128.83
3 | Chattogram | 917 | - | 1 | 1 | 2 |  |  | 2 | 479.6
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | 2 | 2 |  | - | 2 | 187.03 | -
6 | Bogura | 1803.3 | - | 3 |  | 3 | 2 | 1 |  | 101.15
7 | Cumilla | 1648.16 | - | 1 |  | 1 | 1 |  |  | 12.75
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 948.69
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.93%
3 | Chattogram | 99.81%
4 | Khulna | 99.91%
5 | Bheramara (HVDC) | 99.92% | [7 empty] | Executive Engineer
6 | Bogura | 98.5% | [7 empty] | Information Management Division
7 | Cumilla | 99.81% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-04-01 | 15 | - | 2 | 04hr'22 min | 1 | 47 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Joydevpur | 1 | 0:34 | 100 | 56.6667 | Due to tripping of 132/33 kV transformers T-1 ,T 2 & T3
Jamalpur | 1 | 0:54 | 26 | 23.4 | Due to red-hot maint 132/33 kV Transformer T2
Kabirpur | 1 | 0:26 | 200 | 86.6667 | Due to 33 kV feeder fault
Kodda | 1 | 3:34 | 30 | 107 | Due to red-hot maint 132/33 kV Transformer T2
Dhamrai | 1 | 5:31 | 10 | 55.1667 | Due to S/D of 132/33 kV transformer T-2
Mymensingh | 1 | 2:30 | 25 | 62.5 | Due to S/D of 132/33 kV transformer T-1
Kabirur | 2 | 2:22 | 20 | 47.3333 | Due to S/D of 132/33 kV transformer T-2
|  | 1:07 | 200 | 223.3333 | Due to S/D of 132/33 kV transformer T-1
Kodda | 1 | 2:09 | 12 | 25.8 | Due to S/D of 132/33 kV transformer T-2
Joydevpur | 1 | 1:22 | 20 | 27.3333
Sholoshahar | 1 | 2:14 | 55 | 122.8333 | Due to S/D of 132/33 kV transformer T-02
Kabirpur | 1 | 0:47 | 90 | 70.5 | Due to S/D of 132/33 kV transformer T-1
Tongi | 1 | 1:03 | 20 | 21 | Due to S/D of Tongi-Kabirpur 132 kV Ckt-2
Mymensingh | 2 | 0:20 | 55 | 18.3333 | Due to S/D of Mymensingh -Kishoreganj 132 kV Ckt-2
Nawabganj |  | 2:30 | 9 | 22.5 | Due to red-hot maint 132/33 kV Transformer T2
Shyampur | 1 | 0:37 | 150 | 92.5 | Due to tripping of Shyampur-Shyampur (O) 132 kV Ckt-2
Siddhirganj | 1 | 0:05 | 58 | 4.8333 | Due to tripping of Siddhirganj-Matuail 132 kV Ckt
Haripur | 1 | 0:09 | 210 | 31.5 | Due to tripping of Haripur-Bhulta 132 kV Ckt
Cox'sbazar | 2 | 0:17 | 55 | 15.5833 | Due to tripping of 132/33 kV transformer T-3
|  | 0:11 | 62 | 11.3667
Halishahar |  | 0:11 | 50 | 9.1667 | Due to tripping of 132 kV Bus
Dohazari | 1 | 3:10 | 80 | 253.3333 | Due to tripping of 132/33 kV transformer T-2
| 1 | 4:22 | 30 | 131 | Due to tripping of 132/33 kV transformer T-1
Baroierhat | 1 | 4:22 | 12 | 52.4 | Due to S/D of 132/33 kV transformer T-1
Sikalbaha | 1 | 1:27 | 15 | 21.75 | Due to tripping of 132/33 kV transformer T-4
Dohazari |  | 3:12 | 123 | 393.6 | Due to tripping of Dohazari-Cox'sbazar 132 kV Ckt-1
Baraulia | 1 | 2:26 | 20 | 48.6667 | Due to S/D of 132/33 kV transformer T-2
Cox'sbazar | 1 | 0:44 | 100 | 168.3333 | Due to S/D of 132/33 kV transformer T-3
Sikalbaha | 1 | 1:04 | 20 | 21.3333
Dohazari | 1 | 2:52 | 30 | 86 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-1
Cumilla (N) | 1 | 0:19 | 52 | 16.4667 | Due to tripping of 132/33 kV transformers T-3 & T4
Sylhet | 1 | 1:08 | 14 | 15.8667 | Due to tripping of 132/33 kV transformer T-2
Shahjibazar | 1 | 1:20 | 34 | 45.3333 | Due to red-hot maint of 132/33 kV Transformer T4
| 1 | 2:41 | 29 | 77.8167 | Due to red-hot maint of 132/33 kV Transformer T2
Sylhet | 1 | 0:26 | 47 | 39.1667 | Due to tripping of 132/33 kV transformer T-2
Chowmuhani |  | 0:23 | 20 | 7.6667 | Due to 33 kV feeder fault
Shahjibazar | 1 | 5:03 | 20 | 101 | Due to red-hot maint of 132/33 kV Transformer T4
Ramganj |  | 1:40 | 30 | 50 | Due to red-hot maint of 132/33 kV Transformer T1
Fenchuganj |  | 0:17 | 45 | 12.75 | Due to tripping of Fenchuganj-(Beanibazar)-Sylhet 132 kV Ckt
Chowmuhani |  | 3:22 | 60 | 202 | Due to S/D of 132 kV Bus
Feni |  | 0:46 | 34 | 26.0667 | Due to S/D of 132/33 kV transformer T-1
Ramganj | 1 | 0:56 | 35 | 32.6667 | Due to S/D of 132/33 kV transformer T-2
Sylhet |  | 0:21 | 21 | 7.35
Shahjibazar |  | 0:15 | 30 | 7.5 | Due to S/D of 132/33 kV transformer T-4
|  | 0:26 | 40 | 17.3333 | Due to S/D of 132/33 kV transformer T-2
Madaripur | 2 | 0:45 | 26 | 19.5 | Due to red-hot maint of 132/33 kV Transformer T1
Narail |  | 1:43 | 12 | 20.6 | Due to red-hot maint of 132/33 kV Transformer T2
Barisal(N) | 1 | 1:18 | 60 | 78 | Due to tripping of 132/33 kV transformer T-4
Madaripur | 1 | 0:39 | 24 | 15.6 | Due to red-hot maint of 132/33 kV Transformer T1
Bhandaria | 1 | 0:33 | 40 | 22 | Due to tripping of 132/33 kV transformer T-1
Madaripur |  | 3:32 | 20 | 70.67 | Due to S/D of 132/33 kV transformer T-3
Bhandaria |  | 1:28 | 10 | 14.67 | Due to S/D of 132/33 kV transformer T-1
Bagerhat | 1 | 1:07 | 50 | 55.8333 | Due to S/D of 132/33 kV transformer T-3
Madaripur | 1 | 1:34 | 17 | 26.6333 | Due to S/D of 132/33 kV transformer T-2
Narail | 1 | 2:27 | 15 | 36.75 | Due to S/D of 132/33 kV transformer T-2
Ishurdi | 1 | 0:32 | 25 | 13.3333 | Due to tripping of 132/33 kV transformer T-1
Bottail | 1 | 0:09 | 34 | 5.1 | Due to S/D of 132/33 kV transformer T-1
Jhenaidah(O) | 1 | 3:31 | 19 | 66.8167 | Due to red-hot maint of 132/33 kV Transformer T2
Bottail |  | 3:01 | 48 | 144.8 | Due to S/D of 132/33 kV transformer T-2
Bhangura | 1 | 7:46 | 5 | 38.8333 | Due to S/D of Bhangura-Baghabari 132 kV Ckt-1
Jhenaidah | 1 | 2:36 | 57 | 148.2 | Due to S/D of Jhenaidah-Chuadanga(O) 132 kV Ckt
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mohasthangarh | 1 | 0:59 | 12 | 11.8 | Due to tripping of 132/33 kV transformers T1 & T2
Rajshahi | 1 | 0:48 | 63 | 50.4 | Due to red-hot maint.of 132/ 33 kV Transformer T3
Jaldhaka | 1 | 1:11 | 20 | 23.6667 | Due to red-hot maint.of 132/ 33 kV Transformer T2
Bogura | 1 | 2:21 | 60 | 141 | Due to tripping of 132/33 kV transformersT-3 & T4
Joldhaka | 1 | 0:26 | 50 | 21.6667 | Due to tripping of 132/33 kV transformer T-2
Baghabari | 1 | 0:47 | 27 | 21.15 | Due to tripping of Baghabari-Bhangura 132 kV Ckt
Saidpur | 1 | 0:21 | 100 | 35 | Due to tripping of Saidpur-Purbasadipur 132 kV Ckt-1 & 2
Barapukuria | 1 | 0:30 | 90 | 45 | Due to tripping of Barapukuria-Rangpur 132 kV Ckt-1 & 2
Mohastanghor | 1 | 2:54 | 20 | 58 | Due to S/D of 132/33 kV transformer T-2
Purbasadipur | 2 | 1:42 | 50 | 85 | Due to S/D of 132/33 kV transformer T-2
|  | 2:50 | 40 | 113.3333 | Due to S/D of 132/33 kV transformer T-1
Rajshahi |  | 2:19 | 25 | 57.9167 | Due to S/D of 132/33 kV transformer T-3
|  | 1:11 | 20 | 23.6667 | Due to S/D of 132/33 kV transformer T-2
Mithapukur | 1 | 0:33 | 12 | 6.6 | Due to S/D of 132/33 kV transformer T-2
Sherpur(Bogura) | 1 | 2:08 | 37 | 78.9333 | Due to S/D of 132/33 kV transformer T-1
Natore | 1 | 2:15 | 20 | 45 | Due to S/D of 132/33 kV transformer T-3
| Total Unserved energy : |  |  | 4566.19 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Sl | Substation | Max Load Served (MW) | date_time
1 | AKS 132/33kV Grid Sub-Station | 27 | 2022-04-30 17:00
2 | AKSML 230/33kV Grid Sub-Station | 150 | 2022-04-28 06:00
3 | Aftabnagar 132/33kV Grid Sub-Station | 129 | 2022-04-04 11:00
4 | Agargaon 230/132kV Grid Sub-Station | 114 | 2022-04-28 14:00
5 | Agrabad 132/33kV Grid Sub-Station | 152 | 2022-04-26 18:00
6 | Amnura 132/33kV Grid Sub-Station | 77 | 2022-04-16 21:00
7 | Ashuganj 132/33kV Sub-Station | 51 | 2022-04-30 23:00
8 | BSRM 230/33kV Grid Sub-Station | 169 | 2022-04-10 20:00
9 | Bagerhat 132/33kV Grid Sub-Station | 114 | 2022-04-28 21:00
10 | Bakulia 132/33kV Grid Sub-Station | 136 | 2022-04-27 16:00
11 | Banani 132/33kV Grid Sub-Station | 236 | 2022-04-05 15:00
12 | Bangabhaban 132/33kV Grid Sub-Station | 24 | 2022-04-26 10:00
13 | Barapukuria 230/132/33kV Grid Sub-Station | 88 | 2022-04-18 20:00
14 | Barguna 132/33kV Grid Sub-Station | 22 | 2022-04-24 23:00
15 | Barishal 132/33kV Grid Sub-Station | 129 | 2022-04-19 15:00
16 | Barishal 230/132kV Grid Sub-Station | 75 | 2022-04-24 22:00
17 | Baroaulia 132/33kV Grid Sub-Station | 90 | 2022-04-19 23:00
18 | Baroirhat 132/33kV Grid Sub-Station | 67 | 2022-04-30 21:00
19 | Bashundhara 132/33kV Grid Sub-Station | 192 | 2022-04-25 14:00
20 | BashundharaCement 132/33kV Sub-Station | 26 | 2022-04-25 14:00
21 | Beanibazar 132/33kV Grid Sub-Station | 83 | 2022-04-28 22:00
22 | Benapole 132/33kV Grid Sub-Station | 68 | 2022-04-30 19:00
23 | Bhaluka 132/33kV Grid Sub-Station | 152 | 2022-04-10 09:00
24 | Bhandaria 132/33kV Grid Sub-Station | 65 | 2022-04-29 21:00
25 | Bhangura 132/33kV Grid Sub-Station | 48 | 2022-04-19 03:00
26 | Bheramara(GK) 132/33kV Grid Sub-Station | 68.4 | 2022-04-26 21:00
27 | Bog-Sherpur 132/33kV Grid Sub-Station | 72 | 2022-04-19 23:00
28 | Bogura 132/33kV Grid Sub-Station | 193 | 2022-04-17 03:00
29 | Borhanuddin 230/33kV Grid Sub-Station | 244 | 2022-04-05 09:00
30 | Brahmanbaria 132/33kV Grid Sub-Station | 196 | 2022-04-29 23:00
31 | Cantonment 132/33kV GIS Grid Sub-Station | 167 | 2022-04-23 01:00
32 | Chandpur 132/33kV Grid Sub-Station | 85 | 2022-04-28 23:00
33 | Chandraghona 132/33kV Grid Sub-Station | 36 | 2022-04-17 21:00
34 | Chapai 132/33kV Grid Sub-Station | 84 | 2022-04-01 21:00
35 | Charsaidpur 132/33kV Sub-Station | 44 | 2022-04-05 12:00
36 | Chauddagram 132/33kV Grid Sub-Station | 71 | 2022-04-27 21:00
37 | Chhatak 132/33kV Grid Sub-Station | 32 | 2022-04-26 23:00
38 | Chowmuhani 132/33kV Grid Sub-Station | 238 | 2022-04-27 22:00
39 | Chuadanga 132/33kV Grid Sub-Station | 121 | 2022-04-12 21:00
40 | Coxsbazar 132/33kV Grid Sub-Station | 133 | 2022-04-19 19:00
41 | Cumilla(N) 230/132/33kV Grid Sub-Station | 168 | 2022-04-12 21:00
42 | Cumilla(S) 132/33kV Grid Sub-Station | 176 | 2022-04-10 14:00
43 | Daudkandi 132/33kV Grid Sub-Station | 160 | 2022-04-07
44 | Dhaka University 132/33kV Grid Sub-Station | 129 | 2022-04-02 18:30
45 | Dhamrai 132/33kV Grid Sub-Station | 130 | 2022-04-12 14:00
46 | Dohazari 132/33kV Grid Sub-Station | 112 | 2022-04-11 21:00
47 | Faridpur 132/33kV Grid Sub-Station | 170 | 2022-04-27 22:00
48 | Fatullah 132/33kV Grid Sub-Station | 73 | 2022-04-03 15:00
49 | Fenchuganj 230/132/33kV Grid Sub-Station | 57 | 2022-04-24 20:00
50 | Feni 132/33kV Grid Sub-Station | 150 | 2022-04-13 21:00
51 | GPH 230/33kV Grid Sub-Station | 109 | 2022-04-17 19:30
52 | Ghorashal 132/33kV Sub-Station | 158 | 2022-04-09 07:00
53 | Goalpara 132/33kV Grid Sub-Station | 32 | 2022-04-24 21:00
54 | Gollamari 132/33kV Grid Sub-Station | 64 | 2022-04-25 19:30
55 | Gopalganj 132/33kV Grid Sub-Station | 115.2 | 2022-04-09 20:00
56 | Gulshan 132/33kV Grid Sub-Station | 132 | 2022-04-28 13:00
57 | Halishahar 132/33kV Grid Sub-Station | 111.5 | 2022-04-18 07:00
58 | HaripurSBU 132/33kV Sub-Station | 146 | 2022-04-03 16:00
59 | Hasnabad 132/33kV Grid Substation | 174 | 2022-04-18 23:00
60 | Hathazari 230/132/33kV Grid Sub-Station | 108 | 2022-04-26 21:00
61 | Ishurdi 132/33kV Grid Sub-Station | 83 | 2022-04-27 21:00
62 | Jaldhaka 132/33kV Grid Sub-Station | 68 | 2022-04-25 21:00
63 | Jamalpur 132/33kV Grid Sub-Station | 186 | 2022-04-15 20:00
64 | Jashore 132/33kV Grid Sub-Station | 150 | 2022-04-16 21:00
65 | Jhenaidah 132/33kV Grid Sub-Station | 144 | 2022-04-26 22:00
66 | Joypurhat 132/33kV Grid Sub-Station | 79 | 2022-04-19 23:00
67 | Juldah 132/33kV Grid Sub-Station | 31 | 2022-04-18 16:00
68 | KSRM 132/33kV Grid Sub-Station | 40.41 | 2022-04-20 11:00
69 | Kabirpur 132/33kV Grid Sub-Station | 321 | 2022-04-26 14:00
70 | Kachua 132/33kV Grid Sub-Station | 88 | 2022-04-19 23:00
71 | Kallyanpur 132/33kV Grid Sub-Station | 120 | 2022-04-28 19:00
72 | Kamrangirchar 132/33kV Grid Sub-Station | 76 | 2022-04-25 15:00
73 | Kaptai 132/33kV Sub-Station | 34 | 2022-04-10
74 | Kazla 132/33kV Grid Sub-Station | 91 | 2022-04-11 16:00
75 | Keranigonj 230/132/33kV Grid Sub-Station | 92 | 2022-04-04 19:30
76 | Khagrachori 132/33kV Grid Sub-Station | 30 | 2022-04-02 19:00
77 | Khulna (C) 132/33kV Grid Sub-Station | 105 | 2022-04-27 21:00
78 | Khulshi 132/33kV Grid Sub-Station | 201 | 2022-04-20 14:00
79 | Kishoreganj 132/33kV Grid Sub-Station | 178 | 2022-04-29 22:00
80 | Kodda 132/33kV Grid Sub-Station | 347 | 2022-04-27 10:00
81 | Kulaura 132/33kV Grid Sub-Station | 56 | 2022-04-29 21:00
82 | Kurigram 132/33kV Grid Sub-Station | 62 | 2022-04-24 21:00
83 | Kushtia 132/33kV Grid Sub-Station | 156 | 2022-04-27 22:00
84 | Lalbag 132/33kV Grid Sub-Station | 95 | 2022-04-03 13:00
85 | Lalmonirhat 132/33kV Grid Sub-Station | 49 | 2022-04-25 20:00
86 | Madanganj 132/33kV Grid Sub-Station | 179 | 2022-04-06 22:00
87 | Madaripur 132/33kV Grid Sub-Station | 125 | 2022-04-28 21:00
88 | Madartek 132/33kV Grid Sub-Station | 93 | 2022-04-26 19:00
89 | Madunaghat 132/33kV Grid Sub-Station | 118 | 2022-04-03 18:30
90 | Magura 132/33kV Grid Sub-Station | 71 | 2022-04-26 21:00
91 | Mahasthangarh 132/33kV Grid Sub-Station | 82 | 2022-04-15 22:00
92 | Manikganj 132/33kV Grid Sub-Station | 104 | 2022-04-27
93 | Maniknagar 132/33kV Grid Sub-Station | 93 | 2022-04-26 13:00
94 | Matarbari 132/33kV Sub-Station | 128 | 2022-04-25 15:00
95 | Matuail 132/33kV Grid Sub-Station | 85 | 2022-04-21 12:00
96 | Millgate Tongi 132/33kV Grid Sub-Station | 66 | 2022-04-10 15:00
97 | Mirpur 132/33kV Grid Sub-Station | 146 | 2022-04-26 19:30
98 | Mirsorai 230/33kV Grid Sub-Station | 2.53 | 2022-04-25 11:00
99 | Mithapukur 132/33kV Grid Sub-Station | 44 | 2022-04-24 21:00
100 | Modern Steel 132/11kV Grid Sub-Station | 0 | 2022-04-01
101 | Mogbazar 132/33kV Grid Sub-Station | 143 | 2022-04-18 15:00
102 | Mongla 132/33kV Grid Sub-Station | 52 | 2022-04-21 12:00
103 | Motijheel 132/33kV Grid Sub-Station | 41 | 2022-04-26 15:00
104 | Munshiganj 132/33kV Grid Sub-Station | 124 | 2022-04-27 22:00
105 | Mymensingh 132/33kV Grid Sub-Station | 248 | 2022-04-09 23:00
106 | Naogaon 132/33kV Grid Sub-Station | 134 | 2022-04-18 22:00
107 | Narail 132/33kV Grid Sub-Station | 64 | 2022-04-25 22:00
108 | Narinda 132/33kV Grid Sub-Station | 81 | 2022-04-17 13:00
109 | Narshingdi 132/33kV Grid Sub-Station | 203 | 2022-04-19 21:00
110 | Natore 132/33kV Grid Sub-Station | 159 | 2022-04-07 03:00
111 | Nawabganj 132/33kV Grid Sub-Station | 62.6 | 2022-04-26 21:00
112 | Netrakona 132/33kV Grid Sub-Station | 130 | 2022-04-15 18:30
113 | New Tongi 132/33kV Grid Sub-Station | 91.4 | 2022-04-03 11:00
114 | Niamatpur 132/33kV Grid Sub-Station | 114 | 2022-04-01 19:30
115 | Noapara 132/33kV Grid Sub-Station | 76 | 2022-04-03 09:00
116 | PHP 132/33kV Sub-Station | 11 | 2022-04-21 05:00
117 | Pabna 132/33kV Grid Sub-Station | 130 | 2022-04-26 14:00
118 | Palashbari 132/33kV Grid Sub-Station | 136 | 2022-04-16 23:00
119 | Panchagarh 132/33kV Grid Sub-Station | 64 | 2022-04-29 21:00
120 | Patuakhali 132/33kV Grid Sub-Station | 146 | 2022-04-28 22:00
121 | Purbachal 132/33kV Grid Sub-Station | 20 | 2022-04-06 22:00
122 | Purbasadipur 132/33kV Grid Sub-Station | 124 | 2022-04-17 22:00
123 | Rahim Steel 132/33kV Sub-Station | 33 | 2022-04-04 12:00
124 | Rajbari 132/33kV Grid Sub-Station | 80 | 2022-04-27 22:00
125 | Rajendrapur 132/33kV Grid Sub-Station | 127 | 2022-04-17 16:00
126 | Rajshahi 132/33kV Grid Sub-Station | 248 | 2022-04-08 13:00
127 | Rajshahi 230/132/33kV Grid Sub-Station | 50 | 2022-04-16 23:00
128 | Ramganj 132/33kV Grid Sub-Station | 124 | 2022-04-28 22:00
129 | Rampur 230/132/33 kV GIS Grid Sub-Station | 28 | 2022-04-21 21:00
130 | Rangamati 132/33kV Grid Sub-Station | 14 | 2022-04-06 19:00
131 | Rangpur 132/33kV Grid Sub-Station | 153 | 2022-04-25 21:00
132 | Ruppur 132/11kV Grid Sub-Station | 5.6 | 2022-04-26 10:00
133 | SSM 132/33kV Grid Sub-Station | 15 | 2022-04-03 12:00
134 | Saidpur 132/33kV Grid Sub-Station | 114 | 2022-04-25 19:30
135 | Satkhira 132/33kV Grid Sub-Station | 139 | 2022-04-25 21:00
136 | Satmasjid 132/33kV Grid Sub-Station | 115 | 2022-04-18 19:00
137 | Savar 132/33kV Grid Sub-Station | 209 | 2022-04-07 15:00
138 | Shahjadpur 132/33kV Grid Sub-Station | 143 | 2022-04-27 21:00
139 | Shahjibazar 132/33kV Grid Sub-Station | 149 | 2022-04-28 22:00
140 | Shahmirpur 132/33kV Grid Sub-Station | 49 | 2022-04-19 01:00
141 | Shariatpur 132/33kV Grid Sub-Station | 84 | 2022-04-28 22:00
142 | Sherpur 132/33kV Grid Sub-Station | 142 | 2022-04-16 20:00
143 | Shikalbaha 132/33kV Sub-Station | 46 | 2022-04-16 20:00
144 | Shitalakhya 132/33kV Grid Sub-Station | 140 | 2022-04-27 16:00
145 | Shyampur 132/33kV Grid Sub-Station | 184 | 2022-04-28 11:00
146 | Siddhirganj 132/33kV Grid Sub-Station | 130 | 2022-04-11 15:00
147 | Sirajganj 132/33kV Grid Sub-Station | 132 | 2022-04-17 20:00
148 | Sonargaon 132/33kV Grid Sub-Station | 120 | 2022-04-06
149 | Sreemongol 132/33kV Grid Sub-Station | 68 | 2022-04-27 19:00
150 | Srinagar 132/33kV Grid Sub-Station | 52.44 | 2022-04-30
151 | Sunamganj 132/33kV Grid Sub-Station | 57 | 2022-04-26 22:00
152 | Sylhet 132/33kV Grid Sub-Station | 157 | 2022-04-29 21:00
153 | TK chemical 132kV Grid Sub-Station | 32 | 2022-04-26 19:00
154 | Tangail 132/33kV Grid Sub-Station | 260 | 2022-04-08 03:00
155 | Thakurgaon 132/33kV Grid Sub-Station | 100 | 2022-04-17 19:30
156 | Tongi 230/132/33kV Grid Sub-Station | 148 | 2022-04-26 15:00
157 | Ullon 132/33kV Grid Sub-Station | 148 | 2022-04-07 19:30
158 | UttaraNew 132/33kV Grid Sub-Station | 38 | 2022-04-15 14:00
159 | Zigatola 132/33kV Grid Sub-Station | 53 | 2022-04-07 15:00

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April 2022
Area | MW | Date | Hour | Remarks
Dhaka | 5586.33 | 18.04.2022 | 15:00
Chattogram | 1593 | 27.04.2022 | 23:00
Khulna | 1416 | 28.04.2022 | 22:00
Rajshahi | 1156 | 16.04.2022 | 20:00
Cumilla | 604 | 29.04.2022 | 21:00
Mymensingh | 1897 | 28.04.2022 | 21:00
Sylhet | 527.5 | 6.4.2022 | 3:00
Barisal | 1673.4 | 26.04.2022 | 21:00
Rangpur | 921 | 25.04.2022 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Maximum & Minimum Voltages of Grid Sub-Stations. | [12 empty] | Reporting Month
Month: April '2022
2022-04-01
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 418 | 20 | 2022-04-01 | 8:00 | 391 | 7 | 2022-04-01 | 17:00
2 | Bheramara | 400 | 419 | 30 | 2022-04-01 | 8:00 | 380 | 28 | 2022-04-01 | 22:00
3 | Ashuganj(N) | 400 | 415 | 20 | 2022-04-01 | 8:00 | 378 | 7 | 2022-04-01 | 13:00
4 | Payra | 400 | 423 | 12 | 2022-04-01 | 1:00 | 402 | 2 | 2022-04-01 | 1:00
5 | Kaliakoir | 400 | 420 | 20 | 2022-04-01 | 18:30 | 355 | 7 | 2022-04-01 | 12:00
6 | Bhulta | 400 | 414 | 20 | 2022-04-01 | 8:00 | 368 | 16 | 2022-04-01 | 10:00
7 | Gopalganj | 400 | 421 | 13 | 2022-04-01 | 15:00 | 351 | 12 | 2022-04-01 | 3:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2022-04-01 | 20:00 | 227 | 2 | 2022-04-01 | 10:00
2 | Ishurdi | 230 | 238 | 20 | 2022-04-01 | 7:00 | 224 | 15 | 2022-04-01 | 23:00
3 | Ashuganj | 230 | 244 | 25 | 2022-04-01 | 21:00 | 227 | 2 | 2022-04-01 | 11:00
4 | Serajganj | 230 | 240 | 3 | 2022-04-01 | 14:00 | 228 | 15 | 2022-04-01 | 23:00
5 | Baghabari | 230 | 244 | 25 | 2022-04-01 | 22:00 | 227 | 2 | 2022-04-01 | 12:00
6 | Barapukuria | 230 | 238 | 20 | 2022-04-01 | 4:00 | 211 | 12 | 2022-04-01 | 18:00
7 | Bogura | 230 | 244 | 25 | 2022-04-01 | 23:00 | 227 | 2 | 2022-04-01 | 13:00
8 | Rajshahi | 230 | 237 | 24 | 2022-04-01 | 18:00 | 212 | 16 | 2022-04-01 | 4:00
9 | Khulna South | 230 | 244 | 25 | 2022-04-01 | 24:00 | 227 | 2 | 2022-04-01 | 14:00
10 | Rampura | 230 | 238 | 20 | 2022-04-01 | 8:00 | 209 | 6 | 2022-04-01 | 12:00
11 | Haripur | 230 | 244 | 25 | 2022-04-01 | 25:00 | 227 | 2 | 2022-04-01 | 15:00
12 | Hasnabad | 230 | 240 | 20 | 2022-04-01 | 8:00 | 209 | 6 | 2022-04-01 | 11:00
13 | Shyampur | 230 | 244 | 25 | 2022-04-01 | 26:00 | 227 | 2 | 2022-04-01 | 16:00
14 | Aminbazar | 230 | 240 | 20 | 2022-04-01 | 1:00 | 210 | 2 | 2022-04-01 | 2:00
15 | Tongi | 230 | 244 | 25 | 2022-04-01 | 27:00 | 227 | 2 | 2022-04-01 | 17:00
16 | Comilla (N) | 230 | 238 | 20 | 2022-04-01 | 7:00 | 217 | 7 | 2022-04-01 | 13:00
17 | Hathazari | 230 | 244 | 25 | 2022-04-01 | 21:00 | 227 | 2 | 2022-04-01 | 11:00
18 | Megnaghat | 230 | 242 | 20 | 2022-04-01 | 8:00 | 216 | 6 | 2022-04-01 | 11:00
19 | Fenchuganj | 230 | 244 | 25 | 2022-04-01 | 22:00 | 227 | 2 | 2022-04-01 | 12:00
20 | Siddhirganj | 230 | 236 | 20 | 2022-04-01 | 7:00 | 209 | 7 | 2022-04-01 | 11:00 | [7 empty] | 7345
21 | Maniknagar | 230 | 244 | 25 | 2022-04-01 | 23:00 | 227 | 2 | 2022-04-01 | 13:00
22 | Old Airport | 230 | 239 | 20 | 2022-04-01 | 18:00 | 207 | 6 | 2022-04-01 | 12:00
23 | Barisal | 230 | 244 | 25 | 2022-04-01 | 24:00 | 227 | 2 | 2022-04-01 | 14:00
24 | Bhola 225 MW | 230 | 248 | 22 | 2022-04-01 | 19:00 | 228 | 18 | 2022-04-01 | 19:00
25 | AKSML | 230 | 244 | 25 | 2022-04-01 | 25:00 | 227 | 2 | 2022-04-01 | 15:00
26 | BSRM | 230 | 238 | 18 | 2022-04-01 | 7:00 | 216 | 20 | 2022-04-01 | 7:00
27 | Bibiyana | 230 | 244 | 25 | 2022-04-01 | 26:00 | 227 | 2 | 2022-04-01 | 16:00
28 | Bhulta | 230 | 240 | 20 | 2022-04-01 | 8:00 | 209 | 7 | 2022-04-01 | 11:00
29 | Ashuganj (S) | 230 | 243 | 20 | 2022-04-01 | 8:00 | 223 | 7 | 2022-04-01 | 13:00
30 | Kaliakoir | 230 | 244 | 25 | 2022-04-01 | 26:00 | 227 | 2 | 2022-04-01 | 16:00
31 | GPH | 230 | 240 | 20 | 2022-04-01 | 18:30 | 216 | 20 | 2022-04-01 | 7:00
32 | Jhenaidah | 230 | 244 | 25 | 2022-04-01 | 27:00 | 227 | 2 | 2022-04-01 | 17:00
132 kV Substation
1 | Aftabnagar | 132 | 147 | 20 | 2022-04-01 | 06:00 | 123 | 4 | 2022-04-01 | 12:00 | [5 empty] | 1 | Siddhirganj
2 | Agargaon | 132 | 148 | 20 | 2022-04-01 | 07:00 | 121 | 7 | 2022-04-01 | 13:00 | [5 empty] | 2 | Munsiganj
3 | Agrabad | 132 | 139 | 20 | 2022-04-01 | 10:00 | 123 | 30 | 2022-04-01 | 10:00 | [5 empty] | 3 | Sonargaon
4 | AKS | 132 | 138 | 20 | 2022-04-01 | 10:00 | 119 | 30 | 2022-04-01 | 18:00 | [5 empty] | 4 | Shyampur
5 | Aminbazar | 132 | 150 | 20 | 2022-04-01 | 08:00 | 121 | 6 | 2022-04-01 | 12:00 | [5 empty] | 5 | Bhulta
6 | Amnura | 132 | 142 | 20 | 2022-04-01 | 05:00 | 120 | 26 | 2022-04-01 | 11:00 | [5 empty] | 6 | Madanganj
7 | Ashuganj | 132 | 145 | 20 | 2022-04-01 | 08:00 | 129 | 7 | 2022-04-01 | 14:00 | [5 empty] | 7 | Shitalakhya
8 | Bagerhat | 132 | 138 | 30 | 2022-04-01 | 23:00 | 120 | 22 | 2022-04-01 | 23:00 | [5 empty] | 8 | Rahim Steal
9 | Bakulia | 132 | 138 | 20 | 2022-04-01 | 18:30 | 122 | 30 | 2022-04-01 | 11:00 | [5 empty] | 9 | Matuail
10 | Banani | 132 | 147 | 20 | 2022-04-01 | 07:00 | 112 | 7 | 2022-04-01 | 13:00 | [5 empty] | 10 | Ghorasal
11 | Bangabhaban | 132 | 142 | 20 | 2022-04-01 | 07:00 | 119 | 6 | 2022-04-01 | 12:00 | [5 empty] | 11 | Narsinghdi
12 | Barapukuria | 132 | 140 | 30 | 2022-04-01 | 01:00 | 121 | 11 | 2022-04-01 | 09:00 | [5 empty] | 12 | Haripur (SBU)
13 | Barguna | 132 | 141 | 18 | 2022-04-01 | 10:00 | 123 | 18 | 2022-04-01 | 19:00 | [5 empty] | 13 | Sreenagar
14 | Barishal | 132 | 144 | 22 | 2022-04-01 | 19:00 | 122 | 4 | 2022-04-01 | 14:00 | [5 empty] | 14 | Ullon
15 | Barishal | 132 | 145 | 22 | 2022-04-01 | 19:00 | 128 | 18 | 2022-04-01 | 19:00 | [5 empty] | 15 | Hasnabad
16 | Baroaulia | 132 | 141 | 20 | 2022-04-01 | 18:30 | 123 | 30 | 2022-04-01 | 11:00 | [5 empty] | 16 | Magbazar
17 | Baroirhat | 132 | 139 | 20 | 2022-04-01 | 10:00 | 123 | 30 | 2022-04-01 | 05:00 | [5 empty] | 17 | Maniknagar
18 | Bashundhara | 132 | 139 | 1 | 2022-04-01 | 18:00 | 121 | 4 | 2022-04-01 | 14:00
19 | BashundharaCement | 132 | 143 | 20 | 2022-04-01 | 08:00 | 124 | 7 | 2022-04-01 | 11:00 |  | 13 |  |  | Narinda
20 | Beanibazar | 132 | 140 | 20 | 2022-04-01 | 03:00 | 123 | 29 | 2022-04-01 | 22:00 |  | 14 |  |  | Dhanmondi
21 | Benapole | 132 | 138 | 19 | 2022-04-01 | 09:00 | 121 | 1 | 2022-04-01 | 20:00 |  | 15 |  |  | Lalbag
22 | Bhaluka | 132 | 141 | 20 | 2022-04-01 | 07:00 | 108 | 18 | 2022-04-01 | 17:00 |  | 16 |  |  | Madartek
23 | Bhandaria | 132 | 143 | 23 | 2022-04-01 | 06:00 | 121 | 18 | 2022-04-01 | 19:00 |  | 17 |  |  | Dhaka University
24 | Bhangura | 132 | 141 | 20 | 2022-04-01 | 07:00 | 127 | 15 | 2022-04-01 | 22:00 |  | 18 |  |  | Aftabnagar
25 | Bheramara | 132 | 138 | 20 | 2022-04-01 | 07:00 | 123 | 11 | 2022-04-01 | 21:00 |  | 19 |  |  | Fatullah
26 | Bheramara(GK) | 132 | 140 | 20 | 2022-04-01 | 06:00 | 131 | 1 | 2022-04-01 | 20:00 |  |  |  |  | Nawabganj
27 | Bhulta | 132 | 136 | 20 | 2022-04-01 | 09:00 | 112 | 7 | 2022-04-01 | 08:00 |  | 20 |  |  | Mirpur
28 | Bog-Sherpur | 132 | 142 | 20 | 2022-04-01 | 07:00 | 118 | 14 | 2022-04-01 | 12:00 |  | 21 |  |  | Kalyanpur
29 | Bogura | 132 | 142 | 30 | 2022-04-01 | 02:00 | 124 | 14 | 2022-04-01 | 14:00 |  | 22 |  |  | Gulshan
30 | Bogura | 132 | 142 | 30 | 2022-04-01 | 02:00 | 113 | 7 | 2022-04-01 | 14:00 |  | 23 |  |  | Uttara
31 | Brahmanbaria | 132 | 143 | 20 | 2022-04-01 | 08:00 | 123 | 6 | 2022-04-01 | 09:00 |  | 24 |  |  | Uttara(New)
32 | Cantonment | 132 | 145 | 20 | 2022-04-01 | 07:00 | 120 | 7 | 2022-04-01 | 13:00 |  | 25 |  |  | Kamrangirchar
33 | Chandpur | 132 | 142 | 16 | 2022-04-01 | 16:00 | 123 | 12 | 2022-04-01 | 02:00 |  | 26 |  |  | Savar
34 | Chandraghona | 132 | 140 | 20 | 2022-04-01 | 18:00 | 123 | 20 | 2022-04-01 | 07:00 |  | 27 |  |  | Bhasantec
35 | Chapai | 132 | 141 | 20 | 2022-04-01 | 05:00 | 120 | 26 | 2022-04-01 | 12:00 |  | 28 |  |  | Agargaon
36 | Charsaidpur | 132 | 144 | 20 | 2022-04-01 | 08:00 | 123 | 7 | 2022-04-01 | 13:00 |  | 29 |  |  | Satmosjid
37 | Chauddagram | 132 | 139 | 20 | 2022-04-01 | 11:00 | 124 | 12 | 2022-04-01 | 02:00 |  | 30 |  |  | Tongi
38 | Chhatak | 132 | 137 | 20 | 2022-04-01 | 04:00 | 125 | 13 | 2022-04-01 | 21:00 |  | 31 |  |  | Kabirpur
39 | Chowmuhani | 132 | 140 | 20 | 2022-04-01 | 11:00 | 117 | 12 | 2022-04-01 | 05:00 |  | 32 |  |  | Basundhara
40 | Chuadanga | 132 | 142 | 14 | 2022-04-01 | 20:00 | 110 | 1 | 2022-04-01 | 20:00 |  | 33 |  |  | Manikganj
41 | Coxsbazar | 132 | 131 | 20 | 2022-04-01 | 19:00 | 101 | 8 | 2022-04-01 | 01:00 |  | 34 |  |  | Joydevpur
42 | Cumilla(N) | 132 | 141 | 20 | 2022-04-01 | 08:00 | 128 | 27 | 2022-04-01 | 09:00 |  | 35 |  |  | New Tongi
43 | Cumilla(S) | 132 | 139 | 20 | 2022-04-01 | 09:00 | 111 | 22 | 2022-04-01 | 21:00 |  | 36 |  |  | Kodda
44 | Daudkandi | 132 | 142 | 20 | 2022-04-01 | 07:00 | 124 | 2 | 2022-04-01 | 16:00 |  | 37 |  |  | Dhamrai
45 | Dhaka | 132 | 140 | 20 | 2022-04-01 | 07:00 | 123 | 7 | 2022-04-01 | 10:00 |  | 38 |  |  | Rajendrapur
46 | Dhamrai | 132 | 147 | 20 | 2022-04-01 | 07:00 | 115 | 7 | 2022-04-01 | 13:00 |  | 39 |  |  | Valuka
47 | Dhanmondi | 132 | 144 | 20 | 2022-04-01 | 08:00 | 123 | 6 | 2022-04-01 | 12:00 |  | 40 |  |  | Tangail
48 | Dohazari | 132 | 138 | 20 | 2022-04-01 | 18:30 | 116 | 30 | 2022-04-01 | 11:00 |  | 41 |  |  | Mymensing
49 | Faridpur | 132 | 139 | 4 | 2022-04-01 | 08:00 | 118 | 25 | 2022-04-01 | 15:00 |  | 42 |  |  | Kishorganj
50 | Fatullah | 132 | 143 | 20 | 2022-04-01 | 08:00 | 121 | 7 | 2022-04-01 | 13:00 |  | 43 |  |  | Netrokona
51 | Fenchuganj | 132 | 141 | 20 | 2022-04-01 | 08:00 | 131 | 9 | 2022-04-01 | 14:00 |  | 44 |  |  | Jamalpur
52 | Feni | 132 | 140 | 20 | 2022-04-01 | 18:30 | 124 | 30 | 2022-04-01 | 13:00 |  | 45 |  |  | Sherpur
53 | Ghorashal | 132 | 142 | 10 | 2022-04-01 | 21:00 | 129 | 20 | 2022-04-01 | 22:00 |  | 46 |  |  | Srimongal
54 | Goalpara | 132 | 140 | 7 | 2022-04-01 | 18:30 | 126 | 22 | 2022-04-01 | 23:00 |  | 47 |  |  | Shahjibazar
55 | Gollamari | 132 | 141 | 22 | 2022-04-01 | 19:30 | 123 | 2 | 2022-04-01 | 19:30 |  | 48 |  |  | Fenchuganj
56 | Gopalganj | 132 | 142 | 20 | 2022-04-01 | 18:30 | 125 | 2 | 2022-04-01 | 19:30 |  | 49 |  |  | Khulawara
57 | Gopalganj_I | 132 | 143 | 22 | 2022-04-01 | 18:30 | 121 | 12 | 2022-04-01 | 03:00 |  | 50 |  |  | Sylhet
58 | Gulshan | 132 | 139 | 6 | 2022-04-01 | 03:00 | 123 | 3 | 2022-04-01 | 10:00 |  | 51 |  |  | Chattak
59 | Halishahar | 132 | 139 | 14 | 2022-04-01 | 11:00 | 122 | 20 | 2022-04-01 | 07:00 |  | 52 |  |  | Sunamganj
60 | Haripur | 132 | 143 | 20 | 2022-04-01 | 08:00 | 124 | 4 | 2022-04-01 | 12:00 |  | 53 |  |  | Biani Bazar
61 | HaripurSBU | 132 | 142 | 20 | 2022-04-01 | 08:00 | 122 | 7 | 2022-04-01 | 13:00 |  | 54 |  |  | Comilla(South)
62 | Hasnabad | 132 | 145 | 20 | 2022-04-01 | 07:00 | 125 | 6 | 2022-04-01 | 10:00 |  | ok |  |  | Comilla (North)
63 | Hathazari | 132 | 140 | 20 | 2022-04-01 | 15:00 | 126 | 10 | 2022-04-01 | 12:00 |  | 56 |  |  | Chandpur
64 | Ishurdi | 132 | 139 | 20 | 2022-04-01 | 07:00 | 130 | 12 | 2022-04-01 | 03:00 |  | 57 |  |  | Feni
65 | Jaldhaka | 132 | 143 | 30 | 2022-04-01 | 01:00 | 114 | 25 | 2022-04-01 | 21:00 |  | 58 |  |  | Chowmuhani
66 | Jamalpur | 132 | 145 | 20 | 2022-04-01 | 08:00 | 110 | 26 | 2022-04-01 | 23:00 |  | 59 |  |  | Ashuganj
67 | Jashore | 132 | 138 | 19 | 2022-04-01 | 09:00 | 122 | 1 | 2022-04-01 | 20:00 |  | 60 |  |  | Daudkandi
68 | Jhenaidah | 132 | 142 | 22 | 2022-04-01 | 18:00 | 112 | 25 | 2022-04-01 | 18:00 |  | 61 |  |  | Brahminbaria
69 | Jhenaidah | 132 | 142 | 20 | 2022-04-01 | 18:00 | 123 | 1 | 2022-04-01 | 22:00 |  | 62 |  |  | Ramganj
70 | Joydebpur | 132 | 145 | 20 | 2022-04-01 | 07:00 | 126 | 7 | 2022-04-01 | 12:00 |  | 63 |  |  | Chaddagram
71 | Joypurhat | 132 | 142 | 30 | 2022-04-01 | 01:00 | 107 | 16 | 2022-04-01 | 21:00 |  | 64 |  |  | PHP
72 | Juldah | 132 | 138 | 20 | 2022-04-01 | 18:00 | 122 | 30 | 2022-04-01 | 10:00
73 | Kabirpur | 132 | 146 | 20 | 2022-04-01 | 08:00 | 120 | 7 | 2022-04-01 | 19:00 |  | 65 |  |  | Kochua
74 | Kachua | 132 | 140 | 20 | 2022-04-01 | 10:00 | 124 | 12 | 2022-04-01 | 02:00 |  | 66 |  |  | Madanhat
75 | Kaliakoir | 132 | 139 | 19 | 2022-04-01 | 0.125 | 126 | 9 | 2022-04-01 | 15:00 |  | 67 |  |  | Hathazari
76 | Kallyanpur | 132 | 150 | 20 | 2022-04-01 | 07:00 | 121 | 6 | 2022-04-01 | 13:00 |  | 68 |  |  | Khulshi
77 | Kalurghat | 132 | 0 | #N/A | 2022-04-01 | #N/A | 0 | #N/A | 2022-04-01 | #N/A |  | 11 |  |  | Halishahar
78 | Kamrangirchar | 132 | 148 | 8 | 2022-04-01 | 20:00 | 123 | 7 | 2022-04-01 | 13:00 |  | 12 |  |  | Baraulia
79 | Kaptai | 132 | 137 | 20 | 2022-04-01 | 18:00 | 126 | 30 | 2022-04-01 | 16:00
80 | Kazla | 132 | 141 | 20 | 2022-04-01 | 08:00 | 118 | 26 | 2022-04-01 | 12:00
81 | Keranigonj | 132 | 143 | 3 | 2022-04-01 | 18:30 | 122 | 7 | 2022-04-01 | 13:00
82 | Khagrachori | 132 | 138 | 20 | 2022-04-01 | 11:00 | 123 | 20 | 2022-04-01 | 07:00
83 | Khulna | 132 | 140 | 29 | 2022-04-01 | 21:00 | 124 | 22 | 2022-04-01 | 23:00
84 | Khulna(S) | 132 | 140 | 24 | 2022-04-01 | 19:30 | 126 | 22 | 2022-04-01 | 23:00
85 | Khulshi | 132 | 137 | 20 | 2022-04-01 | 18:30 | 119 | 30 | 2022-04-01 | 11:00
86 | Kishoreganj | 132 | 143 | 20 | 2022-04-01 | 08:00 | 116 | 6 | 2022-04-01 | 17:00
87 | Kodda | 132 | 144 | 10 | 2022-04-01 | 21:00 | 120 | 5 | 2022-04-01 | 12:00
88 | KSRM | 132 | 139 | 18 | 2022-04-01 | 07:00 | 125.8 | 23 | 2022-04-01 | 05:00
89 | Kulaura | 132 | 139 | 20 | 2022-04-01 | 02:00 | 130 | 19 | 2022-04-01 | 21:00
90 | Kurigram | 132 | 143 | 30 | 2022-04-01 | 02:00 | 113 | 25 | 2022-04-01 | 21:00
91 | Kushtia | 132 | 139 | 22 | 2022-04-01 | 18:00 | 124 | 25 | 2022-04-01 | 15:00
92 | Lalbag | 132 | 143 | 3 | 2022-04-01 | 18:30 | 121 | 7 | 2022-04-01 | 13:00
93 | Lalmonirhat | 132 | 140 | 30 | 2022-04-01 | 02:00 | 116 | 25 | 2022-04-01 | 21:00
94 | Madanganj | 132 | 143 | 20 | 2022-04-01 | 08:00 | 125 | 6 | 2022-04-01 | 12:00
95 | Madaripur | 132 | 144 | 22 | 2022-04-01 | 18:30 | 122 | 18 | 2022-04-01 | 18:30
96 | Madartek | 132 | 143 | 20 | 2022-04-01 | 07:00 | 100 | 21 | 2022-04-01 | 06:00
97 | Madunaghat | 132 | 139 | 23 | 2022-04-01 | 05:00 | 124 | 30 | 2022-04-01 | 05:00
98 | Magura | 132 | 143 | 21 | 2022-04-01 | 05:00 | 107 | 25 | 2022-04-01 | 18:30
99 | Mahasthangarh | 132 | 141 | 30 | 2022-04-01 | 02:00 | 121 | 16 | 2022-04-01 | 21:00
100 | Manikganj | 132 | 136 | 15 | 2022-04-01 | 13:00 | 118 | 26 | 2022-04-01 | 11:00
101 | Maniknagar | 132 | 137 | 20 | 2022-04-01 | 07:00 | 119 | 7 | 2022-04-01 | 11:00
102 | Matarbari | 132 | 135 | 20 | 2022-04-01 | 12:00 | 100 | 12 | 2022-04-01 | 10:00
103 | Matuail | 132 | 144 | 20 | 2022-04-01 | 08:00 | 123 | 6 | 2022-04-01 | 12:00
104 | Millgate | 132 | 140 | 15 | 2022-04-01 | 13:00 | 115 | 7 | 2022-04-01 | 13:00
105 | Mirpur | 132 | 141 | 22 | 2022-04-01 | 02:00 | 119 | 6 | 2022-04-01 | 11:00
106 | Mithapukur | 132 | 141 | 30 | 2022-04-01 | 03:00 | 119 | 25 | 2022-04-01 | 21:00
107 | Modern | 132 | 137 | 7 | 2022-04-01 | 04:00 | 124 | 30 | 2022-04-01 | 09:00
108 | Mogbazar | 132 | 140 | 6 | 2022-04-01 | 04:00 | 124 | 7 | 2022-04-01 | 13:00
109 | Mongla | 132 | 138 | 29 | 2022-04-01 | 21:00 | 121 | 22 | 2022-04-01 | 22:00
110 | Motijheel | 132 | 142 | 20 | 2022-04-01 | 07:00 | 119 | 6 | 2022-04-01 | 12:00
111 | Munshiganj | 132 | 142 | 20 | 2022-04-01 | 08:00 | 124 | 7 | 2022-04-01 | 13:00
112 | Mymensingh | 132 | 144 | 20 | 2022-04-01 | 08:00 | 110 | 4 | 2022-04-01 | 20:00
113 | Naogaon | 132 | 140 | 20 | 2022-04-01 | 05:00 | 110 | 16 | 2022-04-01 | 21:00
114 | Narail | 132 | 142 | 22 | 2022-04-01 | 18:30 | 108 | 25 | 2022-04-01 | 19:00
115 | Narinda | 132 | 0 | 1 | 2022-04-01 | 00:00 | 0 | #VALUE! | 2022-04-01 | 00:00
116 | Narshingdi | 132 | 143 | 20 | 2022-04-01 | 08:00 | 114 | 7 | 2022-04-01 | 13:00
117 | Natore | 132 | 140 | 20 | 2022-04-01 | 05:00 | 124 | 25 | 2022-04-01 | 21:00
118 | Nawabganj | 132 | 142 | 1 | 2022-04-01 | 18:00 | 125 | 7 | 2022-04-01 | 11:00
119 | Netrakona | 132 | 139 | 20 | 2022-04-01 | 08:00 | 110 | 3 | 2022-04-01 | 21:00
120 | New | 132 | 145 | 20 | 2022-04-01 | 07:00 | 122 | 4 | 2022-04-01 | 15:00
121 | Niamatpur | 132 | 142 | 30 | 2022-04-01 | 02:00 | 102 | 16 | 2022-04-01 | 21:00
122 | Noapara | 132 | 140 | 24 | 2022-04-01 | 19:30 | 125 | 22 | 2022-04-01 | 23:00
123 | Pabna | 132 | 139 | 20 | 2022-04-01 | 07:00 | 123 | 15 | 2022-04-01 | 21:00
124 | Palashbari | 132 | 140 | 30 | 2022-04-01 | 02:00 | 117 | 16 | 2022-04-01 | 15:00
125 | Panchagarh | 132 | 144 | 30 | 2022-04-01 | 03:00 | 110 | 27 | 2022-04-01 | 18:00
126 | Patuakhali | 132 | 141 | 19 | 2022-04-01 | 13:00 | 121 | 18 | 2022-04-01 | 19:00
127 | PHP | 132 | 140 | 20 | 2022-04-01 | 10:00 | 122 | 30 | 2022-04-01 | 05:00
128 | Purbachal | 132 | 139 | 10 | 2022-04-01 | 04:00 | 118 | 7 | 2022-04-01 | 13:00
129 | Purbasadipur | 132 | 144 | 30 | 2022-04-01 | 01:00 | 110 | 10 | 2022-04-01 | 03:00
130 | Rahim | 132 | 143 | 20 | 2022-04-01 | 08:00 | 124 | 4 | 2022-04-01 | 12:00
131 | Rajbari | 132 | 140 | 22 | 2022-04-01 | 18:30 | 114 | 25 | 2022-04-01 | 13:00
132 | Rajendrapur | 132 | 143 | 20 | 2022-04-01 | 08:00 | 104 | 8 | 2022-04-01 | 01:00
133 | Rajshahi | 132 | 143 | 20 | 2022-04-01 | 05:00 | 122 | 26 | 2022-04-01 | 12:00
134 | Rajshahi | 132 | 143 | 20 | 2022-04-01 | 05:00 | 123 | 26 | 2022-04-01 | 09:00
135 | Ramganj | 132 | 140 | 20 | 2022-04-01 | 10:00 | 118 | 12 | 2022-04-01 | 02:00
136 | Rampur | 132 | 137 | 20 | 2022-04-01 | 11:00 | 121 | 30 | 2022-04-01 | 11:00
137 | Rampura | 132 | 140 | 11 | 2022-04-01 | 03:00 | 124 | 3 | 2022-04-01 | 12:00
138 | Rangamati | 132 | 140 | 20 | 2022-04-01 | 18:30 | 123 | 20 | 2022-04-01 | 07:00
139 | Rangpur | 132 | 141 | 20 | 2022-04-01 | 04:00 | 116 | 25 | 2022-04-01 | 21:00
140 | Ruppur | 132 | 139 | 29 | 2022-04-01 | 21:00 | 130 | 15 | 2022-04-01 | 23:00
141 | Saidpur | 132 | 140 | 30 | 2022-04-01 | 01:00 | 116 | 25 | 2022-04-01 | 21:00
142 | Satkhira | 132 | 140 | 29 | 2022-04-01 | 21:00 | 122 | 22 | 2022-04-01 | 23:00
143 | Satmasjid | 132 | 144 | 20 | 2022-04-01 | 07:00 | 123 | 6 | 2022-04-01 | 12:00
144 | Savar | 132 | 143 | 20 | 2022-04-01 | 18:30 | 120 | 2 | 2022-04-01 | 16:00
145 | Shahjadpur | 132 | 142 | 29 | 2022-04-01 | 21:00 | 106 | 14 | 2022-04-01 | 12:00
146 | Shahjibazar | 132 | 143 | 20 | 2022-04-01 | 02:00 | 125 | 26 | 2022-04-01 | 17:00
147 | Shahmirpur | 132 | 137 | 1 | 2022-04-01 | 07:00 | 121 | 30 | 2022-04-01 | 11:00
148 | Shariatpur | 132 | 143 | 22 | 2022-04-01 | 19:00 | 121 | 18 | 2022-04-01 | 19:00
149 | Sherpur | 132 | 144 | 20 | 2022-04-01 | 07:00 | 107 | 14 | 2022-04-01 | 17:00
150 | Shikalbaha | 132 | 139 | 8 | 2022-04-01 | 18:30 | 123 | 2 | 2022-04-01 | 20:00
151 | Shikalbaha | 132 | 139 | 23 | 2022-04-01 | 10:00 | 121 | 20 | 2022-04-01 | 07:00
152 | Shitalakhya | 132 | 144.2 | 20 | 2022-04-01 | 08:00 | 123 | 7 | 2022-04-01 | 13:00
153 | Sholosohor | 132 | 0 | #N/A | 2022-04-01 | #N/A | 0 | #N/A | 2022-04-01 | #N/A
154 | Shyampur | 132 | 145 | 20 | 2022-04-01 | 08:00 | 124 | 11 | 2022-04-01 | 11:00
155 | Shyampur | 132 | 142 | 20 | 2022-04-01 | 08:00 | 120 | 7 | 2022-04-01 | 13:00
156 | Siddhirganj | 132 | 141 | 20 | 2022-04-01 | 08:00 | 124 | 6 | 2022-04-01 | 12:00
157 | Sirajganj | 132 | 141 | 30 | 2022-04-01 | 03:00 | 108 | 14 | 2022-04-01 | 13:00
158 | Sonargaon | 132 | 142 | 20 | 2022-04-01 | 07:00 | 125 | 6 | 2022-04-01 | 17:00
159 | Sreemongol | 132 | 142 | 20 | 2022-04-01 | 08:00 | 130 | 6 | 2022-04-01 | 23:00
160 | Srinagar | 132 | 141 | 1 | 2022-04-01 | 17:00 | 126 | 7 | 2022-04-01 | 11:00
161 | SSM | 132 | 141 | 20 | 2022-04-01 | 10:00 | 122 | 30 | 2022-04-01 | 11:00
162 | Sunamganj | 132 | 137 | 20 | 2022-04-01 | 02:00 | 122 | 9 | 2022-04-01 | 21:00
163 | Sylhet | 132 | 137 | 20 | 2022-04-01 | 02:00 | 128 | 9 | 2022-04-01 | 15:00
164 | Tangail | 132 | 142 | 20 | 2022-04-01 | 07:00 | 119 | 4 | 2022-04-01 | 20:00
165 | Thakurgaon | 132 | 144 | 30 | 2022-04-01 | 01:00 | 109 | 27 | 2022-04-01 | 18:00
166 | TK | 132 | 137 | 4 | 2022-04-01 | 18:00 | 123 | 30 | 2022-04-01 | 11:00
167 | Tongi | 132 | 140 | 7 | 2022-04-01 | 05:00 | 120 | 6 | 2022-04-01 | 07:00
168 | Ullon | 132 | 140 | 11 | 2022-04-01 | 03:00 | 123 | 3 | 2022-04-01 | 10:00
169 | Uttara | 132 | 139 | 17 | 2022-04-01 | 02:00 | 120 | 6 | 2022-04-01 | 11:00
170 | UttaraNew | 132 | 140 | 21 | 2022-04-01 | 00:00 | 119 | 7 | 2022-04-01 | 13:00
171 | Zigatola | 132 | 142 | 20 | 2022-04-01 | 08:00 | 123 | 7 | 2022-04-01 | 13:00

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: April 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 51 | 152
Hasnabad | TR2 | 225 | 51 | 152 | 01.04.2022 | 24:00
| TR3 | 225 | 51 | 152
| TR1 | 225 | 195 | 570 | 26.04.2022 | 13:00
Tongi | TR2 | 225 | 195 | 570
| TR3 | 225 | 195 | 570
Haripur | TR1 | 225 | 117 | 340
| TR2 | 225 | 117 | 340 | 12.04.2022 | 09:00
| TR3 | 225 | 117 | 340
| TR1 | 225 | 199 | 555
Rampura | TR2 | 225 | 199 | 560 | 25.04.2022 | 14:00
| TR3 | 225 | 199 | 560
Keraniganj | ATR1 | 300 | 123 | 351
| ATR2 | 300 | 123 | 351 | 11.04.2022 | 21:00
| ATR3 | 300 | 123 | 351
| TR1 | 225 | 176 | 518
Aminbazar | TR2 | 225 | 176 | 518 | 09.04.2022 | 14:00
| TR3 | 225 | 181 | 536
Agargaon | TR1 | 300 | 184 | 524
| TR2 | 300 | 184 | 524 | 26.04.2022 | 19:00
Maniknagar | TR1 | 300 | 157 | 490 | 26.04.22 | 13:00
| TR2 | 300 | 157 | 490
Cumilla (N) | TR1 | 225 | 174 | 480 | 28.04.22 | 7:00
| TR2 | 225 | 170 | 472
Fenchuganj | AT2 | 300 | 267 | 719 | 25.04.22 | 19:00
| MT1 | 150 | 106 | 303
Hathazari | MT2 | 150 | 106 | 303 | 13.04.22 | 20:00
| MT3 | 150 | 106 | 303
| MT4 | 150 | 106 | 303
| TR1 | 225 | 116 | 357
Ishurdi | TR2 | 225 | 116 | 357 | 25.04.22 | 14:44
| TR3 | 225 | 116 | 357
Khulna(S) | TR1 | 225 | 114 | 299
| TR2 | 225 | 114 | 299 | 24.04.22 | 5:00
| TR3 | 300 | 146 | 383
Bogura | TR1 | 225 | 136 | 383 | 18.04.22 | 22:00
| TR2 | 225 | 136 | 383
| TR3 | 225 | 184 | 510
Baghabari | TR1 | 300 | 188 | 526 | 18.04.22 | 20:00
| TR2 | 225 | 141 | 394
Rajshahi | ATR-01 | 300 | 155 | 452 | 14.04.2022 | 4:00
| ATR-02 | 300 | 155 | 452
Barapukuria | TR1 | 225 | 171 | 800 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 152 | 730 | 16.04.2022 | 2100:0 PM | 132 kV current is being provided
| TR6 | 300 | 118 | 951
Bheramara | Transformer-1 | 225 | 105 | 271 | 25.04.2022 | 3:00
| Transformer-2 | 225 | 105 | 271
Shyampur | ATR-01 | 300 | 102 | 285 | 12.04.2022 | 9:00
| ATR-02 | 300 | 102 | 285
Kaliakoir | TR1 | 300 | 134 | 354 | 27.04.2022 | 9:00
Sikalbaha | ATR-1 | 300 | 203 | 531 | 24.04.2022 | 10:00
| ATR-2 | 300 | 203 | 531
Jhenaidah | T1(230/132 kV) | 300 | 185 | 901 | 21.04.2022 | 22:00
| T2(230/132 kV) | 300 | 185 | 901
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:April 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 288.9 | 441.2 | 24.04.2022 | 10:00
| TR2(400/230 kV) | 520 | 292.2 | 442.7
| TR1(400/132 kV) | 325 | 311.7 | 522 | 19.04.2022 | 19:00
| TR2(400/132 kV) | 325 | 311.9 | 525
Bibiyana | ICT1(400/230 kV) | 520 | 147 | 218 | 29.04.2022 | 22:00
| ICT2(400/230kV) | 520 | 151 | 222 | 10.04.2022 | 19:00
Bhulta | ATR1(400/230 kV) | 520 | 237 | 417 | 09.04.2022 | 9:00
| ATR2(400/230kV) | 520 | 237 | 417
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 380 | 616 | 20.04.2022 | 12:37
Gopalganj | ATR1(400/138 kV) | 325 | 290 | 418 | 28.04.2022 | 22:00
| ATR2(400/138kV) | 325 | 290 | 418
Payra | GSUT1 | 270 | 185.58 | 799.72 | 28.04.2022 | 22:00
| GSUT2 | 270 | 194.65 | 838.15
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:April 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-04-01 | 12585 | 12585 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-01 | 10180 | 10180 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-02 | 13718 | 13718 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-02 | 10811 | 10811 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-03 | 13130 | 13130 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-03 | 11724 | 11724 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-04 | 13712 | 13712 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-04 | 11058 | 11058 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-05 | 13986 | 13986 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-05 | 11914 | 11914 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-06 | 13635 | 13635 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-06 | 11856 | 11856 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-07 | 14008 | 14351 | 350 | 22:00 | 20 | - | 60 | 100 | 20 | 130 | - | - | 20 | - | 2022-04-07 | 10673 | 10673 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-08 | 13442 | 13442 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-08 | 10673 | 10673 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-09 | 13906 | 13906 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-09 | 11742 | 11742 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-10 | 12853 | 12853 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-10 | 11613 | 11613 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-11 | 13832 | 13832 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-11 | 11129 | 11129 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-12 | 14423 | 14423 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-12 | 11626 | 11626 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-13 | 14178 | 14178 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-13 | 11832 | 11832 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-14 | 13465 | 13465 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-14 | 10842 | 10842 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-15 | 13860 | 13860 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-15 | 11031 | 11031 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-16 | 14782 | 14782 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-16 | 11701 | 11701 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-17 | 14387 | 14387 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-17 | 12346 | 12346 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-18 | 14470 | 14470 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-18 | 12320 | 12320 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-19 | 14419 | 14419 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-19 | 12322 | 12322 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-20 | 10043 | 10043 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-20 | 6920 | 6920 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-21 | 13046 | 13046 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-21 | 9731 | 9731 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-22 | 9317 | 9317 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-22 | 9263 | 9263 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-23 | 13766 | 13766 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-23 | 10383 | 10383 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-24 | 13975 | 13975 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-24 | 11995 | 11995 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-25 | 14714 | 14714 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-25 | 12633 | 12633 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-26 | 14716 | 14716 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-26 | 12895 | 12895 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-27 | 14635 | 14635 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-27 | 12323 | 12323 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-28 | 14544 | 14544 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-28 | 12764 | 12764 | - | - | - | - | - | - | - | - | - | - | - | -
2022-04-29 | 13079 | 13079 | - | - | [10 empty] | 2022-04-29 | 11516 | 11516
2022-04-30 | 11464 | 11464 | - | - | [10 empty] | 2022-04-30 | 9186 | 9186
| Max. L/S | - | - | -
Day Peak | Min. L/S | - | - | -
| No. of Days | - | - | -
| Max. L/S | - | - | -
Full Day | Min. L/S | - | - | -
| No. of Days | -
| Average L/S | #DIV/0!
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14782 | 2022-04-16 | 21:00
2 | Maximum Day Peak Genaration | MW | 12895 | 2022-04-26 | 12:00
3 | Maximum Evening Peak Demand | MW | 14782 | 2022-04-16 | 12:00
4 | Minimum Generation | MW | 4262 | 2022-04-20 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13536.3333
6 | Average of the daily day peak Genaration | MW | 11233.4
7 | Maximum load shed | MW | 350 | 2022-04-07 | 22:00
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 1
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 11.6667
11 | Total Generation | MkWh | 8685.7484
12 | Total Generation by BPDB | MkWh | 1929.4341 | % of total Gen. | 22.21%
13 | Total Generation by IPP | MkWh | 3147.6574 | '' | 36.24%
14 | A) Total Generation by Generation Companies | MkWh | 2107.7383 | '' | 24.27%
| B) Total Generation by REB | MkWh | 131.5194 | " | 1.514%
| C) Total Generation by RENTAL | MkWh | 614.893 | " | 7.079%
| D) Total Imported from India (BIPTC) | MkWh | 654.6028 | " | 7.537%
| E) Total Imported from Tripura, India (A.C) | MkWh | 99.9034 | " | 1.15%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4240.1479 | % of total Gen. | 48.82%
| B) Oil | MkWh | 2999.7195 | '' | 34.54%
| C) Hydro | MkWh | 45.2279 | '' | 0.5207%
| D) Solar | MkWh | 36.5217 | '' | 0.4205%
| E) Coal | MkWh | 609.6252 | '' | 7.019%
| F) BIPTC (Import from India) | MkWh | 654.6028 | '' | 7.537%
| G) A.C (Import from Tripura, India) | MkWh | 99.9034 | '' | 1.15%
16 | Maximun of the daily total Generation . | MkWh | 383.5628 | 2022-04-12
17 | Monthly Load factor | % | 87.447
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 35124.1625
| A) Gas | M.Taka | 4213.1872
| B) Liquid fuel | M.Taka | 24177.1034
| C) Coal | M.Taka | 2678.0913
| D) BIPTC (Import from India) | M.Taka | 3338.4745
| E) Tripura(Import from India) | M.Taka | 717.3061
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1403.9196 | 2022-04-19
| A) Gas | M.Taka | 242.8168 | 2022-04-05
| B) Liquid fuel | M.Taka | 1182.9036 | 2022-04-18
| C) Coal | M.Taka | 149.9171 | 2022-04-19
| D) BIPTC (Import from India) | M.Taka | 114.01 | 2022-04-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.7297
| B) Excluding Hydro & Solar | Taka/kWhR | 5.7836
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.4 | 30/04/2022 | 06:00
b) | Actual | FT (MSL) | 75.66 | 30/04/2022 | 06:00
22 | Peak Genaration of April 2021 | MW | 13792 | 2021-04-27 | 20:00
23 | Peak Demand of April 2021 | MW | 14097 | 2021-04-27 | 19:00
24 | Maximum peak Generation recorded upto 30/04/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 30/04/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 30/04/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.