## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-10 | Friday
|  | Date (day): | 2022-06-10 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13840.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14349 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-09 | 2022-06-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 280 | 280 | 280 |  | 85 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 95 | 98 | 98
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 404 | 409 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 340 | 346 | 340 | 340
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 80 | 83 | 90 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 125 | 132 | 150 | 150 | 185 |  | FGMO & Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 93 | 94 | 0 | 0 |  | 102 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M & gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 78 | 91 | 91 | 91 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 68 | 84 | 93 | 93 |  | 9 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 150 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55 |  | 20
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 41 | 52 | 52 |  | 28 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  |  | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 48 | 50 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 293 | 270 | 285 | 285 |  | 15 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 109 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 25 | 0 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 25 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 134 | 130 | 135
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 90 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 83 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
| Dhaka area Total |  |  |  |  | 6263 | 5898 | 3313 | 3339 | 3881 | 3856 | 1006 | 957
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 4 | 15 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 4 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 37 | 44 | 44 |  | 7 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 32 | 32 | 35 | 35 |  | 195 | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 87 | 105 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 90 | 90 |  | 20 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 23 | 15 | 35
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 22 | 43 | 71 | 71 |  | 37 | Engine problem
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 230 | 190 | 285 | 285 |  |  | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 92 | 110 | 110
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 110 | 110
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 1104 | 1116 | 1281 | 1327 | 311 | 742
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 215 | 210 | 210 | 36 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 300 | 330 | 30 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 37 | 37 | 37 |  | 8 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 55 | 55 | 55
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 146 | 140 | 140 |  | 10 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 32 | 50 | 50
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 136 | 200 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 100 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 30 | 0 | 150 | 200
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 114 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 94 | 50 | 94 |  |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 76 | 100 | 100 | 100 |  | 15 | Engine problem
| Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1198 | 1376 | 1640 | 1786 | 905 | 215
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 87 | 109 | 100 | 110 | 92 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 20 | 20
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 140 | 130 | 190 | 200
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 92 | 105 | 105 |  |  | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 3 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 14 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 252 | 375 | 488.6 | 457 | 92 | 8
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem.
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 44 | 46 | 44 | 44
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 62 | 62
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 78 | 78 | 78
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 42 | 41 | 42
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 265 | 310 | 341 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 398 | 401 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 389 | 360 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1623 | 1564 | 1643 | 1675 | 330 | 460
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 922 | 923 | 940 | 940
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 61 | 95 | 95
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 35 | 45 |  | 9 | Engine problem
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 40 | 40 | 150 | 150
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 80 | 0 | 80 |  | 29 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 250 | 250 | 250 | 160 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 90 | 90 | 105
117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 80 | 105 | 105
118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 60 | 0 | 100 | 0
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1303 | 1609 | 1805 | 1910 | 160 | 38
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 48 | 48 |  |  | Rampal Transformar O/L
120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 20 | 23 | 20 | 33
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 73 | 81 | 81 | 113 |  | Gas shortage & GT-2 S/D
122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 780 | 1050 | 1050
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 165 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 938 | 1145 | 1436 | 1449 | 113 | 0
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 34 | 34 |  | 18 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 9 | 0 | 10 |  | 61 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 |  | 7 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 214 | 200 | 215 | -5 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 210 | 210 | 220 |  | HSD running
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 370 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 30 | 40 |  | 10 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 65 | 90 |  | 14 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 190 |  |  | Engine problem
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 80 | 94 | 94 |  | 19 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 76 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 702 | 1180 | 1336 | 1517 | 606 | 147
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 100 | 75 | 100 |  |  | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 72 | 72 | 72 |  | 43 | Engine problem
| Rangpur Area Total |  |  |  |  | 800 | 720 | 244 | 347 | 330 | 372 | 184 | 128
| Total |  |  |  |  | 22348 | 21584 | 10677 | 12051 | 13840.6 | 14349 | 3707 | 2695
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10384.9618 | 11721.38 | 13462.0307 | 13956.5249
A. |  | 2022-06-09 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 13310 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10338 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12051 | MW
3 | Day peak Generation : |  |  | 10677 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11721.38 | MW
4 | Evening peak Generation : |  |  | 12051 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 271.3631 | MKWHr | By Solar | 0.55238 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 130.058 | MKWHr |  | By Oil: | 89.5677 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 25.5563 | MKWHr |  | By Hydro: | 0.76326 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3707 | MW | Dhaka | 4393.63 | 4393.63 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2695 | MW | Chittagong | 1329.15 | 1329.15 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 6402 | MW | Khulna | 1431 | 1431 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 983.12 | MMCFD |  |  | Rajshahi | 1162.6 | 1162.6 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 149561364.21 | ii) Oil : | Taka | 1210743951.35 | Comilla | 934 | 934 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 214322063 | Total | Taka | 1574627378.56 | Mymensingh | 900 | 900 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 486 | 486 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 390 | MW (E to W) at | 19:30 | hrs | Barisal | 277 | 277 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 330 | MW at | 13:00 | hrs | Rangpur | 808 | 808 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 11721.38 | 11721.38 |  | 0
B. |  | 2022-06-10 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 36.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14349 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 1649 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 258.9265 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8452 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3127 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5526 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 71.72 |  | (b) Today: | 71.62 |  | (c) Rule Curve: |  | 78.34
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 402 | 320 |  | 0 | 225 | 140 | 88 | 94 | 55 | 0 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 70 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 210 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 38 | 8 | 19 | 8 | 33 | 19 | 120 | 134 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 56 | 78 | 0 | 0 | 19 | 41 | 10 | 280 | 16 | 11 | 200 | 296 | 202 | 98 | 186 | 97 | 149 | 0 | 90 | 104 | 138 | 401 | 83 | 105 | 105 | 0 | 247 | 54 | 103 | 17 | 13 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 96 | 55 |  | 923 | 0 | 190 | 0 | 94 | 145 | 0 | 0 | 32 | 66 | 40 | 84 | 34 | 48 | 0 | 0 | 0 | 32 | 10 | 89 | 0 | 34 | 16 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 215 | 0 | 30 | 0 | 0 | 420 | 93 | 50 | 94 | 105 | 74 | 0 | 0 | 76 | 1070 | 215 | 0 | 17 | 0 | 0 | 34 |  | 8527 | 4783 | 13310 | 3319 | 923 | 2221 | 677 | 3943 | 1245 | 32 | 360 | 685 | 120 | 0 | 0 | 71.75
2:00 | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 404 | 330 |  | 0 | 225 | 142 | 89 | 94 | 45 | 0 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 71 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 209 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 39 | 8 | 16 | 8 | 33 | 19 | 120 | 127 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 56 | 78 | 0 | 0 | 19 | 41 | 10 | 290 | 16 | 11 | 200 | 296 | 21 | 50 | 186 | 50 | 149 | 0 | 90 | 85 | 135 | 402 | 83 | 105 | 105 | 0 | 247 | 54 | 110 | 17 | 4 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 91 | 55 |  | 923 | 0 | 195 | 0 | 94 | 145 | 0 | 0 | 32 | 66 | 40 | 84 | 34 | 32 | 0 | 0 | 0 | 32 | 10 | 89 | 0 | 34 | 16 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 201 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 414 | 93 | 0 | 94 | 105 | 74 | 0 | 0 | 76 | 1030 | 215 | 0 | 17 | 0 | 0 | 34 |  | 8229 | 4646 | 12875 | 3317 | 923 | 2237 | 321 | 3890 | 1205 | 32 | 359 | 685 | 120 | 0 | 0 | 71.74
3:00 | 0 | 0 | 0 | 180 | 250 | 96 | 0 | 408 | 330 |  | 0 | 225 | 140 | 88 | 94 | 55 | 0 | 0 | 0 | 90 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 71 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 210 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 40 | 8 | 16 | 8 | 33 | 19 | 116 | 130 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 56 | 78 | 0 | 0 | 19 | 41 | 10 | 290 | 16 | 11 | 200 | 296 | 0 | 0 | 200 | 0 | 138 | 0 | 90 | 85 | 135 | 400 | 93 | 105 | 105 | 0 | 247 | 54 | 110 | 17 | 8 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 94 | 55 |  | 923 | 0 | 200 | 0 | 94 | 145 | 0 | 0 | 32 | 66 | 40 | 84 | 33 | 32 | 0 | 0 | 0 | 32 | 0 | 89 | 0 | 34 | 16 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 201 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 421 | 93 | 0 | 94 | 105 | 74 | 0 | 0 | 76 | 1010 | 214 | 0 | 17 | 0 | 0 | 34 |  | 8137 | 4627 | 12764 | 3328 | 923 | 2240 | 200 | 3918 | 1185 | 32 | 360 | 677 | 116 | 0 | 0 | 71.74
4:00 | 0 | 0 | 0 | 180 | 250 | 92 | 0 | 407 | 326 |  | 0 | 225 | 135 | 89 | 94 | 55 | 0 | 0 | 0 | 90 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 51 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 211 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 40 | 8 | 16 | 8 | 33 | 19 | 114 | 130 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 56 | 78 | 0 | 0 | 19 | 41 | 10 | 270 | 16 | 11 | 200 | 293 | 0 | 0 | 184 | 0 | 132 | 0 | 90 | 85 | 128 | 400 | 93 | 105 | 105 | 0 | 247 | 54 | 110 | 17 | 0 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 98 | 55 |  | 923 | 0 | 205 | 0 | 95 | 145 | 0 | 0 | 0 | 0 | 40 | 56 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 89 | 0 | 34 | 0 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 203 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 422 | 93 | 0 | 94 | 105 | 74 | 0 | 0 | 76 | 1000 | 203 | 0 | 17 | 0 | 0 | 34 |  | 8030 | 4473 | 12503 | 3307 | 923 | 2196 | 200 | 3865 | 1175 | 32 | 361 | 546 | 114 | 0 | 0 | 71.73
5:00 | 0 | 0 | 0 | 180 | 250 | 92 | 0 | 408 | 326 |  | 0 | 225 | 138 | 89 | 92 | 55 | 0 | 0 | 0 | 90 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 43 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 212 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 40 | 8 | 16 | 8 | 33 | 19 | 110 | 134 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 57 | 78 | 0 | 0 | 19 | 41 | 10 | 280 | 16 | 11 | 120 | 288 | 0 | 0 | 185 | 0 | 132 | 0 | 90 | 85 | 130 | 400 | 86 | 105 | 105 | 0 | 228 | 54 | 102 | 17 | 0 | 100 | 400 | 104 | 0 | 154 | 90 | 0 | 35 | 0 | 87 | 55 |  | 923 | 0 | 205 | 0 | 95 | 145 | 0 | 0 | 0 | 0 | 40 | 86 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 213 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 422 | 93 | 0 | 94 | 105 | 75 | 0 | 0 | 76 | 1000 | 213 | 0 | 17 | 0 | 0 | 34 |  | 7875 | 4330 | 12205 | 3362 | 923 | 2218 | 120 | 3767 | 1175 | 32 | 360 | 353 | 110 | 0 | 0 | 71.73
6:00 | 0 | 0 | 0 | 180 | 250 | 91 | 0 | 406 | 300 |  | 0 | 225 | 130 | 88 | 92 | 55 | 0 | 0 | 0 | 50 | 48 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 31 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 300 | 213 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 40 | 8 | 16 | 8 | 33 | 19 | 102 | 135 | 0 | 20 | 0 | 44 | 41 | 53 | 47 | 110 | 0 | 57 | 78 | 0 | 0 | 19 | 41 | 10 | 260 | 16 | 11 | 0 | 281 | 0 | 0 | 160 | 0 | 132 | 1 | 90 | 85 | 130 | 365 | 32 | 105 | 105 | 0 | 193 | 54 | 110 | 17 | 0 | 100 | 352 | 104 | 1 | 120 | 90 | 0 | 35 | 0 | 89 | 41 |  | 923 | 0 | 205 | 0 | 95 | 145 | 0 | 0 | 0 | 0 | 40 | 78 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 180 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 383 | 53 | 0 | 94 | 50 | 75 | 0 | 0 | 76 | 970 | 213 | 0 | 17 | 0 | 4 | 34 |  | 7252 | 4126 | 11378 | 3238 | 923 | 2119 | 0 | 3379 | 1145 | 32 | 362 | 289 | 102 | 6 | 0 | 71.72
7:00 | 0 | 0 | 0 | 180 | 250 | 91 | 0 | 407 | 300 |  | 0 | 225 | 132 | 89 | 94 | 55 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 32 | 0 | 31 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 11 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 300 | 212 | 8 | 0 | 27 | 40 | 0 | 44 | 0 | 0 | 8 | 16 | 8 | 33 | 19 | 102 | 128 | 0 | 20 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 56 | 78 | 0 | 0 | 18 | 41 | 10 | 265 | 24 | 11 | 0 | 195 | 0 | 0 | 130 | 0 | 113 | 6 | 90 | 85 | 132 | 364 | 32 | 70 | 105 | 2 | 150 | 54 | 110 | 17 | 0 | 100 | 360 | 91 | 2 | 108 | 90 | 0 | 35 | 0 | 96 | 35 |  | 923 | 0 | 205 | 0 | 66 | 145 | 0 | 0 | 0 | 0 | 16 | 78 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 180 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 383 | 53 | 0 | 50 | 50 | 54 | 0 | 0 | 76 | 940 | 213 | 0 | 17 | 0 | 15 | 34 |  | 6850 | 3988 | 10838 | 3243 | 923 | 2123 | 0 | 2914 | 1115 | 31 | 362 | 217 | 102 | 25 | 0 | 71.72
8:00 | 0 | 0 | 0 | 180 | 250 | 92 | 0 | 407 | 300 |  | 0 | 225 | 135 | 89 | 94 | 55 | 0 | 0 | 0 | 50 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 38 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 13 | 44 | 22 | 11 | 0 | 0 | 0 | 0 | 300 | 209 | 8 | 0 | 27 | 48 | 0 | 44 | 0 | 0 | 8 | 16 | 8 | 33 | 18 | 104 | 109 | 0 | 20 | 0 | 43 | 41 | 53 | 44 | 110 | 0 | 55 | 78 | 0 | 0 | 18 | 41 | 10 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 139 | 0 | 109 | 7 | 63 | 85 | 123 | 399 | 32 | 70 | 105 | 0 | 150 | 54 | 110 | 17 | 0 | 70 | 395 | 92 | 7 | 108 | 90 | 0 | 35 | 0 | 84 | 37 |  | 922 | 0 | 220 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 8 | 86 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 181 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 303 | 35 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 800 | 174 | 0 | 17 | 0 | 25 | 34 |  | 6863 | 3475 | 10338 | 3304 | 922 | 1996 | 0 | 2709 | 975 | 32 | 225 | 217 | 104 | 39 | 0 | 71.71
9:00 | 0 | 0 | 0 | 180 | 250 | 90 | 0 | 408 | 302 |  | 0 | 225 | 148 | 80 | 93 | 55 | 0 | 0 | 0 | 74 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 13 | 44 | 22 | 5 | 0 | 0 | 0 | 0 | 300 | 211 | 8 | 0 | 27 | 50 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 32 | 18 | 108 | 70 | 0 | 20 | 1 | 44 | 41 | 53 | 44 | 110 | 0 | 61 | 75 | 0 | 0 | 18 | 41 | 10 | 275 | 24 | 11 | 0 | 250 | 0 | 0 | 170 | 0 | 125 | 7 | 90 | 85 | 123 | 401 | 32 | 80 | 105 | 3 | 230 | 54 | 110 | 17 | 8 | 80 | 400 | 90 | 13 | 141 | 90 | 0 | 35 | 0 | 77 | 55 |  | 923 | 0 | 200 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 8 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 252 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 680 | 163 | 0 | 17 | 0 | 54 | 34 |  | 7205 | 3136 | 10341 | 3228 | 923 | 1943 | 0 | 2971 | 855 | 32 | 170 | 162 | 108 | 79 | 0 | 71.71
10:00 | 0 | 0 | 0 | 180 | 250 | 90 | 0 | 404 | 340 |  | 0 | 225 | 125 | 80 | 93 | 55 | 0 | 0 | 0 | 78 | 68 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 4 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 90 | 22 | 43 | 22 | 4 | 0 | 0 | 0 | 0 | 300 | 197 | 8 | 0 | 34 | 49 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 30 | 15 | 106 | 87 | 0 | 0 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 60 | 72 | 0 | 0 | 18 | 39 | 10 | 310 | 24 | 11 | 30 | 293 | 109 | 25 | 140 | 25 | 132 | 4 | 90 | 85 | 125 | 398 | 8 | 105 | 105 | 4 | 230 | 54 | 110 | 17 | 8 | 100 | 389 | 83 | 3 | 162 | 90 | 0 | 35 | 0 | 76 | 55 |  | 922 | 0 | 225 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 650 | 165 | 0 | 0 | 0 | 60 | 34 |  | 7490 | 3187 | 10677 | 3178 | 922 | 2087 | 189 | 3080 | 825 | 32 | 170 | 146 | 106 | 72 | 0 | 71.7
11:00 | 0 | 0 | 0 | 180 | 250 | 91 | 0 | 406 | 342 |  | 0 | 225 | 140 | 81 | 93 | 55 | 0 | 0 | 0 | 80 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 8 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 18 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 90 | 61 | 43 | 22 | 4 | 0 | 0 | 0 | 0 | 270 | 181 | 8 | 0 | 34 | 47 | 0 | 44 | 0 | 0 | 8 | 16 | 8 | 28 | 14 | 114 | 87 | 0 | 17 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 60 | 75 | 0 | 0 | 18 | 38 | 10 | 260 | 24 | 11 | 10 | 293 | 12 | 25 | 45 | 25 | 132 | 13 | 90 | 85 | 123 | 359 | 8 | 52 | 101 | 5 | 230 | 54 | 96 | 17 | 8 | 100 | 350 | 71 | 3 | 162 | 90 | 0 | 35 | 0 | 67 | 55 |  | 922 | 0 | 200 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 35 | 15 | 34 | 0 | 2 | 35 | 630 | 164 | 0 | 0 | 0 | 56 | 34 |  | 7091 | 3083 | 10174 | 3020 | 922 | 2001 | 72 | 2943 | 805 | 32 | 170 | 146 | 114 | 79 | 0 | 71.7
12:00 | 0 | 0 | 0 | 180 | 270 | 91 | 0 | 414 | 337 |  | 0 | 225 | 130 | 80 | 93 | 55 | 0 | 0 | 0 | 78 | 94 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 0 | 8 | 0 | 16 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 90 | 33 | 43 | 22 | 6 | 0 | 0 | 0 | 0 | 270 | 201 | 8 | 0 | 30 | 48 | 0 | 44 | 0 | 22 | 8 | 16 | 8 | 16 | 14 | 120 | 87 | 0 | 20 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 60 | 78 | 0 | 0 | 18 | 38 | 10 | 280 | 24 | 11 | 0 | 293 | 0 | 0 | 47 | 0 | 132 | 0 | 90 | 85 | 123 | 402 | 8 | 18 | 105 | 4 | 190 | 54 | 92 | 17 | 8 | 100 | 390 | 71 | 1 | 162 | 90 | 0 | 30 | 0 | 64 | 0 |  | 923 | 0 | 180 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 75 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 15 | 34 | 0 | 3 | 35 | 640 | 214 | 0 | 0 | 0 | 61 | 34 |  | 6875 | 3179 | 10054 | 3071 | 923 | 2108 | 0 | 2724 | 815 | 32 | 170 | 152 | 120 | 69 | 0 | 71.7
13:00 | 0 | 0 | 0 | 180 | 280 | 92 | 0 | 412 | 302 |  | 0 | 225 | 140 | 82 | 93 | 15 | 0 | 0 | 0 | 66 | 74 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 0 | 33 | 0 | 20 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 78 | 19 | 43 | 22 | 9 | 0 | 0 | 0 | 0 | 270 | 212 | 8 | 0 | 30 | 51 | 0 | 44 | 0 | 27 | 8 | 16 | 8 | 16 | 15 | 120 | 84 | 0 | 17 | 1 | 44 | 41 | 53 | 44 | 110 | 0 | 40 | 78 | 0 | 0 | 18 | 41 | 10 | 270 | 24 | 11 | 0 | 265 | 0 | 0 | 75 | 0 | 132 | 0 | 90 | 85 | 132 | 404 | 8 | 25 | 97 | 4 | 120 | 54 | 94 | 17 | 8 | 100 | 394 | 76 | 4 | 126 | 90 | 0 | 5 | 0 | 76 | 11 |  | 923 | 0 | 185 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 15 | 40 | 0 | 4 | 35 | 660 | 182 | 0 | 0 | 0 | 16 | 65 |  | 6716 | 3190 | 9906 | 3121 | 923 | 2056 | 0 | 2577 | 835 | 32 | 170 | 173 | 120 | 29 | 0 | 71.69
14:00 | 0 | 0 | 0 | 180 | 280 | 91 | 0 | 411 | 302 |  | 0 | 225 | 130 | 82 | 93 | 15 | 0 | 0 | 0 | 60 | 74 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 0 | 33 | 0 | 24 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 78 | 0 | 43 | 22 | 9 | 0 | 0 | 0 | 0 | 270 | 214 | 8 | 0 | 38 | 54 | 0 | 44 | 0 | 25 | 8 | 19 | 8 | 25 | 6 | 126 | 72 | 0 | 20 | 1 | 44 | 41 | 53 | 44 | 110 | 0 | 40 | 75 | 0 | 0 | 18 | 41 | 10 | 270 | 22 | 11 | 0 | 260 | 0 | 0 | 75 | 0 | 132 | 0 | 90 | 85 | 133 | 351 | 8 | 34 | 96 | 4 | 65 | 54 | 110 | 17 | 8 | 100 | 360 | 90 | 5 | 126 | 90 | 0 | 17 | 0 | 94 | 32 |  | 923 | 0 | 180 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 45 | 15 | 71 | 0 | 6 | 50 | 650 | 162 | 0 | 0 | 0 | 11 | 72 |  | 6632 | 3211 | 9843 | 3030 | 923 | 2021 | 0 | 2648 | 825 | 32 | 170 | 171 | 126 | 27 | 0 | 71.68
15:00 | 0 | 0 | 0 | 180 | 280 | 93 | 0 | 413 | 332 |  | 0 | 225 | 132 | 78 | 93 | 15 | 0 | 0 | 0 | 60 | 74 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 0 | 33 | 0 | 24 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 78 | 0 | 43 | 22 | 4 | 0 | 0 | 0 | 0 | 270 | 213 | 8 | 0 | 38 | 54 | 0 | 44 | 0 | 0 | 8 | 19 | 8 | 33 | 6 | 84 | 72 | 0 | 14 | 1 | 44 | 41 | 53 | 46 | 110 | 0 | 40 | 75 | 0 | 0 | 18 | 42 | 10 | 295 | 24 | 11 | 0 | 260 | 0 | 0 | 75 | 0 | 132 | 1 | 90 | 85 | 130 | 401 | 8 | 36 | 105 | 2 | 65 | 54 | 110 | 17 | 13 | 100 | 360 | 90 | 5 | 126 | 90 | 0 | 17 | 0 | 100 | 55 |  | 923 | 0 | 180 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 72 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 50 | 15 | 74 | 0 | 4 | 50 | 660 | 162 | 0 | 0 | 0 | 9 | 72 |  | 6708 | 3196 | 9904 | 3085 | 923 | 2065 | 0 | 2672 | 835 | 32 | 170 | 146 | 84 | 22 | 0 | 71.68
16:00 | 0 | 0 | 0 | 180 | 280 | 90 | 0 | 413 | 343 |  | 0 | 225 | 143 | 72 | 94 | 15 | 0 | 0 | 0 | 60 | 74 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 0 | 33 | 0 | 24 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 78 | 0 | 44 | 22 | 6 | 0 | 0 | 0 | 0 | 270 | 209 | 8 | 0 | 38 | 52 | 0 | 44 | 0 | 0 | 8 | 19 | 8 | 33 | 8 | 90 | 72 | 0 | 20 | 0 | 44 | 41 | 53 | 46 | 110 | 0 | 61 | 75 | 0 | 0 | 18 | 40 | 10 | 300 | 24 | 11 | 0 | 210 | 0 | 0 | 75 | 0 | 112 | 0 | 90 | 34 | 137 | 401 | 8 | 70 | 105 | 1 | 65 | 54 | 110 | 17 | 26 | 100 | 398 | 90 | 5 | 90 | 90 | 0 | 17 | 0 | 70 | 55 |  | 923 | 0 | 220 | 0 | 16 | 40 | 0 | 0 | 0 | 2 | 0 | 75 | 8 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 165 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 50 | 15 | 74 | 0 | 3 | 50 | 660 | 179 | 0 | 0 | 0 | 5 | 35 |  | 6688 | 3295 | 9983 | 3218 | 923 | 2174 | 0 | 2505 | 835 | 32 | 170 | 152 | 90 | 14 | 0 | 71.67
17:00 | 0 | 0 | 0 | 100 | 280 | 95 | 0 | 411 | 342 |  | 0 | 225 | 135 | 78 | 94 | 15 | 0 | 0 | 0 | 60 | 74 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 25 | 33 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 44 | 22 | 6 | 0 | 0 | 0 | 0 | 270 | 187 | 8 | 0 | 38 | 55 | 0 | 44 | 0 | 0 | 8 | 19 | 0 | 33 | 14 | 96 | 85 | 0 | 20 | 0 | 43 | 41 | 53 | 45 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 270 | 24 | 11 | 0 | 210 | 0 | 0 | 100 | 0 | 108 | 0 | 90 | 34 | 135 | 364 | 8 | 70 | 92 | 1 | 65 | 54 | 92 | 17 | 26 | 100 | 365 | 90 | 2 | 90 | 90 | 0 | 17 | 0 | 70 | 55 |  | 923 | 0 | 220 | 0 | 22 | 40 | 0 | 0 | 0 | 3 | 0 | 75 | 14 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 380 | 14 | 0 | 50 | 15 | 74 | 0 | 1 | 50 | 670 | 180 | 0 | 0 | 0 | 4 | 72 |  | 6581 | 3362 | 9943 | 3140 | 923 | 2114 | 0 | 2560 | 845 | 32 | 170 | 185 | 96 | 8 | 0 | 71.67
18:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 411 | 341 |  | 0 | 225 | 148 | 82 | 94 | 15 | 0 | 0 | 0 | 30 | 32 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 25 | 33 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 0 | 42 | 22 | 10 | 0 | 0 | 0 | 0 | 270 | 181 | 8 | 0 | 38 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 19 | 96 | 98 | 0 | 20 | 0 | 43 | 41 | 53 | 45 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 275 | 24 | 11 | 0 | 210 | 0 | 0 | 100 | 0 | 109 | 0 | 90 | 34 | 142 | 364 | 11 | 75 | 89 | 0 | 30 | 54 | 92 | 17 | 26 | 100 | 360 | 90 | 1 | 90 | 90 | 0 | 17 | 0 | 70 | 55 |  | 923 | 0 | 220 | 0 | 16 | 40 | 0 | 0 | 2 | 24 | 8 | 81 | 16 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 50 | 15 | 74 | 0 | 0 | 50 | 680 | 200 | 0 | 0 | 0 | 1 | 72 |  | 6570 | 3444 | 10014 | 3255 | 923 | 2154 | 0 | 2449 | 855 | 32 | 170 | 208 | 96 | 2 | 0 | 71.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 411 | 345 |  | 0 | 225 | 150 | 83 | 94 | 25 | 0 | 0 | 0 | 39 | 64 | 82 | 0 | 0 | 0 | 0 | 37 | 55 | 55 | 22 | 25 | 16 | 33 | 25 | 35 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 78 | 17 | 38 | 22 | 18 | 0 | 0 | 0 | 0 | 270 | 211 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 19 | 8 | 19 | 8 | 33 | 19 | 106 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 46 | 110 | 0 | 61 | 78 | 0 | 0 | 18 | 42 | 10 | 280 | 24 | 11 | 0 | 235 | 0 | 0 | 130 | 0 | 124 | 0 | 90 | 40 | 145 | 398 | 40 | 86 | 87 | 0 | 170 | 54 | 93 | 17 | 26 | 100 | 360 | 97 | 0 | 92 | 90 | 0 | 17 | 0 | 84 | 55 |  | 922 | 0 | 220 | 0 | 26 | 40 | 0 | 0 | 39 | 87 | 8 | 81 | 20 | 32 | 0 | 0 | 0 | 32 | 4 | 74 | 0 | 8 | 29 | 8 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 380 | 55 | 0 | 50 | 22 | 90 | 0 | 0 | 70 | 690 | 220 | 0 | 9 | 0 | 0 | 72 |  | 7177 | 3875 | 11052 | 3312 | 922 | 2208 | 0 | 2982 | 865 | 32 | 170 | 585 | 106 | 0 | 0 | 71.65
19:30 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 409 | 346 |  | 0 | 225 | 132 | 83 | 94 | 55 | 0 | 0 | 0 | 91 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 25 | 50 | 0 | 32 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 90 | 43 | 37 | 22 | 23 | 0 | 0 | 0 | 0 | 280 | 215 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 32 | 8 | 19 | 8 | 33 | 20 | 100 | 109 | 0 | 20 | 0 | 43 | 41 | 53 | 46 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 265 | 24 | 11 | 0 | 270 | 0 | 0 | 130 | 0 | 134 | 0 | 90 | 136 | 146 | 401 | 92 | 90 | 87 | 0 | 190 | 54 | 92 | 17 | 94 | 100 | 360 | 104 | 0 | 162 | 90 | 0 | 17 | 0 | 100 | 55 |  | 923 | 0 | 250 | 0 | 61 | 40 | 0 | 0 | 45 | 80 | 40 | 73 | 23 | 32 | 0 | 0 | 0 | 32 | 9 | 90 | 0 | 34 | 32 | 8 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 90 | 0 | 80 | 80 | 100 | 0 | 0 | 113 | 780 | 220 | 0 | 17 | 0 | 0 | 72 |  | 7770 | 4281 | 12051 | 3358 | 923 | 2174 | 0 | 3815 | 955 | 32 | 170 | 654 | 100 | 0 | 0 | 71.66
20:00 | 0 | 0 | 0 | 180 | 250 | 95 | 0 | 411 | 347 |  | 0 | 225 | 126 | 83 | 94 | 55 | 0 | 0 | 0 | 90 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 50 | 0 | 32 | 0 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 100 | 31 | 39 | 22 | 21 | 0 | 0 | 0 | 0 | 280 | 216 | 8 | 0 | 33 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 102 | 113 | 0 | 20 | 0 | 43 | 41 | 53 | 46 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 260 | 24 | 11 | 0 | 295 | 0 | 0 | 130 | 0 | 133 | 0 | 90 | 128 | 145 | 401 | 108 | 90 | 91 | 0 | 155 | 54 | 92 | 17 | 79 | 100 | 348 | 104 | 0 | 162 | 90 | 0 | 17 | 0 | 100 | 55 |  | 922 | 0 | 265 | 0 | 65 | 40 | 0 | 0 | 8 | 80 | 40 | 72 | 24 | 32 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 8 | 12 | 8 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 376 | 90 | 0 | 90 | 105 | 101 | 0 | 0 | 113 | 780 | 220 | 0 | 17 | 0 | 0 | 72 |  | 7663 | 4251 | 11914 | 3342 | 922 | 2169 | 0 | 3828 | 955 | 32 | 170 | 524 | 102 | 0 | 0 | 71.65
21:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 411 | 347 |  | 0 | 225 | 148 | 92 | 94 | 55 | 0 | 0 | 0 | 55 | 48 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 34 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 100 | 0 | 43 | 22 | 33 | 0 | 0 | 0 | 0 | 280 | 213 | 8 | 0 | 36 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 106 | 138 | 0 | 20 | 0 | 44 | 41 | 53 | 46 | 110 | 0 | 61 | 78 | 0 | 0 | 18 | 41 | 10 | 270 | 24 | 11 | 0 | 293 | 0 | 0 | 130 | 0 | 132 | 0 | 90 | 136 | 147 | 402 | 98 | 90 | 105 | 0 | 155 | 54 | 92 | 17 | 93 | 100 | 400 | 104 | 0 | 108 | 90 | 0 | 17 | 0 | 100 | 55 |  | 923 | 0 | 260 | 0 | 81 | 40 | 0 | 0 | 0 | 0 | 40 | 81 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 98 | 0 | 94 | 105 | 102 | 0 | 0 | 113 | 830 | 220 | 0 | 17 | 0 | 0 | 72 |  | 7646 | 4151 | 11797 | 3458 | 923 | 2205 | 0 | 3693 | 1005 | 32 | 170 | 335 | 106 | 0 | 0 | 71.65
22:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 412 | 348 |  | 0 | 225 | 130 | 87 | 94 | 55 | 0 | 0 | 0 | 50 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 32 | 0 | 32 | 0 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 100 | 0 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 280 | 216 | 8 | 0 | 37 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 102 | 132 | 0 | 20 | 0 | 44 | 41 | 53 | 49 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 41 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 130 | 0 | 134 | 0 | 90 | 136 | 147 | 400 | 98 | 90 | 105 | 0 | 115 | 54 | 107 | 17 | 94 | 100 | 400 | 104 | 0 | 100 | 90 | 0 | 17 | 0 | 100 | 55 |  | 922 | 0 | 260 | 0 | 81 | 40 | 0 | 0 | 0 | 0 | 40 | 72 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 105 | 0 | 94 | 105 | 102 | 0 | 0 | 113 | 840 | 220 | 0 | 17 | 0 | 0 | 72 |  | 7375 | 4106 | 11481 | 3445 | 922 | 2204 | 0 | 3487 | 1015 | 32 | 170 | 234 | 102 | 0 | 0 | 71.64
23:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 412 | 347 |  | 0 | 225 | 140 | 83 | 94 | 40 | 0 | 0 | 0 | 9 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 17 | 24 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 0 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 280 | 215 | 8 | 0 | 34 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 31 | 20 | 102 | 132 | 0 | 20 | 0 | 44 | 41 | 53 | 49 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 41 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 130 | 0 | 135 | 0 | 90 | 136 | 147 | 401 | 98 | 90 | 105 | 0 | 120 | 54 | 110 | 62 | 94 | 100 | 312 | 104 | 0 | 54 | 90 | 0 | 17 | 0 | 100 | 55 |  | 922 | 0 | 260 | 0 | 81 | 40 | 0 | 0 | 0 | 0 | 40 | 81 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 427 | 70 | 0 | 94 | 105 | 102 | 0 | 0 | 113 | 840 | 220 | 0 | 17 | 0 | 0 | 72 |  | 7203 | 4097 | 11300 | 3353 | 922 | 2285 | 0 | 3357 | 1015 | 32 | 170 | 194 | 102 | 0 | 0 | 71.76
24:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 412 | 347 |  | 0 | 225 | 142 | 85 | 88 | 40 | 0 | 0 | 0 | 8 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 90 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 0 | 280 | 215 | 8 | 0 | 31 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 19 | 100 | 132 | 0 | 20 | 0 | 44 | 41 | 53 | 49 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 41 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 130 | 0 | 135 | 0 | 90 | 128 | 147 | 399 | 99 | 105 | 105 | 0 | 117 | 54 | 110 | 98 | 31 | 100 | 220 | 101 | 0 | 54 | 90 | 0 | 17 | 0 | 85 | 55 |  | 922 | 0 | 250 | 0 | 81 | 40 | 0 | 0 | 0 | 0 | 40 | 81 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 428 | 70 | 0 | 94 | 105 | 76 | 0 | 0 | 113 | 840 | 222 | 0 | 17 | 0 | 0 | 34 |  | 7071 | 4029 | 11100 | 3258 | 922 | 2290 | 0 | 3249 | 1015 | 32 | 170 | 194 | 100 | 0 | 0 | 71.63
KWH | 0 | 0 | 0 | 4315500 | 6262991 | 2182909 | 0 | 9947130 | 7868000 |  | 0 | 5195900 | 3382255 | 2028480 | 2232384 | 1057764 | 0 | 0 | 0 | 1522790 | 1537488 | 1463520 | 0 | 0 | 0 | 0 | 1206360 | 1334035 | 1055643 | 367632 | 600000 | 472680 | 734400 | 483200 | 858240 | 0 | 763260 | 0 | 2300000 | 0 | 295389 | 0 | 0 | 0 | 0 |  | 552336 | 0 | 104845 | 1922400 | 567360 | 1042560 | 532368 | 532320 | 0 | 0 | 0 | 0 | 6955000 | 5028000 | 200727 | 0 | 754776 | 1179360 | 0 | 1065931 | 0 | 382200 | 200328 | 394776 | 162900 | 756500 | 432730 | 2552640 | 2533440 | 0 | 373284 | 3950 | 1031000 | 934744 | 1279800 | 1102680 | 2672182 | 0 | 1349648 | 1846080 | 0 | 0 | 429000 | 965640 | 256860 | 6902500 | 556425 | 264000 | 1023360 | 6169852 | 477671 | 253829 | 3158400 | 234683 | 3146688 | 55620 | 2071680 | 2151360 | 3246763 | 9374000 | 1195200 | 2016852 | 2464763 | 31680 | 3996982 | 1369641 | 2514107 | 489060 | 607320 | 2375040 | 9042300 | 2315520 | 54330 | 3096000 | 2175382 | 0 | 648000 | 0 | 2090880 | 1179360 |  | 22312727 | 0 | 5331456 | 0 | 1265280 | 1832408 | 0 | 0 | 154560 | 371072 | 496500 | 1931345 | 539770 | 729792 | 0 | 0 | 0 | 186311 | 41235 | 696328 | 0 | 179051 | 95690 | 106565 | 226871 | 502560 | 0 | 201780 | 0 | 0 | 4285000 | 0 | 0 | 4795009 | 0 | 0 | 3987036 | 0 | 86400 | 0 | 0 | 9044436 | 1205760 | 94007 | 1697856 | 1450944 | 1656508 | 0 | 22857 | 1693056 | 21271300 | 4690118 | 0 | 267600 | 4500 | 379440 | 1214400 |  | 176315563 | 95047528 | 271363091 | 78648014 | 22312727 | 51410028 | 2169950 | 77855719 | 25556300 | 763260 | 5819444 | 3722632 | 2552640 | 552377 | 0
Fuel Cost | 0 | 0 | 0 | 6430095 | 7014549.92 | 2903268.97 | 0 | 10444486.5 | 8497440 |  | 0 | 5663531 | 3754303.05 | 22678406.4 | 29579088 | 14015373 | 0 | 0 | 0 | 22263189.8 | 21632456.16 | 23723659.2 | 0 | 0 | 0 | 0 | 15344899.2 | 18009472.5 | 14156172.63 | 275724 | 450000 | 0 | 0 | 0 | 14598662.4 | 0 | 206080.2 | 0 | 4347000 | 0 | 4829610.15 | 0 | 0 | 0 | 0 |  | 7207984.8 | 0 | 1784461.9 | 25971624 | 7194124.8 | 12062419.2 | 676107.36 | 1772625.6 | 0 | 0 | 0 | 0 | 7580950 | 5832480 | 258937.83 | 0 | 852896.88 | 1757246.4 | 0 | 1780104.77 | 0 | 6600594 | 2694411.6 | 540843.12 | 122175 | 1323875 | 324547.5 | 18327955.2 | 2761449.6 | 0 | 507666.24 | 62963 | 1412470 | 1233862.08 | 2226852 | 1907636.4 | 3073009.3 | 0 | 2618317.12 | 4209062.4 | 0 | 0 | 922350 | 1438803.6 | 508582.8 | 6902500 | 417318.75 | 200640 | 21449625.6 | 84218479.8 | 10011984.16 | 5246645.43 | 42575232 | 4850897.61 | 43581628.8 | 650197.8 | 21379737.6 | 29387577.6 | 43084545.01 | 8624080 | 14533632 | 29163679.92 | 31179251.95 | 0 | 46924568.68 | 14915390.49 | 26724957.41 | 6636544.2 | 7828354.8 | 27977971.2 | 8318916 | 29985984 | 785068.5 | 39288240 | 24755847.16 | 0 | 8462880 | 0 | 31300473.6 | 15532171.2 |  | 66938181 | 0 | 5971230.72 | 0 | 13171564.8 | 30234732 | 0 | 0 | 2783625.6 | 6679296 | 7134705 | 2163106.4 | 1047153.8 | 7954732.8 | 0 | 0 | 0 | 3124435.47 | 721200.15 | 10890569.92 | 0 | 2965084.56 | 1618117.9 | 1452480.95 | 3827313.77 | 1040299.2 | 0 | 152747.46 | 0 | 0 | 22667650 | 0 | 0 | 5562210.44 | 0 | 0 | 69613648.56 | 0 | 1812672 | 0 | 0 | 8953991.64 | 16205414.4 | 1971326.79 | 20085636.48 | 20966140.8 | 21037651.6 | 0 | 252569.85 | 20553699.84 | 191654413 | 4783920.36 | 0 | 1980240 | 50895 | 4450831.2 | 18616752 |  | 1065261878.85 | 601090241.46 | 1666352120.31 | 87082095.09 | 66938181 | 62479269.12 | 45343151.59 | 1003799145.29 | 214322063 | 206080.2 | 99848380.56 | 61753273.91 | 18327955.2 | 6252525.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 250 | 90 | 0 | 404 | 340 |  | 0 | 225 | 125 | 80 | 93 | 55 | 0 | 0 | 0 | 78 | 68 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 4 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 90 | 22 | 43 | 22 | 4 | 0 | 0 | 0 | 0 | 300 | 197 | 8 | 0 | 34 | 49 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 30 | 15 | 106 | 87 | 0 | 0 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 60 | 72 | 0 | 0 | 18 | 39 | 10 | 310 | 24 | 11 | 30 | 293 | 109 | 25 | 140 | 25 | 132 | 4 | 90 | 85 | 125 | 398 | 8 | 105 | 105 | 4 | 230 | 54 | 110 | 17 | 8 | 100 | 389 | 83 | 3 | 162 | 90 | 0 | 35 | 0 | 76 | 55 |  | 922 | 0 | 225 | 0 | 16 | 40 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 650 | 165 | 0 | 0 | 0 | 60 | 34 |  | 10677 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 409 | 346 | 0 | 0 | 225 | 132 | 83 | 94 | 55 | 0 | 0 | 0 | 91 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 25 | 50 | 0 | 32 | 0 | 100 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 90 | 43 | 37 | 22 | 23 | 0 | 0 | 0 | 0 | 280 | 215 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 32 | 8 | 19 | 8 | 33 | 20 | 100 | 109 | 0 | 20 | 0 | 43 | 41 | 53 | 46 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 265 | 24 | 11 | 0 | 270 | 0 | 0 | 130 | 0 | 134 | 0 | 90 | 136 | 146 | 401 | 92 | 90 | 87 | 0 | 190 | 54 | 92 | 17 | 94 | 100 | 360 | 104 | 0 | 162 | 90 | 0 | 17 | 0 | 100 | 55 |  | 923 | 0 | 250 | 0 | 61 | 40 | 0 | 0 | 45 | 80 | 40 | 73 | 23 | 32 | 0 | 0 | 0 | 32 | 9 | 90 | 0 | 34 | 32 | 8 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 370 | 90 | 0 | 80 | 80 | 100 | 0 | 0 | 113 | 780 | 220 | 0 | 17 | 0 | 0 | 72 |  | 12051 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 412 | 340 | 0 | 0 | 225 | 150 | 90 | 0 | 55 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 50 | 0 | 35 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 90 | 71 | 44 | 22 | 35 | 0 | 0 | 0 | 0 | 330 | 210 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 165 | 110 | 0 | 20 | 0 | 43 | 41 | 51 | 44 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 42 | 10 | 341 | 24 | 11 | 200 | 285 | 300 | 100 | 200 | 100 | 135 | 0 | 90 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 285 | 54 | 110 | 17 | 94 | 100 | 400 | 104 | 0 | 162 | 110 | 0 | 35 |  | 100 | 55 |  | 940 | 0 | 250 | 0 | 95 | 150 | 0 | 0 | 45 | 80 | 40 | 81 | 33 | 48 | 0 | 0 | 0 | 34 | 10 | 90 | 0 | 34 | 32 | 8 | 40 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 215 | 0 | 0 | 210 | 0 | 100 | 0 | 0 | 414 | 105 | 190 | 94 | 105 | 100 | 0 | 0 | 113 | 1050 | 220 |  | 17 |  |  | 72
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 98 | 0 | 412 | 340 | 0 | 0 | 225 | 150 | 90 | 0 | 55 | 0 | 0 | 0 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 50 | 0 | 35 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 71 | 44 | 22 | 15 | 0 | 0 | 0 | 0 | 300 | 210 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 143 | 100 | 0 | 20 | 1.6 | 43 | 41 | 51 | 44 | 110 | 0 | 62 | 78 | 0 | 0 | 18 | 41 | 10 | 310 | 24 | 11 | 150 | 285 | 300 | 100 | 190 | 100 | 130 | 20 | 90 | 200 | 140 | 400 | 105 | 105 | 105 | 5 | 285 | 54 | 110 | 17 | 50 | 100 | 400 | 104 | 50 | 162 | 110 | 0 | 35 | 30 | 100 | 55 |  | 940 | 0 | 250 | 0 | 95 | 150 | 0 | 0 | 35 | 0 | 40 | 81 | 20 | 48 | 0 | 0 | 0 | 34 | 0 | 65 | 0 | 34 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 414 | 90 | 100 | 94 | 105 | 75 | 0 | 8 | 76 | 1050 | 220 |  | 17 | 6 | 100 | 72
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 75 | 0 | 413 | 283 | 0 | 0 | 225 | 145 | 49 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 27 | 0 | 8 | 0 | 0 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 44 | 22 | 34 | 0 | 0 | 0 | 0 | 280 | 187 | 8 | 0 | 31 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 74 | 132 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 78 | 0 | 0 | 18 | 41 | 10 | 285 | 22 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 17 | 3 | 50 | 17 | 10 | 329 | 0 | 17 | 105 | 1 | 0 | 17 | 110 | 17 | 9 | 100 | 260 | 17 | 3 | 0 | 90 | 0 | 17 | 0 | 100 | 17 | 0 | 923 | 0 | 245 | 0 | 95 | 40 | 0 | 0 | 0 | 0 | 8 | 81 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 620 | 174 | 0 | 17 | 1 | 28 | 34 | 0 |  |  |  |  | 89567745 |  | 0
89567745
| Minimum Generation |  | 10338 | 8:00
| Highest Generation |  | 13310 | 1:00
| Day Peak Generation |  | 10677 | 10:00
| Evening Peak Generation |  | 12051 | 19:30
| HVDC Max Flow |  | 923 | 1:00
| HVDC EvPeak Flow |  | 923 | 19:30
| Load factor L.F |  | 84.95%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-10
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10677 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 8452 | MW
Evening Peak Generation : |  | 12051 | MW Hour : | 19:30 | Available Max Generation : |  | 14349 | MW
E.P. Demand (at gen end) : |  | 12051 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 13310 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1649 | MW
Total Gen. (MKWH) : |  | 271.3631 | System Load Factor : | 84.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 330 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-10
Actual : | 71.62 | Ft.(MSL) , | Rule curve : | 78.34 | Ft.( MSL )
Gas Consumed : | Total = | 983.12 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 149561364.21
: |  | Coal : | 214322063 | Oil : | 1210743951.35 | Total : | 1574627378.56
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4549.018 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1465.1679 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1440.1668 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1288.1736 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1175.868 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 966.6866 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 471.0582 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 294.9237 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 707.1928 |  |  | 0 | 0%
Total | 0 |  | 12358.2556 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-3
9) Ashuganj North
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shyampur(N)-Shyampur(O) 132 kV Ckt-2 tripped at 08:12 Showing Dist. Z2 relay at Shyampur(O) end
and was switched on at 16:07.
b) Mirsharai-Power Gen 230 kV Ckt-1 was under shut down from 12:01 to 14:48 for D/W.
c) Barisal(N) 132/33 kV T-5 transformer was under shut down from 09:10 to 15:34 for C/M.
d) Rajbari-Faridpur 132 kV Ckt-2 was under shut down from 10:04 to 11:54 for D/W.
e) Haripur-Norsingdi 132 Ckt tripped at 12:01 Showing Dist. Z1 A-phase relay at Haripur end and | [5 empty] | About 50 MW power interruption occurred under
was switched on at 12:30. | [5 empty] | Haripur S/S area from 12:01 to 12:30.
f) Rajbari 132/33 kV T-2 transformer was under shut down from 10:15 to 18:05 for C/M.
g) Rajbari-Bheramara 132 kV Ckt-2 was under shut down from 10:05 to 11:30 for D/W.
h) Rajbari-Faridpur 132 kV Ckt-1 was under shut down from 11:57 to 13:14 for D/W.
i) Saidpur-Purbasadipur 132 kV Ckt-1 was under shut down from 09:12 to 16:29 for D/W.
j) Bogura-Naogaon 132 kV Ckt-1 was under shut down from 12:50 to 15:48 for D/W.
k) Ghorasal-Ashuganj 132 kV Ckt-2 tripped at 23:30 Showing Dist. Z2 A,B-phase relay at Ashuganj end
and B-phase PT at Ghorasal got burst.
l) Goalpara-Khulna GT 132 kV Ckt was shut down from 14:00 for C/M.
m) Faridpur 132/33 kV T-1 transformer was under shut down from 13:45 to 14:50 for C/M.
n) Barapukuria 230/132 kV T-6 transformer was switched on at 14:14.
o) Manikganj 132/33 kV T-4 transformer was under shut down from 12:36 to 12:58 for C/M.
p) Chandpur 150 MW CCPP132/33 kV unit transformer & ST was under shut down from 09:52 to
18:23 for C/M.
q) Polashbari-Mithapukur 132 kV Ckt-1 & 2 were under shut down from 14:39 to 15:24 for D/W.
r) Sikalbaha S/S-Intermediate S/S 230 kV Ckt-2 was switched on at 16:27.
s) Bibiyana(S) ST was shut down at 00:26(10-06-2022).
t) Naogaon 132/33 kV T-1 transformer was under shut down from 00:20 to 03:20(10-06-2022) due to | [5 empty] | About 30 MW power interruption occurred under
red hot maintenance at 33 kV end. | [5 empty] | Naogaon S/S area from 00:20 to 03:20(10-06-2022)
u) Madanganj S/S-Madanganj 100 MW P/P 132 kV Ckt was shut down at 01:32(10-06-2022) due to
fire at Madanganj 100 MW P/P.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6262991 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2182909 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9947130
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 346 | 7868000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5195900 | GT-2 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 83 | 2028480 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 132 | 3382255 | Gas shortage & FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 94 | 2232384 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1057764
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 367632
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M & Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1522790 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1537488 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1206360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1463520 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1334035
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1055643
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 1072680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 734400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 483200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 858240 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 6169852 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 477671 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 253829 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 234683 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 3146688 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2016852 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2315520
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3096000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1179360
| Dhaka area Total |  |  |  | 5898 | 3339 | 74999756
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 15 | 295389 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 55620
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 1042560 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 32 | 763260 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 2464763 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 104845 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1922400 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2071680 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 532368
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 532320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 567360 | Low demand
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31680
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 3996982 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1369641
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2514107 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2375040
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2175382 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1116 | 25115397
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 5028000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6955000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 754776 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1179360
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1065931
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 146 | 3246763
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 382200 | Low demand
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2151360 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 394776 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 162900 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 2552640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 756500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 200328 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 432730 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 1023360 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 489060 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 607320 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 648000 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 2090880 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 1376 | 30322611
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 109 | 2533440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 373284
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 130 | 3158400 | Low demand
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 1195200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 54330
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 552336
| Mymensingh Area Total |  |  |  | 622 | 375 | 7870940
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1031000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 934744 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2672182 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1279800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 46 | 1102680 | Engine problem
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1349648
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1846080 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 429000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 42 | 965640 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 556425
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 6902500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9374000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 256860
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 360 | 9042300 | Gas shortage
| Sylhet Area Total |  |  |  | 2477 | 1564 | 38006859
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22312727
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 61 | 1265280 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 45 | 154560 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 40 | 1832408 | Low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 80 | 371072 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 5331456 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 496500
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 86400 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1205760 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 80 | 1450944 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 379440
| Khulna Area Total |  |  |  | 2384 | 1609 | 34886547
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 729792 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 23 | 539770 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 73 | 1931345 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 780 | 21271300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4690118
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 267600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1145 | 29429925
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 186311 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 9 | 41235 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 179051 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 95690 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4795009
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3987036
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 9044436 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 226871 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 502560
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 201780 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 106565 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 696328 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 94007 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 1697856 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1693056
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 4500
| Rajshahi Area Total |  |  |  | 2129 | 1180 | 23552291
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4285000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 1656508 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22857
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 1214400 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 347 | 7178765
| Total |  |  |  | 21584 | 12051 | 271363091
| Eastern Grid Total |  |  |  | 14393 | 7770 | 176315563
| Western Grid Total |  |  |  | 7191 | 4281 | 95047528
| National Grid Total |  |  |  | 21584 | 12051 | 271363091
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-09
(a) ENTIRE EASTERN GRID : |  | 8042.78 | MW | (b) ENTIRE WESTERN GRID : |  | 3678.6 | MW
i) Dhaka area |  | 4393.63 | MW | i) Khulna area |  | 1431 | MW
ii) Chittagong area |  | 1329.15 | MW | ii) Rajshahi area |  | 1162.6 | MW
iii) Comilla area |  | 934 | MW | iii) Barisal area |  | 277 | MW
iv) Mymensingh area |  | 900 | MW | iv) Rangpur area |  | 808 | MW
v) Sylhet area |  | 486 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11721.38 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 34 | 00:00 | Hasnabad | 72 | 01:00 | Palashbari | 96 | 20:00
Agargaon | 99 | 10:00 | Hathazari | 92 | 15:00 | Panchagarh | 57 | 21:00
Agrabad | 88 | 12:00 | Ishurdi | 75 | 01:00 | Patuakhali | 129 | 00:00
AKS | 12 | 11:00 | Jaldhaka | 63 | 19:30 | PHP | 8 | 11:00
AKSML | 9 | 06:00 | Jamalpur | 147 | 00:00 | Purbachal | 20 | 00:00
Amnura | 46 | 01:00 | Jashore | 122 | 00:00 | Purbasadipur | 116 | 00:00
Ashuganj | 40 | 23:00 | Jhenaidah | 124 | 00:00 | Rahim | 23 | 06:00
Bagerhat | 114 | 00:00 | Joydebpur | 184 | 09:00 | Rajbari | 70 | 00:00
Bakulia | 123 | 13:00 | Joypurhat | 62 | 01:00 | Rajendrapur | 108 | 00:00
Banani | 49 | 10:00 | Juldah | 20 | 00:00 | Rajshahi | 172 | 00:00
Bangabhaban | 24 | 10:00 | Kabirpur | 288 | 09:00 | Rajshahi | 38 | 00:00
Barapukuria | 52 | 00:00 | Kachua | 76 | 00:00 | Ramganj | 102 | 00:00
Barguna | 22 | 00:00 | Kallyanpur | 117 | 00:00 | Rampur | 15 | 01:00
Barishal | 118 | 12:00 | Kalurghat | 6 | 10:00 | Rangamati | 12 | 12:00
Barishal | 68 | 00:00 | Kamrangirchar | 69 | 00:00 | Rangpur | 140 | 19:30
Baroaulia | 76 | 00:00 | Kaptai | 4 | 19:00 | Ruppur | 3.8 | 11:00
Baroirhat | 62 | 00:00 | Kazla | 86 | 00:00 | Saidpur | 101 | 19:30
Bashundhara | 176 | 10:00 | Keranigonj | 82 | 00:00 | Satkhira | 130 | 22:00
BashundharaCement | 12 | 00:00 | Khagrachori | 28 | 23:00 | Satmasjid | 97 | 00:00
Beanibazar | 60 | 19:30 | Khulna | 111 | 12:00 | Savar | 183 | 09:00
Benapole | 60 | 00:00 | Khulshi | 190 | 12:00 | Shahjadpur | 96 | 00:00
Bhaluka | 130 | 00:00 | Kishoreganj | 148 | 00:00 | Shahjibazar | 114 | 00:00
Bhandaria | 60 | 00:00 | Kodda | 322 | 08:00 | Shahmirpur | 42.4 | 00:00
Bhangura | 34 | 00:00 | KSRM | 25.5 | 10:00 | Shariatpur | 80 | 00:00
Bheramara(GK) | 58 | 01:00 | Kulaura | 42 | 20:00 | Sherpur | 104 | 21:00
Bhulta | 245 | 03:00 | Kurigram | 56 | 19:00 | Shikalbaha | 32 | 00:00
Bog-Sherpur | 64 | 00:00 | Kushtia | 138 | 01:00 | Shitalakhya | 121 | 11:00
Bogura | 152 | 01:00 | Lalbag | 93 | 11:00 | Sholosohor | N/A | N/A
Borhanuddin | 44 | 00:00 | Lalmonirhat | 45 | 19:00 | Shyampur | 168 | 06:00
Brahmanbaria | 170 | 01:00 | Madanganj | 190 | 09:00 | Siddhirganj | 120 | 11:00
BSRM | 161 | 12:00 | Madaripur | 109 | 00:00 | Sirajganj | 92 | 00:00
Cantonment | 154 | 10:00 | Madartek | 92 | 00:00 | Sonargaon | 96 | 01:00
Chandpur | 74 | 00:00 | Madunaghat | 63 | 10:00 | Sreemongol | 49 | 00:00
Chandraghona | 30 | 00:00 | Magura | 62 | 01:00 | Srinagar | 45.56 | 00:00
Chapai | 77 | 00:00 | Mahasthangarh | 64 | 01:00 | SSM | 3 | 01:00
Charsaidpur | 43 | 00:00 | Manikganj | 86 | 00:00 | Sunamganj | 46 | 21:00
Chauddagram | 43 | 01:00 | Maniknagar | 73 | 10:00 | Sylhet | 131 | 13:00
Chhatak | 26 | 21:00 | Matarbari | 39 | 00:00 | Tangail | 201 | 00:00
Chowmuhani | 206 | 00:00 | Matuail | 66 | 11:00 | Thakurgaon | 81 | 21:00
Chuadanga | 107 | 01:00 | Millgate | 62 | 12:00 | TK | 29 | 00:00
Coxsbazar | 106 | 00:00 | Mirpur | 133 | 00:00 | Tongi | 142 | 10:00
Cumilla(N) | 158 | 00:00 | Mirsorai | N/A | N/A | Ullon | 38 | 00:00
Cumilla(S) | 172 | 00:00 | Mithapukur | 30 | 00:00 | Uttara | 94 | 10:00
Daudkandi | 142 | 00:00 | Modern | 0 | 00:00 | UttaraNew | 19 | 00:00
Dhaka | 46 | 10:00 | Mogbazar | 128 | 10:00 | Zigatola | 46 | 00:00
Dhamrai | 116 | 09:00 | Mongla | 38 | 11:00
Dhanmondi | 156 | 11:00 | Motijheel | 38 | 11:00
Dohazari | 84 | 19:00 | Munshiganj | 110 | 00:00
Faridpur | 160 | 00:00 | Mymensingh | 218 | 00:00
Fatullah | 68 | 10:00 | Naogaon | 114 | 00:00
Fenchuganj | 46 | 19:00 | Narail | 55 | 01:00
Feni | 117 | 00:00 | Narinda | 67 | 14:00
Ghorashal | 63 | 00:00 | Narshingdi | 190 | 00:00
Goalpara | 30 | 00:00 | Natore | 133 | 00:00
Gollamari | 58 | 00:00 | Nawabganj | 56 | 00:00
Gopalganj | 105 | 00:00 | Netrakona | 108 | 00:00
GPH | 87 | 04:00 | New | 85.4 | 09:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 20:00 | 403 | 16:00 | Kaliakoir | 397 | 0.77083 | 383 | 0.66667
| Bheramara | 397 | 8:00 | 389 | 15:00 | Bhulta | 393 | 0.8125 | 373 | 0.41667
| Ashuganj(N) | 400 | 22:00 | 374 | 10:00 | Gopalganj | 421 | 0.625 | 400 | 0.041667
| Payra | 423 | 19:30 | 412 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 230 | 1:00 | Hathazari | 235 | 4:00 | 226 | 15:00
| Ishurdi | 237 | 9:00 | 229 | 1:00 | Megnaghat | 232 | 19:30 | 222 | 7:00
| Ashuganj | 241 | 19:30 | 234 | 16:00 | Fenchuganj | 245 | 20:00 | 237 | 1:00
| Serajganj | 236 | 9:00 | 232 | 16:00 | Siddhirganj | 231 | 19:30 | 223 | 8:00
| Baghabari | 235 | 8:00 | 229 | 1:00 | Maniknagar | 227 | 19:30 | 217 | 10:00
| Barapukuria | 232 | 7:00 | 219 | 21:00 | Agargaon | 228 | 14:00 | 216 | 10:00
| Bogra | 234 | 7:00 | 226 | 1:00 | Barisal | 244 | 14:00 | 233 | 1:00
| Rajshahi | 238 | 8:00 | 226 | 1:00 | Bhola 225 MW | 248 | 15:00 | 233 | 1:00
| Khulna South | 235 | 6:00 | 227 | 16:00 | AKSML | 236 | 22:00 | 225 | 15:00
| Rampura | 229 | 20:00 | 220 | 9:00 | BSRM | 234 | 19:30 | 225 | 16:00
| Haripur | 226 | 24:00 | 216 | 9:00 | Bibiyana | 241 | 19:30 | 235 | 1:00
| Hasnabad | 227 | 19:30 | 217 | 9:00 | Bhulta | 231 | 19:30 | 221 | 9:00
| Shyampur | 227 | 20:00 | 217 | 10:00 | Ashuganj (S) | 247 | 14:00 | 230 | 10:00
| Aminbazar | 230 | 1:00 | 216 | 2:00 | Kaliakoir | 229 | 21:00 | 221 | 9:00
| Tongi | 230 | 20:00 | 217 | 9:00 | GPH | 233 | 10:00 | 224 | 15:00
| Comilla (N) | 232 | 19:30 | 224 | 1:00 | Jhenaidah | 233 | 18:30 | 223 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 20:00 | 128 | 09:00 | Manikganj | 136 | 11:00 | 126 | 00:00
| Agargaon | 136 | 20:00 | 126 | 10:00 | Maniknagar | 134 | 22:00 | 125 | 10:00
| Agrabad | 138 | 20:00 | 131 | 14:00 | Matarbari | 131 | 11:00 | 117 | 00:00
| AKS | 136 | 06:00 | 130 | 13:00 | Matuail | 134.5 | 19:30 | 128 | 10:00
| Aminbazar | 134 | 19:30 | 125 | 09:00 | Millgate | 135 | 22:00 | 125 | 09:00
| Amnura | 135 | 08:00 | 124 | 05:00 | Mirpur | 133 | 19:30 | 123 | 10:00
| Ashuganj | 139 | 07:00 | 134 | 01:00 | Mithapukur | 134 | 01:00 | 127 | 00:00
| Bagerhat | 129 | 18:30 | 123 | 12:00 | Modern | 137 | 06:00 | 132 | 13:00
| Bakulia | 138 | 17:00 | 131 | 15:00 | Mogbazar | 139 | 22:00 | 127 | 10:00
| Banani | 135 | 22:00 | 127 | 09:00 | Mongla | 134 | 05:00 | 126 | 11:00
| Bangabhaban | 134 | 22:00 | 125 | 10:00 | Motijheel | 134 | 22:00 | 125 | 10:00
| Barapukuria | 135 | 16:00 | 127 | 10:00 | Munshiganj | 139 | 20:00 | 129 | 10:00
| Barguna | 136 | 14:00 | 130 | 00:00 | Mymensingh | 134 | 09:00 | 122 | 00:00
| Barishal | 143 | 15:00 | 129 | 10:00 | Naogaon | 136 | 07:00 | 124 | 00:00
| Barishal | 144 | 14:00 | 132 | 00:00 | Narail | 134 | 18:30 | 123 | 00:00
| Baroaulia | 140 | 17:00 | 132 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 134 | 17:00 | 125 | 00:00 | Narshingdi | 131 | 06:00 | 124 | 00:00
| Bashundhara | 135 | 19:30 | 125 | 09:00 | Natore | 137 | 08:00 | 128 | 00:00
| BashundharaCement | 138 | 19:30 | 130 | 09:00 | Nawabganj | 137 | 22:00 | 130 | 10:00
| Beanibazar | 135 | 06:00 | 127 | 00:00 | Netrakona | 133 | 06:00 | 120 | 01:00
| Benapole | 135 | 18:30 | 127 | 21:00 | New | 135 | 19:30 | 128 | 09:00
| Bhaluka | 131 | 06:00 | 118 | 01:00 | Niamatpur | 137 | 07:00 | 121 | 00:00
| Bhandaria | 145 | 15:00 | 126 | 00:00 | Noapara | 137 | 18:30 | 132 | 09:00
| Bhangura | 140 | 09:00 | 134 | 00:00 | Pabna | 138 | 09:00 | 131 | 01:00
| Bheramara | 136 | 09:00 | 131 | 00:00 | Palashbari | 134 | 08:00 | 126 | 13:00
| Bheramara(GK) | 138 | 09:00 | 132 | 00:00 | Panchagarh | 135 | 02:00 | 120 | 21:00
| Bhulta | 127 | 12:00 | 120 | 00:00 | Patuakhali | 136 | 14:00 | 131 | 01:00
| Bog-Sherpur | 139 | 09:00 | 130 | 00:00 | PHP | 136 | 19:30 | 120 | 01:00
| Bogura | 138 | 08:00 | 131 | 00:00 | Purbachal | 135 | 19:30 | 125 | 09:00
| Bogura | 138 | 09:00 | 132 | 00:00 | Purbasadipur | 135 | 02:00 | 123 | 10:00
| Brahmanbaria | 135 | 11:00 | 127 | 00:00 | Rahim | 135 | 19:00 | 129 | 09:00
| Cantonment | 134 | 19:30 | 125 | 10:00 | Rajbari | 137 | 18:30 | 125 | 00:00
| Chandpur | 140 | 19:30 | 118 | 01:00 | Rajendrapur | 137 | 11:00 | 125 | 00:00
| Chandraghona | 139 | 17:00 | 133 | 01:00 | Rajshahi | 135 | 08:00 | 125 | 23:00
| Chapai | 135 | 08:00 | 125 | 05:00 | Rajshahi | 134 | 09:00 | 125 | 23:00
| Charsaidpur | 138 | 13:00 | 131 | 10:00 | Ramganj | 137 | 15:00 | 114 | 01:00
| Chauddagram | 135 | 20:00 | 121 | 01:00 | Rampur | 137 | 06:00 | 131 | 15:00
| Chhatak | 135 | 14:00 | 127 | 00:00 | Rampura | 137 | 20:00 | 128 | 10:00
| Chowmuhani | 135 | 15:00 | 113 | 01:00 | Rangamati | 139 | 17:00 | 131 | 15:00
| Chuadanga | 132 | 18:30 | 118 | 01:00 | Rangpur | 133 | 01:00 | 123 | 13:00
| Coxsbazar | 130 | 10:00 | 115 | 05:00 | Ruppur | 138 | 09:00 | 131 | 00:00
| Cumilla(N) | 137 | 19:30 | 127 | 01:00 | Saidpur | 135 | 02:00 | 122 | 19:30
| Cumilla(S) | 138 | 19:30 | 126 | 01:00 | Satkhira | 134 | 18:30 | 127 | 21:00
| Daudkandi | 136 | 13:00 | 129 | 07:00 | Satmasjid | 135 | 19:30 | 126 | 10:00
| Dhaka | 138 | 21:00 | 128 | 09:00 | Savar | 135 | 20:00 | 126 | 10:00
| Dhamrai | 133 | 19:30 | 122 | 00:00 | Shahjadpur | 142 | 09:00 | 136 | 00:00
| Dhanmondi | 135 | 20:00 | 128 | 09:00 | Shahjibazar | 138 | 08:00 | 133 | 00:00
| Dohazari | 137 | 17:00 | 128 | 01:00 | Shahmirpur | 139 | 05:00 | 133 | 14:00
| Faridpur | 136 | 13:00 | 126 | 00:00 | Shariatpur | 141 | 14:00 | 126 | 00:00
| Fatullah | 135 | 19:30 | 128 | 10:00 | Sherpur | 140 | 09:00 | 123 | 15:00
| Fenchuganj | 139 | 14:00 | 134 | 00:00 | Shikalbaha | 140 | 17:00 | 132 | 15:00
| Feni | 135 | 15:00 | 121 | 01:00 | Shikalbaha | 139 | 06:00 | 133 | 15:00
| Ghorashal | 141 | 20:00 | 135 | 00:00 | Shitalakhya | 139 | 20:00 | 131 | 09:00
| Goalpara | 138 | 06:00 | 133 | 13:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 137 | 06:00 | 133 | 01:00 | Shyampur | 134 | 20:00 | 130 | 06:00
| Gopalganj | 141 | 20:00 | 134 | 00:00 | Shyampur | 135 | 20:00 | 129 | 10:00
| Gopalganj_I | 141 | 18:30 | 134 | 04:00 | Siddhirganj | 135 | 19:00 | 130 | 09:00
| Gulshan | 137 | 20:00 | 127 | 10:00 | Sirajganj | 138 | 09:00 | 130 | 00:00
| Halishahar | 139 | 17:00 | 131 | 14:00 | Sonargaon | 135 | 13:00 | 132 | 00:00
| Haripur | 135 | 18:30 | 129 | 09:00 | Sreemongol | 140 | 06:00 | 133 | 00:00
| HaripurSBU | 136 | 19:30 | 128 | 10:00 | Srinagar | 136 | 19:00 | 129 | 10:00
| Hasnabad | 137 | 19:30 | 130 | 10:00 | SSM | 140 | 09:00 | 135 | 06:00
| Hathazari | 139 | 20:00 | 134 | 00:00 | Sunamganj | 134 | 09:00 | 125 | 00:00
| Ishurdi | 138 | 09:00 | 132 | 00:00 | Sylhet | 135 | 06:00 | 129 | 00:00
| Jaldhaka | 133 | 02:00 | 120 | 21:00 | Tangail | 137 | 11:00 | 125 | 02:00
| Jamalpur | 141 | 09:00 | 125 | 15:00 | Thakurgaon | 134 | 01:00 | 120 | 21:00
| Jashore | 136 | 18:30 | 128 | 22:00 | TK | 140 | 19:30 | 131 | 14:00
| Jhenaidah | 136 | 18:30 | 128 | 00:00 | Tongi | 136 | 20:00 | 128 | 09:00
| Jhenaidah | 136 | 18:30 | 123 | 02:00 | Ullon | 137 | 20:00 | 128 | 10:00
| Joydebpur | 142 | 19:30 | 133 | 12:00 | Uttara | 133 | 20:00 | 123 | 09:00
| Joypurhat | 138 | 07:00 | 120 | 15:00 | UttaraNew | 136 | 22:00 | 124 | 10:00
| Juldah | 140 | 17:00 | 133 | 13:00 | Zigatola | 136 | 12:00 | 130 | 09:00
| Kabirpur | 138 | 11:00 | 122 | 16:00
| Kachua | 139 | 19:30 | 119 | 01:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 135 | 22:00 | 125 | 10:00
| Kalurghat | 139 | 19:30 | 132 | 15:00
| Kamrangirchar | 136 | 19:30 | 129 | 10:00
| Kaptai | 135 | 21:00 | 132 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 530 | 7071 | 4029 | 11100 |  |  |  | QF-LDC-11
0:30 | 548 | 7799 | 4406 | 12205 | Date: | 2022-06-09
1:00 | 566 | 8527 | 4783 | 13310
1:30 | 561 | 8378 | 4714.5 | 13092.5
2:00 | 556 | 8229 | 4646 | 12875
2:30 | 571 | 8183 | 4636.5 | 12819.5 | [5 empty] | Gen. at Eve. Peak | 12051 | 12051 MW (19:30 )
3:00 | 586 | 8137 | 4627 | 12764 | [6 empty] | 19:30
3:30 | 560 | 8083.5 | 4550 | 12633.5 | [5 empty] | Gen. at Day Peak | 10677 | 10677 MW (10:00 )
4:00 | 534 | 8030 | 4473 | 12503 | [6 empty] | 10:00
4:30 | 532 | 7952.5 | 4401.5 | 12354 | [5 empty] | Highest Generation | 13310
5:00 | 530 | 7875 | 4330 | 12205 | [6 empty] | 1:00
5:30 | 624 | 7563.5 | 4228 | 11791.5
6:00 | 718 | 7252 | 4126 | 11378
6:30 | 812 | 7051 | 4057 | 11108
7:00 | 906 | 6850 | 3988 | 10838
7:30 | 896 | 6856.5 | 3731.5 | 10588
8:00 | 886 | 6863 | 3475 | 10338
8:30 | 763 | 7034 | 3305.5 | 10339.5
9:00 | 640 | 7205 | 3136 | 10341
9:30 | 611 | 7347.5 | 3161.5 | 10509
10:00 | 582 | 7490 | 3187 | 10677
10:30 | 508 | 7290.5 | 3135 | 10425.5
11:00 | 434 | 7091 | 3083 | 10174
11:30 | 405 | 6983 | 3131 | 10114
12:00 | 376 | 6875 | 3179 | 10054
12:30 | 353 | 6795.5 | 3184.5 | 9980
13:00 | 330 | 6716 | 3190 | 9906
13:30 | 436 | 6674 | 3200.5 | 9874.5
14:00 | 542 | 6632 | 3211 | 9843
14:30 | 535 | 6670 | 3203.5 | 9873.5
15:00 | 528 | 6708 | 3196 | 9904
15:30 | 587 | 6698 | 3245.5 | 9943.5
16:00 | 646 | 6688 | 3295 | 9983
16:30 | 676 | 6634.5 | 3328.5 | 9963
17:00 | 706 | 6581 | 3362 | 9943
17:30 | 708 | 6575.5 | 3403 | 9978.5
18:00 | 710 | 6570 | 3444 | 10014
18:30 | 585 | 6873.5 | 3659.5 | 10533
19:00 | 460 | 7177 | 3875 | 11052
19:30 | 390 | 7770 | 4281 | 12051
20:00 | 384 | 7663 | 4251 | 11914 |  |  |  | Executive Engineer
20:30 | 377 | 7654.5 | 4201 | 11855.5 |  |  |  | Network Operation Division
21:00 | 370 | 7646 | 4151 | 11797
21:30 | 357 | 7510.5 | 4128.5 | 11639
22:00 | 344 | 7375 | 4106 | 11481 |  |  |  |  | Page 6 of 7
22:30 | 412 | 7289 | 4101.5 | 11390.5
23:00 | 480 | 7203 | 4097 | 11300
23:30 | 505 | 7137 | 4063 | 11200
24:00 | 530 | 7071 | 4029 | 11100
12051 MW (19:30 )
10677 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-09 |  | Energy |  | 271363091
[13 empty] | 2022-06-09 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3258 | 922 | 2290 | 0 | 3249 | 1015 | 32 | 170 | 194 | 100 | 0 | 0
0:30 | 3288.5 | 922.5 | 2255.5 | 338.5 | 3596 | 1130 | 32 | 265 | 439.5 | 110 | 0 | 0 | Date: | 2022-06-09
1:00 | 3319 | 923 | 2221 | 677 | 3943 | 1245 | 32 | 360 | 685 | 120 | 0 | 0
1:30 | 3318 | 923 | 2229 | 499 | 3916.5 | 1225 | 32 | 359.5 | 685 | 120 | 0 | 0 | [7 empty] | Total Energy | 271.3631 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3317 | 923 | 2237 | 321 | 3890 | 1205 | 32 | 359 | 685 | 120 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3322.5 | 923 | 2238.5 | 260.5 | 3904 | 1195 | 32 | 359.5 | 681 | 118 | 0 | 0 | [7 empty] | Energy Requirement | 271.3631
3:00 | 3328 | 923 | 2240 | 200 | 3918 | 1185 | 32 | 360 | 677 | 116 | 0 | 0
3:30 | 3317.5 | 923 | 2218 | 200 | 3891.5 | 1180 | 32 | 360.5 | 611.5 | 115 | 0 | 0 | [5 empty] | Shortage
4:00 | 3307 | 923 | 2196 | 200 | 3865 | 1175 | 32 | 361 | 546 | 114 | 0 | 0
4:30 | 3334.5 | 923 | 2207 | 160 | 3816 | 1175 | 32 | 360.5 | 449.5 | 112 | 0 | 0
5:00 | 3362 | 923 | 2218 | 120 | 3767 | 1175 | 32 | 360 | 353 | 110 | 0 | 0
5:30 | 3300 | 923 | 2168.5 | 60 | 3573 | 1160 | 32 | 361 | 321 | 106 | 3 | 0
6:00 | 3238 | 923 | 2119 | 0 | 3379 | 1145 | 32 | 362 | 289 | 102 | 6 | 0
6:30 | 3240.5 | 923 | 2121 | 0 | 3146.5 | 1130 | 31.5 | 362 | 253 | 102 | 15.5 | 0 |  |  |  | Coal
7:00 | 3243 | 923 | 2123 | 0 | 2914 | 1115 | 31 | 362 | 217 | 102 | 25 | 0
7:30 | 3273.5 | 922.5 | 2059.5 | 0 | 2811.5 | 1045 | 31.5 | 293.5 | 217 | 103 | 32 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3304 | 922 | 1996 | 0 | 2709 | 975 | 32 | 225 | 217 | 104 | 39 | 0
8:30 | 3266 | 922.5 | 1969.5 | 0 | 2840 | 915 | 32 | 197.5 | 189.5 | 106 | 59 | 0
9:00 | 3228 | 923 | 1943 | 0 | 2971 | 855 | 32 | 170 | 162 | 108 | 79 | 0
9:30 | 3203 | 922.5 | 2015 | 94.5 | 3025.5 | 840 | 32 | 170 | 154 | 107 | 75.5 | 0
10:00 | 3178 | 922 | 2087 | 189 | 3080 | 825 | 32 | 170 | 146 | 106 | 72 | 0
10:30 | 3099 | 922 | 2044 | 130.5 | 3011.5 | 815 | 32 | 170 | 146 | 110 | 75.5 | 0
11:00 | 3020 | 922 | 2001 | 72 | 2943 | 805 | 32 | 170 | 146 | 114 | 79 | 0
11:30 | 3045.5 | 922.5 | 2054.5 | 36 | 2833.5 | 810 | 32 | 170 | 149 | 117 | 74 | 0
12:00 | 3071 | 923 | 2108 | 0 | 2724 | 815 | 32 | 170 | 152 | 120 | 69 | 0
12:30 | 3096 | 923 | 2082 | 0 | 2650.5 | 825 | 32 | 170 | 162.5 | 120 | 49 | 0
13:00 | 3121 | 923 | 2056 | 0 | 2577 | 835 | 32 | 170 | 173 | 120 | 29 | 0
13:30 | 3121 | 923 | 2056 | 0 | 2577 | 835 | 32 | 170 | 173 | 120 | 29 | 0
14:00 | 3121 | 923 | 2056 | 0 | 2577 | 835 | 32 | 170 | 173 | 120 | 29 | 0
14:30 | 3103 | 923 | 2060.5 | 0 | 2624.5 | 835 | 32 | 170 | 159.5 | 102 | 25.5 | 0
15:00 | 3085 | 923 | 2065 | 0 | 2672 | 835 | 32 | 170 | 146 | 84 | 22 | 0
15:30 | 3151.5 | 923 | 2119.5 | 0 | 2588.5 | 835 | 32 | 170 | 149 | 87 | 18 | 0
16:00 | 3218 | 923 | 2174 | 0 | 2505 | 835 | 32 | 170 | 152 | 90 | 14 | 0
16:30 | 3140 | 923 | 2144 | 0 | 2532.5 | 840 | 32 | 170 | 168.5 | 93 | 11 | 0
17:00 | 3140 | 923 | 2114 | 0 | 2560 | 845 | 32 | 170 | 185 | 96 | 8 | 0
17:30 | 3197.5 | 923 | 2134 | 0 | 2504.5 | 850 | 32 | 170 | 196.5 | 96 | 5 | 0
18:00 | 3255 | 923 | 2154 | 0 | 2449 | 855 | 32 | 170 | 208 | 96 | 2 | 0
18:30 | 3283.5 | 922.5 | 2181 | 0 | 2715.5 | 860 | 32 | 170 | 396.5 | 101 | 1 | 0
19:00 | 3312 | 922 | 2208 | 0 | 2982 | 865 | 32 | 170 | 585 | 106 | 0 | 0
19:30 | 3358 | 923 | 2174 | 0 | 3815 | 955 | 32 | 170 | 654 | 100 | 0 | 0
20:00 | 3342 | 922 | 2169 | 0 | 3828 | 955 | 32 | 170 | 524 | 102 | 0 | 0
20:30 | 3400 | 922.5 | 2187 | 0 | 3760.5 | 980 | 32 | 170 | 429.5 | 104 | 0 | 0
21:00 | 3458 | 923 | 2205 | 0 | 3693 | 1005 | 32 | 170 | 335 | 106 | 0 | 0
21:30 | 3451.5 | 922.5 | 2204.5 | 0 | 3590 | 1010 | 32 | 170 | 284.5 | 104 | 0 | 0
22:00 | 3445 | 922 | 2204 | 0 | 3487 | 1015 | 32 | 170 | 234 | 102 | 0 | 0
22:30 | 3399 | 922 | 2244.5 | 0 | 3422 | 1015 | 32 | 170 | 214 | 102 | 0 | 0
23:00 | 3353 | 922 | 2285 | 0 | 3357 | 1015 | 32 | 170 | 194 | 102 | 0 | 0
23:30 | 3305.5 | 922 | 2287.5 | 0 | 3303 | 1015 | 32 | 170 | 194 | 101 | 0 | 0 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 3258 | 922 | 2290 | 0 | 3249 | 1015 | 32 | 170 | 194 | 100 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 763260
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 0 |  |  | 0 | 4 | 18 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 15 | 20 | 8 | 8 | 0 | 0 | 295389
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 7 | 7 | 4 | 13 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [8 empty] | 55620
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 34 | 17 | 0 |  |  | 104845
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 101 | 105 | 97 | 96 | 105 | 105 | 92 | 89 |  | 87 | 87 | 91 | 105 | 105 | 105 | 105 | 2464763
| Daudkandi 200 MW PP (B.Trac) | 200 | 200 | 200 | 200 | 120 | 0 |  |  | 0 | 30 | 10 | 0 | [14 empty] | 1023360
14 | Titas 50 MW Peaking PP | 38 | 39 | 40 | 40 | 40 | 40 | 0 |  |  |  | 0 | 22 | 27 | 25 | 0 |  |  | 0 |  | 19 | 32 |  |  |  |  | 0 | 382200
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 296 | 296 | 296 | 293 | 288 | 281 | 195 | 195 | 250 | 293 | 293 | 293 | 265 | 260 | 260 | 210 | 210 | 210 |  | 235 | 270 | 295 | 293 | 145 | 145 | 145 | 6169852
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 100 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 250 | 280 | 280 | 280 | 280 | 6262991
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 34 | 34 | 30 | 30 | 38 | 38 | 38 | 38 | 38 |  | 37 | 37 | 33 | 36 | 37 | 34 | 31 | 754776
33 | Ashuganj 225 MW CCPP | 210 | 209 | 210 | 211 | 212 | 213 | 212 | 209 | 211 | 197 | 181 | 201 | 212 | 214 | 213 | 209 | 187 | 181 |  | 211 | 215 | 216 | 213 | 216 | 215 | 215 | 5028000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 6955000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 48 | 50 | 49 | 47 | 48 | 51 | 54 | 54 | 52 | 55 | 55 |  | 55 | 55 | 55 | 55 | 54 | 55 | 54 | 1179360
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 404 | 408 | 407 | 408 | 406 | 407 | 407 | 408 | 404 | 406 | 414 | 412 | 411 | 413 | 413 | 411 | 411 |  | 411 | 409 | 411 | 411 | 412 | 412 | 412 | 9947130
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5195900
41 | Haripur 360MW CCPP(HPL) | 320 | 330 | 330 | 326 | 326 | 300 | 300 | 300 | 302 | 340 | 342 | 337 | 302 | 302 | 332 | 343 | 342 | 341 |  | 345 | 346 | 347 | 347 | 348 | 347 | 347 | 7868000
42 | RPCL 210MW CCPP | 134 | 127 | 130 | 130 | 134 | 135 | 128 | 109 | 70 | 87 | 87 | 87 | 84 | 72 | 72 | 72 | 85 | 98 |  | 102 | 109 | 113 | 138 | 132 | 132 | 132 | 2533440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 2 | 7 | 13 | 3 | 3 | 1 | 4 | 5 | 5 | 5 | 2 | 1 | [8 empty] | 54330
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 |  | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 1031000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 934744
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 57 | 57 | 56 | 55 | 61 | 60 | 60 | 60 | 40 | 40 | 40 | 61 | 62 | 62 |  | 61 | 62 | 62 | 61 | 62 | 62 | 62 | 1349648
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 72 | 75 | 78 | 78 | 75 | 75 | 75 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1846080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429000
52 | Sylhet 50MW PP (EPL) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 39 | 38 | 38 | 41 | 41 | 42 | 40 | 42 | 42 |  | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 965640
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 256860
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1279800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 22 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 556425
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 290 | 270 | 280 | 260 | 265 | 280 | 275 | 310 | 260 | 280 | 270 | 270 | 295 | 300 | 270 | 275 |  | 280 | 265 | 260 | 270 | 280 | 290 | 290 | 6902500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 352 | 360 | 395 | 400 | 389 | 350 | 390 | 394 | 360 | 360 | 398 | 365 | 360 |  | 360 | 360 | 348 | 400 | 400 | 312 | 220 | 9042300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 45 | 55 | 55 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1055643
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14 | 17 | 20 | 21 | 20 | 14 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 552336
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 532368
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [5 empty] | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 367632
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 17 | 20 | 17 | 20 | 14 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 373284
63 | Impoprt (Tripura) | 120 | 120 | 116 | 114 | 110 | 102 | 102 | 104 | 108 | 106 | 114 | 120 | 120 | 126 | 84 | 90 | 96 | 96 |  | 106 | 100 | 102 | 106 | 102 | 102 | 100 | 2552640
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 11 | 5 | 4 | 4 | 6 | 9 | 9 | 4 | 6 | 6 | 10 |  | 18 | 23 | 21 | 33 | 36 | 38 | 39 | 532320
65 | Feni 22MW PP (Doreen) | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 394776
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 162900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 28 | 16 | 16 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 31 | 33 | 756500
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 15 | 14 | 14 | 15 | 6 | 6 | 8 | 14 | 19 |  | 19 | 20 | 20 | 20 | 20 | 20 | 19 | 432730
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 0 |  | 0 | 0 | 0 | 25 | 25 |  | 16 | 16 | 25 | 26 | 27 | 27 | 27 | 472680
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 734400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 0 | 0 | 0 | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 483200
73 | Ghorashal 108MW PP (Regent) | 96 | 96 | 96 | 92 | 92 | 91 | 91 | 92 | 90 | 90 | 91 | 91 | 92 | 91 | 93 | 90 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 97 | 97 | 2182909
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 62 | 98 | 489060
| Chowmuhani 113 MW | 13 | 4 | 8 | 0 |  |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 13 | 26 | 26 | 26 |  | 26 | 94 | 79 | 93 | 94 | 94 | 31 | 607320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 154 | 120 | 108 | 108 | 141 | 162 | 162 | 162 | 126 | 126 | 126 | 90 | 90 | 90 |  | 92 | 162 | 162 | 108 | 100 | 54 | 54 | 3096000
77 | Siddhirganj 100 PP(Dutch Bangla) | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 74 | 78 | 80 | 78 | 66 | 60 | 60 | 60 | 60 | 30 |  | 39 | 91 | 90 | 55 | 50 | 9 | 8 | 1522790
78 | Gazipur 52 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 38 | 48 | 48 | 24 | 16 | 20 | 24 | 24 | 24 | 24 | 24 |  | 35 | 50 | 50 | 34 | 32 | 24 | 24 | 858240
79 | Kodda 150MW PP | 150 | 150 | 150 | 132 | 98 | 32 | 0 | 32 | 32 | 16 | 16 | 0 | 16 | 16 | 16 | 16 | 48 | 48 |  | 82 | 115 | 98 | 98 | 64 | 64 | 64 | 1463520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200328
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 80 | 105 | 52 | 18 | 25 | 34 | 36 | 70 | 70 | 75 |  | 86 | 90 | 90 | 90 | 90 | 90 | 105 | 2016852
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 0 | 3 | 4 | 5 | 4 | 4 | 4 | 2 | 1 | 1 | 0 | [8 empty] | 31680
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1369641
| Karnaphuli Power Ltd. | 103 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 96 | 92 | 94 | 110 | 110 | 110 | 92 | 92 |  | 93 | 92 | 92 | 92 | 107 | 110 | 110 | 2514107
82 | Madanganj 102 PP(Summit) | 94 | 94 | 94 | 94 | 92 | 92 | 94 | 94 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 88 | 2232384
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 140 | 142 | 140 | 135 | 138 | 130 | 132 | 135 | 148 | 125 | 140 | 130 | 140 | 130 | 132 | 143 | 135 | 148 |  | 150 | 132 | 126 | 148 | 130 | 140 | 142 | 3382255
87 | Meghnaghat 100 MW(IEL) | 88 | 89 | 88 | 89 | 89 | 88 | 89 | 89 | 80 | 80 | 81 | 80 | 82 | 82 | 78 | 72 | 78 | 82 |  | 83 | 83 | 83 | 92 | 87 | 83 | 85 | 2028480
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 91 | 92 | 90 | 83 | 71 | 71 | 76 | 90 | 90 | 90 | 90 | 90 |  | 97 | 104 | 104 | 104 | 104 | 104 | 101 | 2315520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 90 | 90 | 90 | 90 | 80 | 40 | 40 | 90 | 90 | 90 | 90 | 78 | 78 | 78 | 78 | 80 | 40 |  | 78 | 90 | 100 | 100 | 100 | 90 | 90 | 1922400
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 45 | 45 |  | 46 | 46 | 46 | 46 | 49 | 49 | 49 | 1102680
93 | Ashuganj 51 MW PP (Midland) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 51 | 51 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1065931
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 93 | 94 | 94 | 48 | 48 | 48 | 0 | 68 | 94 | 94 | 74 | 74 | 74 | 74 | 74 | 32 |  | 64 | 84 | 94 | 48 | 24 | 7 | 7 | 1537488
95 | Patenga 50MW PP (Baraka) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 42 |  | 38 | 37 | 39 | 43 | 44 | 44 | 44 | 1042560
96 | Chattogram 108 MW PP (ECPV) | 70 | 71 | 71 | 51 | 43 | 31 | 11 | 13 | 13 | 22 | 61 | 33 | 19 | [6 empty] | 17 | 43 | 31 |  |  |  | 0 | 567360
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 |  | 25 | 55 | 55 | 55 | 55 | 40 | 40 | 1057764
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1334035
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2672182
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 3950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 |  | 37 | 54 | 54 | 54 | 54 | 54 | 54 | 1206360
104 | Keranigonj 300 MW PP (APR) | 202 | 21 | 0 | [5 empty] | 0 | 109 | 12 | 0 | [13 empty] | 0 | 477671
105 | Bramhangoan 100 MW PP (Aggreko) | 98 | 50 | 0 | [5 empty] | 0 | 25 | 25 | 0 | [13 empty] | 0 | 253829
106 | Mymensingh 200 MW PP (United) | 186 | 186 | 200 | 184 | 185 | 160 | 130 | 139 | 170 | 140 | 45 | 47 | 75 | 75 | 75 | 75 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3158400
112 | Aurahati 100MW PP (Aggreko) | 97 | 50 | 0 | [5 empty] | 0 | 25 | 25 | 0 | [13 empty] | 0 | 234683
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 138 | 132 | 132 | 132 | 113 | 109 | 125 | 132 | 132 | 132 | 132 | 132 | 132 | 112 | 108 | 109 |  | 124 | 134 | 133 | 132 | 134 | 135 | 135 | 3146688
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 63 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2071680
116 | Chandpur 200MW (Desh energy) | 104 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 34 | 34 | 34 |  | 40 | 136 | 128 | 136 | 136 | 136 | 128 | 2151360
117 | Ashuganj 150MW PP (Midland) | 138 | 135 | 135 | 128 | 130 | 130 | 132 | 123 | 123 | 125 | 123 | 123 | 132 | 133 | 130 | 137 | 135 | 142 |  | 145 | 146 | 145 | 147 | 147 | 147 | 147 | 3246763
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 400 | 400 | 400 | 365 | 364 | 399 | 401 | 398 | 359 | 402 | 404 | 351 | 401 | 401 | 364 | 364 |  | 398 | 401 | 401 | 402 | 400 | 401 | 399 | 9374000
| Jamalpur 115 MW PP (United) | 83 | 83 | 93 | 93 | 86 | 32 | 32 | 32 | 32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 40 | 92 | 108 | 98 | 98 | 98 | 99 | 1195200
| Anwara 300 MW PP (United) | 247 | 247 | 247 | 247 | 228 | 193 | 150 | 150 | 230 | 230 | 230 | 190 | 120 | 65 | 65 | 65 | 65 | 30 |  | 170 | 190 | 155 | 155 | 115 | 120 | 117 | 3996982
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2375040
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2175382
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 5 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 648000
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 96 | 91 | 94 | 98 | 87 | 89 | 96 | 84 | 77 | 76 | 67 | 64 | 76 | 94 | 100 | 70 | 70 | 70 |  | 84 | 100 | 100 | 100 | 100 | 100 | 85 | 2090880
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 41 | 35 | 37 | 55 | 55 | 55 | 0 | 11 | 32 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1179360
120 | Eastern Zone Total | 8527 | 8229 | 8137 | 8030 | 7875 | 7252 | 6850 | 6863 | 7205 | 7490 | 7091 | 6875 | 6716 | 6632 | 6708 | 6688 | 6581 | 6570 |  | 7177 | 7770 | 7663 | 7646 | 7375 | 7203 | 7071 | 176315563
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 94 | 94 | 94 | 95 | 95 | 95 | 66 | 51 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 16 |  | 26 | 61 | 65 | 81 | 81 | 81 | 81 | 1265280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 32 | 32 | 32 | 0 | [13 empty] | 2 |  | 39 | 45 | 8 |  |  |  |  | 154560
| Khulna 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1832408
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 93 | 93 | 53 | 53 | 35 | 17 | 17 | 0 | [5 empty] | 14 | 17 |  | 55 | 90 | 90 | 98 | 105 | 70 | 70 | 1205760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 15 | 25 | 54 | 60 | 56 | 61 | 16 | 11 | 9 | 5 | 4 | 1 | [8 empty] | 379440
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [9 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 267600
133 | Bhola Nutan Biddut BD LTD (GAS) | 215 | 215 | 214 | 203 | 213 | 213 | 213 | 174 | 163 | 165 | 164 | 214 | 182 | 162 | 162 | 179 | 180 | 200 |  | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 4690118
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 729792
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 84 | 84 | 84 | 56 | 86 | 78 | 78 | 86 | 86 | 87 | 87 | 75 | 75 | 75 | 72 | 75 | 75 | 81 |  | 81 | 73 | 72 | 81 | 72 | 81 | 81 | 1931345
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 33 | 32 | 31 | 26 | 25 | 22 | 20 | 20 | 21 | 20 | 21 | 19 | 6 | 8 | 14 | 16 |  | 20 | 23 | 24 | 23 | 24 | 24 | 24 | 539770
141 | Noapara 100 MW PP (Bangla Trac) | 30 | 0 | [23 empty] | 0 | 86400
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 8 | 8 | 8 | 0 | [6 empty] | 8 |  | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 496500
143 | Gopalganj 100 MW Peaking PP | 66 | 66 | 66 | 0 | [11 empty] | 2 | 3 | 24 |  | 87 | 80 | 80 |  |  |  |  | 371072
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 50 | 50 | 32 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 22 | 80 | 105 | 105 | 105 | 105 | 105 | 1450944
146 | Bheramara HVDC | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 922 | 923 | 922 | 922 | 923 | 923 | 923 | 923 | 923 | 923 | 923 |  | 922 | 923 | 922 | 923 | 922 | 922 | 922 | 22312727
147 | Bheramara 410 MW CCPP | 190 | 195 | 200 | 205 | 205 | 205 | 205 | 220 | 200 | 225 | 200 | 180 | 185 | 180 | 180 | 220 | 220 | 220 |  | 220 | 250 | 265 | 260 | 260 | 260 | 250 | 5331456
148 | Payra 1320 MW | 1070 | 1030 | 1010 | 1000 | 1000 | 970 | 940 | 800 | 680 | 650 | 630 | 640 | 660 | 650 | 660 | 660 | 670 | 680 |  | 690 | 780 | 780 | 830 | 840 | 840 | 840 | 21271300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4285000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 0 | [14 empty] | 32 | 32 | 34 | 0 |  |  |  | 186311
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 200 | 201 | 201 | 203 | 213 | 180 | 180 | 181 | 150 | 130 | 130 | 140 | 160 | 160 | 160 | 165 | 200 | 214 |  | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 4795009
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 215 | 214 | 215 | 216 | 215 | 217 | 217 | 185 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3987036
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 414 | 421 | 422 | 422 | 383 | 383 | 303 | 252 | 350 | 303 | 350 | 354 | 352 | 352 | 420 | 380 | 370 |  | 380 | 370 | 376 | 370 | 370 | 427 | 428 | 9044436
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 10 | 10 | 0 | [12 empty] | 4 | 4 | 4 |  | 4 | 9 | 0 |  |  |  |  | 41235
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  |  | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 11 | 8 | 8 | 11 | 201780
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 0 | [14 empty] | 8 | 34 | 8 | 0 |  |  |  | 179051
167 | Katakhali 50 MW Peaking PP | 16 | 16 | 16 | 0 | [15 empty] | 29 | 32 | 12 | 0 |  |  |  | 95690
168 | Santahar 50 MW Peaking PP | 37 | 37 | 37 | 37 | 0 | [14 empty] | 38 | 38 | 38 | 0 |  |  | 0 | 226871
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 106565
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 0 | [14 empty] | 74 | 90 | 90 | 90 | 40 | 0 |  | 696328
171 | Baghabari 200 MW PP (Paramount) | 50 | 0 | [23 empty] | 0 | 94007
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 50 | 50 | 50 | 50 |  | 50 | 80 | 90 | 94 | 94 | 94 | 94 | 1697856
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 50 | 50 | 50 | 50 |  | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 1693056
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 74 | 74 | 74 | 74 | 75 | 75 | 54 | 34 | 34 | 34 | 34 | 34 | 40 | 71 | 74 | 74 | 74 | 74 |  | 90 | 100 | 101 | 102 | 102 | 102 | 76 | 1656508
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 1 | 2 | 3 | 4 | 6 | 4 | 3 | 1 | 0 | [8 empty] | 22857
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 65 | 72 | 72 | 35 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 34 | 1214400
178