## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-16 | Thursday
|  |  | Date (day): | 2022-06-16 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13031.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14696 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-15 | 2022-06-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 280 | 280 | 280 |  | 85 | Condencer problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 97 | 97 | 97 |  | 11 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 399 | 409 | 405 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 311 | 337 | 330 | 330
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-2 S/D due to Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 85 | 79 | 90 |  | 10 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Machine problem.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 94 | 0 | 0 | 0 | 210 |  | GT-2 U/M & gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 88 | 100 | 90 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 335 | 300 | 335 | 0
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 42 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 43 | 47 | 48 | 48
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 276 | 290 | 285 | 290 |  | 10 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 301 | 25 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 90 | 90 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 80 | 50 | 98 | 98
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 132 | 130 | 135 |  | 14 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 90 | 90 | 90 |  |  | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 92 | 93 | 93 |  | 11 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3513 | 3647 | 3951 | 3994 | 486 | 1323
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 20 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 44 | 44 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 32 | 32 | 38 | 38 |  | 192 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 34 | 17 | 35 |  | 63 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 78 | 90 | 78 | 90 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 30 | 5 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 78 | 78 | 81 |  | 27 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 248 | 265 | 265 | 265 |  | 35 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 90 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1150 | 1320 | 1246 | 1330 | 311 | 744
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 213 | 210 | 210 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 10 | 100 | 250 | 110 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 280 | 270 | 280 | 80 |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 34 | 38 | 38 |  | 7 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 5 | 10 | 5 |  |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 92 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 110 | 133 | 140 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 40 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 91 | 90 | 90 |  | 163 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 16 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 82 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 25 | 50 | 0 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 13 | 9 | 9 | 104 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 102 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1289 | 1417 | 1478 | 1905 | 781 | 214
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 87 | 142 | 110 | 120 | 82 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 14 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 188 | 191 | 180 | 191 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 85 | 97 | 95 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 11 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 414 | 466 | 478.6 | 458 | 82 | 18
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 50 | 50 | 50 | 50 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 62 | 65
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 125 | 100 | 200 |  |  | Machine problem
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 19 | 19
| 103 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 37 | 31 | 41 | 41
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 24 | 24 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 275 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 285 | 285 | 285 |  |  | ST S/D.
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 102 | 400 | 100 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 934 | 1619 | 1338 | 1772 | 330 | 229
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 907 | 920 | 920
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 60 | 78 | 92 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 38 | 38 |  | 16 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 217 | 120 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 205 | 230 | 230 | 180 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 40 | 40
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 0 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 20 | 93 | 93 | 93
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 55 | 89 | 70 | 89
| 118 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 81 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1490 | 1740 | 1703 | 1905 | 180 | 65
| 119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 48 | 48 | 48 |  |  | Rampal Transformar O/L
| 120 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 40 | 40 | 19 | 32 | 23 | 33
| 121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 83 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
| 122 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1000 | 1050 | 1050 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 222 | 180 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1235 | 1402 | 1403 | 1453 | 109 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 8 | 0 | 0 |  | 71 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 8 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 216 | 130 | 210 |  |  | Running on HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 175 | 180 | 210 |  |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 350 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 30 | 40 |  | 10 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 11 | 20 | 100 | 190 |  | 10 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 94 | 94 |  |  | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 95 | 95 |  |  | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1095 | 1283 | 1084 | 1476 | 433 | 157
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 74 | 87 | 95 | 95 |  | 13 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 108 | 72 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 286 | 370 | 350 | 403 | 269 | 20
|  | Total |  |  |  |  | 22348 | 21396 | 11406 | 13264 | 13031.6 | 14696 | 2981 | 2770
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10981.1901 | 12769.99 | 12546.2456 | 14148.656
| A. |  | 2022-06-15 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13306 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10479 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13264 | MW
| 3 | Day peak Generation : |  |  | 11406 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12769.99 | MW
| 4 | Evening peak Generation : |  |  | 13264 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 287.8091 | MKWHr | By Solar | 0.73198 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 121.1252 | MKWHr |  | By Oil: | 112.7534 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 28.3564 | MKWHr |  | By Hydro: | 0.80442 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2981 | MW | Dhaka | 4769.15 | 4769.15 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2770 | MW | Chittagong | 1245.44 | 1245.44 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5751 | MW | Khulna | 1657.4 | 1657.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1014.9 | MMCFD |  |  | Rajshahi | 1453 | 1453 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 143025320.692 | ii) Oil : | Taka | 1587530837.84 | Comilla | 1110 | 1110 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 239553196 | Total | Taka | 1970109354.532 | Mymensingh | 984 | 984 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 385 | 385 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 318 | MW (E to W) at | 21:00 | hrs | Barisal | 413 | 413 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 314 | MW at | 24:00 | hrs | Rangpur | 753 | 753 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.3° C |  |  | Total | 12769.99 | 12769.99 |  | 0
| B. |  | 2022-06-16 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14696 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11300 | MW
| 4 | Reserve(Generation end) |  |  |  | 696 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 302.8203 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10104 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.92 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1178 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 71.79 |  | (b) Today: | 74.02 |  | (c) Rule Curve: |  | 79.95
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 399 | 332 |  | 0 | 225 | 0 | 78 | 0 | 42 | 0 | 0 | 97 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 23 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 34 | 0 | 90 | 81 | 39 | 22 | 36 | 0 | 0 | 0 | 0 | 349 | 158 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 33 | 20 | 104 | 124 | 0 | 20 | 0 | 43 | 41 | 51 | 47 | 110 | 0 | 64 | 81 | 0 | 0 | 19 | 38 | 10 | 300 | 24 | 11 | 25 | 291 | 304 | 96 | 187 | 94 | 121 | 0 | 90 | 180 | 122 | 0 | 94 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 14 | 100 | 50 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 906 | 0 | 280 | 0 | 111 | 223 | 0 | 0 | 33 | 54 | 8 | 146 | 31 | 48 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 34 | 24 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 60 | 197 | 0 | 414 | 94 | 189 | 94 | 88 | 75 | 0 | 0 | 95 | 1060 | 109 | 0 | 17 | 0 | 0 | 72 |  | 7706 | 5044 | 12750 | 2860 | 906 | 2074 | 768 | 3838 | 1235 | 32 | 436 | 710 | 104 | 0 | 0 | 71.65
2:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 397 | 331 |  | 0 | 225 | 0 | 79 | 0 | 55 | 0 | 0 | 97 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 23 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 80 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 349 | 163 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 102 | 121 | 0 | 17 | 0 | 43 | 41 | 50 | 44 | 110 | 0 | 64 | 81 | 0 | 0 | 19 | 38 | 10 | 280 | 16 | 11 | 25 | 293 | 250 | 96 | 200 | 94 | 132 | 0 | 90 | 100 | 128 | 0 | 85 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 50 | 94 | 0 | 162 | 75 | 0 | 35 | 0 | 101 | 55 |  | 907 | 0 | 280 | 0 | 112 | 223 | 0 | 0 | 33 | 43 | 0 | 147 | 28 | 48 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 34 | 24 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 10 | 196 | 0 | 419 | 94 | 186 | 94 | 88 | 75 | 0 | 0 | 95 | 1050 | 108 | 0 | 17 | 0 | 0 | 36 |  | 7472 | 4933 | 12405 | 2849 | 907 | 2050 | 661 | 3736 | 1226 | 32 | 439 | 619 | 102 | 0 | 0 | 71.67
3:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 397 | 331 |  | 0 | 225 | 0 | 79 | 0 | 55 | 0 | 0 | 97 | 91 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 81 | 44 | 0 | 36 | 0 | 0 | 0 | 0 | 338 | 173 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 98 | 123 | 0 | 17 | 0 | 43 | 41 | 51 | 44 | 110 | 0 | 64 | 81 | 0 | 0 | 19 | 38 | 10 | 280 | 23 | 11 | 25 | 293 | 206 | 95 | 188 | 95 | 132 | 0 | 90 | 100 | 133 | 0 | 85 | 90 | 105 | 0 | 248 | 54 | 110 | 0 | 9 | 100 | 50 | 90 | 0 | 162 | 90 | 0 | 35 | 0 | 97 | 55 |  | 906 | 0 | 275 | 0 | 111 | 210 | 0 | 0 | 33 | 43 | 0 | 148 | 33 | 48 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 34 | 24 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 195 | 0 | 422 | 94 | 0 | 94 | 88 | 76 | 0 | 0 | 95 | 1020 | 108 | 0 | 17 | 0 | 0 | 36 |  | 7394 | 4638 | 12032 | 2829 | 906 | 2059 | 421 | 3720 | 1195 | 32 | 413 | 562 | 98 | 0 | 0 | 71.7
4:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 398 | 331 |  | 0 | 225 | 0 | 79 | 0 | 55 | 0 | 0 | 97 | 91 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 81 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 345 | 178 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 98 | 136 | 0 | 17 | 0 | 43 | 41 | 50 | 40 | 110 | 0 | 64 | 81 | 0 | 0 | 19 | 38 | 10 | 290 | 23 | 11 | 0 | 293 | 40 | 97 | 190 | 95 | 132 | 0 | 90 | 100 | 132 | 0 | 86 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 50 | 97 | 0 | 162 | 90 | 0 | 35 | 0 | 85 | 55 |  | 907 | 0 | 273 | 0 | 110 | 120 | 0 | 0 | 33 | 30 | 0 | 148 | 33 | 48 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 34 | 24 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 192 | 0 | 420 | 94 | 0 | 94 | 88 | 76 | 0 | 0 | 95 | 1020 | 108 | 0 | 17 | 0 | 0 | 35 |  | 7264 | 4454 | 11718 | 2872 | 907 | 2062 | 232 | 3724 | 1195 | 32 | 250 | 476 | 98 | 0 | 0 | 71.73
5:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 398 | 331 |  | 0 | 225 | 0 | 79 | 0 | 40 | 0 | 0 | 98 | 91 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 48 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 75 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 349 | 178 | 73 | 0 | 37 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 96 | 136 | 0 | 17 | 0 | 43 | 41 | 51 | 44 | 110 | 0 | 64 | 78 | 0 | 0 | 19 | 38 | 10 | 280 | 23 | 11 | 0 | 293 | 0 | 25 | 191 | 0 | 132 | 0 | 90 | 100 | 130 | 0 | 86 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 50 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 907 | 0 | 273 | 0 | 110 | 120 | 0 | 0 | 29 | 30 | 0 | 148 | 30 | 48 | 0 | 0 | 0 | 25 | 0 | 46 | 0 | 34 | 24 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 191 | 0 | 420 | 94 | 0 | 94 | 88 | 75 | 0 | 0 | 95 | 990 | 108 | 0 | 17 | 0 | 0 | 36 |  | 7044 | 4416 | 11460 | 2876 | 907 | 2052 | 25 | 3715 | 1165 | 32 | 250 | 472 | 96 | 0 | 0 | 71.76
6:00 | 0 | 0 | 0 | 180 | 280 | 94 | 0 | 397 | 282 |  | 0 | 225 | 0 | 79 | 0 | 40 | 0 | 0 | 60 | 91 | 85 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 80 | 49 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 356 | 172 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 86 | 123 | 0 | 18 | 0 | 43 | 41 | 50 | 44 | 110 | 0 | 65 | 78 | 0 | 0 | 19 | 38 | 10 | 270 | 23 | 11 | 0 | 281 | 0 | 0 | 190 | 0 | 118 | 1 | 90 | 100 | 132 | 0 | 85 | 90 | 105 | 0 | 210 | 54 | 107 | 0 | 9 | 100 | 50 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 44 |  | 906 | 0 | 275 | 0 | 110 | 120 | 0 | 0 | 0 | 30 | 0 | 151 | 26 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 24 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 300 | 94 | 0 | 50 | 88 | 46 | 0 | 0 | 50 | 940 | 109 | 0 | 17 | 0 | 2 | 36 |  | 6700 | 3961 | 10661 | 2801 | 906 | 1865 | 0 | 3409 | 1115 | 32 | 250 | 324 | 86 | 3 | 0 | 71.79
7:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 397 | 282 |  | 0 | 225 | 0 | 72 | 0 | 40 | 0 | 0 | 60 | 91 | 85 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 24 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 43 | 44 | 22 | 36 | 0 | 0 | 0 | 0 | 349 | 172 | 73 | 0 | 37 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 9 | 84 | 120 | 0 | 17 | 0 | 43 | 41 | 11 | 10 | 110 | 0 | 65 | 40 | 0 | 0 | 19 | 38 | 10 | 290 | 23 | 11 | 0 | 285 | 0 | 0 | 190 | 0 | 128 | 1 | 90 | 100 | 135 | 0 | 86 | 90 | 105 | 1 | 210 | 54 | 110 | 0 | 9 | 100 | 50 | 92 | 3 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 906 | 0 | 275 | 0 | 108 | 120 | 0 | 0 | 0 | 0 | 0 | 149 | 22 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 24 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 300 | 94 | 0 | 50 | 88 | 38 | 0 | 0 | 50 | 880 | 108 | 0 | 17 | 0 | 13 | 36 |  | 6618 | 3865 | 10483 | 2777 | 906 | 1771 | 0 | 3426 | 1055 | 32 | 250 | 294 | 84 | 18 | 0 | 71.82
8:00 | 0 | 0 | 0 | 180 | 260 | 91 | 0 | 397 | 251 |  | 0 | 225 | 0 | 77 | 0 | 40 | 0 | 0 | 40 | 86 | 85 | 130 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 25 | 28 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 78 | 44 | 44 | 22 | 9 | 0 | 0 | 0 | 0 | 356 | 162 | 73 | 0 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 82 | 107 | 0 | 17 | 0 | 43 | 41 | 44 | 30 | 110 | 0 | 63 | 78 | 0 | 0 | 19 | 38 | 10 | 270 | 23 | 11 | 0 | 291 | 0 | 0 | 190 | 0 | 132 | 4 | 90 | 100 | 133 | 0 | 86 | 90 | 105 | 3 | 244 | 54 | 110 | 0 | 9 | 100 | 50 | 92 | 3 | 162 | 90 | 0 | 35 | 0 | 102 | 55 |  | 907 | 0 | 275 | 0 | 108 | 120 | 0 | 0 | 0 | 0 | 0 | 149 | 20 | 48 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 24 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 340 | 70 | 0 | 50 | 50 | 40 | 0 | 1 | 50 | 860 | 108 | 0 | 17 | 1 | 39 | 36 |  | 6627 | 3852 | 10479 | 2724 | 907 | 1817 | 0 | 3402 | 1035 | 32 | 250 | 309 | 82 | 51 | 0 | 71.85
9:00 | 0 | 0 | 0 | 180 | 260 | 94 | 0 | 399 | 322 |  | 0 | 225 | 0 | 78 | 0 | 40 | 0 | 0 | 96 | 82 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 15 | 33 | 24 | 47 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 78 | 58 | 44 | 22 | 4 | 0 | 0 | 0 | 0 | 300 | 177 | 45 | 0 | 36 | 54 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 90 | 107 | 0 | 17 | 0 | 43 | 41 | 45 | 47 | 110 | 0 | 62 | 75 | 0 | 0 | 19 | 38 | 10 | 300 | 23 | 11 | 10 | 293 | 105 | 93 | 200 | 88 | 132 | 7 | 90 | 100 | 120 | 0 | 86 | 90 | 105 | 2 | 244 | 54 | 110 | 0 | 9 | 100 | 50 | 92 | 4 | 162 | 90 | 0 | 35 | 0 | 102 | 55 |  | 906 | 0 | 220 | 0 | 94 | 120 | 0 | 0 | 0 | 0 | 0 | 146 | 18 | 42 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 178 | 0 | 416 | 53 | 0 | 50 | 50 | 40 | 0 | 1 | 50 | 830 | 122 | 0 | 17 | 1 | 45 | 36 |  | 7075 | 3830 | 10905 | 2691 | 906 | 1990 | 296 | 3394 | 1005 | 32 | 250 | 321 | 90 | 60 | 0 | 71.88
10:00 | 0 | 0 | 0 | 180 | 260 | 90 | 0 | 399 | 324 |  | 0 | 225 | 0 | 74 | 0 | 40 | 0 | 0 | 93 | 82 | 84 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 15 | 33 | 15 | 47 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 79 | 44 | 22 | 3 | 0 | 0 | 0 | 0 | 335 | 205 | 45 | 0 | 34 | 52 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 92 | 71 | 0 | 17 | 1 | 44 | 41 | 45 | 47 | 110 | 0 | 62 | 75 | 0 | 0 | 19 | 38 | 10 | 320 | 23 | 11 | 25 | 278 | 303 | 92 | 200 | 94 | 132 | 12 | 90 | 83 | 117 | 0 | 85 | 90 | 105 | 4 | 248 | 54 | 110 | 0 | 9 | 100 | 85 | 91 | 7 | 144 | 90 | 0 | 35 | 0 | 101 | 55 |  | 906 | 0 | 220 | 0 | 65 | 120 | 0 | 0 | 0 | 0 | 0 | 149 | 19 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 197 | 0 | 414 | 17 | 0 | 50 | 50 | 68 | 0 | 2 | 90 | 840 | 180 | 0 | 17 | 2 | 59 | 36 |  | 7331 | 3919 | 11250 | 2765 | 906 | 2061 | 514 | 3355 | 1015 | 32 | 250 | 303 | 92 | 87 | 0 | 71.91
11:00 | 0 | 0 | 0 | 180 | 260 | 91 | 0 | 401 | 339 |  | 0 | 225 | 0 | 72 | 0 | 40 | 0 | 0 | 93 | 82 | 85 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 15 | 33 | 15 | 40 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 78 | 79 | 37 | 22 | 3 | 0 | 0 | 0 | 0 | 320 | 207 | 63 | 0 | 34 | 54 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 94 | 85 | 0 | 17 | 1 | 44 | 41 | 50 | 47 | 110 | 0 | 62 | 75 | 0 | 0 | 18 | 37 | 9 | 300 | 15 | 11 | 25 | 278 | 301 | 90 | 190 | 80 | 123 | 18 | 90 | 68 | 113 | 0 | 85 | 90 | 105 | 5 | 247 | 54 | 106 | 0 | 9 | 100 | 94 | 91 | 4 | 156 | 90 | 0 | 35 | 0 | 101 | 55 |  | 907 | 0 | 240 | 0 | 60 | 120 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 193 | 0 | 414 | 17 | 2 | 70 | 50 | 75 | 0 | 1 | 95 | 860 | 220 | 0 | 17 | 3 | 74 | 36 |  | 7286 | 3997 | 11283 | 2721 | 907 | 2116 | 498 | 3341 | 1035 | 32 | 260 | 313 | 94 | 106 | 0 | 71.98
12:00 | 0 | 0 | 0 | 180 | 260 | 90 | 0 | 399 | 311 |  | 0 | 225 | 0 | 70 | 0 | 40 | 0 | 0 | 94 | 88 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 15 | 25 | 24 | 43 | 0 | 32 | 0 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 78 | 77 | 37 | 22 | 3 | 0 | 0 | 0 | 0 | 305 | 208 | 92 | 0 | 34 | 51 | 0 | 43 | 0 | 40 | 0 | 19 | 8 | 32 | 14 | 100 | 87 | 0 | 20 | 1 | 43 | 41 | 47 | 50 | 110 | 0 | 62 | 78 | 0 | 0 | 19 | 37 | 9 | 310 | 15 | 11 | 25 | 276 | 301 | 90 | 188 | 80 | 115 | 2 | 90 | 68 | 110 | 0 | 85 | 90 | 105 | 2 | 248 | 54 | 90 | 0 | 9 | 100 | 102 | 91 | 11 | 162 | 90 | 0 | 35 | 0 | 96 | 55 |  | 906 | 0 | 240 | 0 | 60 | 120 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 8 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 187 | 0 | 414 | 20 | 11 | 94 | 55 | 74 | 0 | 1 | 95 | 860 | 223 | 0 | 17 | 2 | 81 | 36 |  | 7300 | 4106 | 11406 | 2708 | 906 | 2132 | 507 | 3340 | 1035 | 32 | 314 | 426 | 100 | 100 | 0 | 72
13:00 | 0 | 0 | 0 | 180 | 260 | 90 | 0 | 401 | 293 |  | 0 | 225 | 0 | 69 | 0 | 40 | 1 | 0 | 94 | 89 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 22 | 33 | 8 | 47 | 0 | 32 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 77 | 37 | 22 | 7 | 0 | 0 | 0 | 0 | 305 | 186 | 92 | 0 | 34 | 53 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 32 | 20 | 84 | 87 | 0 | 17 | 1 | 43 | 41 | 47 | 50 | 110 | 0 | 63 | 78 | 0 | 0 | 19 | 37 | 9 | 310 | 15 | 11 | 25 | 275 | 303 | 90 | 188 | 80 | 122 | 2 | 90 | 68 | 133 | 0 | 85 | 90 | 105 | 5 | 248 | 54 | 88 | 0 | 8 | 100 | 118 | 91 | 17 | 162 | 89 | 0 | 35 | 0 | 101 | 55 |  | 905 | 0 | 235 | 0 | 60 | 120 | 0 | 0 | 0 | 0 | 8 | 83 | 22 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 8 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 181 | 0 | 414 | 64 | 73 | 94 | 89 | 65 | 0 | 2 | 95 | 890 | 223 | 0 | 17 | 2 | 54 | 36 |  | 7335 | 4243 | 11578 | 2696 | 905 | 2122 | 571 | 3452 | 1065 | 32 | 327 | 448 | 84 | 83 | 0 | 72.18
14:00 | 0 | 0 | 0 | 180 | 260 | 94 | 0 | 400 | 317 |  | 0 | 225 | 0 | 72 | 0 | 40 | 1 | 0 | 95 | 87 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 22 | 33 | 16 | 46 | 0 | 32 | 0 | 100 | 0 | 19 | 0 | 0 | 0 | 0 |  | 8 | 16 | 0 | 90 | 77 | 37 | 22 | 4 | 0 | 0 | 0 | 35 | 305 | 172 | 92 | 0 | 33 | 52 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 33 | 20 | 98 | 86 | 0 | 17 | 2 | 43 | 41 | 47 | 50 | 110 | 0 | 62 | 78 | 0 | 0 | 19 | 37 | 10 | 290 | 23 | 11 | 25 | 278 | 200 | 90 | 185 | 80 | 116 | 5 | 90 | 82 | 125 | 0 | 85 | 90 | 105 | 3 | 262 | 54 | 88 | 0 | 9 | 100 | 128 | 91 | 19 | 162 | 89 | 0 | 35 | 0 | 101 | 55 |  | 905 | 0 | 225 | 0 | 60 | 140 | 0 | 0 | 0 | 0 | 8 | 83 | 23 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 174 | 0 | 414 | 88 | 140 | 94 | 89 | 73 | 0 | 1 | 95 | 930 | 223 | 0 | 17 | 2 | 76 | 35 |  | 7319 | 4416 | 11735 | 2724 | 905 | 2128 | 535 | 3486 | 1105 | 32 | 349 | 474 | 98 | 108 | 0 | 72.28
15:00 | 0 | 0 | 0 | 180 | 260 | 91 | 0 | 400 | 318 |  | 0 | 225 | 0 | 70 | 0 | 40 | 1 | 0 | 94 | 88 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 22 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 19 | 0 | 90 | 76 | 37 | 22 | 2 | 0 | 0 | 0 | 180 | 305 | 160 | 26 | 0 | 33 | 5 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 33 | 20 | 96 | 85 | 0 | 17 | 1 | 43 | 42 | 48 | 50 | 110 | 0 | 63 | 75 | 0 | 0 | 19 | 37 | 10 | 310 | 23 | 11 | 25 | 275 | 302 | 90 | 176 | 80 | 115 | 10 | 90 | 70 | 115 | 0 | 85 | 90 | 105 | 1 | 248 | 54 | 88 | 0 | 8 | 100 | 240 | 91 | 17 | 162 | 90 | 0 | 19 | 0 | 101 | 55 |  | 905 | 0 | 185 | 0 | 60 | 120 | 0 | 0 | 0 | 0 | 8 | 83 | 23 | 32 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 34 | 20 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 165 | 0 | 375 | 93 | 140 | 94 | 88 | 74 | 0 | 1 | 95 | 950 | 207 | 0 | 17 | 2 | 28 | 35 |  | 7540 | 4271 | 11811 | 2929 | 905 | 1974 | 637 | 3463 | 1125 | 32 | 328 | 470 | 96 | 60 | 0 | 72.38
16:00 | 0 | 0 | 0 | 180 | 260 | 94 | 0 | 397 | 328 |  | 0 | 225 | 0 | 68 | 0 | 40 | 1 | 0 | 95 | 88 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 22 | 33 | 0 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 0 | 90 | 77 | 37 | 22 | 3 | 0 | 0 | 0 | 130 | 270 | 138 | 8 | 0 | 33 | 5 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 33 | 0 | 96 | 98 | 0 | 14 | 1 | 43 | 43 | 48 | 50 | 110 | 0 | 63 | 75 | 0 | 110 | 19 | 37 | 10 | 260 | 23 | 11 | 25 | 278 | 200 | 90 | 185 | 80 | 115 | 0 | 90 | 89 | 122 | 0 | 94 | 90 | 105 | 0 | 248 | 54 | 87 | 0 | 9 | 100 | 300 | 91 | 11 | 162 | 90 | 0 | 32 | 0 | 85 | 55 |  | 906 | 0 | 150 | 0 | 78 | 120 | 0 | 0 | 0 | 0 | 8 | 84 | 22 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 34 | 32 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 144 | 0 | 360 | 93 | 100 | 94 | 89 | 74 | 0 | 1 | 95 | 900 | 213 | 0 | 17 | 2 | 20 | 90 |  | 7430 | 4209 | 11639 | 2879 | 906 | 1910 | 495 | 3580 | 1075 | 32 | 332 | 511 | 96 | 35 | 0 | 72.48
17:00 | 0 | 0 | 0 | 180 | 260 | 94 | 0 | 403 | 332 |  | 0 | 225 | 0 | 64 | 0 | 55 | 53 | 0 | 96 | 93 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 20 | 33 | 16 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 0 | 90 | 77 | 37 | 22 | 15 | 0 | 0 | 0 | 110 | 285 | 143 | 8 | 0 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 48 | 98 | 0 | 14 | 0 | 43 | 42 | 48 | 50 | 110 | 0 | 63 | 78 | 0 | 140 | 14 | 37 | 10 | 290 | 23 | 11 | 0 | 278 | 0 | 0 | 185 | 0 | 125 | 1 | 90 | 121 | 115 | 0 | 94 | 90 | 105 | 0 | 248 | 54 | 91 | 0 | 9 | 100 | 400 | 91 | 9 | 162 | 90 | 0 | 35 | 0 | 90 | 55 |  | 906 | 0 | 145 | 0 | 78 | 120 | 0 | 0 | 0 | 0 | 8 | 84 | 21 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 34 | 32 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 145 | 0 | 362 | 90 | 0 | 94 | 89 | 85 | 0 | 1 | 95 | 890 | 220 | 0 | 17 | 1 | 10 | 90 |  | 7227 | 4070 | 11297 | 3072 | 906 | 1967 | 0 | 3651 | 1065 | 32 | 302 | 414 | 48 | 22 | 0 | 72.58
18:00 | 0 | 0 | 0 | 180 | 280 | 95 | 0 | 405 | 263 |  | 0 | 225 | 0 | 68 | 0 | 55 | 165 | 0 | 9 | 95 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 7 | 0 | 0 | 0 | 0 |  | 22 | 34 | 17 | 50 | 78 | 42 | 22 | 13 | 0 | 0 | 0 | 10 | 270 | 172 | 8 | 30 | 34 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 46 | 98 | 0 | 14 | 0 | 43 | 42 | 49 | 50 | 110 | 0 | 40 | 78 | 0 | 125 | 19 | 31 | 10 | 280 | 23 | 11 | 0 | 288 | 0 | 0 | 185 | 0 | 132 | 0 | 90 | 167 | 122 | 82 | 95 | 90 | 105 | 0 | 248 | 54 | 107 | 0 | 9 | 87 | 384 | 91 | 2 | 108 | 90 | 0 | 35 | 0 | 91 | 55 |  | 906 | 0 | 160 | 0 | 80 | 120 | 0 | 0 | 5 | 0 | 24 | 82 | 21 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 34 | 32 | 0 | 33 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 149 | 0 | 278 | 90 | 0 | 94 | 88 | 87 | 0 | 0 | 95 | 650 | 163 | 0 | 17 | 0 | 2 | 108 |  | 7198 | 3719 | 10917 | 3145 | 906 | 1741 | 0 | 3681 | 825 | 32 | 250 | 417 | 46 | 4 | 0 | 72.68
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 412 | 314 |  | 0 | 225 | 0 | 79 | 0 | 55 | 235 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 43 | 22 | 17 | 0 | 0 | 0 | 20 | 270 | 206 | 8 | 90 | 34 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 74 | 99 | 0 | 14 | 0 | 43 | 41 | 50 | 50 | 110 | 0 | 63 | 81 | 0 | 125 | 19 | 31 | 10 | 280 | 23 | 11 | 150 | 292 | 157 | 90 | 186 | 25 | 132 | 0 | 90 | 200 | 125 | 80 | 96 | 90 | 105 | 0 | 264 | 54 | 110 | 0 | 9 | 83 | 400 | 91 | 0 | 118 | 90 | 0 | 35 | 0 | 86 | 55 |  | 907 | 0 | 185 | 0 | 80 | 140 | 0 | 0 | 30 | 25 | 32 | 83 | 32 | 32 | 0 | 0 | 0 | 34 | 8 | 90 | 0 | 34 | 32 | 0 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 2 | 157 | 0 | 400 | 93 | 8 | 94 | 89 | 87 | 0 | 0 | 95 | 670 | 221 | 0 | 17 | 0 | 0 | 108 |  | 8119 | 4175 | 12294 | 3402 | 907 | 1995 | 432 | 3830 | 845 | 32 | 285 | 637 | 74 | 0 | 0 | 72.98
19:30 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 410 | 337 |  | 0 | 225 | 0 | 73 | 0 | 55 | 250 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 43 | 22 | 23 | 0 | 0 | 0 | 20 | 270 | 210 | 8 | 91 | 34 | 5 | 0 | 43 | 0 | 15 | 0 | 19 | 8 | 33 | 20 | 76 | 105 | 0 | 14 | 0 | 43 | 42 | 53 | 50 | 110 | 0 | 65 | 78 | 0 | 125 | 19 | 31 | 10 | 275 | 23 | 11 | 200 | 292 | 298 | 90 | 187 | 80 | 132 | 0 | 90 | 200 | 126 | 100 | 96 | 90 | 105 | 0 | 264 | 54 | 110 | 0 | 9 | 100 | 400 | 91 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 906 | 0 | 195 | 0 | 80 | 165 | 0 | 0 | 44 | 45 | 32 | 83 | 31 | 48 | 0 | 0 | 0 | 34 | 8 | 90 | 0 | 34 | 32 | 0 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 97 | 170 | 0 | 418 | 93 | 180 | 94 | 89 | 87 | 0 | 0 | 95 | 750 | 201 | 0 | 17 | 0 | 0 | 108 |  | 8531 | 4696 | 13227 | 3478 | 906 | 2016 | 945 | 3918 | 925 | 32 | 391 | 751 | 76 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 409 | 337 |  | 0 | 225 | 0 | 74 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 40 | 22 | 25 | 20 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 43 | 22 | 20 | 0 | 0 | 0 | 20 | 270 | 214 | 8 | 90 | 34 | 5 | 0 | 43 | 0 | 26 | 0 | 16 | 8 | 33 | 21 | 76 | 124 | 0 | 16 | 0 | 43 | 42 | 53 | 50 | 110 | 0 | 65 | 78 | 0 | 125 | 19 | 31 | 10 | 270 | 24 | 11 | 200 | 293 | 37 | 90 | 191 | 80 | 132 | 0 | 90 | 200 | 127 | 120 | 96 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 400 | 91 | 0 | 162 | 90 | 0 | 35 | 0 | 102 | 55 |  | 906 | 0 | 200 | 0 | 78 | 210 | 0 | 0 | 39 | 66 | 32 | 85 | 28 | 48 | 0 | 0 | 0 | 34 | 8 | 90 | 0 | 34 | 32 | 0 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 9 | 0 | 0 | 0 | 214 | 0 | 67 | 172 | 0 | 414 | 93 | 150 | 94 | 89 | 87 | 0 | 0 | 95 | 880 | 189 | 0 | 17 | 0 | 0 | 108 |  | 8414 | 4827 | 13241 | 3614 | 906 | 1989 | 624 | 3930 | 1055 | 32 | 448 | 781 | 76 | 0 | 0 | 72.88
21:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 409 | 337 |  | 0 | 225 | 0 | 85 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 44 | 22 | 30 | 0 | 0 | 0 | 10 | 280 | 213 | 8 | 91 | 34 | 5 | 0 | 43 | 0 | 40 | 0 | 16 | 8 | 33 | 21 | 82 | 142 | 0 | 14 | 0 | 43 | 41 | 53 | 50 | 110 | 0 | 64 | 78 | 0 | 125 | 19 | 31 | 10 | 275 | 24 | 11 | 50 | 290 | 25 | 90 | 191 | 50 | 132 | 0 | 90 | 200 | 133 | 285 | 97 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 13 | 100 | 400 | 92 | 0 | 162 | 90 | 0 | 35 | 0 | 102 | 55 |  | 907 | 0 | 205 | 0 | 78 | 217 | 0 | 0 | 39 | 60 | 32 | 83 | 32 | 48 | 0 | 0 | 0 | 34 | 8 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 20 | 175 | 0 | 414 | 93 | 20 | 94 | 89 | 87 | 0 | 0 | 95 | 1000 | 222 | 0 | 17 | 0 | 0 | 108 |  | 8469 | 4795 | 13264 | 3796 | 907 | 2042 | 255 | 3966 | 1175 | 32 | 433 | 792 | 82 | 0 | 0 | 72.98
22:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 410 | 337 |  | 0 | 225 | 0 | 78 | 0 | 55 | 331 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 25 | 47 | 0 | 40 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 44 | 22 | 35 | 0 | 0 | 0 | 0 | 295 | 206 | 8 | 91 | 38 | 25 | 0 | 43 | 0 | 48 | 0 | 19 | 8 | 33 | 9 | 86 | 130 | 0 | 14 | 0 | 43 | 41 | 53 | 50 | 110 | 0 | 63 | 78 | 0 | 125 | 19 | 31 | 10 | 290 | 24 | 11 | 0 | 292 | 135 | 50 | 191 | 0 | 133 | 0 | 90 | 200 | 140 | 295 | 96 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 907 | 0 | 210 | 0 | 80 | 217 | 0 | 0 | 39 | 54 | 32 | 83 | 34 | 48 | 0 | 0 | 0 | 34 | 9 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 177 | 0 | 414 | 93 | 0 | 94 | 89 | 87 | 0 | 0 | 95 | 1010 | 222 | 0 | 17 | 0 | 0 | 108 |  | 8483 | 4770 | 13253 | 3790 | 907 | 2084 | 185 | 3965 | 1185 | 40 | 432 | 794 | 86 | 0 | 0 | 73.08
23:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 401 | 322 |  | 0 | 225 | 0 | 88 | 0 | 55 | 330 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 19 | 33 | 25 | 47 | 0 | 40 | 0 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 44 | 22 | 38 | 0 | 0 | 0 | 0 | 290 | 209 | 8 | 90 | 38 | 25 | 0 | 43 | 0 | 48 | 0 | 19 | 8 | 33 | 9 | 90 | 130 | 0 | 17 | 0 | 43 | 41 | 53 | 50 | 110 | 0 | 62 | 78 | 0 | 125 | 19 | 31 | 10 | 300 | 24 | 11 | 0 | 293 | 166 | 50 | 191 | 0 | 132 | 0 | 90 | 200 | 142 | 292 | 96 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 907 | 0 | 210 | 0 | 95 | 219 | 0 | 0 | 38 | 54 | 32 | 83 | 35 | 48 | 0 | 0 | 0 | 34 | 4 | 90 | 0 | 34 | 32 | 0 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 178 | 0 | 414 | 93 | 0 | 94 | 89 | 94 | 0 | 0 | 95 | 1020 | 221 | 0 | 17 | 0 | 0 | 108 |  | 8508 | 4798 | 13306 | 3779 | 907 | 2081 | 216 | 3991 | 1195 | 40 | 434 | 788 | 90 | 0 | 0 | 73.18
24:00 | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 400 | 330 |  | 0 | 225 | 0 | 84 | 0 | 55 | 332 | 0 | 0 | 100 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 25 | 47 | 0 | 40 | 0 | 100 | 0 | 19 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 90 | 78 | 44 | 22 | 31 | 0 | 0 | 0 | 0 | 270 | 212 | 8 | 93 | 37 | 25 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 33 | 9 | 90 | 143 | 0 | 17 | 0 | 43 | 41 | 53 | 50 | 110 | 0 | 64 | 78 | 0 | 125 | 19 | 31 | 10 | 300 | 24 | 11 | 0 | 293 | 180 | 90 | 190 | 0 | 133 | 0 | 90 | 180 | 145 | 297 | 106 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 90 | 0 | 35 | 0 | 101 | 55 |  | 906 | 0 | 215 | 0 | 95 | 223 | 0 | 0 | 34 | 54 | 32 | 84 | 35 | 48 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 178 | 0 | 414 | 93 | 0 | 94 | 89 | 78 | 0 | 0 | 95 | 1020 | 217 | 0 | 17 | 0 | 0 | 72 |  | 8558 | 4745 | 13303 | 3789 | 906 | 2079 | 270 | 3929 | 1196 | 40 | 438 | 781 | 90 | 0 | 0 | 73.3
KWH | 0 | 0 | 0 | 4378500 | 6473536 | 2219500 | 0 | 9744380 | 7554000 |  | 0 | 5146500 | 0 | 1828800 | 0 | 1146529 | 1934092 | 0 | 1680000 | 2206685 | 2124864 | 3282240 | 0 | 0 | 0 | 0 | 874080 | 1329258 | 810995 | 443556 | 600000 | 431640 | 793600 | 506100 | 1085760 | 0 | 804420 | 0 | 2400000 | 0 | 514774 | 0 | 0 | 0 | 0 |  | 530880 | 370032 | 312738 | 2033760 | 1774080 | 1008000 | 504864 | 501120 | 0 | 0 | 0 | 607500 | 7645000 | 4369000 | 1137454 | 519700 | 841392 | 899520 | 0 | 942628 | 0 | 478032 | 0 | 430812 | 191520 | 795000 | 345200 | 2117760 | 2580480 | 0 | 362268 | 8000 | 1028000 | 958344 | 1126200 | 1090440 | 2722990 | 0 | 1459872 | 1809600 | 0 | 1051800 | 435000 | 851960 | 253980 | 7181500 | 526440 | 264000 | 647232 | 6884942 | 3699459 | 1568027 | 4490400 | 1272699 | 3082032 | 58185 | 2114880 | 3007680 | 3059418 | 1290000 | 2118000 | 2148000 | 2526643 | 27000 | 6056945 | 1368789 | 2530825 | 0 | 230160 | 2394240 | 4401800 | 2228160 | 107230 | 3843360 | 2132727 | 0 | 865440 | 0 | 2370240 | 1328760 |  | 21920000 | 0 | 5713632 | 0 | 2055360 | 3816000 | 0 | 0 | 371040 | 499968 | 251250 | 2659654 | 615476 | 1022304 | 0 | 0 | 0 | 696208 | 44505 | 832984 | 0 | 629776 | 510170 | 75840 | 424720 | 470160 | 0 | 249696 | 0 | 0 | 4284400 | 15000 | 6000 | 0 | 0 | 0 | 4473527 | 0 | 211200 | 4575727 | 0 | 9312072 | 1932480 | 1280660 | 2106240 | 1967184 | 1743734 | 0 | 11666 | 2143104 | 24072000 | 4097973 | 0 | 445200 | 23100 | 496800 | 1518336 |  | 180233948 | 107575146 | 287809094 | 73192105 | 21920000 | 47933073 | 8679277 | 87940914 | 28356400 | 804420 | 8310527 | 7822637 | 2117760 | 731981 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 7250360.32 | 2951935 | 0 | 10231599 | 8158320 |  | 0 | 5609685 | 0 | 20445984 | 0 | 15191509.25 | 2166183.04 | 0 | 2940000 | 32261734.7 | 29896836.48 | 53205110.4 | 0 | 0 | 0 | 0 | 11118297.6 | 17944983 | 10875442.95 | 332667 | 450000 | 0 | 0 | 0 | 18468777.6 | 0 | 217193.4 | 0 | 4536000 | 0 | 8416554.9 | 0 | 0 | 0 | 0 |  | 6927984 | 6172133.76 | 5322800.76 | 27476097.6 | 22495334.4 | 11662560 | 641177.28 | 1668729.6 | 0 | 0 | 0 | 674325 | 8333050 | 5068040 | 1467315.66 | 634034 | 950772.96 | 1340284.8 | 0 | 1574188.76 | 0 | 8255612.64 | 0 | 590212.44 | 143640 | 1391250 | 258900 | 15205516.8 | 2812723.2 | 0 | 492684.48 | 127520 | 1408360 | 1265014.08 | 1959588 | 1886461.2 | 3131438.5 | 0 | 2832151.68 | 4125888 | 0 | 1062318 | 935250 | 1269420.4 | 502880.4 | 7181500 | 394830 | 200640 | 13565982.72 | 93979458.3 | 77540660.64 | 32411118.09 | 60530592 | 26306688.33 | 42686143.2 | 680182.65 | 21825561.6 | 41084908.8 | 40598476.86 | 1186800 | 25754880 | 31060080 | 31962033.95 | 0 | 71108534.3 | 14906112.21 | 26902669.75 | 0 | 2966762.4 | 28204147.2 | 4049656 | 28854672 | 1549473.5 | 48772238.4 | 24270433.26 | 0 | 11302646.4 | 0 | 35482492.8 | 17499769.2 |  | 65760000 | 0 | 6399267.84 | 0 | 21396297.6 | 62964000 | 0 | 0 | 6682430.4 | 8999424 | 3610462.5 | 2978812.48 | 1194023.44 | 11143113.6 | 0 | 0 | 0 | 11675408.16 | 778392.45 | 13027869.76 | 0 | 10429090.56 | 8626974.7 | 1033699.2 | 7165026.4 | 973231.2 | 0 | 189019.872 | 0 | 0 | 22664476 | 630300 | 210900 | 0 | 0 | 0 | 78107781.42 | 0 | 4430976 | 5307843.32 | 0 | 9218951.28 | 25972531.2 | 26855440.2 | 24916819.2 | 28425808.8 | 22145421.8 | 0 | 128909.3 | 26017282.56 | 216888720 | 4179932.46 | 0 | 3294480 | 261261 | 5827464 | 23276090.88 |  | 1286078941.6 | 773787933.582 | 2059866875.182 | 84631546.992 | 65760000 | 58393773.7 | 181110865.98 | 1134595807.01 | 239553196 | 217193.4 | 141912981.42 | 129911183.43 | 15205516.8 | 8574810.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 260 | 90 | 0 | 399 | 311 |  | 0 | 225 | 0 | 70 | 0 | 40 | 0 | 0 | 94 | 88 | 85 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 15 | 25 | 24 | 43 | 0 | 32 | 0 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 78 | 77 | 37 | 22 | 3 | 0 | 0 | 0 | 0 | 305 | 208 | 92 | 0 | 34 | 51 | 0 | 43 | 0 | 40 | 0 | 19 | 8 | 32 | 14 | 100 | 87 | 0 | 20 | 1 | 43 | 41 | 47 | 50 | 110 | 0 | 62 | 78 | 0 | 0 | 19 | 37 | 9 | 310 | 15 | 11 | 25 | 276 | 301 | 90 | 188 | 80 | 115 | 2 | 90 | 68 | 110 | 0 | 85 | 90 | 105 | 2 | 248 | 54 | 90 | 0 | 9 | 100 | 102 | 91 | 11 | 162 | 90 | 0 | 35 | 0 | 96 | 55 |  | 906 | 0 | 240 | 0 | 60 | 120 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 32 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 8 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 187 | 0 | 414 | 20 | 11 | 94 | 55 | 74 | 0 | 1 | 95 | 860 | 223 | 0 | 17 | 2 | 81 | 36 |  | 11406 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 409 | 337 | 0 | 0 | 225 | 0 | 85 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 25 | 47 | 0 | 32 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 34 | 51 | 90 | 78 | 44 | 22 | 30 | 0 | 0 | 0 | 10 | 280 | 213 | 8 | 91 | 34 | 5 | 0 | 43 | 0 | 40 | 0 | 16 | 8 | 33 | 21 | 82 | 142 | 0 | 14 | 0 | 43 | 41 | 53 | 50 | 110 | 0 | 64 | 78 | 0 | 125 | 19 | 31 | 10 | 275 | 24 | 11 | 50 | 290 | 25 | 90 | 191 | 50 | 132 | 0 | 90 | 200 | 133 | 285 | 97 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 13 | 100 | 400 | 92 | 0 | 162 | 90 | 0 | 35 | 0 | 102 | 55 |  | 907 | 0 | 205 | 0 | 78 | 217 | 0 | 0 | 39 | 60 | 32 | 83 | 32 | 48 | 0 | 0 | 0 | 34 | 8 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 20 | 175 | 0 | 414 | 93 | 20 | 94 | 89 | 87 | 0 | 0 | 95 | 1000 | 222 | 0 | 17 | 0 | 0 | 108 |  | 13264 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 90 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 51 | 90 | 81 | 44 | 22 | 30 | 0 | 0 | 0 | 250 | 280 | 210 | 8 | 90 | 38 | 5 | 0 | 43 | 0 | 50 | 0 | 21 | 8 | 33 | 20 | 165 | 120 | 0 | 20 | 0 | 43 | 41 | 51 | 50 | 110 | 0 | 65 | 81 | 0 | 200 | 19 | 41 | 10 | 341 | 24 | 11 | 200 | 290 | 300 | 100 | 191 | 98 | 135 | 0 | 90 | 200 | 140 | 285 | 105 | 90 | 105 | 0 | 265 | 54 | 110 | 0 | 9 | 100 | 400 | 93 | 0 | 162 | 90 | 0 | 35 |  | 100 | 55 |  | 920 | 0 | 230 | 0 | 115 | 220 | 0 | 0 | 38 | 60 | 40 | 85 | 33 | 48 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 34 | 32 | 0 | 40 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 0 | 210 | 0 | 100 | 210 | 0 | 414 | 93 | 190 | 94 | 89 | 95 | 0 | 0 | 95 | 1050 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 405 | 330 | 0 | 0 | 225 | 0 | 79 | 0 | 55 | 300 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 78 | 78 | 44 | 22 | 5 | 0 | 0 | 0 | 100 | 270 | 210 | 8 | 90 | 38 | 10 | 0 | 43 | 0 | 50 | 0 | 21 | 8 | 33 | 20 | 143 | 110 | 0 | 20 | 1.6 | 43 | 41 | 51 | 50 | 110 | 0 | 62 | 81 | 0 | 100 | 19 | 41 | 10 | 310 | 24 | 11 | 0 | 285 | 300 | 100 | 180 | 98 | 130 | 20 | 90 | 150 | 140 | 285 | 95 | 90 | 105 | 5 | 265 | 54 | 110 | 0 | 9 | 100 | 100 | 93 | 50 | 162 | 90 | 0 | 35 | 30 | 100 | 55 |  | 920 | 0 | 230 | 0 | 92 | 120 | 0 | 0 | 38 | 0 | 40 | 85 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 180 | 0 | 350 | 93 | 100 | 94 | 70 | 95 | 0 | 8 | 95 | 1050 | 180 |  | 17 | 6 | 100 | 72
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 97 | 0 | 405 | 321 | 0 | 0 | 225 | 0 | 78 | 0 | 15 | 270 | 0 | 0 | 24 | 40 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 19 | 33 | 25 | 16 | 0 | 38 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 78 | 0 | 30 | 22 | 10 | 0 | 0 | 0 | 0 | 270 | 216 | 130 | 30 | 33 | 55 | 0 | 43 | 0 | 8 | 0 | 19 | 8 | 32 | 18 | 72 | 116 | 0 | 14 | 1 | 43 | 41 | 48 | 50 | 110 | 0 | 40 | 72 | 0 | 20 | 18 | 31 | 10 | 285 | 23 | 11 | 0 | 112 | 0 | 0 | 170 | 0 | 99 | 7 | 90 | 34 | 140 | 285 | 45 | 50 | 105 | 1 | 100 | 54 | 110 | 0 | 9 | 100 | 400 | 91 | 14 | 109 | 90 | 0 | 35 | 0 | 101 | 55 | 0 | 906 | 0 | 230 | 0 | 92 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 177 | 0 | 340 | 93 | 0 | 94 | 67 | 60 | 0 | 1 | 75 | 310 | 196 | 0 | 0 | 1 | 34 | 35 | 0 |  |  |  |  | 112753355 |  | 0
112753355
| Minimum Generation |  | 10479 | 8:00
| Highest Generation |  | 13306 | 23:00
| Day Peak Generation |  | 11406 | 12:00
| Evening Peak Generation |  | 13264 | 21:00
| HVDC Max Flow |  | 907 | 2:00
| HVDC EvPeak Flow |  | 907 | 21:00
| Load factor L.F |  | 90.13%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-16
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11406 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10104 | MW
Evening Peak Generation : |  | 13264 | MW Hour : | 21:00 | Available Max Generation : |  | 14696 | MW
E.P. Demand (at gen end) : |  | 13264 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13306 | MW Hour : | 23:00 | Reserve(Generation end) |  | 696 | MW
Total Gen. (MKWH) : |  | 287.8091 | System Load Factor : | 90.13% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 314 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-16
Actual : | 74.02 | Ft.(MSL) , | Rule curve : | 79.95 | Ft.( MSL )
Gas Consumed : | Total = | 1014.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 143025320.692
: |  | Coal : | 239553196 | Oil : | 1587530837.84 | Total : | 1970109354.532
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4865.6401 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1309.9784 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1717.974 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1539.1194 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1363.7889 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1003.128 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 555.9913 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 364.4715 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 767.7976 |  |  | 0 | 0%
Total | 0 |  | 13487.8892 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bibiyana(South) ST was synchronized at 09:53.
b) Khulna© 132/33 kV T-3 transformer was under shut down from 08:06 to 10:35 for C/M.
c) Bhola Nutun Biddut GT-1 was synchronized at 08:24.
d) Bhola 225 MW CCPP GT-2 was shut down at 10:11 due to gas shortage.
e) Aminbazar-Meghnaghat 230 kV Ckt-1 was under shut down from 09:14 to 16:58 for C/M.
f) Saver 132/33 kV T-2 transformer was under shut down from 09:04 to 10:26 for C/M.
g) Ghorasal GIS-Ghoresal-3 P/P 132 kV Ckt was switched on at 11:08.
h) Gopalganj P/P 132/33 kV T-2 transformer was under shut down from 10:52 to 12:24 for C/M.
i) Siddhirganj 335 MW GT was synchronized at 12:24.
j) Sunamganj-Chattak 132 kV Ckt-1 tripped at 12:15 showing VT fuse fail relay at Sunamganj end
and was switched on at 12:21.
k) Aminbazar 230 kV Bus-1 was under shut down from 13:01 to 15:35 for C/M.
l) Ashuganj(N) GT was synchronized at 13:55.
m) Sylhet 225 MW CCPP GT synchronized at 15:09.
n) Siddhirganj 335 MW ST was synchronized at 16:01.
o) Bibiyana-3 GT was synchronized at 17:17.
p) Chandpur CCPP GT was synchronized at 17:54.
q) Hathazari-AKSM 230 kV Ckt was under shut down from 15:00 to 17:08 due to B-phase PT at Hathazari
end got out order.
r) Tongi-Uttara 132 kV Ckt was under shut down from 17:45 to 21:09 due to CVT problem at Tongi end.
s) Sonargaon-Daudkandi 132 kV Ckt-1 tripped at 15:44 from both end showing Dist. Z1, R-phase relay
and was switched on at 15:53.
t) Chandpur 132/33 kV T-2 transformer was switched on at 15:48.
u) Feni-Chauddagram 132 kV Ckt-1 tripped at 18:32 from Feni end showing Dist. Z1, A-phase relay
and was switched on at 18:45.
v) Mithapukur-Rangpur Confidence P/P 132 kV Ckt-1was switched on at 18:14.
w) Kishoreganj 132/33 kV T-1 & T2 transformers along with 33 kV Bus section were under shut down from | [5 empty] | About 90 MW power interruption occurred under
00:07(16-06-2022) to 01:36(16-06-2022) due to red hot at 33 kV Bus sectionalized. | [5 empty] | Kishoreganj S/S area from 00:07 to 01:36.
x) Gopalganj-Rampal 400 kV Ckt was shut down at 05:45(16-06-2022) for D/W.
y) Payra Bus coupler was switched on at 05:24(16-06-2022) for D/W.
z) Kabirpur 132/33 kV T-3 transformer was under shut down from 06:23(16/06/2022) to 07:59(16/06/2022)
due to red hot at 33 kV incoming.
aa) Rajshahi(O) 132/33 kV T-3 transformer was shut down at 07:04(16/06/2022) due to red hot at 33 kV | [5 empty] | About 40 MW power interruption occurred under
isolator. | [5 empty] | Rajshahi S/S area from 07:04(16/06/2022) to till.
ab) Payra unit-2 was shut down at 07:26(16-06-2022) due to Gopalganj-Rampal 400 kV Ckt was shut down.
ac) Ullon-Dhanmondi 132 kV underground cable-3 tripped at 03:50(16-06-2022) showing Dist. C-phase,
general trip at Ullon end.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6473536 | Condencer problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 2219500 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9744380
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7554000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5146500 | GT-1 S/D, Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 85 | 1828800 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1146529
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 443556
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1680000 | GT-2 U/M
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2206685
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 1934092
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2124864 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 874080 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3282240
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1329258
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 810995
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1031640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 793600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 506100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 47 | 1085760 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 290 | 6884942
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 25 | 3699459 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1568027 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 1272699 | Low demand.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3082032 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2148000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2228160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3843360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1328760
| Dhaka area Total |  |  |  | 5847 | 3647 | 82650054
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 514774
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 58185
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1008000 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 32 | 804420 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2526643
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 370032 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 312738 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2033760 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2114880 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504864
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 501120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 78 | 1774080 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 265 | 6056945 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1368789
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2530825
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2394240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2132727 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1320 | 29434022
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4369000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 10 | 607500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7645000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 841392 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 899520 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1137454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 942628 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 3059418 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 478032 | Low demand.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 519700 | ST-under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3007680
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 430812
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 191520
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 2117760 | Bad weather.
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 795000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 345200
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 647232 | Low demand.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 13 | 230160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 865440 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 102 | 2370240 | Engine problem
| Cumilla Area Total |  |  |  | 2885 | 1417 | 31500688
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 142 | 2580480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 362268
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 191 | 4490400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 2118000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 107230
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 530880
| Mymensingh Area Total |  |  |  | 614 | 466 | 10197258
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1028000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 958344 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2722990 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1126200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 50 | 50 | 1090440
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1459872
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1809600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 125 | 1051800 | Sync at 15:09.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 435000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 31 | 851960 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 526440
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7181500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 285 | 1290000 | GT synchronized at 17:17.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253980
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 4401800
| Sylhet Area Total |  |  |  | 2477 | 1619 | 26451926
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21920000
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 78 | 2055360 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 371040 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 217 | 3816000
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 499968 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 205 | 5713632 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 251250
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 20 | 211200 | Low demand.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1932480 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 1967184 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 496800
| Khulna Area Total |  |  |  | 2384 | 1740 | 39234914
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 1022304 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 40 | 32 | 615476 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 83 | 2659654 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1000 | 24072000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4097973 | Machine problem
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 445200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1402 | 32912607
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 696208 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 8 | 44505 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 629776 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 510170 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 216 | 4473527
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4575727 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9312072 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 424720 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 470160
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249696
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 75840 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 832984 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 20 | 1280660 | Low demand.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2106240 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 2143104
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23100
| Rajshahi Area Total |  |  |  | 2129 | 1283 | 27848489
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4284400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 15000 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 6000 | Engine problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 87 | 1743734 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11666
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1518336 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 370 | 7579136
| Total |  |  |  | 21396 | 13264 | 287809094
| Eastern Grid Total |  |  |  | 14205 | 8469 | 180233948
| Western Grid Total |  |  |  | 7191 | 4795 | 107575146
| National Grid Total |  |  |  | 21396 | 13264 | 287809094
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-15
(a) ENTIRE EASTERN GRID : |  | 8493.59 | MW | (b) ENTIRE WESTERN GRID : |  | 4276.4 | MW
i) Dhaka area |  | 4769.15 | MW | i) Khulna area |  | 1657.4 | MW
ii) Chittagong area |  | 1245.44 | MW | ii) Rajshahi area |  | 1453 | MW
iii) Comilla area |  | 1110 | MW | iii) Barisal area |  | 413 | MW
iv) Mymensingh area |  | 984 | MW | iv) Rangpur area |  | 753 | MW
v) Sylhet area |  | 385 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12769.99 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 13:00 | Hasnabad | 76 | 00:00 | Palashbari | 118 | 22:00
Agargaon | 100 | 13:00 | Hathazari | 97 | 19:30 | Panchagarh | 60 | 19:30
Agrabad | 96 | 14:00 | Ishurdi | 76 | 00:00 | Patuakhali | 129 | 23:00
AKS | 10 | 18:30 | Jaldhaka | 53 | 19:30 | PHP | 8 | 01:00
AKSML | 148 | 11:00 | Jamalpur | 154 | 20:00 | Purbachal | 20 | 15:00
Amnura | 52 | 22:00 | Jashore | 133 | 19:30 | Purbasadipur | 127 | 22:00
Ashuganj | 36 | 15:00 | Jhenaidah | 122 | 19:30 | Rahim | 20 | 23:00
Bagerhat | 115 | 22:00 | Joydebpur | 202 | 19:00 | Rajbari | 70 | 19:30
Bakulia | 120 | 11:00 | Joypurhat | 67 | 21:00 | Rajendrapur | 108 | 20:00
Banani | 49 | 15:00 | Juldah | 24 | 00:00 | Rajshahi | 164 | 00:00
Bangabhaban | 24 | 10:00 | Kabirpur | 277 | 16:00 | Rajshahi | 30 | 00:00
Barapukuria | 52 | 22:00 | Kachua | 70 | 00:00 | Ramganj | 118 | 22:00
Barguna | 22 | 00:00 | Kallyanpur | 114 | 00:00 | Rampur | 15 | 19:00
Barishal | 128 | 21:00 | Kalurghat | 37 | 21:00 | Rangamati | 12 | 19:00
Barishal | 54 | 21:00 | Kamrangirchar | 97 | 18:00 | Rangpur | 142 | 19:30
Baroaulia | 71 | 00:00 | Kaptai | 4 | 19:30 | Ruppur | 4.6 | 11:00
Baroirhat | 64 | 19:30 | Kazla | 85 | 18:30 | Saidpur | 101 | 20:00
Bashundhara | 181 | 15:00 | Keranigonj | 80 | 19:30 | Satkhira | 135 | 19:30
BashundharaCement | 12 | 00:00 | Khagrachori | 24 | 18:30 | Satmasjid | 96 | 13:00
Beanibazar | 38 | 00:00 | Khulna | 92 | 21:00 | Savar | 193 | 12:00
Benapole | 56 | 23:00 | Khulshi | 186 | 14:00 | Shahjadpur | 107 | 20:00
Bhaluka | 144 | 19:30 | Kishoreganj | 130 | 23:00 | Shahjibazar | 103 | 01:00
Bhandaria | 62 | 22:00 | Kodda | 319 | 15:00 | Shahmirpur | 43.5 | 18:30
Bhangura | 36 | 21:00 | KSRM | 25.3 | 12:00 | Shariatpur | 72 | 02:00
Bheramara(GK) | 63 | 22:00 | Kulaura | 32 | 19:00 | Sherpur | 114 | 22:00
Bhulta | 243 | 00:00 | Kurigram | 50 | 19:30 | Shikalbaha | 32 | 00:00
Bog-Sherpur | 64 | 21:00 | Kushtia | 144 | 20:00 | Shitalakhya | 129 | 15:00
Bogura | 172 | 20:00 | Lalbag | 98 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 45 | 22:00 | Lalmonirhat | 38 | 21:00 | Shyampur | 168 | 01:00
Brahmanbaria | 160 | 02:00 | Madanganj | 86 | 22:00 | Siddhirganj | 118 | 09:00
BSRM | 169 | 18:00 | Madaripur | 108 | 00:00 | Sirajganj | 118 | 21:00
Cantonment | 162 | 15:00 | Madartek | 88 | 00:00 | Sonargaon | 94 | 15:00
Chandpur | 77 | 22:00 | Madunaghat | 55 | 19:00 | Sreemongol | 45 | 19:00
Chandraghona | 28 | 20:00 | Magura | 64 | 19:30 | Srinagar | 43.97 | 00:00
Chapai | 69 | 21:00 | Mahasthangarh | 68 | 21:00 | SSM | 18 | 02:00
Charsaidpur | 43 | 12:00 | Manikganj | 84 | 22:00 | Sunamganj | 35 | 19:30
Chauddagram | 39 | 23:00 | Maniknagar | 88 | 13:00 | Sylhet | 102 | 20:00
Chhatak | 19 | 19:30 | Matarbari | 40 | 22:00 | Tangail | 216 | 23:00
Chowmuhani | 200 | 19:00 | Matuail | 68 | 10:00 | Thakurgaon | 82 | 21:00
Chuadanga | 107 | 23:00 | Millgate | 64 | 12:00 | TK | 27.5 | 21:00
Coxsbazar | 110 | 21:00 | Mirpur | 132 | 13:00 | Tongi | 131 | 15:00
Cumilla(N) | 153 | 22:00 | Mirsorai | N/A | N/A | Ullon | 42 | 00:00
Cumilla(S) | 146 | 00:00 | Mithapukur | 28 | 23:00 | Uttara | 99 | 00:00
Daudkandi | 126 | 23:00 | Modern | 0 | 00:00 | UttaraNew | 18 | 15:00
Dhaka | 42 | 12:00 | Mogbazar | 132 | 12:00 | Zigatola | 45 | 12:00
Dhamrai | 124 | 16:00 | Mongla | 34 | 12:00
Dhanmondi | 166 | 13:00 | Motijheel | 43 | 12:00
Dohazari | 78 | 00:00 | Munshiganj | 107 | 00:00
Faridpur | 153 | 00:00 | Mymensingh | 219 | 22:00
Fatullah | 70 | 10:00 | Naogaon | 112 | 21:00
Fenchuganj | 34 | 21:00 | Narail | 56 | 00:00
Feni | 107 | 19:00 | Narinda | 77 | 12:00
Ghorashal | 69 | 01:00 | Narshingdi | 176 | 00:00
Goalpara | 34 | 00:00 | Natore | 142 | 23:00
Gollamari | 57 | 22:00 | Nawabganj | 53.6 | 00:00
Gopalganj | 102.8 | 00:00 | Netrakona | 102 | 20:00
GPH | 95 | 17:00 | New | 89.1 | 15:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiana | 410 | 06:00 | 400 | 12:00 | Kaliakoir | 399 | 0.25 | 380 | 0.70833
| Bheramara | 399 | 6:00 | 393 | 13:00 | Bhulta | 395 | 06:00 | 372 | 11:00
| Ashuganj(N) | 398 | 6:00 | 380 | 11:00 | Gopalganj_I | 421 | 18:30 | 399 | 00:00
| Payra | 422 | 18:00 | 410 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 06:00 | 214 | 11:00 | Haripur | 224 | 03:00 | 214 | 11:00
| AKSML | 235 | 07:00 | 223 | 16:00 | Hasnabad | 225 | 04:00 | 216 | 10:00
| Aminbazar | 227 | 03:00 | 216 | 10:00 | Hathazari | 241 | 17:00 | 228 | 01:00
| Ashuganj | 240 | 5:00 | 230 | 11:00 | Ishurdi | 235 | 04:00 | 235 | 18:30
| Ashuganj(S) | 242 | 6:00 | 231 | 12:00 | Jhenaidah | 233 | 18:30 | 219 | 23:00
| Baghabari | 234 | 05:00 | 226 | 21:00 | Kaliakoir | 228 | 5:00 | 215 | 18:00
| Barapukuria | 233 | 05:00 | 218 | 20:00 | Keranigonj | 226 | 04:00 | 214 | 11:00
| Barishal | 243 | 18:00 | 232 | 00:00 | Khulna(S) | 237 | 18:00 | 224 | 23:00
| Bheramara | 233 | 05:00 | 221 | 21:00 | Maniknagar | 226 | 04:00 | 225 | 03:00
| Bhulta | 228 | 04:00 | 217 | 11:00 | Meghnaghat | 229 | 05:00 | 221 | 14:00
| Bibiana | 240 | 02:00 | 234 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 05:00 | 222 | 21:00 | Rajshahi | 235 | 06:00 | 222 | 21:00
| Bogura | 233 | 06:00 | 220 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 09:00 | 237 | 00:00 | Rampura | 227 | 05:00 | 215 | 11:00
| BSRM | 232 | 06:00 | 225 | 16:00 | Shikalbaha | 237 | 17:00 | 230 | 00:00
| Cumilla(N) | 229 | 08:00 | 221 | 11:00 | Shyampur | 226 | 03:00 | 216 | 10:00
| Fenchuganj | 247 | 06:00 | 238 | 16:00 | Siddhirganj | 224 | 19:30 | 217 | 11:00
| Ghorashal | 230 | 1:00 | 230 | 1:00 | Sirajgonj | 234 | 04:00 | 228 | 21:00
| GPH | 235 | 07:00 | 228 | 10:00 | Tongi | 230 | 05:00 | 215 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 06:00 | 126 | 11:00 | Manikganj | 131 | 05:00 | 124 | 23:00
| Agargaon | 135 | 04:00 | 125 | 11:00 | Maniknagar | 133 | 05:00 | 124 | 13:00
| Agrabad | 141 | 17:00 | 133 | 11:00 | Matarbari | 133 | 16:00 | 120 | 23:00
| AKS | 140 | 17:00 | 131 | 08:00 | Matuail | 133 | 04:00 | 127 | 11:00
| Aminbazar | 134 | 05:00 | 124 | 11:00 | Millgate | 133 | 07:00 | 124 | 11:00
| Amnura | 133 | 18:30 | 121 | 14:00 | Mirpur | 132 | 04:00 | 123 | 11:00
| Ashuganj | 139 | 06:00 | 135 | 00:00 | Mithapukur | 137 | 06:00 | 126 | 13:00
| Bagerhat | 135 | 08:00 | 126 | 23:00 | Modern | 137 | 16:00 | 134 | 02:00
| Bakulia | 140 | 08:00 | 132 | 11:00 | Mogbazar | 135 | 02:00 | 120 | 10:00
| Banani | 133 | 03:00 | 123 | 16:00 | Mongla | 135 | 07:00 | 127 | 23:00
| Bangabhaban | 132 | 03:00 | 124 | 13:00 | Motijheel | 132 | 06:00 | 125 | 11:00
| Barapukuria | 140 | 05:00 | 129 | 20:00 | Munshiganj | 135 | 06:00 | 128 | 11:00
| Barguna | 138 | 07:00 | 129 | 23:00 | Mymensingh | 132 | 04:00 | 122 | 19:30
| Barishal | 141 | 18:00 | 129 | 23:00 | Naogaon | 133 | 18:30 | 120 | 21:00
| Barishal | 141 | 18:00 | 133 | 00:00 | Narail | 132 | 18:00 | 121 | 21:00
| Baroaulia | 139 | 16:00 | 133 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 133 | 08:00 | 123 | 23:00 | Narshingdi | 129 | 15:00 | 122 | 11:00
| Bashundhara | 134 | 05:00 | 124 | 16:00 | Natore | 135 | 05:00 | 124 | 21:00
| BashundharaCement | 133 | 04:00 | 127 | 11:00 | Nawabganj | 136 | 02:00 | 128 | 11:00
| Beanibazar | 138 | 07:00 | 132 | 00:00 | Netrakona | 132 | 04:00 | 122 | 18:00
| Benapole | 136 | 18:00 | 125 | 23:00 | New | 133 | 07:00 | 125 | 14:00
| Bhaluka | 131 | 05:00 | 117 | 20:00 | Niamatpur | 133 | 18:30 | 116 | 21:00
| Bhandaria | 139 | 09:00 | 127 | 00:00 | Noapara | 138 | 18:00 | 129 | 23:00
| Bhangura | 138 | 05:00 | 130 | 21:00 | Pabna | 135 | 18:30 | 127 | 21:00
| Bheramara | 136 | 05:00 | 130 | 21:00 | Palashbari | 132 | 07:00 | 122 | 21:00
| Bheramara(GK) | 139 | 06:00 | 134 | 21:00 | Panchagarh | 138 | 03:00 | 121 | 10:00
| Bhulta | 124 | 07:00 | 119 | 12:00 | Patuakhali | 138 | 18:30 | 131 | 22:00
| Bog-Sherpur | 136 | 05:00 | 126 | 21:00 | PHP | 132 | 17:00 | 122 | 01:00
| Bogura | 137 | 05:00 | 127 | 21:00 | Purbachal | 135 | 06:00 | 123 | 14:00
| Bogura | 137 | 06:00 | 120 | 21:00 | Purbasadipur | 135 | 00:00 | 124 | 11:00
| Brahmanbaria | 134 | 07:00 | 128 | 23:00 | Rahim | 134 | 03:00 | 128 | 11:00
| Cantonment | 134 | 04:00 | 124 | 10:00 | Rajbari | 136 | 18:30 | 127 | 00:00
| Chandpur | 140 | 17:00 | 129 | 10:00 | Rajendrapur | 132 | 06:00 | 123 | 15:00
| Chandraghona | 140 | 08:00 | 134 | 19:00 | Rajshahi | 133 | 18:30 | 123 | 21:00
| Chapai | 134 | 18:30 | 123 | 14:00 | Rajshahi | 133 | 18:30 | 123 | 13:00
| Charsaidpur | 134 | 03:00 | 128 | 13:00 | Ramganj | 134 | 17:00 | 121 | 14:00
| Chauddagram | 132 | 07:00 | 125 | 01:00 | Rampur | 136 | 00:00 | 133 | 12:00
| Chhatak | 137 | 06:00 | 131 | 00:00 | Rampura | 136 | 04:00 | 125 | 11:00
| Chowmuhani | 130 | 17:00 | 120 | 22:00 | Rangamati | 140 | 17:00 | 134 | 02:00
| Chuadanga | 130 | 18:30 | 116 | 23:00 | Rangpur | 138 | 05:00 | 123 | 21:00
| Coxsbazar | 132 | 17:00 | 119 | 19:00 | Ruppur | 136 | 02:00 | 130 | 21:00
| Cumilla(N) | 133 | 07:00 | 128 | 14:00 | Saidpur | 138 | 04:00 | 124 | 20:00
| Cumilla(S) | 136 | 18:00 | 127 | 01:00 | Satkhira | 135 | 08:00 | 126 | 23:00
| Daudkandi | 138 | 19:30 | 127 | 01:00 | Satmasjid | 135 | 06:00 | 125 | 10:00
| Dhaka | 137 | 06:00 | 126 | 11:00 | Savar | 135 | 05:00 | 123 | 11:00
| Dhamrai | 132 | 06:00 | 123 | 16:00 | Shahjadpur | 140 | 05:00 | 133 | 23:00
| Dhanmondi | 134 | 05:00 | 128 | 12:00 | Shahjibazar | 138 | 08:00 | 133 | 23:00
| Dohazari | 141 | 17:00 | 131 | 14:00 | Shahmirpur | 141 | 17:00 | 134 | 11:00
| Faridpur | 136 | 18:30 | 128 | 00:00 | Shariatpur | 138 | 17:00 | 128 | 00:00
| Fatullah | 135 | 04:00 | 128 | 14:00 | Sherpur | 138 | 05:00 | 127 | 00:00
| Fenchuganj | 141 | 08:00 | 136 | 00:00 | Shikalbaha | 142 | 17:00 | 127 | 18:00
| Feni | 131 | 17:00 | 123 | 01:00 | Shikalbaha | 140 | 08:00 | 135 | 00:00
| Ghorashal | 137 | 01:00 | 136 | 00:00 | Shitalakhya | 135 | 04:00 | 127 | 11:00
| Goalpara | 139 | 18:30 | 132 | 23:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 138 | 18:00 | 131 | 23:00 | Shyampur | 132 | 04:00 | 127 | 09:00
| Gopalganj | 140 | 18:00 | 134 | 23:00 | Shyampur | 134 | 02:00 | 127 | 13:00
| Gopalganj_I | 140 | 18:00 | 132 | 23:00 | Siddhirganj | 133 | 05:00 | 127 | 11:00
| Gulshan | 136 | 06:00 | 125 | 11:00 | Sirajganj | 135 | 16:00 | 127 | 20:00
| Halishahar | 140 | 17:00 | 136 | 00:00 | Sonargaon | 134 | 20:00 | 129 | 10:00
| Haripur | 134 | 03:00 | 128 | 11:00 | Sreemongol | 140 | 07:00 | 136 | 00:00
| HaripurSBU | 134 | 05:00 | 128 | 11:00 | Srinagar | 137 | 02:00 | 129 | 11:00
| Hasnabad | 135 | 01:00 | 130 | 10:00 | SSM | 140 | 00:00 | 134 | 10:00
| Hathazari | 141 | 17:00 | 134 | 01:00 | Sunamganj | 137 | 08:00 | 129 | 01:00
| Ishurdi | 137 | 18:30 | 130 | 21:00 | Sylhet | 138 | 08:00 | 133 | 00:00
| Jaldhaka | 138 | 05:00 | 122 | 20:00 | Tangail | 134 | 05:00 | 125 | 19:30
| Jamalpur | 139 | 05:00 | 129 | 20:00 | Thakurgaon | 137 | 00:00 | 120 | 11:00
| Jashore | 136 | 18:30 | 125 | 23:00 | TK | 139 | 17:00 | 133 | 11:00
| Jhenaidah | 136 | 18:30 | 125 | 23:00 | Tongi | 136 | 05:00 | 127 | 13:00
| Jhenaidah | 136 | 18:30 | 126 | 23:00 | Ullon | 136 | 05:00 | 126 | 14:00
| Joydebpur | 140 | 05:00 | 134 | 16:00 | Uttara | 133 | 06:00 | 124 | 12:00
| Joypurhat | 132 | 18:30 | 117 | 21:00 | UttaraNew | 133 | 05:00 | 123 | 11:00
| Juldah | 143 | 17:00 | 134 | 10:00 | Zigatola | 137 | 04:00 | 128 | 11:00
| Kabirpur | 134 | 06:00 | 120 | 16:00
| Kachua | 138 | 17:00 | 125 | 01:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 133 | 04:00 | 124 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 314 | 8558 | 4745 | 13303 |  |  |  | QF-LDC-11
0:30 | 637 | 8132 | 4894.5 | 13026.5 | Date: | 2022-06-15
1:00 | 960 | 7706 | 5044 | 12750
1:30 | 962 | 7589 | 4988.5 | 12577.5
2:00 | 964 | 7472 | 4933 | 12405
2:30 | 925 | 7433 | 4785.5 | 12218.5 | [5 empty] | Gen. at Eve. Peak | 13264 | 13264 MW (21:00 )
3:00 | 886 | 7394 | 4638 | 12032 | [6 empty] | 21:00
3:30 | 855 | 7329 | 4546 | 11875 | [5 empty] | Gen. at Day Peak | 11406 | 11406 MW (12:00 )
4:00 | 824 | 7264 | 4454 | 11718 | [6 empty] | 12:00
4:30 | 883 | 7154 | 4435 | 11589 | [5 empty] | Highest Generation | 13306
5:00 | 942 | 7044 | 4416 | 11460 | [6 empty] | 23:00
5:30 | 878 | 6872 | 4188.5 | 11060.5
6:00 | 814 | 6700 | 3961 | 10661
6:30 | 797 | 6659 | 3913 | 10572
7:00 | 780 | 6618 | 3865 | 10483
7:30 | 829 | 6622.5 | 3858.5 | 10481
8:00 | 878 | 6627 | 3852 | 10479
8:30 | 888 | 6851 | 3841 | 10692
9:00 | 898 | 7075 | 3830 | 10905
9:30 | 893 | 7203 | 3874.5 | 11077.5
10:00 | 888 | 7331 | 3919 | 11250
10:30 | 917 | 7308.5 | 3958 | 11266.5
11:00 | 946 | 7286 | 3997 | 11283
11:30 | 926 | 7293 | 4051.5 | 11344.5
12:00 | 906 | 7300 | 4106 | 11406
12:30 | 790 | 7317.5 | 4174.5 | 11492
13:00 | 674 | 7335 | 4243 | 11578
13:30 | 829 | 7327 | 4329.5 | 11656.5
14:00 | 984 | 7319 | 4416 | 11735
14:30 | 860 | 7429.5 | 4343.5 | 11773
15:00 | 736 | 7540 | 4271 | 11811
15:30 | 782 | 7485 | 4240 | 11725
16:00 | 828 | 7430 | 4209 | 11639
16:30 | 760 | 7328.5 | 4139.5 | 11468
17:00 | 692 | 7227 | 4070 | 11297
17:30 | 657 | 7212.5 | 3894.5 | 11107
18:00 | 622 | 7198 | 3719 | 10917
18:30 | 597 | 7658.5 | 3947 | 11605.5
19:00 | 572 | 8119 | 4175 | 12294
19:30 | 474 | 8531 | 4696 | 13227
20:00 | 480 | 8414 | 4827 | 13241 |  |  |  | Executive Engineer
20:30 | 399 | 8441.5 | 4811 | 13252.5 |  |  |  | Network Operation Division
21:00 | 318 | 8469 | 4795 | 13264
21:30 | 331 | 8476 | 4782.5 | 13258.5
22:00 | 344 | 8483 | 4770 | 13253 |  |  |  |  | Page 6 of 7
22:30 | 350 | 8495.5 | 4784 | 13279.5
23:00 | 356 | 8508 | 4798 | 13306
23:30 | 335 | 8533 | 4771.5 | 13304.5
24:00 | 314 | 8558 | 4745 | 13303
13264 MW (21:00 )
11406 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-15 |  | Energy |  | 287809094
[13 empty] | 2022-06-15 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3789 | 906 | 2079 | 270 | 3929 | 1196 | 40 | 438 | 781 | 90 | 0 | 0
0:30 | 3324.5 | 906 | 2076.5 | 519 | 3883.5 | 1215.5 | 36 | 437 | 745.5 | 97 | 0 | 0 | Date: | 2022-06-15
1:00 | 2860 | 906 | 2074 | 768 | 3838 | 1235 | 32 | 436 | 710 | 104 | 0 | 0
1:30 | 2854.5 | 906.5 | 2062 | 714.5 | 3787 | 1230.5 | 32 | 437.5 | 664.5 | 103 | 0 | 0 | [7 empty] | Total Energy | 287.8091 | Total Energy Gen 287.809 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 287.809 MKWHr
2:00 | 2849 | 907 | 2050 | 661 | 3736 | 1226 | 32 | 439 | 619 | 102 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2839 | 906.5 | 2054.5 | 541 | 3728 | 1210.5 | 32 | 426 | 590.5 | 100 | 0 | 0 | [7 empty] | Energy Requirement | 287.8091
3:00 | 2829 | 906 | 2059 | 421 | 3720 | 1195 | 32 | 413 | 562 | 98 | 0 | 0
3:30 | 2850.5 | 906.5 | 2060.5 | 326.5 | 3722 | 1195 | 32 | 331.5 | 519 | 98 | 0 | 0 | [5 empty] | Shortage
4:00 | 2872 | 907 | 2062 | 232 | 3724 | 1195 | 32 | 250 | 476 | 98 | 0 | 0
4:30 | 2874 | 907 | 2057 | 128.5 | 3719.5 | 1180 | 32 | 250 | 474 | 97 | 0 | 0
5:00 | 2876 | 907 | 2052 | 25 | 3715 | 1165 | 32 | 250 | 472 | 96 | 0 | 0
5:30 | 2838.5 | 906.5 | 1958.5 | 12.5 | 3562 | 1140 | 32 | 250 | 398 | 91 | 1.5 | 0
6:00 | 2801 | 906 | 1865 | 0 | 3409 | 1115 | 32 | 250 | 324 | 86 | 3 | 0
6:30 | 2789 | 906 | 1818 | 0 | 3417.5 | 1085 | 32 | 250 | 309 | 85 | 10.5 | 0 |  |  |  | Coal
7:00 | 2777 | 906 | 1771 | 0 | 3426 | 1055 | 32 | 250 | 294 | 84 | 18 | 0
7:30 | 2750.5 | 906.5 | 1794 | 0 | 3414 | 1045 | 32 | 250 | 301.5 | 83 | 34.5 | 0 |  |  | Oil |  |  |  | ,
8:00 | 2724 | 907 | 1817 | 0 | 3402 | 1035 | 32 | 250 | 309 | 82 | 51 | 0
8:30 | 2707.5 | 906.5 | 1903.5 | 148 | 3398 | 1020 | 32 | 250 | 315 | 86 | 55.5 | 0
9:00 | 2691 | 906 | 1990 | 296 | 3394 | 1005 | 32 | 250 | 321 | 90 | 60 | 0
9:30 | 2728 | 906 | 2025.5 | 405 | 3374.5 | 1010 | 32 | 250 | 312 | 91 | 73.5 | 0
10:00 | 2765 | 906 | 2061 | 514 | 3355 | 1015 | 32 | 250 | 303 | 92 | 87 | 0
10:30 | 2743 | 906.5 | 2088.5 | 506 | 3348 | 1025 | 32 | 255 | 308 | 93 | 96.5 | 0
11:00 | 2721 | 907 | 2116 | 498 | 3341 | 1035 | 32 | 260 | 313 | 94 | 106 | 0
11:30 | 2714.5 | 906.5 | 2124 | 502.5 | 3340.5 | 1035 | 32 | 287 | 369.5 | 97 | 103 | 0
12:00 | 2708 | 906 | 2132 | 507 | 3340 | 1035 | 32 | 314 | 426 | 100 | 100 | 0
12:30 | 2702 | 905.5 | 2127 | 539 | 3396 | 1050 | 32 | 320.5 | 437 | 92 | 91.5 | 0
13:00 | 2696 | 905 | 2122 | 571 | 3452 | 1065 | 32 | 327 | 448 | 84 | 83 | 0
13:30 | 2696 | 905 | 2122 | 571 | 3452 | 1065 | 32 | 327 | 448 | 84 | 83 | 0
14:00 | 2696 | 905 | 2122 | 571 | 3452 | 1065 | 32 | 327 | 448 | 84 | 83 | 0
14:30 | 2812.5 | 905 | 2048 | 604 | 3457.5 | 1095 | 32 | 327.5 | 459 | 90 | 71.5 | 0
15:00 | 2929 | 905 | 1974 | 637 | 3463 | 1125 | 32 | 328 | 470 | 96 | 60 | 0
15:30 | 2904 | 905.5 | 1942 | 566 | 3521.5 | 1100 | 32 | 330 | 490.5 | 96 | 47.5 | 0
16:00 | 2879 | 906 | 1910 | 495 | 3580 | 1075 | 32 | 332 | 511 | 96 | 35 | 0
16:30 | 3072 | 906 | 1938.5 | 247.5 | 3615.5 | 1070 | 32 | 317 | 462.5 | 72 | 28.5 | 0
17:00 | 3072 | 906 | 1967 | 0 | 3651 | 1065 | 32 | 302 | 414 | 48 | 22 | 0
17:30 | 3108.5 | 906 | 1854 | 0 | 3666 | 945 | 32 | 276 | 415.5 | 47 | 13 | 0
18:00 | 3145 | 906 | 1741 | 0 | 3681 | 825 | 32 | 250 | 417 | 46 | 4 | 0
18:30 | 3273.5 | 906.5 | 1868 | 216 | 3755.5 | 835 | 32 | 267.5 | 527 | 60 | 2 | 0
19:00 | 3402 | 907 | 1995 | 432 | 3830 | 845 | 32 | 285 | 637 | 74 | 0 | 0
19:30 | 3478 | 906 | 2016 | 945 | 3918 | 925 | 32 | 391 | 751 | 76 | 0 | 0
20:00 | 3614 | 906 | 1989 | 624 | 3930 | 1055 | 32 | 448 | 781 | 76 | 0 | 0
20:30 | 3705 | 906.5 | 2015.5 | 439.5 | 3948 | 1115 | 32 | 440.5 | 786.5 | 79 | 0 | 0
21:00 | 3796 | 907 | 2042 | 255 | 3966 | 1175 | 32 | 433 | 792 | 82 | 0 | 0
21:30 | 3793 | 907 | 2063 | 220 | 3965.5 | 1180 | 36 | 432.5 | 793 | 84 | 0 | 0
22:00 | 3790 | 907 | 2084 | 185 | 3965 | 1185 | 40 | 432 | 794 | 86 | 0 | 0
22:30 | 3784.5 | 907 | 2082.5 | 200.5 | 3978 | 1190 | 40 | 433 | 791 | 88 | 0 | 0
23:00 | 3779 | 907 | 2081 | 216 | 3991 | 1195 | 40 | 434 | 788 | 90 | 0 | 0
23:30 | 3784 | 906.5 | 2080 | 243 | 3960 | 1195.5 | 40 | 436 | 784.5 | 90 | 0 | 0 | Max Temp. in Dhaka |  | 33.3° C
24:00 | 3789 | 906 | 2079 | 270 | 3929 | 1196 | 40 | 438 | 781 | 90 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 287.809 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 287.809 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 804420
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 19 | 25 | 25 | 25 | 7 |  | 25 | 25 | 25 | 25 | 25 | 17 | 19 | 514774
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 1 | 4 | 7 | 12 | 18 | 2 | 2 | 5 | 10 | 0 | 1 | 0 | [8 empty] | 58185
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 312738
12 | Hathazari 100 MW peaking PP | 34 | 0 | [10 empty] | 0 | 16 | 19 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 370032
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2526643
| Daudkandi 200 MW PP (B.Trac) | 25 | 25 | 25 | 0 |  |  |  |  | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  |  | 150 | 200 | 200 | 50 |  |  |  | 647232
14 | Titas 50 MW Peaking PP | 49 | 0 | [9 empty] | 40 | 49 | 49 | 49 | 49 | 0 |  |  | 0 | 15 | 26 | 40 | 48 | 48 | 49 | 478032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 97 | 97 | 97 | 98 | 60 | 60 | 40 | 96 | 93 | 93 | 94 | 94 | 95 | 94 | 95 | 96 | 9 |  | 0 | [5 empty] | 0 | 1680000
17 | Siddhirganj 335 MW CCPP | [12 empty] | 1 | 1 | 1 | 1 | 53 | 165 |  | 235 | 250 | 335 | 335 | 331 | 330 | 332 | 1934092
18 | Kodda 300 MW PP Unit-2 (Summit) | 291 | 293 | 293 | 293 | 293 | 281 | 285 | 291 | 293 | 278 | 278 | 276 | 275 | 278 | 275 | 278 | 278 | 288 |  | 292 | 292 | 293 | 290 | 292 | 293 | 293 | 6884942
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 45 | 45 | 63 | 92 | 92 | 92 | 26 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1137454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6473536
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 34 |  | 34 | 34 | 34 | 34 | 38 | 38 | 37 | 841392
33 | Ashuganj 225 MW CCPP | 158 | 163 | 173 | 178 | 178 | 172 | 172 | 162 | 177 | 205 | 207 | 208 | 186 | 172 | 160 | 138 | 143 | 172 |  | 206 | 210 | 214 | 213 | 206 | 209 | 212 | 4369000
34 | Ashuganj 450 MW CCPP(South) | 349 | 349 | 338 | 345 | 349 | 356 | 349 | 356 | 300 | 335 | 320 | 305 | 305 | 305 | 305 | 270 | 285 | 270 |  | 270 | 270 | 270 | 280 | 295 | 290 | 270 | 7645000
| Ashuganj 450 MW CCPP(North) | [13 empty] | 35 | 180 | 130 | 110 | 10 |  | 20 | 20 | 20 | 10 |  |  | 0 | 607500
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 56 | 55 | 56 | 55 | 54 | 52 | 54 | 51 | 53 | 52 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 899520
36 | Chandpur 150 MW CCPP | [17 empty] | 30 |  | 90 | 91 | 90 | 91 | 91 | 90 | 93 | 519700
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 399 | 397 | 397 | 398 | 398 | 397 | 397 | 397 | 399 | 399 | 401 | 399 | 401 | 400 | 400 | 397 | 403 | 405 |  | 412 | 410 | 409 | 409 | 410 | 401 | 400 | 9744380
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5146500
41 | Haripur 360MW CCPP(HPL) | 332 | 331 | 331 | 331 | 331 | 282 | 282 | 251 | 322 | 324 | 339 | 311 | 293 | 317 | 318 | 328 | 332 | 263 |  | 314 | 337 | 337 | 337 | 337 | 322 | 330 | 7554000
42 | RPCL 210MW CCPP | 124 | 121 | 123 | 136 | 136 | 123 | 120 | 107 | 107 | 71 | 85 | 87 | 87 | 86 | 85 | 98 | 98 | 98 |  | 99 | 105 | 124 | 142 | 130 | 130 | 143 | 2580480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 3 | 4 | 7 | 4 | 11 | 17 | 19 | 17 | 11 | 9 | 2 |  | 0 | [6 empty] | 107230
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1028000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 43 | 42 | 42 |  | 41 | 42 | 42 | 41 | 41 | 41 | 41 | 958344
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 63 | 62 | 62 | 62 | 62 | 63 | 62 | 63 | 63 | 63 | 40 |  | 63 | 65 | 65 | 64 | 63 | 62 | 64 | 1459872
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 40 | 78 | 75 | 75 | 75 | 78 | 78 | 78 | 75 | 75 | 78 | 78 |  | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 1809600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [15 empty] | 110 | 140 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 1051800
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 19 | 19 | 14 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435000
52 | Sylhet 50MW PP (EPL) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 851960
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253980
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 50 | 51 | 50 | 51 | 50 | 11 | 44 | 45 | 45 | 50 | 47 | 47 | 47 | 48 | 48 | 48 | 49 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 1126200
56 | Shahjahanulla 25 MW PP | 24 | 16 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 15 | 15 | 15 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 526440
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 280 | 280 | 290 | 280 | 270 | 290 | 270 | 300 | 320 | 300 | 310 | 310 | 290 | 310 | 260 | 290 | 280 |  | 280 | 275 | 270 | 275 | 290 | 300 | 300 | 7181500
| Bibiyana South 400 MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 85 | 94 | 102 | 118 | 128 | 240 | 300 | 400 | 384 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 4401800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 40 | 55 | 55 | 55 | 55 | 810995
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 8 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530880
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504864
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 443556
62 | Tangail 22 MW PP (Doreen) | 20 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 | 14 | 14 | 14 |  | 14 | 14 | 16 | 14 | 14 | 17 | 17 | 362268
63 | Impoprt (Tripura) | 104 | 102 | 98 | 98 | 96 | 86 | 84 | 82 | 90 | 92 | 94 | 100 | 84 | 98 | 96 | 96 | 48 | 46 |  | 74 | 76 | 76 | 82 | 86 | 90 | 90 | 2117760
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 9 | 4 | 3 | 3 | 3 | 7 | 4 | 2 | 3 | 15 | 13 |  | 17 | 23 | 20 | 30 | 35 | 38 | 31 | 501120
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 430812
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191520
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 9 | 14 | 14 | 20 | 20 | 14 | 20 | 20 | 20 | 0 |  | 0 |  | 14 | 20 | 21 | 21 | 9 | 9 | 9 | 345200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 20 | 20 |  | 20 | 20 | 20 | 17 | 17 | 19 | 17 | 431640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 15 | 15 | 24 | 8 | 16 | 25 | 0 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 506100
73 | Ghorashal 108MW PP (Regent) | 97 | 97 | 97 | 97 | 97 | 94 | 95 | 91 | 94 | 90 | 91 | 90 | 90 | 94 | 91 | 94 | 94 | 95 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2219500
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 14 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 9 | 9 | 9 |  | 9 | 9 | 9 | 13 | 9 | 9 | 9 | 230160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 156 | 162 | 162 | 162 | 162 | 162 | 162 | 108 |  | 118 | 162 | 162 | 162 | 162 | 162 | 162 | 3843360
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 86 | 82 | 82 | 82 | 88 | 89 | 87 | 88 | 88 | 93 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2206685
78 | Gazipur 52 MW PP | 47 | 47 | 47 | 48 | 48 | 24 | 24 | 28 | 47 | 47 | 40 | 43 | 47 | 46 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1085760
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 115 | 115 | 130 | 150 | 132 | 132 | 150 | 150 | 150 | 150 | 150 | 132 | 132 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3282240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2148000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 2 | 4 | 5 | 2 | 5 | 3 | 1 | 0 | 0 | [9 empty] | 27000
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1368789
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 107 | 110 | 110 | 110 | 110 | 106 | 90 | 88 | 88 | 88 | 87 | 91 | 107 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2530825
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 78 | 79 | 79 | 79 | 79 | 79 | 72 | 77 | 78 | 74 | 72 | 70 | 69 | 72 | 70 | 68 | 64 | 68 |  | 79 | 73 | 74 | 85 | 78 | 88 | 84 | 1828800
| Meghnaghat 104 MW PP (OPCL) | 94 | 94 | 90 | 97 | 94 | 94 | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 92 | 92 | 92 | 92 | 2228160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 78 | 78 | 90 | 78 | 78 | 90 | 90 | 90 | 90 | 90 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2033760
92 | Fenchuganj 44MW (Energyprima) | 47 | 44 | 44 | 40 | 44 | 44 | 10 | 30 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1090440
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 942628
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 85 | 85 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 93 | 2124864
95 | Patenga 50MW PP (Baraka) | 39 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 42 |  | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 1008000
96 | Chattogram 108 MW PP (ECPV) | 81 | 80 | 81 | 81 | 75 | 49 | 43 | 44 | 58 | 79 | 79 | 77 | 77 | 77 | 76 | 77 | 77 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1774080
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 42 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1146529
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329258
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2722990
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 8000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 874080
104 | Keranigonj 300 MW PP (APR) | 304 | 250 | 206 | 40 | 0 |  |  |  | 105 | 303 | 301 | 301 | 303 | 200 | 302 | 200 | 0 |  |  | 157 | 298 | 37 | 25 | 135 | 166 | 180 | 3699459
105 | Bramhangoan 100 MW PP (Aggreko) | 96 | 96 | 95 | 97 | 25 | 0 |  |  | 93 | 92 | 90 | 90 | 90 | 90 | 90 | 90 | 0 |  |  | 90 | 90 | 90 | 90 | 50 | 50 | 90 | 1568027
106 | Mymensingh 200 MW PP (United) | 187 | 200 | 188 | 190 | 191 | 190 | 190 | 190 | 200 | 200 | 190 | 188 | 188 | 185 | 176 | 185 | 185 | 185 |  | 186 | 187 | 191 | 191 | 191 | 191 | 190 | 4490400
112 | Aurahati 100MW PP (Aggreko) | 94 | 94 | 95 | 95 | 0 |  |  |  | 88 | 94 | 80 | 80 | 80 | 80 | 80 | 80 | 0 |  |  | 25 | 80 | 80 | 50 |  |  | 0 | 1272699
114 | Kodda 149 MW PP Unit-1 (Summit) | 121 | 132 | 132 | 132 | 132 | 118 | 128 | 132 | 132 | 132 | 123 | 115 | 122 | 116 | 115 | 115 | 125 | 132 |  | 132 | 132 | 132 | 132 | 133 | 132 | 133 | 3082032
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2114880
116 | Chandpur 200MW (Desh energy) | 180 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 83 | 68 | 68 | 68 | 82 | 70 | 89 | 121 | 167 |  | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 3007680
117 | Ashuganj 150MW PP (Midland) | 122 | 128 | 133 | 132 | 130 | 132 | 135 | 133 | 120 | 117 | 113 | 110 | 133 | 125 | 115 | 122 | 115 | 122 |  | 125 | 126 | 127 | 133 | 140 | 142 | 145 | 3059418
118 | Bibiyana-III 400 MW CCPP | [17 empty] | 82 |  | 80 | 100 | 120 | 285 | 295 | 292 | 297 | 1290000
| Jamalpur 115 MW PP (United) | 94 | 85 | 85 | 86 | 86 | 85 | 86 | 86 | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 94 | 94 | 95 |  | 96 | 96 | 96 | 97 | 96 | 96 | 106 | 2118000
| Anwara 300 MW PP (United) | 265 | 265 | 248 | 265 | 265 | 210 | 210 | 244 | 244 | 248 | 247 | 248 | 248 | 262 | 248 | 248 | 248 | 248 |  | 264 | 264 | 265 | 265 | 265 | 265 | 265 | 6056945
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 87 |  | 83 | 100 | 100 | 100 | 100 | 100 | 100 | 2394240
| Anlima Energy Ltd. | 90 | 75 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 89 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2132727
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 19 | 32 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 865440
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 101 | 101 | 97 | 85 | 101 | 101 | 101 | 102 | 102 | 101 | 101 | 96 | 101 | 101 | 101 | 85 | 90 | 91 |  | 86 | 101 | 102 | 102 | 101 | 101 | 101 | 2370240
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1328760
120 | Eastern Zone Total | 7706 | 7472 | 7394 | 7264 | 7044 | 6700 | 6618 | 6627 | 7075 | 7331 | 7286 | 7300 | 7335 | 7319 | 7540 | 7430 | 7227 | 7198 |  | 8119 | 8531 | 8414 | 8469 | 8483 | 8508 | 8558 | 180233948
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 111 | 112 | 111 | 110 | 110 | 110 | 108 | 108 | 94 | 65 | 60 | 60 | 60 | 60 | 60 | 78 | 78 | 80 |  | 80 | 80 | 78 | 78 | 80 | 95 | 95 | 2055360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 33 | 33 | 33 | 29 | 0 | [11 empty] | 5 |  | 30 | 44 | 39 | 39 | 39 | 38 | 34 | 371040
| Khulna 225 MW CCPP | 223 | 223 | 210 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 | 120 | 120 | 120 | 120 |  | 140 | 165 | 210 | 217 | 217 | 219 | 223 | 3816000
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 70 | 53 | 17 | 17 | 20 | 64 | 88 | 93 | 93 | 90 | 90 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1932480
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 13 | 39 | 45 | 59 | 74 | 81 | 54 | 76 | 28 | 20 | 10 | 2 |  | 0 | [6 empty] | 496800
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445200
133 | Bhola Nutan Biddut BD LTD (GAS) | 109 | 108 | 108 | 108 | 108 | 109 | 108 | 108 | 122 | 180 | 220 | 223 | 223 | 223 | 207 | 213 | 220 | 163 |  | 221 | 201 | 189 | 222 | 222 | 221 | 217 | 4097973
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 42 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 1022304
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 146 | 147 | 148 | 148 | 148 | 151 | 149 | 149 | 146 | 149 | 83 | 84 | 83 | 83 | 83 | 84 | 84 | 82 |  | 83 | 83 | 85 | 83 | 83 | 83 | 84 | 2659654
140 | Bhola 33 MW PP (Venture) | 31 | 28 | 33 | 33 | 30 | 26 | 22 | 20 | 18 | 19 | 19 | 19 | 22 | 23 | 23 | 22 | 21 | 21 |  | 32 | 31 | 28 | 32 | 34 | 35 | 35 | 615476
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 10 | 0 | [16 empty] | 2 | 97 | 67 | 20 |  |  | 0 | 211200
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 251250
143 | Gopalganj 100 MW Peaking PP | 54 | 43 | 43 | 30 | 30 | 30 | 0 | [12 empty] | 25 | 45 | 66 | 60 | 54 | 54 | 54 | 499968
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 50 | 50 | 50 | 50 | 55 | 89 | 89 | 88 | 89 | 89 | 88 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1967184
146 | Bheramara HVDC | 906 | 907 | 906 | 907 | 907 | 906 | 906 | 907 | 906 | 906 | 907 | 906 | 905 | 905 | 905 | 906 | 906 | 906 |  | 907 | 906 | 906 | 907 | 907 | 907 | 906 | 21920000
147 | Bheramara 410 MW CCPP | 280 | 280 | 275 | 273 | 273 | 275 | 275 | 275 | 220 | 220 | 240 | 240 | 235 | 225 | 185 | 150 | 145 | 160 |  | 185 | 195 | 200 | 205 | 210 | 210 | 215 | 5713632
148 | Payra 1320 MW | 1060 | 1050 | 1020 | 1020 | 990 | 940 | 880 | 860 | 830 | 840 | 860 | 860 | 890 | 930 | 950 | 900 | 890 | 650 |  | 670 | 750 | 880 | 1000 | 1010 | 1020 | 1020 | 24072000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 176 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 176 | 4284400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 | 34 | 34 | 24 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 696208
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 23100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 213 | 216 | 203 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 194 | 207 | 209 | 208 | 212 | 182 | 130 |  | 145 | 211 | 214 | 216 | 215 | 215 | 215 | 4473527
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 197 | 196 | 195 | 192 | 191 | 160 | 160 | 160 | 178 | 197 | 193 | 187 | 181 | 174 | 165 | 144 | 145 | 149 |  | 157 | 170 | 172 | 175 | 177 | 178 | 178 | 4575727
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 419 | 422 | 420 | 420 | 300 | 300 | 340 | 416 | 414 | 414 | 414 | 414 | 414 | 375 | 360 | 362 | 278 |  | 400 | 418 | 414 | 414 | 414 | 414 | 414 | 9312072
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 8 | 8 | 8 | 8 | 9 | 4 | 0 | 44505
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 17 | 20 | 19 | 19 | 19 | 19 | 19 | 19 |  | 21 | 21 | 21 | 22 | 22 | 21 | 22 | 470160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249696
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 629776
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 8 | 8 | 16 | 20 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 510170
168 | Santahar 50 MW Peaking PP | 38 | 38 | 38 | 38 | 38 | 0 | [10 empty] | 0 | 33 |  | 38 | 37 | 37 | 38 | 38 | 38 | 38 | 424720
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [15 empty] | 0 | 75840
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 46 | 46 | 46 | 0 | [13 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 832984
171 | Baghabari 200 MW PP (Paramount) | 189 | 186 | 0 | [7 empty] | 2 | 11 | 73 | 140 | 140 | 100 | 0 |  |  | 8 | 180 | 150 | 20 | 0 |  | 0 | 1280660
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 50 | 50 | 50 | 50 | 50 | 70 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2106240
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 50 | 50 | 90 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2143104
173 | Rangpur 20 MW GTPP | [20 empty] | 15 | 15 | 0 |  |  |  | 15000
175 | Saidpur 20 MW GTPP | [21 empty] | 9 | 0 |  |  |  | 6000
176 | Rangpur 113 MW PP (Confidence) | 75 | 75 | 76 | 76 | 75 | 46 | 38 | 40 | 40 | 68 | 75 | 74 | 65 | 73 | 74 | 74 | 85 | 87 |  | 87 | 87 | 87 | 87 | 87 | 94 | 78 | 1743734
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 11666
178 | Energypac Power Venture Thakurgaon Ltd. | 72 | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 90 | 90 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 72 | 1518336
178