## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-19 | Sunday
|  |  | Date (day): | 2022-06-19 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13491.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14916 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-18 | 2022-06-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 270 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 90 | 97 | 97 |  | 11 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 401 | 399 | 405 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas line problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 390 | 390 | 60 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 80 | 88 | 80 | 90 |  | 10 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 245 | 300 | 300 |  | 35 | GT-1 S/D due to gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M & gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 70 | 100 | 90 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 78 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 42 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 50 | 48 | 48
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 153 | 293 | 285 | 290 |  | 10 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 98 | 98
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 90 | 71 | 135 | 135 |  | 14 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 64 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 47 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2974 | 3076 | 3792 | 3894 | 681 | 1273
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 3 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 45 | 45 | 45 |  | 5 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 99 | 96 | 96 |  | 134 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 4 | 17 | 35 |  | 63 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 5 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 22 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 29 | 0 | 78 | 81 |  | 27 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 190 | 265 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 19 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 71 | 92 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 93 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 886 | 1108 | 1317 | 1399 | 311 | 665
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 216 | 200 | 220
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 360 | 280 | 360
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 360 | 280 | 360
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 35 | 35 | 35 | 10 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 2 | 30 | 51
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 110 | 137 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 135 | 135 | 135 |  | 28 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 184 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 19 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 110 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 96 | 96 | 96 | 17 |  | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 8 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 89 | 76 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1421 | 1876 | 1916 | 2299 | 514 | 62
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 179 | 160 | 190 | 12 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 170 | 191 | 180 | 191 |  | 9 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 97 | 95 | 107 |  | 8 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 11 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 437 | 498 | 528.6 | 530 | 12 | 25
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 29 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 45 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 41 | 62 | 62 | 65
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 280 | 280 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 382 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1418 | 1488 | 1532 | 1555 | 330 | 229
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 830 | 924 | 941 | 941
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 47 | 79 | 99 | 99 |  | 16 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 38 | 38 |  | 16 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 120 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 200 | 0 | 300 | 110 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 24 | 32 | 32 | 32
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 90 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 70 | 89 |  | 16 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 14 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1185 | 1340 | 1493 | 1972 | 110 | 109
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 48 |  |  | Rampal Transformar O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 11 | 25 | 20 | 25
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 86 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 550 | 1050 | 1050 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 200 | 222 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 615 | 916 | 1440 | 1445 | 109 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 0 | 0 |  | 71 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 0 | 0 |  | 50 | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 119 | 137 | 130 | 180 | 40 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 145 | 166 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 414 | 350 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 30 | 40 |  | 10 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 190 |  | 10 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 64 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 771 | 1178 | 1087 | 1419 | 513 | 191
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 62 | 87 | 95 | 95 |  | 18 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 108 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 271 | 370 | 386 | 403 | 269 | 25
|  | Total |  |  |  |  | 22348 | 21396 | 9978 | 11850 | 13491.6 | 14916 | 2849 | 2579
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9739.9847 | 11567.33 | 13169.7713 | 14560.1936
| A. |  | 2022-06-18 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 11850 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8424 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11850 | MW
| 3 | Day peak Generation : |  |  | 9978 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11567.33 | MW
| 4 | Evening peak Generation : |  |  | 11850 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 236.859 | MKWHr | By Solar | 0.43846 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 142.6344 | MKWHr |  | By Oil: | 55.1561 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.2214 | MKWHr |  | By Hydro: | 1.8425 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2849 | MW | Dhaka | 4288.03 | 4288.03 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2579 | MW | Chittagong | 1167.7 | 1167.7 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5428 | MW | Khulna | 1540 | 1540 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1052.95 | MMCFD |  |  | Rajshahi | 1303.6 | 1303.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163139169.974 | ii) Oil : | Taka | 710182635.18 | Comilla | 1049 | 1049 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 121232886 | Total | Taka | 994554691.154 | Mymensingh | 904 | 904 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.788 | MKWHr. | Sylhet | 231 | 231 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -320 | MW (E to W) at | 21:00 | hrs | Barisal | 370 | 370 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -320 | MW at | 21:00 | hrs | Rangpur | 714 | 714 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.1° C |  |  | Total | 11567.33 | 11567.33 |  | 0
| B. |  | 2022-06-19 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14916 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1916 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 259.8454 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9042 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.2487 | MKWHr. | ii) HVDC Flow at Peak Time |  | 924 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3174 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.62 |  | (b) Today: | 76.89 |  | (c) Rule Curve: |  | 80.76
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 305 | 0 |  | 0 | 380 | 255 | 78 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 28 | 28 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 280 | 265 | 193 | 0 | 135 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 94 | 196 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 66 | 84 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 145 | 0 | 34 | 0 | 90 | 155 | 80 | 400 | 0 | 0 | 105 | 0 | 0 | 54 | 96 | 0 | 41 | 100 | 400 | 92 | 0 | 0 | 90 | 0 | 0 | 0 | 100 | 17 |  | 640 | 0 | 315 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 210 | 0 | 384 | 0 | 0 | 70 | 0 | 35 | 0 | 0 | 70 | 410 | 227 | 0 | 0 | 0 | 0 | 34 |  | 6500 | 2947 | 9447 | 4336 | 640 | 1972 | 0 | 1754 | 585 | 66 | 0 | 0 | 94 | 0 | 0 | 75.22
2:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 305 | 0 |  | 0 | 380 | 260 | 79 | 0 | 30 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 20 | 28 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 280 | 265 | 207 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 88 | 193 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 66 | 84 | 0 | 130 | 0 | 0 | 0 | 265 | 0 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 28 | 0 | 90 | 155 | 10 | 400 | 0 | 0 | 105 | 0 | 0 | 54 | 92 | 0 | 28 | 100 | 400 | 92 | 0 | 0 | 90 | 0 | 0 | 0 | 101 | 17 |  | 640 | 0 | 315 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 210 | 0 | 394 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 70 | 410 | 227 | 0 | 0 | 0 | 0 | 34 |  | 6345 | 2925 | 9270 | 4341 | 640 | 1971 | 0 | 1579 | 585 | 66 | 0 | 0 | 88 | 0 | 0 | 75.3
3:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 306 | 0 |  | 0 | 380 | 265 | 79 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 20 | 28 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 280 | 265 | 213 | 0 | 135 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 84 | 195 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 66 | 84 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 0 | 90 | 155 | 10 | 400 | 0 | 0 | 105 | 0 | 0 | 54 | 92 | 0 | 29 | 100 | 278 | 92 | 0 | 0 | 90 | 0 | 0 | 0 | 100 | 17 |  | 640 | 0 | 300 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 209 | 0 | 386 | 0 | 0 | 35 | 0 | 10 | 0 | 0 | 35 | 410 | 227 | 0 | 0 | 0 | 0 | 34 |  | 6150 | 2840 | 8990 | 4207 | 640 | 1971 | 0 | 1437 | 585 | 66 | 0 | 0 | 84 | 0 | 0 | 75.38
4:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 340 | 0 |  | 0 | 380 | 255 | 78 | 0 | 30 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 20 | 25 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 280 | 265 | 214 | 0 | 135 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 88 | 196 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 65 | 84 | 0 | 130 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 0 | 90 | 155 | 10 | 400 | 0 | 0 | 105 | 0 | 0 | 54 | 85 | 0 | 29 | 100 | 260 | 92 | 0 | 0 | 90 | 0 | 0 | 0 | 91 | 17 |  | 640 | 0 | 295 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 206 | 0 | 324 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 440 | 227 | 0 | 0 | 0 | 0 | 34 |  | 6106 | 2773 | 8879 | 4193 | 640 | 1923 | 0 | 1354 | 615 | 66 | 0 | 0 | 88 | 0 | 0 | 75.46
5:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 342 | 0 |  | 0 | 380 | 275 | 79 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 20 | 25 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 280 | 265 | 214 | 0 | 135 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 82 | 194 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 66 | 84 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 90 | 120 | 10 | 400 | 0 | 0 | 105 | 0 | 0 | 35 | 92 | 0 | 28 | 100 | 15 | 72 | 0 | 0 | 90 | 0 | 0 | 0 | 101 | 17 |  | 640 | 0 | 285 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 205 | 0 | 392 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 480 | 227 | 0 | 0 | 0 | 0 | 34 |  | 5777 | 2863 | 8640 | 3931 | 640 | 2005 | 0 | 1261 | 655 | 66 | 0 | 0 | 82 | 0 | 0 | 75.54
6:00 | 0 | 0 | 0 | 180 | 250 | 99 | 0 | 342 | 0 |  | 0 | 380 | 260 | 79 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 20 | 25 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 22 | 41 | 0 | 0 | 0 | 360 | 265 | 214 | 0 | 135 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 78 | 195 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 52 | 84 | 0 | 90 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 70 | 100 | 10 | 400 | 0 | 0 | 68 | 0 | 0 | 35 | 68 | 0 | 29 | 100 | 60 | 72 | 0 | 0 | 90 | 0 | 0 | 0 | 100 | 0 |  | 640 | 0 | 275 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 160 | 0 | 351 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 530 | 163 | 0 | 0 | 0 | 1 | 34 |  | 5680 | 2744 | 8424 | 3907 | 640 | 1883 | 0 | 1143 | 705 | 66 | 0 | 0 | 78 | 2 | 0 | 75.62
7:00 | 0 | 0 | 0 | 180 | 250 | 95 | 0 | 342 | 0 |  | 0 | 380 | 275 | 77 | 0 | 30 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 5 | 22 | 25 | 20 | 25 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 45 | 22 | 35 | 0 | 0 | 0 | 360 | 260 | 179 | 0 | 135 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 80 | 192 | 0 | 20 | 0 | 43 | 42 | 11 | 10 | 110 | 0 | 64 | 78 | 0 | 90 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 2 | 70 | 85 | 10 | 400 | 2 | 0 | 68 | 0 | 0 | 35 | 68 | 0 | 29 | 100 | 80 | 72 | 1 | 0 | 68 | 0 | 0 | 0 | 96 | 6 |  | 640 | 0 | 265 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 35 | 0 | 29 | 0 | 0 | 35 | 520 | 163 | 0 | 0 | 0 | 10 | 34 |  | 5703 | 2819 | 8522 | 3934 | 640 | 1943 | 0 | 1151 | 695 | 66 | 0 | 0 | 80 | 13 | 0 | 75.7
8:00 | 0 | 0 | 0 | 180 | 250 | 95 | 0 | 342 | 0 |  | 0 | 380 | 290 | 75 | 0 | 30 | 333 | 0 | 0 | 6 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 19 | 25 | 0 | 0 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 45 | 22 | 13 | 0 | 0 | 0 | 305 | 285 | 173 | 0 | 135 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 92 | 192 | 0 | 20 | 0 | 43 | 41 | 11 | 10 | 110 | 0 | 63 | 78 | 0 | 90 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 5 | 0 | 0 | 80 | 0 | 20 | 9 | 90 | 91 | 10 | 351 | 8 | 0 | 105 | 0 | 0 | 50 | 86 | 0 | 28 | 100 | 320 | 87 | 6 | 17 | 79 | 0 | 15 | 0 | 97 | 17 |  | 640 | 0 | 240 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 149 | 0 | 370 | 13 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 460 | 163 | 0 | 0 | 0 | 25 | 34 |  | 6168 | 2680 | 8848 | 4036 | 640 | 1886 | 0 | 1453 | 635 | 66 | 0 | 0 | 92 | 40 | 0 | 75.78
9:00 | 0 | 0 | 0 | 180 | 250 | 91 | 0 | 343 | 0 |  | 0 | 380 | 250 | 77 | 0 | 55 | 335 | 0 | 0 | 8 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 19 | 25 | 0 | 9 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 50 | 0 | 13 | 22 | 2 | 0 | 0 | 0 | 300 | 270 | 161 | 0 | 136 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 98 | 192 | 0 | 20 | 0 | 43 | 41 | 11 | 10 | 110 | 0 | 63 | 79 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 15 | 0 | 0 | 98 | 0 | 36 | 4 | 90 | 136 | 15 | 355 | 20 | 25 | 105 | 1 | 0 | 54 | 92 | 0 | 28 | 100 | 400 | 91 | 4 | 17 | 90 | 0 | 17 | 0 | 92 | 28 |  | 640 | 0 | 230 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 370 | 17 | 0 | 37 | 0 | 34 | 0 | 0 | 60 | 410 | 163 | 0 | 0 | 0 | 24 | 34 |  | 6479 | 2636 | 9115 | 4053 | 640 | 1862 | 0 | 1762 | 585 | 66 | 0 | 16 | 98 | 33 | 0 | 75.87
10:00 | 0 | 0 | 0 | 180 | 250 | 89 | 0 | 389 | 0 |  | 0 | 380 | 305 | 79 | 0 | 55 | 250 | 0 | 0 | 8 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 16 | 25 | 0 | 16 | 0 | 36 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 0 | 28 | 22 | 6 | 0 | 0 | 0 | 300 | 270 | 178 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 17 | 98 | 173 | 0 | 20 | 2 | 43 | 41 | 11 | 10 | 110 | 0 | 40 | 79 | 0 | 90 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 98 | 0 | 0 | 100 | 0 | 83 | 4 | 30 | 155 | 50 | 354 | 32 | 35 | 105 | 1 | 0 | 17 | 51 | 0 | 28 | 90 | 401 | 91 | 4 | 17 | 90 | 0 | 17 | 0 | 101 | 55 |  | 830 | 0 | 220 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 70 | 350 | 180 | 0 | 0 | 1 | 39 | 34 |  | 6463 | 2718 | 9181 | 3941 | 830 | 1812 | 0 | 1842 | 525 | 66 | 0 | 16 | 98 | 51 | 0 | 75.96
11:00 | 0 | 0 | 0 | 180 | 250 | 89 | 0 | 401 | 0 |  | 0 | 380 | 305 | 77 | 0 | 55 | 250 | 0 | 0 | 23 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 42 | 55 | 22 | 25 | 16 | 25 | 0 | 20 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 40 | 0 | 38 | 22 | 6 | 0 | 0 | 0 | 270 | 260 | 115 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 11 | 104 | 162 | 0 | 20 | 1 | 43 | 41 | 11 | 10 | 110 | 0 | 62 | 81 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 130 | 0 | 0 | 115 | 0 | 81 | 4 | 63 | 155 | 81 | 352 | 45 | 42 | 105 | 0 | 30 | 17 | 55 | 0 | 28 | 81 | 401 | 79 | 17 | 70 | 90 | 0 | 17 | 0 | 90 | 55 |  | 830 | 0 | 210 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 414 | 28 | 0 | 35 | 0 | 62 | 0 | 0 | 100 | 330 | 200 | 0 | 0 | 1 | 20 | 34 |  | 6707 | 2865 | 9572 | 3749 | 830 | 1995 | 0 | 2198 | 505 | 100 | 0 | 48 | 104 | 43 | 0 | 75.96
12:00 | 0 | 0 | 0 | 180 | 250 | 89 | 0 | 401 | 0 |  | 0 | 380 | 300 | 80 | 0 | 55 | 250 | 0 | 0 | 70 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 11 | 25 | 0 | 42 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 29 | 37 | 22 | 6 | 0 | 0 | 0 | 270 | 260 | 202 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 16 | 17 | 104 | 154 | 0 | 20 | 2 | 43 | 41 | 11 | 10 | 110 | 0 | 41 | 81 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 153 | 0 | 0 | 170 | 0 | 90 | 3 | 90 | 100 | 110 | 400 | 45 | 64 | 105 | 1 | 30 | 19 | 71 | 0 | 28 | 93 | 400 | 72 | 24 | 144 | 90 | 0 | 17 | 0 | 89 | 47 |  | 830 | 0 | 200 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 24 | 84 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 145 | 0 | 300 | 70 | 0 | 64 | 0 | 62 | 0 | 0 | 113 | 320 | 200 | 0 | 0 | 5 | 14 | 34 |  | 7136 | 2842 | 9978 | 3879 | 830 | 1831 | 0 | 2642 | 495 | 100 | 0 | 48 | 104 | 49 | 0 | 0
13:00 | 0 | 0 | 0 | 180 | 200 | 45 | 0 | 402 | 0 |  | 0 | 380 | 235 | 78 | 0 | 55 | 250 | 0 | 0 | 80 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 0 | 25 | 0 | 48 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 52 | 38 | 22 | 8 | 0 | 0 | 0 | 270 | 260 | 216 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 96 | 152 | 0 | 20 | 1 | 43 | 41 | 11 | 10 | 110 | 0 | 40 | 81 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 233 | 0 | 0 | 130 | 0 | 106 | 1 | 90 | 74 | 127 | 354 | 16 | 70 | 105 | 2 | 15 | 52 | 81 | 0 | 28 | 90 | 350 | 69 | 23 | 162 | 90 | 0 | 17 | 0 | 90 | 0 |  | 830 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 130 | 0 | 230 | 35 | 0 | 82 | 0 | 67 | 0 | 0 | 113 | 270 | 157 | 0 | 0 | 2 | 4 | 34 |  | 6839 | 2629 | 9468 | 3689 | 830 | 1600 | 0 | 2637 | 445 | 100 | 0 | 38 | 96 | 33 | 0 | 0
14:00 | 0 | 0 | 0 | 180 | 190 | 22 | 0 | 398 | 0 |  | 0 | 380 | 280 | 77 | 0 | 55 | 250 | 0 | 0 | 29 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 0 | 25 | 0 | 16 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 20 | 0 | 0 | 10 | 0 | 0 | 0 | 270 | 260 | 214 | 0 | 135 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 5 | 0 | 16 | 11 | 110 | 151 | 0 | 20 | 1 | 43 | 41 | 11 | 10 | 110 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 230 | 0 | 0 | 103 | 0 | 95 | 6 | 50 | 85 | 90 | 353 | 16 | 70 | 105 | 1 | 15 | 35 | 51 | 0 | 28 | 90 | 340 | 60 | 24 | 72 | 90 | 0 | 0 | 0 | 79 | 0 |  | 829 | 0 | 205 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 130 | 0 | 251 | 35 | 0 | 35 | 0 | 66 | 0 | 2 | 35 | 250 | 160 | 0 | 0 | 2 | 7 | 34 |  | 6177 | 2516 | 8693 | 3620 | 829 | 1573 | 0 | 1961 | 425 | 100 | 0 | 32 | 110 | 43 | 0 | 76.01
15:00 | 0 | 0 | 0 | 180 | 230 | 22 | 0 | 400 | 0 |  | 0 | 380 | 295 | 74 | 0 | 55 | 250 | 0 | 0 | 16 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 0 | 25 | 0 | 16 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 22 | 0 | 22 | 6 | 0 | 0 | 0 | 300 | 260 | 212 | 0 | 135 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 102 | 150 | 0 | 20 | 1 | 43 | 40 | 11 | 10 | 110 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 230 | 0 | 0 | 130 | 0 | 70 | 1 | 50 | 85 | 90 | 369 | 16 | 70 | 105 | 0 | 15 | 35 | 51 | 0 | 29 | 90 | 340 | 35 | 19 | 72 | 90 | 0 | 0 | 0 | 76 | 0 |  | 889 | 0 | 215 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 130 | 0 | 330 | 35 | 0 | 35 | 0 | 61 | 0 | 2 | 35 | 250 | 185 | 0 | 0 | 1 | 15 | 34 |  | 6291 | 2689 | 8980 | 3739 | 889 | 1737 | 0 | 1917 | 425 | 100 | 0 | 32 | 102 | 39 | 0 | 76.03
16:00 | 0 | 0 | 0 | 180 | 270 | 22 | 0 | 400 | 0 |  | 0 | 380 | 255 | 73 | 0 | 55 | 60 | 0 | 0 | 16 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 18 | 25 | 0 | 16 | 0 | 67 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 10 | 23 | 21 | 22 | 6 | 0 | 0 | 0 | 360 | 290 | 214 | 0 | 135 | 5 | 0 | 0 | 43 | 0 | 2 | 0 | 0 | 8 | 25 | 18 | 104 | 158 | 0 | 20 | 1 | 43 | 41 | 11 | 10 | 110 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 230 | 0 | 0 | 130 | 0 | 71 | 1 | 50 | 85 | 90 | 400 | 16 | 70 | 105 | 0 | 15 | 35 | 51 | 0 | 46 | 92 | 400 | 35 | 0 | 72 | 90 | 0 | 0 | 0 | 89 | 0 |  | 925 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 149 | 0 | 380 | 35 | 0 | 35 | 0 | 66 | 0 | 2 | 35 | 290 | 165 | 0 | 0 | 0 | 21 | 34 |  | 6351 | 2814 | 9165 | 3838 | 925 | 1702 | 0 | 1975 | 465 | 97 | 0 | 34 | 104 | 25 | 0 | 76.08
17:00 | 0 | 0 | 0 | 180 | 270 | 22 | 0 | 401 | 0 |  | 0 | 380 | 280 | 79 | 0 | 55 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 8 | 25 | 0 | 16 | 0 | 30 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 40 | 22 | 10 | 0 | 0 | 0 | 360 | 290 | 216 | 8 | 135 | 24 | 0 | 0 | 43 | 0 | 8 | 0 | 0 | 8 | 33 | 16 | 100 | 156 | 0 | 20 | 0 | 43 | 41 | 11 | 10 | 110 | 0 | 40 | 78 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 180 | 0 | 0 | 130 | 0 | 70 | 2 | 50 | 85 | 90 | 400 | 8 | 70 | 105 | 0 | 15 | 35 | 51 | 0 | 95 | 100 | 400 | 35 | 1 | 35 | 90 | 0 | 0 | 0 | 100 | 15 |  | 924 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 167 | 0 | 350 | 17 | 0 | 35 | 0 | 70 | 0 | 2 | 35 | 290 | 185 | 0 | 0 | 0 | 14 | 108 |  | 6358 | 2891 | 9249 | 3800 | 924 | 1820 | 0 | 2025 | 465 | 60 | 0 | 36 | 100 | 19 | 0 | 76.13
18:00 | 0 | 0 | 0 | 180 | 270 | 44 | 0 | 400 | 0 |  | 0 | 380 | 269 | 86 | 0 | 55 | 43 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 8 | 25 | 0 | 16 | 0 | 30 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 10 | 0 | 0 | 0 | 300 | 290 | 215 | 8 | 136 | 35 | 0 | 0 | 51 | 0 | 8 | 0 | 0 | 8 | 30 | 20 | 100 | 176 | 0 | 20 | 0 | 43 | 40 | 11 | 10 | 110 | 0 | 63 | 84 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 145 | 0 | 0 | 80 | 0 | 58 | 0 | 50 | 85 | 90 | 400 | 8 | 70 | 105 | 0 | 15 | 35 | 51 | 0 | 96 | 100 | 400 | 35 | 1 | 35 | 90 | 0 | 0 | 0 | 101 | 47 |  | 925 | 0 | 200 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 32 | 0 | 25 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 168 | 0 | 300 | 17 | 0 | 35 | 0 | 80 | 0 | 1 | 35 | 290 | 203 | 0 | 0 | 0 | 1 | 90 |  | 6366 | 2933 | 9299 | 3841 | 925 | 1818 | 0 | 1970 | 465 | 60 | 0 | 117 | 100 | 3 | 0 | 76.2
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 70 | 0 | 399 | 0 |  | 0 | 380 | 305 | 87 | 0 | 55 | 41 | 0 | 0 | 39 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 11 | 33 | 0 | 16 | 0 | 30 | 30 | 100 | 0 | 3 | 0 | 0 | 0 | 0 |  | 22 | 11 | 47 | 10 | 13 | 45 | 22 | 20 | 0 | 0 | 0 | 300 | 290 | 214 | 8 | 135 | 35 | 0 | 0 | 51 | 0 | 18 | 0 | 0 | 8 | 33 | 21 | 114 | 176 | 0 | 20 | 0 | 43 | 40 | 11 | 10 | 110 | 0 | 40 | 84 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 208 | 0 | 0 | 118 | 0 | 58 | 0 | 90 | 131 | 105 | 371 | 20 | 70 | 105 | 0 | 50 | 40 | 59 | 0 | 95 | 100 | 360 | 60 | 0 | 115 | 90 | 0 | 0 | 0 | 101 | 55 |  | 925 | 0 | 200 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 25 | 16 | 0 | 0 | 0 | 34 | 5 | 52 | 0 | 8 | 32 | 3 | 38 | 21 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 150 | 0 | 250 | 35 | 0 | 38 | 30 | 86 | 0 | 0 | 95 | 370 | 183 | 0 | 5 | 0 | 0 | 104 |  | 6985 | 3227 | 10212 | 3772 | 925 | 1798 | 0 | 2713 | 545 | 60 | 0 | 285 | 114 | 0 | 0 | 76.44
19:30 | 0 | 0 | 0 | 180 | 270 | 83 | 0 | 400 | 0 |  | 0 | 380 | 285 | 87 | 0 | 55 | 41 | 0 | 0 | 80 | 84 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 12 | 33 | 0 | 40 | 0 | 30 | 30 | 100 | 0 | 15 | 0 | 0 | 0 | 0 |  | 22 | 30 | 51 | 80 | 45 | 45 | 22 | 24 | 0 | 0 | 0 | 300 | 320 | 215 | 8 | 135 | 35 | 0 | 0 | 51 | 0 | 33 | 0 | 0 | 8 | 33 | 21 | 108 | 167 | 0 | 20 | 0 | 43 | 40 | 50 | 10 | 110 | 0 | 63 | 84 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 293 | 0 | 0 | 191 | 0 | 70 | 0 | 90 | 175 | 133 | 400 | 103 | 105 | 105 | 0 | 170 | 46 | 73 | 17 | 96 | 100 | 400 | 88 | 0 | 162 | 90 | 0 | 0 | 0 | 101 | 55 |  | 924 | 0 | 200 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 25 | 16 | 0 | 0 | 0 | 34 | 5 | 52 | 0 | 34 | 32 | 8 | 38 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 163 | 0 | 420 | 90 | 0 | 60 | 50 | 87 | 0 | 0 | 113 | 490 | 233 | 0 | 17 | 0 | 0 | 108 |  | 7970 | 3744 | 11714 | 3892 | 924 | 2074 | 0 | 3668 | 665 | 60 | 0 | 323 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 270 | 80 | 0 | 399 | 0 |  | 0 | 380 | 250 | 88 | 0 | 55 | 41 | 0 | 0 | 93 | 94 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 12 | 33 | 0 | 50 | 0 | 30 | 30 | 100 | 0 | 21 | 0 | 0 | 0 | 0 |  | 19 | 34 | 51 | 90 | 51 | 45 | 22 | 17 | 0 | 0 | 0 | 330 | 355 | 216 | 8 | 135 | 32 | 0 | 0 | 51 | 0 | 33 | 0 | 0 | 8 | 33 | 21 | 108 | 176 | 0 | 0 | 0 | 43 | 40 | 53 | 38 | 110 | 0 | 65 | 84 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 293 | 0 | 0 | 191 | 0 | 70 | 0 | 90 | 179 | 130 | 400 | 95 | 105 | 105 | 0 | 186 | 54 | 77 | 17 | 96 | 100 | 400 | 88 | 0 | 162 | 90 | 0 | 0 | 0 | 98 | 55 |  | 924 | 0 | 205 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 26 | 16 | 0 | 0 | 0 | 34 | 5 | 52 | 0 | 34 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 164 | 0 | 420 | 90 | 0 | 104 | 23 | 86 | 0 | 0 | 113 | 500 | 222 | 0 | 17 | 0 | 0 | 108 |  | 8084 | 3756 | 11840 | 3955 | 924 | 2050 | 0 | 3741 | 675 | 60 | 0 | 327 | 108 | 0 | 0 | 76.36
21:00 | 0 | 0 | 0 | 180 | 270 | 90 | 0 | 399 | 0 |  | 0 | 380 | 245 | 88 | 0 | 55 | 78 | 0 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 17 | 33 | 0 | 50 | 0 | 69 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 4 | 5 | 90 | 0 | 45 | 22 | 22 | 0 | 0 | 0 | 360 | 360 | 216 | 8 | 135 | 35 | 2 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 110 | 179 | 0 | 20 | 0 | 43 | 29 | 53 | 45 | 110 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 293 | 0 | 0 | 191 | 0 | 71 | 0 | 90 | 184 | 137 | 400 | 97 | 105 | 105 | 0 | 190 | 54 | 92 | 17 | 96 | 100 | 382 | 104 | 0 | 162 | 90 | 0 | 8 | 0 | 76 | 55 |  | 924 | 0 | 200 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 32 | 86 | 25 | 16 | 0 | 0 | 0 | 34 | 6 | 52 | 0 | 34 | 30 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 166 | 0 | 414 | 90 | 0 | 113 | 15 | 87 | 0 | 0 | 113 | 550 | 222 | 0 | 17 | 0 | 0 | 108 |  | 8046 | 3804 | 11850 | 4048 | 924 | 2053 | 0 | 3706 | 725 | 99 | 0 | 185 | 110 | 0 | 0 | 76.44
22:00 | 0 | 0 | 0 | 180 | 270 | 92 | 0 | 399 | 0 |  | 0 | 380 | 265 | 86 | 0 | 55 | 335 | 0 | 0 | 64 | 48 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 0 | 24 | 0 | 69 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 90 | 0 | 45 | 22 | 27 | 0 | 0 | 0 | 300 | 330 | 217 | 8 | 135 | 35 | 20 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 33 | 21 | 110 | 178 | 0 | 20 | 0 | 43 | 30 | 53 | 47 | 110 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 230 | 0 | 0 | 193 | 0 | 88 | 0 | 90 | 200 | 140 | 400 | 55 | 105 | 105 | 0 | 135 | 54 | 92 | 17 | 94 | 100 | 401 | 104 | 0 | 162 | 105 | 0 | 17 | 0 | 77 | 48 |  | 924 | 0 | 190 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 32 | 86 | 30 | 16 | 0 | 0 | 0 | 34 | 6 | 52 | 0 | 0 | 30 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 165 | 0 | 360 | 93 | 0 | 113 | 15 | 87 | 0 | 0 | 113 | 580 | 222 | 0 | 17 | 0 | 0 | 108 |  | 8058 | 3739 | 11797 | 4237 | 924 | 2051 | 0 | 3460 | 756 | 99 | 0 | 160 | 110 | 0 | 0 | 75.08
23:00 | 0 | 0 | 0 | 180 | 270 | 85 | 0 | 399 | 0 |  | 0 | 380 | 262 | 86 | 0 | 55 | 335 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 0 | 24 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 0 | 45 | 22 | 27 | 0 | 0 | 0 | 300 | 330 | 216 | 8 | 136 | 35 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 106 | 178 | 0 | 20 | 0 | 43 | 29 | 53 | 50 | 110 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 228 | 0 | 0 | 192 | 0 | 92 | 0 | 90 | 200 | 138 | 400 | 55 | 105 | 105 | 0 | 80 | 54 | 92 | 0 | 96 | 100 | 401 | 104 | 0 | 108 | 108 | 0 | 17 | 0 | 100 | 30 |  | 924 | 0 | 190 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 30 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 164 | 0 | 360 | 53 | 0 | 113 | 0 | 88 | 0 | 0 | 113 | 580 | 227 | 0 | 17 | 0 | 0 | 108 |  | 7886 | 3632 | 11518 | 4234 | 924 | 2038 | 0 | 3270 | 755 | 100 | 0 | 91 | 106 | 0 | 0 | 75.11
24:00 | 0 | 0 | 0 | 180 | 270 | 85 | 0 | 401 | 0 |  | 0 | 390 | 250 | 85 | 0 | 55 | 335 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 0 | 24 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 0 | 45 | 22 | 38 | 0 | 0 | 0 | 300 | 330 | 214 | 0 | 137 | 35 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 106 | 186 | 0 | 20 | 0 | 43 | 29 | 53 | 50 | 110 | 0 | 64 | 84 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 228 | 0 | 0 | 193 | 0 | 97 | 0 | 90 | 200 | 138 | 401 | 55 | 105 | 105 | 0 | 50 | 54 | 100 | 0 | 40 | 100 | 400 | 104 | 0 | 72 | 108 | 0 | 17 | 0 | 100 | 30 |  | 925 | 0 | 190 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 30 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 160 | 0 | 414 | 35 | 0 | 113 | 0 | 66 | 0 | 0 | 113 | 560 | 227 | 0 | 17 | 0 | 0 | 108 |  | 7810 | 3620 | 11430 | 4236 | 925 | 2133 | 0 | 3104 | 735 | 100 | 0 | 91 | 106 | 0 | 0 | 75.14
KWH | 0 | 0 | 0 | 4347000 | 6038809 | 1835818 | 0 | 9054210 | 0 |  | 0 | 9028750 | 6591215 | 1939200 | 0 | 1145368 | 5587957 | 0 | 0 | 695347 | 549360 | 298080 | 0 | 0 | 0 | 0 | 1198440 | 825657 | 541613 | 289440 | 600000 | 360180 | 703800 | 0 | 410880 | 0 | 1114484 | 728000 | 2400000 | 0 | 31384 | 0 | 0 | 0 | 0 |  | 409920 | 61440 | 95068 | 831840 | 224640 | 924960 | 508848 | 547200 | 0 | 0 | 0 | 7759500 | 7001000 | 4845000 | 66909 | 3231370 | 248976 | 78720 | 0 | 1099095 | 0 | 61616 | 0 | 338040 | 161460 | 640800 | 484260 | 2317440 | 4152960 | 0 | 429372 | 10250 | 1027000 | 911576 | 461400 | 456984 | 2743691 | 0 | 1377888 | 1665600 | 0 | 1186970 | 0 | 0 | 0 | 6988500 | 0 | 14500 | 0 | 3246762 | 0 | 0 | 2930400 | 0 | 1389456 | 38475 | 1848000 | 3228960 | 1895200 | 9251000 | 668400 | 1202400 | 2535854 | 6602 | 908291 | 1108190 | 1933664 | 57000 | 1207920 | 2340480 | 8054700 | 1911360 | 123670 | 1605600 | 2192945 | 0 | 189720 | 0 | 2260800 | 655920 |  | 19248727 | 0 | 5901120 | 0 | 1451520 | 0 | 0 | 0 | 0 | 0 | 232500 | 2071926 | 471195 | 89184 | 0 | 0 | 0 | 123517 | 36884 | 282096 | 0 | 65942 | 250935 | 22080 | 217883 | 471600 | 0 | 126162 | 0 | 0 | 4277400 | 0 | 0 | 0 | 0 | 3502473 | 0 | 0 | 0 | 4256155 | 0 | 8589454 | 832800 | 0 | 1481568 | 97632 | 1206816 | 0 | 15140 | 1663488 | 10944000 | 4673809 | 0 | 93600 | 19680 | 224640 | 1445568 |  | 162471554 | 74387494 | 236859048 | 96864452 | 19248727 | 45769940 | 0 | 53728629 | 15221400 | 1842484 | 0 | 1427519 | 2317440 | 438457 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6763466.08 | 2441637.94 | 0 | 9506920.5 | 0 |  | 0 | 9841337.5 | 7316248.65 | 21680256 | 0 | 15176126 | 6258511.84 | 0 | 0 | 10165973.14 | 7729495.2 | 4831876.8 | 0 | 0 | 0 | 0 | 15244156.8 | 11146369.5 | 7263030.33 | 217080 | 450000 | 0 | 0 | 0 | 6989068.8 | 0 | 300910.68 | 196560 | 4536000 | 0 | 513128.4 | 0 | 0 | 0 | 0 |  | 5349456 | 1024819.2 | 1618057.36 | 11238158.4 | 2848435.2 | 10701787.2 | 646236.96 | 1822176 | 0 | 0 | 0 | 8613045 | 7631090 | 5620200 | 86312.61 | 3942271.4 | 281342.88 | 117292.8 | 0 | 1835488.65 | 0 | 1064108.32 | 0 | 463114.8 | 121095 | 1121400 | 363195 | 16639219.2 | 4526726.4 | 0 | 583945.92 | 163385 | 1406990 | 1203280.32 | 802836 | 790582.32 | 3155244.65 | 0 | 2673102.72 | 3797568 | 0 | 1198839.7 | 0 | 0 | 0 | 6988500 | 0 | 11020 | 0 | 44318301.3 | 0 | 0 | 39501792 | 0 | 19243965.6 | 449772.75 | 19071360 | 44107593.6 | 25149304 | 8510920 | 8127744 | 17386704 | 32078553.1 | 0 | 10663336.34 | 12068189.1 | 20554848.32 | 773490 | 15570088.8 | 27570854.4 | 7410324 | 24752112 | 1787031.5 | 20375064 | 24955714.1 | 0 | 2477743.2 | 0 | 33844176 | 8638466.4 |  | 57746181 | 0 | 6609254.4 | 0 | 15110323.2 | 0 | 0 | 0 | 0 | 0 | 3341025 | 2320557.12 | 914118.3 | 972105.6 | 0 | 0 | 0 | 2071380.09 | 645101.16 | 4411981.44 | 0 | 1091999.52 | 4243310.85 | 300950.4 | 3675686.21 | 976212 | 0 | 95504.634 | 0 | 0 | 22627446 | 0 | 0 | 0 | 0 | 4483165.44 | 0 | 0 | 0 | 4937139.8 | 0 | 8503559.46 | 11192832 | 0 | 17526949.44 | 1410782.4 | 15326563.2 | 0 | 167297 | 20194744.32 | 98605440 | 4767285.18 | 0 | 692640 | 222580.8 | 2635027.2 | 22160557.44 |  | 734882955.68 | 339979700.604 | 1074862656.284 | 108982769.914 | 57746181 | 54156400.06 | 0 | 686596313.75 | 121232886 | 497470.68 | 0 | 23586321.43 | 16639219.2 | 5425094.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 250 | 89 | 0 | 401 | 0 |  | 0 | 380 | 300 | 80 | 0 | 55 | 250 | 0 | 0 | 70 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 11 | 25 | 0 | 42 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 29 | 37 | 22 | 6 | 0 | 0 | 0 | 270 | 260 | 202 | 0 | 136 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 16 | 17 | 104 | 154 | 0 | 20 | 2 | 43 | 41 | 11 | 10 | 110 | 0 | 41 | 81 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 153 | 0 | 0 | 170 | 0 | 90 | 3 | 90 | 100 | 110 | 400 | 45 | 64 | 105 | 1 | 30 | 19 | 71 | 0 | 28 | 93 | 400 | 72 | 24 | 144 | 90 | 0 | 17 | 0 | 89 | 47 |  | 830 | 0 | 200 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 24 | 84 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 145 | 0 | 300 | 70 | 0 | 64 | 0 | 62 | 0 | 0 | 113 | 320 | 200 | 0 | 0 | 5 | 14 | 34 |  | 9978 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 270 | 90 | 0 | 399 | 0 | 0 | 0 | 380 | 245 | 88 | 0 | 55 | 78 | 0 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 17 | 33 | 0 | 50 | 0 | 69 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 4 | 5 | 90 | 0 | 45 | 22 | 22 | 0 | 0 | 0 | 360 | 360 | 216 | 8 | 135 | 35 | 2 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 110 | 179 | 0 | 20 | 0 | 43 | 29 | 53 | 45 | 110 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 293 | 0 | 0 | 191 | 0 | 71 | 0 | 90 | 184 | 137 | 400 | 97 | 105 | 105 | 0 | 190 | 54 | 92 | 17 | 96 | 100 | 382 | 104 | 0 | 162 | 90 | 0 | 8 | 0 | 76 | 55 |  | 924 | 0 | 200 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 32 | 86 | 25 | 16 | 0 | 0 | 0 | 34 | 6 | 52 | 0 | 34 | 30 | 8 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 166 | 0 | 414 | 90 | 0 | 113 | 15 | 87 | 0 | 0 | 113 | 550 | 222 | 0 | 17 | 0 | 0 | 108 |  | 11850 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 412 | 0 | 0 | 0 | 390 | 300 | 90 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 66 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 51 | 90 | 81 | 45 | 22 | 20 | 0 | 0 | 0 | 360 | 360 | 220 | 8 | 135 | 35 | 51 | 0 | 51 | 0 | 50 | 0 | 21 | 8 | 33 | 21 | 165 | 190 | 0 | 20 | 0 | 43 | 41 | 51 | 50 | 110 | 0 | 65 | 84 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 200 | 290 | 300 | 100 | 191 | 98 | 135 | 0 | 90 | 200 | 150 | 400 | 107 | 105 | 105 | 0 | 285 | 54 | 110 | 0 | 96 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 |  | 100 | 55 |  | 941 | 0 | 300 | 0 | 99 | 220 | 0 | 0 | 38 | 60 | 32 | 85 | 25 | 48 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 0 | 32 | 0 | 40 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 180 | 0 | 0 | 100 | 180 | 0 | 414 | 93 | 190 | 113 | 89 | 95 | 0 | 0 | 113 | 1050 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 405 | 0 | 0 | 0 | 390 | 300 | 80 | 0 | 55 | 335 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 48 | 0 | 66 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 90 | 78 | 45 | 22 | 5 | 0 | 0 | 0 | 280 | 280 | 200 | 8 | 135 | 35 | 30 | 0 | 51 | 0 | 50 | 0 | 21 | 8 | 33 | 21 | 143 | 160 | 0 | 20 | 1.6 | 43 | 41 | 51 | 50 | 110 | 0 | 62 | 84 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 11 | 100 | 285 | 200 | 100 | 180 | 98 | 135 | 20 | 90 | 150 | 140 | 400 | 95 | 105 | 105 | 5 | 265 | 54 | 110 | 0 | 96 | 100 | 400 | 104 | 50 | 162 | 90 | 0 | 35 | 30 | 100 | 55 |  | 941 | 0 | 0 | 0 | 99 | 120 | 0 | 0 | 38 | 0 | 32 | 85 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 180 | 0 | 350 | 93 | 100 | 113 | 70 | 95 | 0 | 8 | 113 | 1050 | 220 |  | 17 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 82 | 0 | 401 | 0 | 0 | 0 | 390 | 300 | 71 | 0 | 40 | 250 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 12 | 33 | 0 | 8 | 0 | 66 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 0 | 45 | 0 | 13 | 0 | 0 | 0 | 330 | 325 | 213 | 8 | 135 | 33 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 94 | 191 | 0 | 17 | 0 | 43 | 29 | 45 | 47 | 110 | 0 | 40 | 78 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 30 | 0 | 0 | 170 | 0 | 69 | 2 | 60 | 68 | 132 | 386 | 4 | 17 | 105 | 1 | 15 | 35 | 68 | 0 | 28 | 60 | 370 | 73 | 14 | 17 | 90 | 0 | 17 | 0 | 101 | 30 | 0 | 926 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 184 | 0 | 340 | 0 | 0 | 94 | 0 | 66 | 0 | 0 | 113 | 360 | 182 | 0 | 17 | 0 | 33 | 34 | 0 |  |  |  |  | 55156148 |  | 0
55156148
| Minimum Generation |  | 8424 | 6:00
| Highest Generation |  | 11850 | 21:00
| Day Peak Generation |  | 9978 | 12:00
| Evening Peak Generation |  | 11850 | 21:00
| HVDC Max Flow |  | 925 | 16:00
| HVDC EvPeak Flow |  | 924 | 21:00
| Load factor L.F |  | 83.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-19
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9978 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9042 | MW
Evening Peak Generation : |  | 11850 | MW Hour : | 21:00 | Available Max Generation : |  | 14916 | MW
E.P. Demand (at gen end) : |  | 11850 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 11850 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1916 | MW
Total Gen. (MKWH) : |  | 236.859 | System Load Factor : | 83.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -320 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-19
Actual : | 76.89 | Ft.(MSL) , | Rule curve : | 80.76 | Ft.( MSL )
Gas Consumed : | Total = | 1052.95 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163139169.974
: |  | Coal : | 121232886 | Oil : | 710182635.18 | Total : | 994554691.154
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4580.5101 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1226.8154 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1618.1785 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1448.8282 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1284.5861 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 946.102 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 522.7262 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 346.2548 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 721.86 |  |  | 0 | 0%
Total | 0 |  | 12695.8614 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 08:15 to 16:41 for C/M.
b) Jamalpur 132/33 kV T-2 transformer was under shut down from 08:28 to 14:36 for C/M.
c) Rampura-Bashundhara 132 kV Ckt-1 tripped at 09:25 from both ends showing Dist.Z1, B-φ at Rampura
end & Dist. Z1, main protection trip at Bashundhara end and was switched on at 09:34.
d) Gollamari 132/33 kV T-2 transformer tripped at 09:24 due to 33 kV Potherbazar(WZPDCL) feeder fault | [5 empty] | About 26 MW power interruption occurred under
and was switched on at 09:45. | [5 empty] | Gollamari S/S area from 09:24 to 09:45.
e) Jashore-Noapara 132 kV Ckt-1 was under shut down from 10:32 to 12:12 due to R/H maintenance.
f) Matarbari 132/33 kV T-1 transformer was under shutdown from 11:15 to 15:45 due to relay change.
g) 33 kV Side of Bhandaria 132/33 kV T-1 & T-2 transformers tripped at 09:58 showing O/C, E/F and were | [5 empty] | About 28 MW power interruption occurred under
switched on at 10:12. | [5 empty] | Bhandaria S/S area from 09:58 to 10:12.
h) Kabirpur 132/33 kV T-1 transformer was under shutdown from 09:12 to 21:14 due to 33 kV Y-φ CT
Oil leakage.
i) Madaripur 132/33 kV T-3 transformer tripped at 12:12 due to 33 kV Takerhat(PBS) feeder fault and was | [5 empty] | About 3 MW power interruption occurred under
switched on at 12:33. | [5 empty] | Matarbari S/S area from 12:12 to 12:33.
j) Barishal(N)-Bhola 230 kV Ckt-1 tripped at 13:52 from Barishal(N) end showing Dist.Z1 and was switched
on at 14:39.
k) Sylhet-Fenchuganj S/S 132 Ckt was opened at 10:34 from Sylhet end for flood level high.
l) Mymensingh-Kishoreganj 132 kV Ckt-2 tripped at 15:39 from both ends showing Dist.Z1 at Mymensingh
end & Dist. Z2, A-φ at Kishoreganj end and was switched on at 15:45.
m) Hathazari-Kaptai 132 kV Ckt-1 & Ckt-2 tripped at 14:48 from both ends showing Dist.Z2, R-φ(Ckt-1) &
Dist. Z3, Z4, 3-φ(Ckt-2) at Hathazari end & Dist. Z1, R-φ at Kaptai end and were switched on at 14:56.
n) Siddhirganj 335 MW ST tripped at 14:57 due to Valve problem and was synchronized at 20:40.
o) Gollamari 132/33 kV T-1 transformer is under shut down since 06:12(19/06/2022) for D/W.
p) Mymensingh-Kishoreganj 132 kV Ckt-2 is under shut down since 07:41(19/06/2022) for C/M.
q) Ghorashal unit-7 tripped at 04:49(19/06/2022) showing GT Generator protection trip.
r) Bheramara 410 MW CCPP was shutdown at 05:09(19/06/2022) for filter change.
s) Sirajganj 132/33 kV T-4 transformer is under shut down since 07:20(19/06/2022) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6038809 | Condenser problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 90 | 1835818 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9054210
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 9028750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 88 | 1939200 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 245 | 6591215 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1145368
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 289440
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 100 | 695347
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 78 | 5587957 | ST start up process
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 549360 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1198440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 298080 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 825657
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 541613 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 960180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 703800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 0 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 410880 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 293 | 3246762
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 71 | 1389456 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1202400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1911360
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1605600
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 655920
| Dhaka area Total |  |  |  | 5847 | 3076 | 62052622
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 31384
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 38475
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 924960 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 99 | 1842484 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2535854
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 4 | 61440 | Low demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 5 | 95068 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 90 | 831840 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1848000 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508848
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 547200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 224640 | Reserve.
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 6602
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 908291 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1108190
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1933664 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2340480
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2192945 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1108 | 20380365
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4845000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7759500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 360 | 7001000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 248976 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 2 | 78720 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 66909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1099095
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 1895200 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 61616 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3231370 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 184 | 3228960 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 338040 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 161460 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2317440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 640800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 484260 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 57000 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1207920 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 8 | 189720 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 2260800 | Engine problem
| Cumilla Area Total |  |  |  | 2885 | 1876 | 37173786
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 179 | 4152960 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 429372
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10250
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 191 | 2930400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 668400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 123670
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 409920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 498 | 8724972
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1027000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 911576 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2743691 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 461400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 45 | 456984
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 14500
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1377888
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1665600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1186970 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6988500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9251000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 382 | 8054700
| Sylhet Area Total |  |  |  | 2477 | 1488 | 34139809
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 924 | 19248727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 79 | 1451520 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5901120 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 232500 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 832800 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 97632 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 224640
| Khulna Area Total |  |  |  | 2384 | 1340 | 27988939
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 89184 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 25 | 471195 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2071926 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 10944000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4673809
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 93600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 916 | 18343714
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 123517 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 36884 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 65942 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 250935 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 137 | 3502473
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 166 | 4256155 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8589454
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 217883 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 471600
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 126162
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 22080 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 52 | 282096 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1481568
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1663488
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19680
| Rajshahi Area Total |  |  |  | 2129 | 1178 | 21109917
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4277400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 87 | 1206816 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 15140
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1445568 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 370 | 6944924
| Total |  |  |  | 21396 | 11850 | 236859048
| Eastern Grid Total |  |  |  | 14205 | 8046 | 162471554
| Western Grid Total |  |  |  | 7191 | 3804 | 74387494
| National Grid Total |  |  |  | 21396 | 11850 | 236859048
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-18
(a) ENTIRE EASTERN GRID : |  | 7639.73 | MW | (b) ENTIRE WESTERN GRID : |  | 3927.6 | MW
i) Dhaka area |  | 4288.03 | MW | i) Khulna area |  | 1540 | MW
ii) Chittagong area |  | 1167.7 | MW | ii) Rajshahi area |  | 1303.6 | MW
iii) Comilla area |  | 1049 | MW | iii) Barisal area |  | 370 | MW
iv) Mymensingh area |  | 904 | MW | iv) Rangpur area |  | 714 | MW
v) Sylhet area |  | 231 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11567.33 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 28 | 12:00 | Hasnabad | 70 | 11:00 | Palashbari | 120 | 21:00
Agargaon | 79 | 13:00 | Hathazari | 85 | 20:00 | Panchagarh | 55 | 19:30
Agrabad | 72 | 13:00 | Ishurdi | 77 | 22:00 | Patuakhali | 112 | 22:00
AKS | 12 | 15:00 | Jaldhaka | 63 | 20:00 | PHP | 8 | 00:00
AKSML | 129 | 22:00 | Jamalpur | 136 | 22:00 | Purbachal | 17 | 12:00
Amnura | 48 | 22:00 | Jashore | 121 | 19:30 | Purbasadipur | 128 | 21:00
Ashuganj | 48 | 19:30 | Jhenaidah | 109 | 19:30 | Rahim | 29 | 20:00
Bagerhat | 101 | 21:00 | Joydebpur | 175 | 12:00 | Rajbari | 58 | 21:00
Bakulia | 108 | 19:30 | Joypurhat | 61 | 23:00 | Rajendrapur | 106 | 12:00
Banani | 37 | 12:00 | Juldah | 20 | 13:00 | Rajshahi | 136 | 19:30
Bangabhaban | 10 | 11:00 | Kabirpur | 225 | 12:00 | Rajshahi | 38 | 20:00
Barapukuria | 51 | 21:00 | Kachua | 62 | 22:00 | Ramganj | 96 | 20:00
Barguna | 20 | 00:00 | Kallyanpur | 96 | 13:00 | Rampur | 20 | 19:30
Barishal | 110 | 21:00 | Kalurghat | 6 | 10:00 | Rangamati | 34 | 06:00
Barishal | 46 | 23:00 | Kamrangirchar | 68 | 12:00 | Rangpur | 146 | 20:00
Baroaulia | 61 | 13:00 | Kaptai | 4 | 20:00 | Ruppur | 3.4 | 10:00
Baroirhat | 57 | 21:00 | Kazla | 82 | 13:00 | Saidpur | 106 | 22:00
Bashundhara | 162 | 13:00 | Keranigonj | 56 | 10:00 | Satkhira | 112 | 00:00
BashundharaCement | 1 | 07:00 | Khagrachori | 24 | 21:00 | Satmasjid | 85 | 14:00
Beanibazar | 36 | 21:00 | Khulna | 100 | 20:00 | Savar | 185 | 12:00
Benapole | 62 | 21:00 | Khulshi | 162 | 16:00 | Shahjadpur | 86 | 19:30
Bhaluka | 130 | 21:00 | Kishoreganj | 114 | 21:00 | Shahjibazar | 95 | 22:00
Bhandaria | 52 | 00:00 | Kodda | 303 | 12:00 | Shahmirpur | 41.5 | 21:00
Bhangura | 30 | 19:30 | KSRM | 34.3 | 16:00 | Shariatpur | 64 | 21:00
Bheramara(GK) | 53 | 22:00 | Kulaura | 24 | 00:00 | Sherpur | 118 | 21:00
Bhulta | 244 | 23:00 | Kurigram | 48 | 19:30 | Shikalbaha | 20 | 03:00
Bog-Sherpur | 60 | 21:00 | Kushtia | 130 | 21:00 | Shitalakhya | 113 | 12:00
Bogura | 154 | 22:00 | Lalbag | 86 | 13:00 | Sholosohor | N/A | N/A
Borhanuddin | 41 | 22:00 | Lalmonirhat | 43 | 20:00 | Shyampur | 168 | 10:00
Brahmanbaria | 120 | 22:00 | Madanganj | 91 | 23:00 | Siddhirganj | 102 | 22:00
BSRM | 160 | 07:00 | Madaripur | 91 | 21:00 | Sirajganj | 97 | 21:00
Cantonment | 136 | 13:00 | Madartek | 68 | 23:00 | Sonargaon | 82 | 20:00
Chandpur | 56 | 00:00 | Madunaghat | 55 | 17:00 | Sreemongol | 35 | 20:00
Chandraghona | 28 | 20:00 | Magura | 54 | 19:30 | Srinagar | 37.83 | 21:00
Chapai | 64 | 21:00 | Mahasthangarh | 66 | 23:00 | SSM | 4 | 01:00
Charsaidpur | 40 | 09:00 | Manikganj | 71 | 22:00 | Sunamganj | N/A | N/A
Chauddagram | 44 | 23:00 | Maniknagar | 65 | 12:00 | Sylhet | 49 | 00:00
Chhatak | N/A | N/A | Matarbari | 35 | 19:30 | Tangail | 163 | 22:00
Chowmuhani | 194 | 23:00 | Matuail | 60 | 12:00 | Thakurgaon | 96 | 20:00
Chuadanga | 95 | 19:30 | Millgate | 58 | 12:00 | TK | 25 | 22:00
Coxsbazar | 107 | 20:00 | Mirpur | 121 | 13:00 | Tongi | 112 | 13:00
Cumilla(N) | 128 | 23:00 | Mirsorai | N/A | N/A | Ullon | 32 | 21:00
Cumilla(S) | 140 | 19:00 | Mithapukur | 32 | 19:30 | Uttara | 90 | 12:00
Daudkandi | 128 | 23:00 | Modern | 0 | 00:00 | UttaraNew | 14 | 12:00
Dhaka | 34 | 12:00 | Mogbazar | 114 | 12:00 | Zigatola | 39 | 12:00
Dhamrai | 102 | 21:00 | Mongla | 38 | 10:00
Dhanmondi | 127 | 12:00 | Motijheel | 35 | 13:00
Dohazari | 80 | 19:00 | Munshiganj | 88 | 21:00
Faridpur | 130 | 20:00 | Mymensingh | 176 | 20:00
Fatullah | 66 | 12:00 | Naogaon | 110 | 21:00
Fenchuganj | 32 | 21:00 | Narail | 52 | 21:00
Feni | 94 | 19:30 | Narinda | 65 | 12:00
Ghorashal | 49 | 21:00 | Narshingdi | 154 | 23:00
Goalpara | 26 | 00:00 | Natore | 140 | 22:00
Gollamari | 48 | 00:00 | Nawabganj | 46.7 | 22:00
Gopalganj | 91.8 | 20:00 | Netrakona | 80 | 21:00
GPH | 87 | 11:00 | New | 82.3 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bhulta | 402 | 17:00 | 387 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bibiana | 416 | 16:00 | 404 | 10:00 | Payra | 425 | 17:00 | 417 | 22:00
| BIPTC | 403 | 17:00 | 394 | 00:00
| Gopalganj_I | 419 | 09:00 | 403 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 17:00 | 219 | 12:00 | Hathazari | 236 | 15:00 | 217 | 10:00
| AKSML | 237 | 14:00 | 212 | 10:00 | Ishurdi | 238 | 17:00 | 226 | 23:00
| Aminbazar | 231 | 16:00 | 222 | 00:00 | Jhenaidah | 235 | 18:00 | 213 | 23:00
| Baghabari | 235 | 18:00 | 226 | 22:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Barapukuria | 232 | 05:00 | 219 | 00:00 | Keranigonj | 230 | 19:30 | 219 | 12:00
| Barishal | 243 | 09:00 | 235 | 00:00 | Khulna(S) | 237 | 18:00 | 213 | 23:00
| Bheramara | 235 | 05:00 | 223 | 23:00 | Maniknagar | 231 | 19:30 | 224 | 12:00
| Bhulta | 234 | 17:00 | 227 | 18:30 | Meghnaghat | 232 | 17:00 | 226 | 00:00
| Bibiana | 244 | 17:00 | 235 | 05:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 238 | 17:00 | 222 | 23:00 | Rajshahi | 238 | 18:30 | 223 | 23:00
| Bogura | 235 | 17:00 | 222 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 10:00 | 239 | 23:00 | Rampura | 232 | 17:00 | 224 | 12:00
| BSRM | 236 | 14:00 | 218 | 10:00 | Shikalbaha | 237 | 01:00 | 216 | 11:00
| Cumilla(N) | 233 | 15:00 | 223 | 11:00 | Shyampur | 229 | 15:00 | 221 | 12:00
| Fenchuganj | 248 | 15:00 | 239 | 23:00 | Siddhirganj | 233 | 15:00 | 226 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 17:00 | 227 | 23:00
| GPH | 238 | 14:00 | 217 | 11:00 | Tongi | 235 | 16:00 | 220 | 11:00
| Haripur | 231 | 17:00 | 222 | 12:00
| Hasnabad | 230 | 15:00 | 222 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 03:00 | 129 | 10:00 | Manikganj | 131 | 14:00 | 124 | 08:00
| Agargaon | 136 | 04:00 | 129 | 11:00 | Maniknagar | 136 | 04:00 | 128 | 17:00
| Agrabad | 139 | 19:30 | 130 | 10:00 | Matarbari | 134 | 01:00 | 116 | 00:00
| AKS | 139 | 20:00 | 128 | 18:00 | Matuail | 134.4 | 13:00 | 127 | 15:00
| Aminbazar | 134 | 00:00 | 128 | 10:00 | Millgate | 135 | 03:00 | 128 | 11:00
| Amnura | 133 | 18:30 | 122 | 16:00 | Mirpur | 132 | 06:00 | 123 | 10:00
| Ashuganj | 140 | 14:00 | 135 | 20:00 | Mithapukur | 133 | 18:30 | 123 | 20:00
| Bagerhat | 137 | 11:00 | 122 | 01:00 | Modern | 140 | 19:00 | 132 | 15:00
| Bakulia | 140 | 19:30 | 130 | 18:00 | Mogbazar | 137 | 06:00 | 130 | 10:00
| Banani | 136 | 07:00 | 128 | 10:00 | Mongla | 137 | 09:00 | 121 | 18:00
| Bangabhaban | 136 | 04:00 | 129 | 11:00 | Motijheel | 136 | 04:00 | 129 | 11:00
| Barapukuria | 135 | 05:00 | 126 | 19:30 | Munshiganj | 136 | 13:00 | 129 | 16:00
| Barguna | 141 | 10:00 | 130 | 22:00 | Mymensingh | 136 | 09:00 | 127 | 06:00
| Barishal | 140 | 11:00 | 130 | 23:00 | Naogaon | 133 | 07:00 | 121 | 15:00
| Barishal | 141 | 09:00 | 132 | 00:00 | Narail | 135 | 09:00 | 121 | 20:00
| Baroaulia | 140 | 20:00 | 130 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 136 | 13:00 | 127 | 00:00 | Narshingdi | 136 | 14:00 | 123 | 11:00
| Bashundhara | 136 | 05:00 | 127 | 10:00 | Natore | 133 | 09:00 | 126 | 16:00
| BashundharaCement | 136 | 13:00 | 129 | 16:00 | Nawabganj | 138 | 04:00 | 130 | 10:00
| Beanibazar | 140 | 13:00 | 135 | 19:00 | Netrakona | 135 | 10:00 | 125 | 22:00
| Benapole | 137 | 09:00 | 120 | 19:30 | New | 136 | 13:00 | 128 | 10:00
| Bhaluka | 134 | 09:00 | 123 | 18:00 | Niamatpur | 131 | 09:00 | 119 | 15:00
| Bhandaria | 144 | 10:00 | 126 | 21:00 | Noapara | 139 | 09:00 | 124 | 18:00
| Bhangura | 139 | 04:00 | 133 | 16:00 | Pabna | 136 | 04:00 | 130 | 15:00
| Bheramara | 137 | 04:00 | 131 | 19:30 | Palashbari | 131 | 07:00 | 121 | 19:30
| Bheramara(GK) | 137 | 07:00 | 134 | 00:00 | Panchagarh | 134 | 21:00 | 118 | 14:00
| Bhulta | 126 | 13:00 | 120 | 16:00 | Patuakhali | 137 | 07:00 | 131 | 23:00
| Bog-Sherpur | 135 | 07:00 | 127 | 15:00 | PHP | 135 | 13:00 | 127 | 00:00
| Bogura | 135 | 06:00 | 128 | 15:00 | Purbachal | 136 | 03:00 | 128 | 11:00
| Bogura | 136 | 09:00 | 128 | 15:00 | Purbasadipur | 134 | 17:00 | 120 | 15:00
| Brahmanbaria | 136 | 14:00 | 129 | 23:00 | Rahim | 135 | 05:00 | 129 | 10:00
| Cantonment | 135 | 04:00 | 127 | 17:00 | Rajbari | 136 | 13:00 | 126 | 23:00
| Chandpur | 138 | 18:30 | 134 | 00:00 | Rajendrapur | 133 | 14:00 | 121 | 09:00
| Chandraghona | 138 | 13:00 | 130 | 10:00 | Rajshahi | 131 | 18:30 | 122 | 22:00
| Chapai | 133 | 18:30 | 121 | 15:00 | Rajshahi | 131 | 18:30 | 122 | 16:00
| Charsaidpur | 135 | 03:00 | 129 | 16:00 | Ramganj | 136 | 13:00 | 129 | 00:00
| Chauddagram | 134 | 13:00 | 128 | 23:00 | Rampur | 138 | 19:30 | 132 | 11:00
| Chhatak | N/A | N/A | N/A | N/A | Rampura | 136 | 02:00 | 129 | 10:00
| Chowmuhani | 132 | 00:00 | 125 | 05:00 | Rangamati | 139 | 20:00 | 131 | 18:00
| Chuadanga | 132 | 09:00 | 116 | 19:30 | Rangpur | 130 | 07:00 | 120 | 19:30
| Coxsbazar | 128 | 15:00 | 115 | 00:00 | Ruppur | 137 | 05:00 | 131 | 19:30
| Cumilla(N) | 137 | 13:00 | 131 | 10:00 | Saidpur | 132 | 07:00 | 121 | 20:00
| Cumilla(S) | 136 | 13:00 | 126 | 20:00 | Satkhira | 137 | 08:00 | 122 | 19:30
| Daudkandi | 137 | 13:00 | 129 | 10:00 | Satmasjid | 135 | 01:00 | 129 | 10:00
| Dhaka | 137 | 04:00 | 129 | 11:00 | Savar | 132 | 13:00 | 124 | 10:00
| Dhamrai | 134 | 13:00 | 128 | 11:00 | Shahjadpur | 140 | 00:00 | 135 | 10:00
| Dhanmondi | 135 | 04:00 | 128 | 17:00 | Shahjibazar | 137 | 00:00 | 132 | 21:00
| Dohazari | 138 | 13:00 | 126 | 00:00 | Shahmirpur | 140 | 19:30 | 131 | 18:00
| Faridpur | 137 | 13:00 | 127 | 22:00 | Shariatpur | 140 | 12:00 | 127 | 23:00
| Fatullah | 135 | 06:00 | 128 | 10:00 | Sherpur | 137 | 12:00 | 124 | 05:00
| Fenchuganj | 140 | 08:00 | 137 | 02:00 | Shikalbaha | 141 | 20:00 | 132 | 16:00
| Feni | 135 | 13:00 | 127 | 23:00 | Shikalbaha | 139 | 19:30 | 132 | 00:00
| Ghorashal | 138 | 07:00 | 129 | 01:00 | Shitalakhya | 136 | 13:00 | 129 | 15:00
| Goalpara | 141 | 09:00 | 127 | 18:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gollamari | 140 | 13:00 | 126 | 22:00 | Shyampur | 132 | 03:00 | 129 | 10:00
| Gopalganj | 140 | 12:00 | 127 | 23:00 | Shyampur | 134 | 04:00 | 129 | 16:00
| Gopalganj_I | 142 | 12:00 | 130 | 23:00 | Siddhirganj | 134 | 02:00 | 128 | 10:00
| Gulshan | 135 | 04:00 | 128 | 11:00 | Sirajganj | 135 | 04:00 | 129 | 15:00
| Halishahar | 139 | 13:00 | 131 | 10:00 | Sonargaon | 136 | 02:00 | 129 | 11:00
| Haripur | 135 | 05:00 | 129 | 10:00 | Sreemongol | 140 | 06:00 | 135 | 22:00
| HaripurSBU | 135 | 04:00 | 130 | 10:00 | Srinagar | 137 | 04:00 | 130 | 10:00
| Hasnabad | 137 | 02:00 | 131 | 10:00 | SSM | 139 | 04:00 | 129 | 18:00
| Hathazari | 140 | 20:00 | 131 | 18:00 | Sunamganj | N/A | N/A | N/A | N/A
| Ishurdi | 137 | 04:00 | 131 | 15:00 | Sylhet | 137 | 03:00 | 134 | 23:00
| Jaldhaka | 131 | 07:00 | 117 | 20:00 | Tangail | 135 | 14:00 | 130 | 00:00
| Jamalpur | 139 | 18:30 | 126 | 05:00 | Thakurgaon | 135 | 21:00 | 118 | 14:00
| Jashore | 138 | 09:00 | 123 | 18:00 | TK | 140 | 19:30 | 130 | 18:00
| Jhenaidah | 135 | 09:00 | 124 | 19:30 | Tongi | 137 | 03:00 | 130 | 09:00
| Jhenaidah | 136 | 09:00 | 124 | 19:30 | Ullon | 135 | 01:00 | 128 | 11:00
| Joydebpur | 142 | 13:00 | 133 | 17:00 | Uttara | 132 | 22:00 | 123 | 10:00
| Joypurhat | 134 | 07:00 | 122 | 13:00 | UttaraNew | 133 | 00:00 | 125 | 18:00
| Juldah | 140 | 13:00 | 131 | 18:00 | Zigatola | 138 | 06:00 | 129 | 18:00
| Kabirpur | 134 | 14:00 | 125 | 11:00
| Kachua | 137 | 13:00 | 131 | 10:00
| Kaliakoir | N/A | N/A | N/A | N/A
| Kallyanpur | 132 | 03:00 | 126 | 10:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 278 | 7810 | 3620 | 11430 |  |  |  | QF-LDC-11
0:30 | 275 | 7155 | 3283.5 | 10438.5 | Date: | 2022-06-18
1:00 | 272 | 6500 | 2947 | 9447
1:30 | 254 | 6422.5 | 2936 | 9358.5
2:00 | 236 | 6345 | 2925 | 9270
2:30 | 236 | 6247.5 | 2882.5 | 9130 | [5 empty] | Gen. at Eve. Peak | 11850 | 11850 MW (21:00 )
3:00 | 236 | 6150 | 2840 | 8990 | [6 empty] | 21:00
3:30 | 218 | 6128 | 2806.5 | 8934.5 | [5 empty] | Gen. at Day Peak | 9978 | 9978 MW (12:00 )
4:00 | 200 | 6106 | 2773 | 8879 | [6 empty] | 12:00
4:30 | 132 | 5941.5 | 2818 | 8759.5 | [5 empty] | Highest Generation | 11850
5:00 | 64 | 5777 | 2863 | 8640 | [6 empty] | 21:00
5:30 | 54 | 5728.5 | 2803.5 | 8532
6:00 | 44 | 5680 | 2744 | 8424
6:30 | 23 | 5691.5 | 2781.5 | 8473
7:00 | 2 | 5703 | 2819 | 8522
7:30 | 11 | 5935.5 | 2749.5 | 8685
8:00 | 20 | 6168 | 2680 | 8848
8:30 | 67 | 6323.5 | 2658 | 8981.5
9:00 | 114 | 6479 | 2636 | 9115
9:30 | 192 | 6471 | 2677 | 9148
10:00 | 270 | 6463 | 2718 | 9181
10:30 | 313 | 6585 | 2791.5 | 9376.5
11:00 | 356 | 6707 | 2865 | 9572
11:30 | 302 | 6921.5 | 2853.5 | 9775
12:00 | 248 | 7136 | 2842 | 9978
12:30 | 169 | 6987.5 | 2735.5 | 9723
13:00 | 90 | 6839 | 2629 | 9468
13:30 | 97 | 6508 | 2572.5 | 9080.5
14:00 | 104 | 6177 | 2516 | 8693
14:30 | 101 | 6234 | 2602.5 | 8836.5
15:00 | 98 | 6291 | 2689 | 8980
15:30 | 115 | 6321 | 2751.5 | 9072.5
16:00 | 132 | 6351 | 2814 | 9165
16:30 | 139 | 6354.5 | 2852.5 | 9207
17:00 | 146 | 6358 | 2891 | 9249
17:30 | 182 | 6362 | 2912 | 9274
18:00 | 218 | 6366 | 2933 | 9299
18:30 | 119 | 6675.5 | 3080 | 9755.5
19:00 | 20 | 6985 | 3227 | 10212
19:30 | 44 | 7970 | 3744 | 11714
20:00 | 40 | 8084 | 3756 | 11840 |  |  |  | Executive Engineer
20:30 | 180 | 8065 | 3780 | 11845 |  |  |  | Network Operation Division
21:00 | 320 | 8046 | 3804 | 11850
21:30 | 308 | 8052 | 3771.5 | 11823.5
22:00 | 296 | 8058 | 3739 | 11797 |  |  |  |  | Page 6 of 7
22:30 | 306 | 7972 | 3685.5 | 11657.5
23:00 | 316 | 7886 | 3632 | 11518
23:30 | 297 | 7848 | 3626 | 11474
24:00 | 278 | 7810 | 3620 | 11430
11850 MW (21:00 )
9978 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-18 |  | Energy |  | 236859048
[13 empty] | 2022-06-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4236 | 925 | 2133 | 0 | 3104 | 735 | 100 | 0 | 91 | 106 | 0 | 0
0:30 | 4286 | 782.5 | 2052.5 | 0 | 2429 | 660 | 83 | 0 | 45.5 | 100 | 0 | 0 | Date: | 2022-06-18
1:00 | 4336 | 640 | 1972 | 0 | 1754 | 585 | 66 | 0 | 0 | 94 | 0 | 0
1:30 | 4338.5 | 640 | 1971.5 | 0 | 1666.5 | 585 | 66 | 0 | 0 | 91 | 0 | 0 | [8 empty] | Total Energy | 236.859 | Total Energy Gen 236.859 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.859 MKWHr
2:00 | 4341 | 640 | 1971 | 0 | 1579 | 585 | 66 | 0 | 0 | 88 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4274 | 640 | 1971 | 0 | 1508 | 585 | 66 | 0 | 0 | 86 | 0 | 0 | [8 empty] | Energy Requirement | 236.859
3:00 | 4207 | 640 | 1971 | 0 | 1437 | 585 | 66 | 0 | 0 | 84 | 0 | 0
3:30 | 4200 | 640 | 1947 | 0 | 1395.5 | 600 | 66 | 0 | 0 | 86 | 0 | 0 | [6 empty] | Shortage
4:00 | 4193 | 640 | 1923 | 0 | 1354 | 615 | 66 | 0 | 0 | 88 | 0 | 0
4:30 | 4062 | 640 | 1964 | 0 | 1307.5 | 635 | 66 | 0 | 0 | 85 | 0 | 0
5:00 | 3931 | 640 | 2005 | 0 | 1261 | 655 | 66 | 0 | 0 | 82 | 0 | 0
5:30 | 3919 | 640 | 1944 | 0 | 1202 | 680 | 66 | 0 | 0 | 80 | 1 | 0
6:00 | 3907 | 640 | 1883 | 0 | 1143 | 705 | 66 | 0 | 0 | 78 | 2 | 0
6:30 | 3920.5 | 640 | 1913 | 0 | 1147 | 700 | 66 | 0 | 0 | 79 | 7.5 | 0 |  |  |  |  | Coal
7:00 | 3934 | 640 | 1943 | 0 | 1151 | 695 | 66 | 0 | 0 | 80 | 13 | 0
7:30 | 3985 | 640 | 1914.5 | 0 | 1302 | 665 | 66 | 0 | 0 | 86 | 26.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4036 | 640 | 1886 | 0 | 1453 | 635 | 66 | 0 | 0 | 92 | 40 | 0
8:30 | 4044.5 | 640 | 1874 | 0 | 1607.5 | 610 | 66 | 0 | 8 | 95 | 36.5 | 0
9:00 | 4053 | 640 | 1862 | 0 | 1762 | 585 | 66 | 0 | 16 | 98 | 33 | 0
9:30 | 3997 | 735 | 1837 | 0 | 1802 | 555 | 66 | 0 | 16 | 98 | 42 | 0
10:00 | 3941 | 830 | 1812 | 0 | 1842 | 525 | 66 | 0 | 16 | 98 | 51 | 0
10:30 | 3845 | 830 | 1903.5 | 0 | 2020 | 515 | 83 | 0 | 32 | 101 | 47 | 0
11:00 | 3749 | 830 | 1995 | 0 | 2198 | 505 | 100 | 0 | 48 | 104 | 43 | 0
11:30 | 3814 | 830 | 1913 | 0 | 2420 | 500 | 100 | 0 | 48 | 104 | 46 | 0
12:00 | 3879 | 830 | 1831 | 0 | 2642 | 495 | 100 | 0 | 48 | 104 | 49 | 0
12:30 | 3784 | 830 | 1715.5 | 0 | 2639.5 | 470 | 100 | 0 | 43 | 100 | 41 | 0
13:00 | 3689 | 830 | 1600 | 0 | 2637 | 445 | 100 | 0 | 38 | 96 | 33 | 0
13:30 | 3689 | 830 | 1600 | 0 | 2637 | 445 | 100 | 0 | 38 | 96 | 33 | 0
14:00 | 3689 | 830 | 1600 | 0 | 2637 | 445 | 100 | 0 | 38 | 96 | 33 | 0
14:30 | 3714 | 859.5 | 1668.5 | 0 | 2277 | 435 | 100 | 0 | 35 | 99 | 36 | 0
15:00 | 3739 | 889 | 1737 | 0 | 1917 | 425 | 100 | 0 | 32 | 102 | 39 | 0
15:30 | 3788.5 | 907 | 1719.5 | 0 | 1946 | 445 | 98.5 | 0 | 33 | 103 | 32 | 0
16:00 | 3838 | 925 | 1702 | 0 | 1975 | 465 | 97 | 0 | 34 | 104 | 25 | 0
16:30 | 3800 | 924.5 | 1761 | 0 | 2000 | 465 | 78.5 | 0 | 35 | 102 | 22 | 0
17:00 | 3800 | 924 | 1820 | 0 | 2025 | 465 | 60 | 0 | 36 | 100 | 19 | 0
17:30 | 3820.5 | 924.5 | 1819 | 0 | 1997.5 | 465 | 60 | 0 | 76.5 | 100 | 11 | 0
18:00 | 3841 | 925 | 1818 | 0 | 1970 | 465 | 60 | 0 | 117 | 100 | 3 | 0
18:30 | 3806.5 | 925 | 1808 | 0 | 2341.5 | 505 | 60 | 0 | 201 | 107 | 1.5 | 0
19:00 | 3772 | 925 | 1798 | 0 | 2713 | 545 | 60 | 0 | 285 | 114 | 0 | 0
19:30 | 3892 | 924 | 2074 | 0 | 3668 | 665 | 60 | 0 | 323 | 108 | 0 | 0
20:00 | 3955 | 924 | 2050 | 0 | 3741 | 675 | 60 | 0 | 327 | 108 | 0 | 0
20:30 | 4001.5 | 924 | 2051.5 | 0 | 3723.5 | 700 | 79.5 | 0 | 256 | 109 | 0 | 0
21:00 | 4048 | 924 | 2053 | 0 | 3706 | 725 | 99 | 0 | 185 | 110 | 0 | 0
21:30 | 4142.5 | 924 | 2052 | 0 | 3583 | 740.5 | 99 | 0 | 172.5 | 110 | 0 | 0
22:00 | 4237 | 924 | 2051 | 0 | 3460 | 756 | 99 | 0 | 160 | 110 | 0 | 0
22:30 | 4235.5 | 924 | 2044.5 | 0 | 3365 | 755.5 | 99.5 | 0 | 125.5 | 108 | 0 | 0
23:00 | 4234 | 924 | 2038 | 0 | 3270 | 755 | 100 | 0 | 91 | 106 | 0 | 0
23:30 | 4235 | 924.5 | 2085.5 | 0 | 3187 | 745 | 100 | 0 | 91 | 106 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.1° C
24:00 | 4236 | 925 | 2133 | 0 | 3104 | 735 | 100 | 0 | 91 | 106 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 236.859 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.859 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 70 | 70 | 70 | 70 | 70 | 67 | 30 | 30 |  | 30 | 30 | 30 | 69 | 69 | 70 | 70 | 1114484
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 3 | 15 | 21 | 0 |  |  |  | 31384
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 9 | 4 | 4 | 4 | 3 | 1 | 6 | 1 | 1 | 2 | 0 | [8 empty] | 38475
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 47 | 51 | 51 | 5 |  |  |  | 95068
12 | Hathazari 100 MW peaking PP | [17 empty] | 0 |  | 11 | 30 | 34 | 4 |  |  |  | 61440
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2535854
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [14 empty] | 0 | 2 | 8 | 8 |  | 18 | 33 | 33 | 0 |  |  |  | 61616
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 336 | 335 | 336 | 335 | 280 | 331 | 333 | 335 | 250 | 250 | 250 | 250 | 250 | 250 | 60 | 0 | 43 |  | 41 | 41 | 41 | 78 | 335 | 335 | 335 | 5587957
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 5 | 15 | 98 | 130 | 153 | 233 | 230 | 230 | 230 | 180 | 145 |  | 208 | 293 | 293 | 293 | 230 | 228 | 228 | 3246762
19 | Ashuganj 195MW PP (APSCL-United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 200 | 190 | 230 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6038809
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [7 empty] | 0 |  |  | 0 | 0 |  |  |  | 5 | 24 | 35 |  | 35 | 35 | 32 | 35 | 35 | 35 | 35 | 248976
33 | Ashuganj 225 MW CCPP | 193 | 207 | 213 | 214 | 214 | 214 | 179 | 173 | 161 | 178 | 115 | 202 | 216 | 214 | 212 | 214 | 216 | 215 |  | 214 | 215 | 216 | 216 | 217 | 216 | 214 | 4845000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 260 | 285 | 270 | 270 | 260 | 260 | 260 | 260 | 260 | 290 | 290 | 290 |  | 290 | 320 | 355 | 360 | 330 | 330 | 330 | 7001000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 360 | 360 | 305 | 300 | 300 | 270 | 270 | 270 | 270 | 300 | 360 | 360 | 300 |  | 300 | 300 | 330 | 360 | 300 | 300 | 300 | 7759500
35 | Ashuganj 55 MW PP (Precision) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2 | 20 | 20 | 30 | 78720
36 | Chandpur 150 MW CCPP | 135 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 136 | 136 | 136 | 136 | 136 | 135 | 135 | 135 | 135 | 136 |  | 135 | 135 | 135 | 135 | 135 | 136 | 137 | 3231370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 305 | 305 | 306 | 340 | 342 | 342 | 342 | 342 | 343 | 389 | 401 | 401 | 402 | 398 | 400 | 400 | 401 | 400 |  | 399 | 400 | 399 | 399 | 399 | 399 | 401 | 9054210
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 390 | 9028750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 196 | 193 | 195 | 196 | 194 | 195 | 192 | 192 | 192 | 173 | 162 | 154 | 152 | 151 | 150 | 158 | 156 | 176 |  | 176 | 167 | 176 | 179 | 178 | 178 | 186 | 4152960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 6 | 4 | 4 | 17 | 24 | 23 | 24 | 19 | 0 | 1 | 1 |  | 0 | [6 empty] | 123670
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1027000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 41 | 40 |  | 40 | 40 | 40 | 29 | 30 | 29 | 29 | 911576
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 65 | 66 | 52 | 64 | 63 | 63 | 40 | 62 | 41 | 40 | 40 | 61 | 65 | 40 | 63 |  | 40 | 63 | 65 | 62 | 62 | 62 | 64 | 1377888
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 78 | 78 | 79 | 79 | 81 | 81 | 81 | 0 |  | 0 | 78 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1665600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 90 | 90 | 90 | 90 | 90 | 0 | [15 empty] | 1186970
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 |  | 11 | 0 |  |  | 8 | 8 | 8 | 14500
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 50 | 53 | 53 | 53 | 53 | 53 | 461400
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 265 | 270 | 285 | 280 | 280 | 280 | 275 | 305 | 260 | 310 | 270 | 260 | 260 | 310 | 290 | 300 | 300 |  | 270 | 290 | 290 | 280 | 280 | 270 | 300 | 6988500
| Bibiyana South 400 MW | 400 | 400 | 278 | 260 | 15 | 60 | 80 | 320 | 400 | 401 | 401 | 400 | 350 | 340 | 340 | 400 | 400 | 400 |  | 360 | 400 | 400 | 382 | 401 | 401 | 400 | 8054700
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 |  |  |  |  | 5 | 17 | 35 | 35 | 55 | 35 | 0 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 541613
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 |  |  |  |  | 10 | 20 | 18 | 19 | 22 | 22 | 22 | 22 | 21 | 22 | 22 |  | 22 | 22 | 19 | 11 | 20 | 23 | 22 | 409920
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508848
61 | Narshingdi 22 MW PP (Doreen) | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 289440
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 429372
63 | Impoprt (Tripura) | 94 | 88 | 84 | 88 | 82 | 78 | 80 | 92 | 98 | 98 | 104 | 104 | 96 | 110 | 102 | 104 | 100 | 100 |  | 114 | 108 | 108 | 110 | 110 | 106 | 106 | 2317440
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 41 | 35 | 13 | 2 | 6 | 6 | 6 | 8 | 10 | 6 | 6 | 10 | 10 |  | 20 | 24 | 17 | 22 | 27 | 27 | 38 | 547200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 5 | 0 | [7 empty] | 19 | 20 | 21 | 21 | 338040
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 161460
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 16 | 16 | 16 | 16 | 25 | 33 | 30 |  | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 640800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 17 | 11 | 17 | 17 | 11 | 11 | 18 | 16 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 484260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 16 | 16 | 11 | 0 | 0 | 0 | 18 | 8 | 8 |  | 11 | 12 | 12 | 17 | 18 | 18 | 18 | 360180
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 703800
72 | Rupganj 33 MW PP(Summit)
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 95 | 95 | 91 | 89 | 89 | 89 | 45 | 22 | 22 | 22 | 22 | 44 |  | 70 | 83 | 80 | 90 | 92 | 85 | 85 | 1835818
| Feni Lanka Power | [20 empty] | 17 | 17 | 17 | 17 |  |  | 57000
| Chowmuhani 113 MW | 41 | 28 | 29 | 29 | 28 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 46 | 95 | 96 |  | 95 | 96 | 96 | 96 | 94 | 96 | 40 | 1207920
| Manikgonj 162MW PP(MPGL) | [7 empty] | 17 | 17 | 17 | 70 | 144 | 162 | 72 | 72 | 72 | 35 | 35 |  | 115 | 162 | 162 | 162 | 162 | 108 | 72 | 1605600
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 6 | 8 | 8 | 23 | 70 | 80 | 29 | 16 | 16 | 16 | 16 |  | 39 | 80 | 93 | 100 | 64 | 50 | 50 | 695347
78 | Gazipur 52 MW PP | [8 empty] | 9 | 16 | 20 | 42 | 48 | 16 | 16 | 16 | 16 | 16 |  | 16 | 40 | 50 | 50 | 24 | 24 | 24 | 410880
79 | Kodda 150MW PP | [8 empty] | 16 | 16 | 48 | 48 | 32 | 16 | 16 | 16 | 0 |  |  | 48 | 48 | 48 | 16 |  |  |  | 298080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [7 empty] | 0 | 25 | 35 | 42 | 64 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 1202400
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | [9 empty] | 6602
| Jodiac Power | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 50 | 54 | 17 | 17 | 19 | 52 | 35 | 35 | 35 | 35 | 35 |  | 40 | 46 | 54 | 54 | 54 | 54 | 54 | 1108190
| Karnaphuli Power Ltd. | 96 | 92 | 92 | 85 | 92 | 68 | 68 | 86 | 92 | 51 | 55 | 71 | 81 | 51 | 51 | 51 | 51 | 51 |  | 59 | 73 | 77 | 92 | 92 | 92 | 100 | 1933664
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 255 | 260 | 265 | 255 | 275 | 260 | 275 | 290 | 250 | 305 | 305 | 300 | 235 | 280 | 295 | 255 | 280 | 269 |  | 305 | 285 | 250 | 245 | 265 | 262 | 250 | 6591215
87 | Meghnaghat 100 MW(IEL) | 78 | 79 | 79 | 78 | 79 | 79 | 77 | 75 | 77 | 79 | 77 | 80 | 78 | 77 | 74 | 73 | 79 | 86 |  | 87 | 87 | 88 | 88 | 86 | 86 | 85 | 1939200
| Meghnaghat 104 MW PP (OPCL) | 92 | 92 | 92 | 92 | 72 | 72 | 72 | 87 | 91 | 91 | 79 | 72 | 69 | 60 | 35 | 35 | 35 | 35 |  | 60 | 88 | 88 | 104 | 104 | 104 | 104 | 1911360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 0 |  |  |  | 10 | 10 | 50 | 10 | 40 | 90 | 90 | 10 | 10 | 10 | 10 | 10 |  | 10 | 80 | 90 | 90 | 90 | 90 | 90 | 831840
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 38 | 45 | 47 | 50 | 50 | 456984
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 50 | 50 | 50 | 50 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1099095
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 7 | 32 | 32 | 32 | 32 | 32 | 7 | 7 | 7 | 7 | 7 |  | 64 | 84 | 94 | 94 | 48 | 24 | 7 | 549360
95 | Patenga 50MW PP (Baraka) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 13 | 28 | 38 | 37 | 38 | 0 | 0 | 21 | 40 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 924960
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | 29 | 52 | 20 | 22 | 23 | 0 |  |  | 13 | 45 | 51 | 0 |  |  |  | 224640
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1145368
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | [5 empty] | 17 | 17 | 17 | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 825657
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2743691
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 10250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1198440
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 145 | 110 | 80 | 45 | 24 | 24 | 24 | 80 | 98 | 100 | 115 | 170 | 130 | 103 | 130 | 130 | 130 | 80 |  | 118 | 191 | 191 | 191 | 193 | 192 | 193 | 2930400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 28 | 16 | 15 | 0 |  |  | 20 | 36 | 83 | 81 | 90 | 106 | 95 | 70 | 71 | 70 | 58 |  | 58 | 70 | 70 | 71 | 88 | 92 | 97 | 1389456
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 90 | 90 | 30 | 63 | 90 | 90 | 50 | 50 | 50 | 50 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1848000
116 | Chandpur 200MW (Desh energy) | 155 | 155 | 155 | 155 | 120 | 100 | 85 | 91 | 136 | 155 | 155 | 100 | 74 | 85 | 85 | 85 | 85 | 85 |  | 131 | 175 | 179 | 184 | 200 | 200 | 200 | 3228960
117 | Ashuganj 150MW PP (Midland) | 80 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 50 | 81 | 110 | 127 | 90 | 90 | 90 | 90 | 90 |  | 105 | 133 | 130 | 137 | 140 | 138 | 138 | 1895200
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 351 | 355 | 354 | 352 | 400 | 354 | 353 | 369 | 400 | 400 | 400 |  | 371 | 400 | 400 | 400 | 400 | 400 | 401 | 9251000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 8 | 20 | 32 | 45 | 45 | 16 | 16 | 16 | 16 | 8 | 8 |  | 20 | 103 | 95 | 97 | 55 | 55 | 55 | 668400
| Anwara 300 MW PP (United) | [10 empty] | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 |  | 50 | 170 | 186 | 190 | 135 | 80 | 50 | 908291
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 81 | 93 | 90 | 90 | 90 | 92 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2340480
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 68 | 79 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 105 | 108 | 108 | 2192945
| Bhairob 54.5 MW | [7 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 0 | [7 empty] | 0 | 8 | 17 | 17 | 17 | 189720
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 100 | 101 | 100 | 91 | 101 | 100 | 96 | 97 | 92 | 101 | 90 | 89 | 90 | 79 | 76 | 89 | 100 | 101 |  | 101 | 101 | 98 | 76 | 77 | 100 | 100 | 2260800
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 |  | 6 | 17 | 28 | 55 | 55 | 47 | 0 |  |  |  | 15 | 47 |  | 55 | 55 | 55 | 55 | 48 | 30 | 30 | 655920
120 | Eastern Zone Total | 6500 | 6345 | 6150 | 6106 | 5777 | 5680 | 5703 | 6168 | 6479 | 6463 | 6707 | 7136 | 6839 | 6177 | 6291 | 6351 | 6358 | 6366 |  | 6985 | 7970 | 8084 | 8046 | 8058 | 7886 | 7810 | 162471554
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 55 | 60 | 63 | 65 | 65 | 65 | 64 | 46 | 61 | 47 | 47 | 47 | 49 | 49 | 49 | 49 | 49 | 53 |  | 85 | 85 | 79 | 79 | 79 | 95 | 96 | 1451520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 13 | 17 | 17 | 28 | 70 | 35 | 35 | 35 | 35 | 17 | 17 |  | 35 | 90 | 90 | 90 | 93 | 53 | 35 | 832800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 10 | 25 | 24 | 39 | 20 | 14 | 4 | 7 | 15 | 21 | 14 | 1 |  | 0 | [6 empty] | 224640
131
132 | United Payra Power Ltd. | [19 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 93600
133 | Bhola Nutan Biddut BD LTD (GAS) | 227 | 227 | 227 | 227 | 227 | 163 | 163 | 163 | 163 | 180 | 200 | 200 | 157 | 160 | 185 | 165 | 185 | 203 |  | 183 | 233 | 222 | 222 | 222 | 227 | 227 | 4673809
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 89184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 86 | 87 | 85 | 85 | 86 | 84 | 85 | 84 | 85 | 85 | 83 | 85 | 87 | 87 |  | 87 | 86 | 87 | 86 | 86 | 87 | 87 | 2071926
140 | Bhola 33 MW PP (Venture) | 26 | 25 | 23 | 25 | 24 | 22 | 20 | 18 | 18 | 17 | 15 | 11 | 12 | 10 | 10 | 13 | 15 | 18 |  | 25 | 25 | 26 | 25 | 30 | 29 | 29 | 471195
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [9 empty] | 8 | 8 | 24 | 8 | 0 | [5 empty] | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 232500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 30 | 50 | 23 | 15 | 15 |  |  | 97632
146 | Bheramara HVDC | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 830 | 830 | 830 | 830 | 829 | 889 | 925 | 924 | 925 |  | 925 | 924 | 924 | 924 | 924 | 924 | 925 | 19248727
147 | Bheramara 410 MW CCPP | 315 | 315 | 300 | 295 | 285 | 275 | 265 | 240 | 230 | 220 | 210 | 200 | 200 | 205 | 215 | 200 | 200 | 200 |  | 200 | 200 | 205 | 200 | 190 | 190 | 190 | 5901120
148 | Payra 1320 MW | 410 | 410 | 410 | 440 | 480 | 530 | 520 | 460 | 410 | 350 | 330 | 320 | 270 | 250 | 250 | 290 | 290 | 290 |  | 370 | 490 | 500 | 550 | 580 | 580 | 560 | 10944000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 176 | 175 | 175 | 4277400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 34 | 34 | 34 | 34 | 34 |  |  | 123517
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 5 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 19680
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 182 | 182 | 179 | 158 | 153 | 144 | 143 | 131 | 120 | 120 | 120 | 119 | 117 | 117 | 117 | 117 | 117 | 121 |  | 130 | 130 | 130 | 137 | 140 | 137 | 133 | 3502473
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 210 | 210 | 209 | 206 | 205 | 160 | 160 | 149 | 130 | 130 | 130 | 145 | 130 | 130 | 130 | 149 | 167 | 168 |  | 150 | 163 | 164 | 166 | 165 | 164 | 160 | 4256155
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 384 | 394 | 386 | 324 | 392 | 351 | 414 | 370 | 370 | 300 | 414 | 300 | 230 | 251 | 330 | 380 | 350 | 300 |  | 250 | 420 | 420 | 414 | 360 | 360 | 414 | 8589454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 5 | 5 | 6 | 6 |  |  | 36884
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 18 | 18 | 17 | 17 | 18 | 20 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 471600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 126162
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 34 | 34 | 34 |  |  |  | 65942
167 | Katakhali 50 MW Peaking PP | [11 empty] | 0 | 6 | 16 | 16 | 16 | 28 | 32 |  | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 250935
168 | Santahar 50 MW Peaking PP | [17 empty] | 25 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 217883
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 3 | 8 | 8 | 8 |  |  |  | 22080
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 52 |  | 52 | 52 | 52 | 52 | 52 | 23 | 23 | 282096
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 35 | 35 | 64 | 82 | 35 | 35 | 35 | 35 | 35 |  | 38 | 60 | 104 | 113 | 113 | 113 | 113 | 1481568
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 70 | 100 | 113 | 113 | 35 | 35 | 35 | 35 | 35 |  | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 1663488
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 34 | 10 |  |  |  | 29 | 34 | 34 | 34 | 62 | 62 | 67 | 66 | 61 | 66 | 70 | 80 |  | 86 | 87 | 86 | 87 | 87 | 88 | 66 | 1206816
177 | Sympa Solar Power 8MW | [5 empty] | 0 | [7 empty] | 2 | 2 | 2 | 2 | 1 |  | 0 | [6 empty] | 15140
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 108 | 90 |  | 104 | 108 | 108 | 108 | 108 | 108 | 108 | 1445568
178