## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-21 | Tuesday
|  |  | Date (day): | 2022-06-21 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13283.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14787 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-20 | 2022-06-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 56 | 59 | 85 | 85 |  | 23 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 421 | 420 | 405 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas line problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 390 | 390 | 390 | 60 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 66 | 62 | 80 | 85 |  | 15 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 275 | 260 | 285 | 300 |  | 35 | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 47 | 0 | 0 | 210 |  | GT-2 U/M & gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 100 | 90 | 95 |  |  | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 335 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 85 | 85 | 85 |  | 17 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 47 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 45 | 45 | 45 |  | 35 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 48 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 178 | 275 | 285 | 290 |  | 10 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 25 | 98 |  |  | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 107 | 104 | 135 | 135 |  | 14 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 90 | 90 |  |  | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 92 | 92 | 92
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 152 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2791 | 3214 | 3651 | 3833 | 681 | 1304
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 6 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 44 | 45 | 45 |  | 5 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 103 | 104 | 107 | 107 |  | 123 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 82 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 35 |  | 63 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 70 | 50 | 100 | 100 |  | 10 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 76 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 25 | 7 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 80 | 92 |  | 16 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 230 | 265 | 300 |  | 0 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 910 | 1134 | 1324 | 1445 | 311 | 610
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 216 | 220 | 220
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 330 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 300 | 305 | 305 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 37 | 35 | 35 | 10 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 53 | 53 | 52 | 53
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 92 | 88 | 88 | 88 | 107 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 145 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 10 | 0 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 135 | 135 | 135 |  | 28 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 6 | 8 | 8
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 110 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 12 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 95 | 96 | 96 | 17 |  | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 100 | 101 | 100 | 100 |  | 15 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1670 | 1937 | 2095 | 2296 | 434 | 62
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 163 | 180 | 180 | 22 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 160 | 184 | 180 | 190 |  | 9 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 106 | 95 | 107 |  | 8 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 30 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 408 | 491 | 548.6 | 519 | 22 | 25
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 41 | 41 |  | 49 | Machine problem.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 49 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 62 | 65 | 65
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 140 | 140
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 18 | 21 | 21
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 285 | 300 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 222 | 400 | 220 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1446 | 1652 | 1554 | 1775 | 330 | 229
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 924 | 941 | 941
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 31 | 93 | 93 | 93 |  | 16 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 39 |  | 15 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 320 | 330 | 330 | 80 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 70 | 89 |  | 16 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 3 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1305 | 1509 | 1667 | 2005 | 80 | 108
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 48 |  |  | Rampal Transformar O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 26 | 20 | 25
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 87 | 87 | 87 | 107 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 390 | 540 | 622 | 622 |  | 622 | Line O/L & Unit-1 S/D
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 227 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 716 | 896 | 1014 | 1019 | 107 | 622
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 214 | 130 | 215 | 5
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 211 | 180 | 200 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 373 | 350 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 190 |  | 10 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 94 | 100 | 100
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 847 | 1255 | 1044 | 1492 | 478 | 160
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 86 | 95 | 95 |  | 18 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 243 | 351 | 386 | 403 | 269 | 25
|  | Total |  |  |  |  | 22348 | 21396 | 10336 | 12439 | 13283.6 | 14787 | 2712 | 3145
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9972.8648 | 12001.98 | 12816.9066 | 14267.4876
| A. |  | 2022-06-20 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12439 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8586 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12439 | MW
| 3 | Day peak Generation : |  |  | 10336 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12001.98 | MW
| 4 | Evening peak Generation : |  |  | 12439 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 252.8953 | MKWHr | By Solar | 0.55895 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 150.8454 | MKWHr |  | By Oil: | 59.6427 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.6839 | MKWHr |  | By Hydro: | 2.5013 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2712 | MW | Dhaka | 4409.9 | 4409.9 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3145 | MW | Chittagong | 1188.5 | 1188.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5857 | MW | Khulna | 1489.4 | 1489.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1141.24 | MMCFD |  |  | Rajshahi | 1362.4 | 1362.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 173559231.08 | ii) Oil : | Taka | 774886825.03 | Comilla | 1051 | 1051 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 116341279 | Total | Taka | 1064787335.11 | Mymensingh | 1014 | 1014 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.636 | MKWHr. | Sylhet | 335 | 335 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -240 | MW (E to W) at | 21:00 | hrs | Barisal | 336.78 | 336.78 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -364 | MW at | 24:00 | hrs | Rangpur | 815 | 815 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.1° C |  |  | Total | 12001.98 | 12001.98 |  | 0
| B. |  | 2022-06-21 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14787 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 887 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 282.5987 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9143 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3331 | MKWHr. | ii) HVDC Flow at Peak Time |  | 924 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3299 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.24 |  | (b) Today: | 83.23 |  | (c) Rule Curve: |  | 81.03
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 403 | 0 |  | 0 | 390 | 285 | 78 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 20 | 33 | 0 | 16 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 0 | 42 | 22 | 38 | 0 | 0 | 0 | 320 | 310 | 213 | 73 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 21 | 94 | 184 | 0 | 20 | 0 | 43 | 29 | 53 | 47 | 110 | 0 | 57 | 84 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 50 | 0 | 90 | 145 | 90 | 401 | 0 | 90 | 105 | 0 | 0 | 35 | 110 | 0 | 37 | 100 | 400 | 104 | 0 | 0 | 90 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 330 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 184 | 0 | 370 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 70 | 350 | 165 | 0 | 0 | 0 | 0 | 34 |  | 7007 | 3033 | 10040 | 4273 | 924 | 2114 | 0 | 2010 | 525 | 100 | 0 | 0 | 94 | 0 | 0 | 79.39
2:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 404 | 0 |  | 0 | 390 | 274 | 77 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 20 | 33 | 0 | 0 | 0 | 73 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 0 | 45 | 22 | 31 | 0 | 0 | 0 | 320 | 310 | 213 | 73 | 137 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 21 | 94 | 192 | 0 | 20 | 0 | 43 | 29 | 53 | 47 | 110 | 0 | 57 | 84 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 50 | 0 | 90 | 68 | 90 | 400 | 0 | 50 | 105 | 0 | 0 | 35 | 110 | 0 | 31 | 100 | 400 | 104 | 0 | 0 | 90 | 0 | 17 | 0 | 101 | 55 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 181 | 0 | 349 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 70 | 350 | 165 | 0 | 0 | 0 | 0 | 34 |  | 6835 | 3000 | 9835 | 4279 | 923 | 2080 | 0 | 1831 | 525 | 103 | 0 | 0 | 94 | 0 | 0 | 79.56
3:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 403 | 0 |  | 0 | 390 | 255 | 77 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 20 | 33 | 0 | 0 | 0 | 74 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 0 | 45 | 22 | 31 | 0 | 0 | 0 | 320 | 310 | 215 | 73 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 22 | 21 | 94 | 192 | 0 | 20 | 0 | 43 | 29 | 53 | 47 | 110 | 0 | 57 | 84 | 0 | 140 | 0 | 0 | 8 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 37 | 0 | 90 | 68 | 90 | 400 | 0 | 50 | 105 | 0 | 0 | 35 | 110 | 0 | 28 | 100 | 400 | 104 | 0 | 0 | 90 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 174 | 0 | 323 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 70 | 350 | 163 | 0 | 0 | 0 | 0 | 34 |  | 6741 | 2964 | 9705 | 4261 | 924 | 2021 | 0 | 1776 | 525 | 104 | 0 | 0 | 94 | 0 | 0 | 79.73
4:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 402 | 0 |  | 0 | 390 | 270 | 77 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 20 | 33 | 0 | 0 | 0 | 74 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 37 | 0 | 0 | 0 | 320 | 310 | 216 | 73 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 20 | 21 | 88 | 193 | 0 | 20 | 0 | 43 | 0 | 53 | 47 | 110 | 0 | 57 | 84 | 0 | 140 | 0 | 0 | 8 | 275 | 8 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 50 | 68 | 90 | 400 | 0 | 50 | 51 | 0 | 0 | 35 | 51 | 0 | 29 | 98 | 400 | 85 | 0 | 0 | 87 | 0 | 17 | 0 | 100 | 55 | 0 |  | 922 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 174 | 0 | 328 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 350 | 164 | 0 | 0 | 0 | 0 | 34 |  | 6479 | 2919 | 9398 | 4242 | 922 | 2044 | 0 | 1473 | 525 | 104 | 0 | 0 | 88 | 0 | 0 | 79.9
5:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 402 | 0 |  | 0 | 390 | 252 | 77 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 20 | 33 | 0 | 0 | 0 | 74 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 39 | 0 | 0 | 0 | 300 | 310 | 216 | 73 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 15 | 21 | 84 | 192 | 0 | 20 | 0 | 43 | 0 | 53 | 44 | 110 | 0 | 65 | 78 | 0 | 140 | 0 | 0 | 8 | 285 | 8 | 11 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 50 | 68 | 90 | 400 | 0 | 35 | 51 | 0 | 0 | 35 | 51 | 0 | 29 | 50 | 400 | 54 | 0 | 0 | 51 | 0 | 17 | 0 | 100 | 55 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 175 | 0 | 329 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 350 | 165 | 0 | 0 | 0 | 0 | 34 |  | 6223 | 2920 | 9143 | 4225 | 923 | 2028 | 0 | 1254 | 525 | 104 | 0 | 0 | 84 | 0 | 0 | 80.07
6:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 401 | 0 |  | 0 | 390 | 275 | 78 | 0 | 55 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 20 | 33 | 0 | 0 | 0 | 74 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 31 | 22 | 37 | 0 | 0 | 0 | 275 | 270 | 214 | 73 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 13 | 21 | 78 | 192 | 0 | 20 | 0 | 43 | 0 | 53 | 47 | 110 | 0 | 65 | 78 | 0 | 140 | 0 | 0 | 8 | 270 | 8 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 68 | 30 | 400 | 0 | 17 | 34 | 0 | 0 | 35 | 34 | 0 | 28 | 45 | 220 | 35 | 1 | 0 | 34 | 0 | 17 | 0 | 101 | 34 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 176 | 0 | 320 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 350 | 165 | 0 | 0 | 0 | 1 | 34 |  | 5675 | 2911 | 8586 | 3921 | 923 | 2026 | 0 | 1007 | 525 | 104 | 0 | 0 | 78 | 2 | 0 | 80.24
7:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 402 | 0 |  | 0 | 390 | 295 | 70 | 0 | 55 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 17 | 33 | 0 | 0 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 31 | 22 | 36 | 0 | 0 | 0 | 310 | 315 | 213 | 73 | 136 | 34 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 74 | 187 | 0 | 20 | 0 | 43 | 0 | 53 | 47 | 110 | 0 | 63 | 78 | 0 | 140 | 0 | 0 | 0 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 2 | 1 | 30 | 68 | 30 | 400 | 0 | 17 | 34 | 0 | 0 | 35 | 34 | 0 | 29 | 30 | 220 | 35 | 1 | 0 | 34 | 0 | 17 | 0 | 101 | 34 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 183 | 0 | 332 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 350 | 164 | 0 | 0 | 0 | 5 | 34 |  | 5751 | 2928 | 8679 | 3998 | 923 | 2065 | 0 | 987 | 525 | 100 | 0 | 0 | 74 | 7 | 0 | 80.48
8:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 402 | 0 |  | 0 | 390 | 285 | 72 | 0 | 55 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 2 | 22 | 25 | 17 | 33 | 0 | 16 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 33 | 22 | 8 | 0 | 0 | 0 | 290 | 290 | 214 | 92 | 135 | 34 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 84 | 181 | 0 | 20 | 0 | 43 | 0 | 53 | 47 | 110 | 0 | 65 | 78 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 17 | 1 | 30 | 68 | 30 | 400 | 0 | 34 | 34 | 1 | 0 | 35 | 34 | 0 | 29 | 40 | 220 | 34 | 2 | 0 | 34 | 0 | 17 | 0 | 100 | 34 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 181 | 0 | 370 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 350 | 184 | 0 | 0 | 0 | 7 | 34 |  | 5757 | 2995 | 8752 | 3946 | 923 | 2111 | 0 | 1049 | 525 | 100 | 0 | 0 | 84 | 14 | 0 | 80.6
9:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 402 | 0 |  | 0 | 390 | 290 | 75 | 0 | 55 | 280 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 17 | 33 | 0 | 16 | 0 | 70 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 0 | 45 | 22 | 3 | 0 | 0 | 0 | 305 | 310 | 213 | 92 | 136 | 33 | 49 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 12 | 20 | 92 | 167 | 0 | 20 | 0 | 43 | 0 | 53 | 47 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 300 | 8 | 11 | 0 | 12 | 0 | 0 | 65 | 0 | 30 | 4 | 75 | 68 | 40 | 400 | 8 | 34 | 57 | 2 | 0 | 35 | 40 | 0 | 29 | 100 | 220 | 36 | 6 | 9 | 73 | 0 | 17 | 0 | 101 | 39 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 189 | 0 | 370 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 350 | 184 | 0 | 0 | 2 | 42 | 34 |  | 6103 | 3039 | 9142 | 3951 | 923 | 2117 | 0 | 1374 | 525 | 100 | 0 | 0 | 92 | 60 | 0 | 80.7
10:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 402 | 0 |  | 0 | 390 | 275 | 67 | 0 | 55 | 280 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 53 | 55 | 22 | 25 | 17 | 33 | 0 | 49 | 0 | 72 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 0 | 45 | 22 | 2 | 0 | 0 | 0 | 295 | 295 | 213 | 92 | 136 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 0 | 6 | 6 | 20 | 100 | 158 | 0 | 20 | 1 | 43 | 0 | 50 | 47 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 290 | 5 | 11 | 0 | 47 | 0 | 0 | 84 | 0 | 88 | 8 | 90 | 68 | 78 | 401 | 8 | 34 | 68 | 3 | 15 | 35 | 94 | 0 | 28 | 100 | 220 | 56 | 7 | 68 | 90 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 178 | 0 | 367 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 350 | 184 | 0 | 0 | 3 | 77 | 34 |  | 6541 | 3037 | 9578 | 3874 | 924 | 2073 | 0 | 1876 | 525 | 102 | 0 | 0 | 100 | 104 | 0 | 80.8
11:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 402 | 0 |  | 0 | 390 | 280 | 61 | 0 | 40 | 280 | 0 | 0 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 0 | 49 | 0 | 72 | 30 | 100 | 0 | 1 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 45 | 22 | 2 | 0 | 0 | 0 | 290 | 290 | 214 | 92 | 135 | 35 | 50 | 0 | 43 | 0 | 0 | 0 | 0 | 6 | 8 | 20 | 100 | 159 | 0 | 20 | 1 | 44 | 0 | 48 | 47 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 290 | 5 | 11 | 0 | 95 | 0 | 0 | 108 | 0 | 107 | 2 | 90 | 68 | 135 | 402 | 12 | 34 | 68 | 5 | 15 | 35 | 108 | 0 | 29 | 100 | 220 | 92 | 3 | 108 | 90 | 0 | 17 | 0 | 101 | 55 | 0 |  | 923 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 188 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 360 | 223 | 0 | 0 | 3 | 33 | 34 |  | 6777 | 3117 | 9894 | 3892 | 923 | 2170 | 0 | 2120 | 534 | 102 | 0 | 0 | 100 | 53 | 0 | 80.88
12:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 421 | 0 |  | 0 | 390 | 275 | 66 | 0 | 40 | 333 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 47 | 55 | 55 | 22 | 25 | 17 | 33 | 0 | 42 | 0 | 73 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 70 | 0 | 44 | 22 | 2 | 0 | 0 | 0 | 295 | 295 | 213 | 92 | 136 | 35 | 53 | 0 | 43 | 0 | 10 | 0 | 0 | 6 | 12 | 20 | 104 | 151 | 0 | 20 | 1 | 44 | 0 | 50 | 50 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 280 | 8 | 11 | 0 | 178 | 0 | 0 | 160 | 0 | 107 | 6 | 90 | 68 | 142 | 402 | 24 | 70 | 82 | 3 | 45 | 35 | 110 | 0 | 29 | 100 | 222 | 92 | 30 | 152 | 90 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 330 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 191 | 0 | 380 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 390 | 223 | 0 | 0 | 4 | 3 | 34 |  | 7225 | 3111 | 10336 | 3992 | 924 | 2130 | 0 | 2461 | 565 | 103 | 0 | 10 | 104 | 47 | 0 | 80.96
13:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 415 | 0 |  | 0 | 390 | 275 | 71 | 0 | 55 | 335 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 17 | 33 | 0 | 42 | 0 | 74 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 16 | 0 | 70 | 0 | 44 | 22 | 7 | 0 | 0 | 0 | 295 | 295 | 212 | 92 | 135 | 35 | 54 | 0 | 51 | 0 | 16 | 0 | 0 | 6 | 13 | 20 | 106 | 148 | 0 | 20 | 1 | 44 | 0 | 50 | 47 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 290 | 8 | 11 | 0 | 270 | 0 | 0 | 180 | 0 | 101 | 0 | 90 | 68 | 140 | 402 | 24 | 70 | 85 | 4 | 45 | 35 | 110 | 0 | 28 | 100 | 220 | 93 | 54 | 162 | 90 | 0 | 17 | 0 | 96 | 55 | 0 |  | 923 | 0 | 330 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 177 | 0 | 390 | 70 | 0 | 40 | 0 | 49 | 0 | 6 | 45 | 390 | 223 | 0 | 0 | 3 | 5 | 34 |  | 7420 | 3267 | 10687 | 4007 | 923 | 2161 | 0 | 2716 | 565 | 104 | 0 | 32 | 106 | 73 | 0 | 81.04
14:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 412 | 0 |  | 0 | 390 | 280 | 73 | 0 | 55 | 335 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 17 | 0 | 80 | 0 | 44 | 22 | 4 | 0 | 0 | 0 | 280 | 275 | 182 | 97 | 137 | 32 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 16 | 20 | 104 | 137 | 0 | 20 | 1 | 43 | 0 | 50 | 50 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 280 | 8 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 115 | 4 | 90 | 68 | 143 | 401 | 24 | 50 | 88 | 1 | 15 | 35 | 110 | 0 | 29 | 100 | 317 | 89 | 19 | 162 | 90 | 0 | 17 | 0 | 93 | 55 | 0 |  | 923 | 0 | 330 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 180 | 0 | 340 | 70 | 0 | 50 | 0 | 49 | 0 | 3 | 50 | 360 | 202 | 0 | 0 | 1 | 12 | 34 |  | 7394 | 3180 | 10574 | 4030 | 923 | 2080 | 0 | 2739 | 535 | 105 | 0 | 17 | 104 | 41 | 0 | 81.12
15:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 409 | 0 |  | 0 | 390 | 265 | 78 | 0 | 40 | 335 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 17 | 0 | 80 | 0 | 39 | 22 | 2 | 0 | 0 | 0 | 330 | 300 | 183 | 88 | 136 | 34 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 25 | 20 | 116 | 143 | 0 | 20 | 1 | 43 | 0 | 50 | 49 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 300 | 8 | 11 | 0 | 260 | 0 | 0 | 200 | 0 | 119 | 3 | 90 | 68 | 138 | 401 | 38 | 50 | 97 | 1 | 15 | 35 | 110 | 0 | 29 | 100 | 400 | 90 | 19 | 162 | 90 | 0 | 24 | 0 | 101 | 55 | 0 |  | 923 | 0 | 320 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 186 | 0 | 370 | 70 | 0 | 57 | 0 | 55 | 0 | 0 | 95 | 320 | 203 | 0 | 0 | 3 | 17 | 108 |  | 7579 | 3307 | 10886 | 4197 | 923 | 2110 | 0 | 2879 | 495 | 105 | 0 | 17 | 116 | 44 | 0 | 81.2
16:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 414 | 0 |  | 0 | 390 | 275 | 72 | 0 | 55 | 270 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 17 | 0 | 30 | 0 | 39 | 22 | 2 | 0 | 0 | 0 | 280 | 275 | 182 | 88 | 136 | 31 | 51 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 25 | 0 | 100 | 154 | 0 | 20 | 1 | 43 | 0 | 50 | 49 | 110 | 0 | 40 | 78 | 0 | 120 | 0 | 5 | 8 | 290 | 8 | 11 | 0 | 255 | 0 | 0 | 160 | 0 | 115 | 2 | 76 | 68 | 142 | 402 | 54 | 50 | 105 | 1 | 15 | 35 | 110 | 0 | 35 | 100 | 400 | 93 | 9 | 162 | 90 | 0 | 0 | 0 | 101 | 55 | 10 |  | 924 | 0 | 310 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 174 | 0 | 309 | 70 | 0 | 76 | 0 | 67 | 0 | 4 | 113 | 320 | 204 | 0 | 0 | 1 | 33 | 108 |  | 7304 | 3276 | 10580 | 4017 | 924 | 2053 | 0 | 2818 | 495 | 105 | 0 | 17 | 100 | 51 | 0 | 81.32
17:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 421 | 0 |  | 0 | 390 | 275 | 70 | 0 | 55 | 240 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 11 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 17 | 0 | 30 | 0 | 39 | 22 | 6 | 0 | 0 | 0 | 280 | 275 | 182 | 88 | 135 | 34 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 25 | 3 | 98 | 155 | 0 | 20 | 0 | 44 | 0 | 50 | 49 | 110 | 0 | 40 | 81 | 0 | 120 | 0 | 8 | 8 | 270 | 8 | 11 | 0 | 248 | 0 | 0 | 160 | 0 | 122 | 1 | 60 | 105 | 142 | 360 | 32 | 50 | 105 | 0 | 15 | 35 | 68 | 0 | 95 | 50 | 398 | 93 | 11 | 108 | 90 | 0 | 16 | 0 | 101 | 55 | 0 |  | 924 | 0 | 315 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 193 | 0 | 304 | 35 | 0 | 50 | 0 | 78 | 0 | 2 | 70 | 300 | 173 | 0 | 0 | 1 | 36 | 72 |  | 7114 | 3130 | 10244 | 3947 | 924 | 2010 | 0 | 2617 | 475 | 105 | 0 | 17 | 98 | 51 | 0 | 81.44
18:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 417 | 0 |  | 0 | 390 | 295 | 72 | 0 | 55 | 240 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 11 | 33 | 0 | 49 | 0 | 78 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 17 | 0 | 30 | 0 | 45 | 22 | 7 | 0 | 0 | 0 | 285 | 280 | 194 | 88 | 135 | 34 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 25 | 20 | 102 | 154 | 0 | 20 | 0 | 44 | 0 | 50 | 49 | 110 | 0 | 40 | 40 | 0 | 120 | 0 | 13 | 8 | 290 | 8 | 11 | 0 | 260 | 0 | 0 | 120 | 0 | 117 | 0 | 20 | 155 | 140 | 364 | 32 | 50 | 105 | 0 | 15 | 35 | 68 | 0 | 96 | 20 | 360 | 70 | 3 | 108 | 90 | 0 | 10 | 0 | 101 | 55 | 0 |  | 923 | 0 | 315 | 0 | 45 | 0 | 0 | 0 | 17 | 0 | 8 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 130 | 0 | 250 | 17 | 0 | 50 | 0 | 70 | 0 | 1 | 70 | 300 | 173 | 0 | 0 | 0 | 8 | 72 |  | 7042 | 2967 | 10009 | 3877 | 923 | 1962 | 0 | 2516 | 475 | 108 | 0 | 34 | 102 | 12 | 0 | 81.56
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 417 | 0 |  | 0 | 390 | 305 | 75 | 0 | 55 | 240 | 0 | 0 | 43 | 85 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 11 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 3 | 0 | 0 | 0 | 0 |  | 22 | 32 | 51 | 70 | 12 | 45 | 22 | 19 | 0 | 0 | 0 | 310 | 305 | 214 | 88 | 136 | 37 | 55 | 0 | 51 | 0 | 25 | 0 | 0 | 6 | 33 | 20 | 110 | 160 | 0 | 20 | 0 | 44 | 0 | 50 | 49 | 110 | 0 | 40 | 84 | 0 | 120 | 0 | 16 | 8 | 290 | 8 | 11 | 0 | 275 | 0 | 0 | 137 | 0 | 112 | 0 | 76 | 157 | 142 | 401 | 42 | 70 | 105 | 0 | 100 | 35 | 74 | 0 | 95 | 29 | 400 | 57 | 0 | 112 | 90 | 0 | 17 | 0 | 101 | 55 | 0 |  | 923 | 0 | 324 | 0 | 93 | 0 | 0 | 0 | 37 | 0 | 40 | 84 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 16 | 14 | 0 | 24 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 130 | 0 | 250 | 35 | 0 | 54 | 0 | 81 | 0 | 0 | 100 | 370 | 173 | 0 | 0 | 0 | 0 | 72 |  | 7777 | 3313 | 11090 | 4024 | 923 | 2037 | 0 | 3011 | 545 | 105 | 0 | 335 | 110 | 0 | 0 | 82
19:30 | 0 | 0 | 0 | 180 | 0 | 58 | 0 | 421 | 0 |  | 0 | 390 | 275 | 79 | 0 | 55 | 335 | 0 | 0 | 70 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 17 | 33 | 0 | 49 | 0 | 75 | 30 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 32 | 51 | 80 | 45 | 44 | 22 | 25 | 0 | 0 | 0 | 280 | 275 | 215 | 88 | 136 | 37 | 55 | 0 | 51 | 0 | 37 | 0 | 0 | 6 | 33 | 20 | 112 | 161 | 0 | 20 | 0 | 43 | 0 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 120 | 0 | 17 | 8 | 285 | 8 | 11 | 0 | 275 | 0 | 0 | 185 | 0 | 100 | 0 | 76 | 200 | 145 | 400 | 104 | 90 | 105 | 0 | 250 | 35 | 110 | 0 | 96 | 100 | 400 | 93 | 0 | 162 | 108 | 0 | 17 | 0 | 102 | 55 | 0 |  | 924 | 0 | 325 | 0 | 93 | 0 | 0 | 0 | 45 | 0 | 40 | 87 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 34 | 32 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 175 | 0 | 395 | 93 | 0 | 80 | 0 | 86 | 0 | 0 | 113 | 500 | 227 | 0 | 0 | 0 | 0 | 72 |  | 8531 | 3885 | 12416 | 4172 | 924 | 2211 | 0 | 3745 | 675 | 105 | 0 | 472 | 112 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 58 | 0 | 420 | 0 |  | 0 | 390 | 250 | 79 | 0 | 55 | 335 | 0 | 0 | 92 | 85 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 49 | 0 | 73 | 30 | 100 | 0 | 24 | 0 | 0 | 0 | 0 |  | 22 | 32 | 51 | 80 | 54 | 44 | 22 | 30 | 0 | 0 | 0 | 280 | 280 | 216 | 88 | 136 | 37 | 56 | 0 | 51 | 0 | 42 | 0 | 9 | 6 | 33 | 20 | 108 | 163 | 0 | 20 | 0 | 43 | 0 | 53 | 49 | 110 | 0 | 40 | 81 | 0 | 120 | 0 | 17 | 8 | 290 | 8 | 11 | 0 | 275 | 0 | 0 | 193 | 0 | 98 | 0 | 76 | 200 | 143 | 400 | 106 | 95 | 105 | 0 | 265 | 35 | 104 | 0 | 96 | 100 | 400 | 90 | 0 | 162 | 108 | 0 | 17 | 0 | 100 | 55 | 0 |  | 923 | 0 | 325 | 0 | 94 | 0 | 0 | 0 | 39 | 0 | 40 | 87 | 26 | 16 | 0 | 0 | 0 | 18 | 0 | 88 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 190 | 0 | 296 | 93 | 0 | 92 | 0 | 86 | 0 | 0 | 113 | 520 | 228 | 0 | 0 | 0 | 0 | 52 |  | 8550 | 3842 | 12392 | 4196 | 923 | 2103 | 0 | 3791 | 695 | 103 | 0 | 473 | 108 | 0 | 0 | 81.85
21:00 | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 420 | 0 |  | 0 | 390 | 260 | 62 | 0 | 55 | 335 | 0 | 47 | 100 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 49 | 0 | 74 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 50 | 0 | 44 | 22 | 25 | 0 | 0 | 0 | 330 | 300 | 216 | 88 | 135 | 37 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 33 | 20 | 110 | 163 | 0 | 20 | 0 | 44 | 0 | 53 | 49 | 110 | 0 | 62 | 84 | 0 | 120 | 0 | 18 | 8 | 285 | 8 | 11 | 0 | 275 | 0 | 0 | 184 | 0 | 104 | 0 | 76 | 200 | 145 | 400 | 106 | 105 | 105 | 0 | 230 | 35 | 110 | 0 | 95 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 17 | 0 | 101 | 55 | 0 |  | 924 | 0 | 320 | 0 | 93 | 0 | 0 | 0 | 39 | 0 | 40 | 87 | 26 | 16 | 0 | 0 | 0 | 26 | 0 | 88 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 211 | 0 | 373 | 93 | 0 | 94 | 0 | 86 | 0 | 0 | 113 | 540 | 227 | 0 | 0 | 0 | 0 | 90 |  | 8428 | 4011 | 12439 | 4352 | 924 | 2181 | 0 | 3716 | 715 | 104 | 0 | 337 | 110 | 0 | 0 | 82
22:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 423 | 0 |  | 0 | 390 | 255 | 66 | 0 | 55 | 335 | 0 | 37 | 100 | 85 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 49 | 0 | 73 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 50 | 0 | 44 | 22 | 25 | 0 | 0 | 0 | 330 | 300 | 216 | 88 | 136 | 37 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 20 | 108 | 163 | 0 | 20 | 0 | 43 | 0 | 53 | 49 | 110 | 0 | 40 | 84 | 0 | 120 | 0 | 21 | 8 | 270 | 8 | 11 | 0 | 275 | 0 | 0 | 184 | 0 | 114 | 0 | 90 | 200 | 145 | 400 | 106 | 105 | 105 | 0 | 190 | 35 | 110 | 0 | 95 | 100 | 400 | 94 | 0 | 162 | 92 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 315 | 0 | 93 | 0 | 0 | 0 | 39 | 0 | 40 | 87 | 27 | 0 | 0 | 0 | 0 | 26 | 0 | 90 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 211 | 0 | 377 | 93 | 0 | 94 | 0 | 93 | 0 | 0 | 113 | 570 | 228 | 0 | 0 | 0 | 0 | 90 |  | 8311 | 4033 | 12344 | 4321 | 924 | 2173 | 0 | 3682 | 745 | 103 | 0 | 288 | 108 | 0 | 0 | 82.15
23:00 | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 421 | 0 |  | 0 | 390 | 276 | 79 | 0 | 55 | 335 | 0 | 39 | 100 | 85 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 32 | 0 | 74 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 50 | 0 | 45 | 22 | 38 | 0 | 0 | 0 | 330 | 300 | 214 | 88 | 136 | 37 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 20 | 104 | 163 | 0 | 20 | 0 | 43 | 0 | 50 | 49 | 110 | 0 | 40 | 84 | 0 | 120 | 0 | 21 | 8 | 280 | 8 | 11 | 0 | 275 | 0 | 0 | 174 | 0 | 132 | 0 | 90 | 200 | 147 | 401 | 106 | 105 | 105 | 0 | 135 | 30 | 110 | 0 | 95 | 100 | 401 | 93 | 0 | 162 | 92 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 305 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 212 | 0 | 420 | 93 | 0 | 94 | 0 | 94 | 0 | 0 | 113 | 570 | 226 | 0 | 0 | 0 | 0 | 90 |  | 8262 | 3817 | 12079 | 4297 | 924 | 2255 | 0 | 3581 | 745 | 104 | 0 | 69 | 104 | 0 | 0 | 82.3
24:00 | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 418 | 0 |  | 0 | 390 | 252 | 85 | 0 | 55 | 335 | 0 | 95 | 100 | 85 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 32 | 0 | 75 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 0 | 44 | 22 | 38 | 0 | 0 | 0 | 330 | 300 | 215 | 88 | 135 | 34 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 108 | 160 | 0 | 20 | 0 | 43 | 0 | 51 | 49 | 110 | 0 | 40 | 84 | 0 | 120 | 0 | 21 | 8 | 295 | 8 | 11 | 0 | 275 | 0 | 0 | 164 | 0 | 134 | 0 | 90 | 200 | 140 | 400 | 106 | 105 | 105 | 0 | 135 | 35 | 110 | 0 | 42 | 100 | 400 | 93 | 0 | 162 | 108 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 295 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 209 | 0 | 390 | 93 | 0 | 94 | 0 | 76 | 0 | 0 | 113 | 560 | 226 | 0 | 0 | 0 | 0 | 72 |  | 8247 | 3715 | 11962 | 4347 | 924 | 2215 | 0 | 3475 | 735 | 105 | 0 | 53 | 108 | 0 | 0 | 82.45
KWH | 0 | 0 | 0 | 4347000 | 0 | 1330863 | 0 | 9967610 | 0 |  | 0 | 9298000 | 6630691 | 1766400 | 0 | 1314308 | 7462458 | 0 | 178000 | 864960 | 788688 | 408480 | 0 | 0 | 0 | 0 | 1276560 | 907435 | 964065 | 418212 | 600000 | 413460 | 806760 | 0 | 742560 | 0 | 1765347 | 736000 | 2400000 | 0 | 175510 | 0 | 0 | 0 | 0 |  | 529200 | 149136 | 71951 | 1110360 | 76800 | 1028160 | 523344 | 499200 | 0 | 0 | 0 | 7697300 | 7215000 | 5046000 | 2074181 | 3237460 | 802512 | 1279680 | 0 | 1184238 | 0 | 64432 | 0 | 25920 | 213300 | 562700 | 479430 | 2329920 | 3923520 | 0 | 441504 | 8250 | 1032000 | 114224 | 1242000 | 1154088 | 2707936 | 0 | 1306560 | 1896000 | 0 | 3069590 | 0 | 118020 | 178380 | 7057000 | 167472 | 235206 | 0 | 3618108 | 0 | 0 | 3374400 | 0 | 1905264 | 33480 | 1728960 | 2589120 | 2714836 | 9544000 | 856800 | 1492800 | 2096763 | 24121 | 1287164 | 888962 | 2239772 | 0 | 1198680 | 2034240 | 8072100 | 1937280 | 158690 | 2194560 | 2032363 | 0 | 438840 | 0 | 2416320 | 1270080 | 2327 |  | 22333090 | 0 | 8032896 | 0 | 1121280 | 0 | 0 | 0 | 163680 | 0 | 340875 | 2010800 | 455700 | 42432 | 0 | 0 | 0 | 69499 | 0 | 338272 | 0 | 130865 | 88237 | 0 | 179162 | 478560 | 0 | 201240 | 0 | 0 | 4290500 | 0 | 0 | 0 | 0 | 4706964 | 0 | 0 | 0 | 4697600 | 0 | 8471527 | 871680 | 0 | 1425600 | 0 | 1295577 | 0 | 35427 | 1681632 | 10393400 | 4834873 | 0 | 0 | 31140 | 267840 | 1339584 |  | 172565371 | 80329932 | 252895303 | 99954469 | 22333090 | 50890937 | 0 | 58109843 | 14683900 | 2501347 | 0 | 1532849 | 2329920 | 558948 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 1770047.79 | 0 | 10465990.5 | 0 |  | 0 | 10134820 | 7360067.01 | 19748352 | 0 | 17414581 | 8357952.96 | 0 | 311500 | 12645715.2 | 11096840.16 | 6621460.8 | 0 | 0 | 0 | 0 | 16237843.2 | 12250372.5 | 12928111.65 | 313659 | 450000 | 0 | 0 | 0 | 12630945.6 | 0 | 476643.69 | 198720 | 4536000 | 0 | 2869588.5 | 0 | 0 | 0 | 0 |  | 6906060 | 2487588.48 | 1224606.02 | 15000963.6 | 973824 | 11895811.2 | 664646.88 | 1662336 | 0 | 0 | 0 | 8544003 | 7864350 | 5853360 | 2675693.49 | 3949701.2 | 906838.56 | 1906723.2 | 0 | 1977677.46 | 0 | 1112740.64 | 0 | 35510.4 | 159975 | 984725 | 359572.5 | 16728825.6 | 4276636.8 | 0 | 600445.44 | 131505 | 1413840 | 150775.68 | 2161080 | 1996572.24 | 3114126.4 | 0 | 2534726.4 | 4322880 | 0 | 3100285.9 | 0 | 175849.8 | 353192.4 | 7057000 | 125604 | 178756.56 | 0 | 49387174.2 | 0 | 0 | 45486912 | 0 | 26387906.4 | 391381.2 | 17842867.2 | 35367379.2 | 36025873.72 | 8780480 | 10418688 | 21585888 | 26524051.95 | 0 | 15111305.36 | 9680796.18 | 23808776.36 | 0 | 15450985.2 | 23963347.2 | 7426332 | 25087776 | 2293070.5 | 27848966.4 | 23128290.94 | 0 | 5731250.4 | 0 | 36172310.4 | 16726953.6 | 0 |  | 66999270 | 0 | 8996843.52 | 0 | 11672524.8 | 0 | 0 | 0 | 2947876.8 | 0 | 4898373.75 | 2252096 | 884058 | 462508.8 | 0 | 0 | 0 | 1165498.23 | 0 | 5290574.08 | 0 | 2167124.4 | 1492087.67 | 0 | 3022462.94 | 990619.2 | 0 | 152338.68 | 0 | 0 | 22696745 | 0 | 0 | 0 | 0 | 6024913.92 | 0 | 0 | 0 | 5449216 | 0 | 8386811.73 | 11715379.2 | 0 | 16864848 | 0 | 16453827.9 | 0 | 391468.35 | 20415012.48 | 93644534 | 4931570.46 | 0 | 0 | 352193.4 | 3141763.2 | 20535822.72 |  | 811493812.82 | 344398363.23 | 1155892176.05 | 111698105.9 | 66999270 | 61861125.18 | 0 | 749521929.37 | 116341279 | 675363.69 | 0 | 25364895.66 | 16728825.6 | 6701381.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 421 | 0 |  | 0 | 390 | 275 | 66 | 0 | 40 | 333 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 47 | 55 | 55 | 22 | 25 | 17 | 33 | 0 | 42 | 0 | 73 | 30 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 70 | 0 | 44 | 22 | 2 | 0 | 0 | 0 | 295 | 295 | 213 | 92 | 136 | 35 | 53 | 0 | 43 | 0 | 10 | 0 | 0 | 6 | 12 | 20 | 104 | 151 | 0 | 20 | 1 | 44 | 0 | 50 | 50 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 0 | 8 | 280 | 8 | 11 | 0 | 178 | 0 | 0 | 160 | 0 | 107 | 6 | 90 | 68 | 142 | 402 | 24 | 70 | 82 | 3 | 45 | 35 | 110 | 0 | 29 | 100 | 222 | 92 | 30 | 152 | 90 | 0 | 17 | 0 | 100 | 55 | 0 |  | 924 | 0 | 330 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 191 | 0 | 380 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 390 | 223 | 0 | 0 | 4 | 3 | 34 |  | 10336 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 420 | 0 | 0 | 0 | 390 | 260 | 62 | 0 | 55 | 335 | 0 | 47 | 100 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 49 | 0 | 74 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 50 | 0 | 44 | 22 | 25 | 0 | 0 | 0 | 330 | 300 | 216 | 88 | 135 | 37 | 53 | 0 | 51 | 0 | 0 | 0 | 0 | 6 | 33 | 20 | 110 | 163 | 0 | 20 | 0 | 44 | 0 | 53 | 49 | 110 | 0 | 62 | 84 | 0 | 120 | 0 | 18 | 8 | 285 | 8 | 11 | 0 | 275 | 0 | 0 | 184 | 0 | 104 | 0 | 76 | 200 | 145 | 400 | 106 | 105 | 105 | 0 | 230 | 35 | 110 | 0 | 95 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 17 | 0 | 101 | 55 | 0 |  | 924 | 0 | 320 | 0 | 93 | 0 | 0 | 0 | 39 | 0 | 40 | 87 | 26 | 16 | 0 | 0 | 0 | 26 | 0 | 88 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 211 | 0 | 373 | 93 | 0 | 94 | 0 | 86 | 0 | 0 | 113 | 540 | 227 | 0 | 0 | 0 | 0 | 90 |  | 12439 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 412 | 0 | 0 | 0 | 390 | 300 | 85 | 0 | 55 | 335 | 0 | 0 | 95 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 77 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 51 | 100 | 92 | 45 | 22 | 20 | 0 | 0 | 0 | 330 | 305 | 220 | 88 | 135 | 35 | 53 | 0 | 51 | 0 | 50 | 0 | 21 | 8 | 33 | 21 | 165 | 180 | 0 | 20 | 0 | 43 | 41 | 51 | 50 | 110 | 0 | 65 | 84 | 0 | 140 | 0 | 21 | 10 | 341 | 8 | 11 | 200 | 290 | 300 | 100 | 190 | 98 | 135 | 0 | 90 | 200 | 150 | 400 | 107 | 90 | 105 | 0 | 300 | 35 | 110 | 0 | 96 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 35 |  | 100 | 55 |  |  | 941 | 0 | 330 | 0 | 93 | 220 | 0 | 0 | 39 | 60 | 40 | 87 | 25 | 48 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 215 | 0 | 0 | 100 | 200 | 0 | 414 | 93 | 190 | 100 | 89 | 95 | 0 | 0 | 113 | 622 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 405 | 0 | 0 | 0 | 390 | 285 | 80 | 0 | 55 | 335 | 0 | 0 | 90 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 48 | 0 | 77 | 30 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 100 | 80 | 45 | 22 | 7 | 0 | 0 | 0 | 330 | 305 | 220 | 88 | 135 | 35 | 52 | 0 | 51 | 0 | 50 | 0 | 21 | 8 | 33 | 21 | 143 | 180 | 0 | 20 | 1.6 | 43 | 41 | 51 | 50 | 110 | 0 | 65 | 84 | 0 | 140 | 0 | 21 | 10 | 300 | 8 | 11 | 100 | 285 | 200 | 100 | 180 | 25 | 135 | 20 | 90 | 150 | 140 | 400 | 95 | 90 | 105 | 5 | 265 | 35 | 110 | 0 | 96 | 100 | 220 | 92 | 50 | 162 | 108 | 0 | 17 | 30 | 100 | 55 |  |  | 941 | 0 | 330 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 180 | 0 | 350 | 93 | 100 | 100 | 70 | 95 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 59 | 0 | 417 | 0 | 0 | 0 | 390 | 275 | 40 | 0 | 55 | 270 | 0 | 60 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 20 | 33 | 0 | 16 | 0 | 77 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 0 | 45 | 22 | 7 | 0 | 0 | 0 | 330 | 305 | 216 | 88 | 136 | 34 | 54 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 14 | 92 | 181 | 0 | 20 | 0 | 43 | 0 | 50 | 49 | 110 | 0 | 64 | 40 | 0 | 120 | 0 | 21 | 8 | 280 | 0 | 0 | 0 | 15 | 0 | 0 | 65 | 0 | 50 | 4 | 76 | 68 | 10 | 365 | 8 | 52 | 75 | 1 | 3 | 19 | 76 | 0 | 28 | 60 | 360 | 53 | 18 | 17 | 108 | 0 | 17 | 0 | 51 | 55 | 0 | 0 | 923 | 0 | 295 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 160 | 0 | 330 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 50 | 340 | 228 | 0 | 0 | 1 | 5 | 35 | 0 |  |  |  |  | 59642692 |  | 0
59642692
| Minimum Generation |  | 8586 | 6:00
| Highest Generation |  | 12439 | 21:00
| Day Peak Generation |  | 10336 | 12:00
| Evening Peak Generation |  | 12439 | 21:00
| HVDC Max Flow |  | 924 | 1:00
| HVDC EvPeak Flow |  | 924 | 21:00
| Load factor L.F |  | 84.71%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-21
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10336 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9143 | MW
Evening Peak Generation : |  | 12439 | MW Hour : | 21:00 | Available Max Generation : |  | 14787 | MW
E.P. Demand (at gen end) : |  | 12439 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13900 | MW
Maximum Generation : |  | 12439 | MW Hour : | 21:00 | Reserve(Generation end) |  | 887 | MW
Total Gen. (MKWH) : |  | 252.8953 | System Load Factor : | 84.71% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -364 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-21
Actual : | 83.23 | Ft.(MSL) , | Rule curve : | 81.03 | Ft.( MSL )
Gas Consumed : | Total = | 1141.24 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 173559231.08
: |  | Coal : | 116341279 | Oil : | 774886825.03 | Total : | 1064787335.11
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4841.3562 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1302.8956 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1709.4747 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1531.4295 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1357.0434 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 998.2712 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 553.1582 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 362.92 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 763.8852 |  |  | 0 | 0%
Total | 0 |  | 13420.4339 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Netrokona 132/33 kV T-2 transformer 33 kV side was under shut down from 07:58 to 09:18 due to red | [5 empty] | About 10 MW power interruption occurred under
hot maintenance at bus isolator. | [5 empty] | Netrokona S/S area from 07:58 to 09:18.
b) Rajshahi 230 kV bus-1 was under shut down from 09:16 to 11:56 for D/W.
c) Bhaluka 132/33 kV T-2 transformer was under shut down from 09:36 to 10:02 for D/W. | [5 empty] | About 15 MW power interruption occurred under
Bhaluka S/S area from 09:36 to 10:02.
d) Bogura(O)-Bogura(N) 132 kV Ckt-1 was under shut down from 07:43 to 08:12 for C/M.
e) Bogura(O)-Bogura(N) 132 kV Ckt-2 was under shut down from 08:15 to 08:32 for C/M.
f) Bogura 230/132 kV T-1 transformer was under shut down from 08:36 to 10:46 for C/M.
g) Sylhet 132/33 kV T-1 transformer tripped at 09:10 from LT side showing lockout relay and was switched | [5 empty] | About 10 MW power interruption occurred under
on at 16:49. | [5 empty] | Sylhet S/S area from 09:10 to 09:32.
h) Kallyanpur 132/33 kV T-1 transformer was under shut down from 08:14 to 09:32 for C/M. | [5 empty] | About 24 MW power interruption occurred under
Kallyanpur S/S area from 08:14 to 09:32.
i) Aminbazar-Kallyanpur 132 kV Ckt-2 was under shut down from 10:12 to 16:55 for D/W.
j) Bhaluka 132/33 kV T-1 transformer was under shut down from 10:10 to 14:10 for D/W. | [5 empty] | About 15 MW power interruption occurred under
Bhaluka S/S area from 10:10 to 14:10.
k) Dohazari 132/33 kV T-1 & T-2 transformer tripped at 10:52 showing O/C,IDMT RYB phase due to tree | [5 empty] | About 55 MW power interruption occurred under
branch fall into auxiliary transformer and were switched on at 11:20,13:51 respectively. | [5 empty] | Dohazari S/S area from 10:52 to 11:20.
l) Payra-Gopalganj 400 kV Ckt-1 was under shut down at 11:58 for test purpose.
m) Kabirpur 132/33 kV T-1 transformer 33 kV side was under shut down from 12:16 to 13:58 for C/M. | [5 empty] | About 80 MW power interruption occurred under
Kabirpur S/S area from 12:16 to 13:58.
n) Bogura 230/132 kV T-2 transformer was under shut down from 12:34 to 13:26 for C/M.
o) Ashuganj(East) GT was synchronized at 15:48 and was shut down at 16:09.
p) Cumilla(S) 132/33 kV T-2 transformer tripped at 15:38 showing E/F relay due to 33 kV Kosba feeder | [5 empty] | About 20 MW power interruption occurred under
fault and was switched 15:59. | [5 empty] | Cumilla S/S area from 15:38 to 15:59.
q) After maint Natore-Rajshahi 132 kV Ckt-2 was switched on at 18:43.
r) Siddhirganj GT-1 was synchronized at 20:55.
s) Sreenagar 132/33 kV T-1 transformer was under shut down from 23:36 to 00:04 for red hot maint at
33 kV CB R-phase bolt.
t) Ishurdi 132/33 kV T-2 transformer was under shut down since at 02:16(21-06-2022) for sparking & fire | [5 empty] | About 25 MW power interruption occurred under
occurred at 33 kV R-phase CT box and was switched on at 09:06. | [5 empty] | Ishurdi S/S area from 02:16 to 09:06.
u) Gallamari 132/33 kV T-1 transformer was under shut down since at 06:04(21-06-2022) for D/W.
v) Jhenaidah 132/33 kV T-2 transformer was under shut down since at 07:18(21-06-2022) for 33 kV bus | [5 empty] | About 32 MW power interruption occurred under
isolator red hot maintenance and was switched on at 09:03. | [5 empty] | Jhenaidah S/S area from 07:18 to 09:03.
w) Cumilla(N)-BSRM 230 kV Ckt-1 tripped at 07:09 from Cumilla(N) end and was switched on at 09:50.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 59 | 1330863 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 420 | 9967610
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 390 | 9298000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 62 | 1766400 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 260 | 6630691 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1314308
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 418212
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 47 | 178000 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 100 | 864960
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7462458
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 788688 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1276560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 408480 | Gas shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 907435
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 964065
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1013460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 806760
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 0 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 742560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 3618108 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 104 | 1905264 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1492800 | Transformer O/L.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1937280 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2194560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1270080
| Dhaka area Total |  |  |  | 5847 | 3214 | 62904602
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 175510
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 33480
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1028160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 104 | 2501347 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2096763
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 149136 | Gas shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 71951 | Gas shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 50 | 1110360 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1728960 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 523344
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 499200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 76800 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 230 | 1287164 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 888962 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2239772
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2034240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2032363
| Chattogram area Total |  |  |  | 2382 | 1134 | 20901633
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 5046000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7697300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7215000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 2327 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 802512 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 53 | 1279680
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 88 | 2074181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1184238
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 2714836 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 64432 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3237460 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2589120
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 25920 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 213300
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2329920
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 562700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 479430
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1198680 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 438840 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 2416320
| Cumilla Area Total |  |  |  | 2885 | 1937 | 41572196
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 163 | 3923520 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 441504
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8250
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 184 | 3374400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 856800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 158690
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 529200
| Mymensingh Area Total |  |  |  | 614 | 491 | 9292364
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1032000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 114224 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2707936 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1242000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 1154088
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 235206
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1306560
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1896000
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 3069590 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 18 | 118020 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 167472 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7057000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9544000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 178380
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8072100
| Sylhet Area Total |  |  |  | 2477 | 1652 | 37894576
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 924 | 22333090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 93 | 1121280 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 163680
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8032896 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 340875
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 871680 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve.
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 267840
| Khulna Area Total |  |  |  | 2384 | 1509 | 33131341
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 42432 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 26 | 455700 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2010800 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 10393400 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 227 | 4834873
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 896 | 17737205
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 69499 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 130865 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 88237 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 214 | 4706964
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 211 | 4697600 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 373 | 8471527
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 179162 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 478560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 201240
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 338272 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1425600 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1681632
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31140
| Rajshahi Area Total |  |  |  | 2129 | 1255 | 22500298
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4290500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 86 | 1295577 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35427
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1339584 | Low demand
| Rangpur Area Total |  |  |  | 720 | 351 | 6961088
| Total |  |  |  | 21396 | 12439 | 252895303
| Eastern Grid Total |  |  |  | 14205 | 8428 | 172565371
| Western Grid Total |  |  |  | 7191 | 4011 | 80329932
| National Grid Total |  |  |  | 21396 | 12439 | 252895303
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-20
(a) ENTIRE EASTERN GRID : |  | 7998.4 | MW | (b) ENTIRE WESTERN GRID : |  | 4003.58 | MW
i) Dhaka area |  | 4409.9 | MW | i) Khulna area |  | 1489.4 | MW
ii) Chittagong area |  | 1188.5 | MW | ii) Rajshahi area |  | 1362.4 | MW
iii) Comilla area |  | 1051 | MW | iii) Barisal area |  | 336.78 | MW
iv) Mymensingh area |  | 1014 | MW | iv) Rangpur area |  | 815 | MW
v) Sylhet area |  | 335 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12001.98 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 28 | 13:00 | Hasnabad | 78 | 18:00 | Palashbari | 114 | 22:00
Agargaon | 83 | 14:00 | Hathazari | 76 | 20:00 | Panchagarh | 56 | 19:30
Agrabad | 70 | 19:00 | Ishurdi | 78 | 19:30 | Patuakhali | 108 | 22:00
AKS | 10 | 18:00 | Jaldhaka | 60 | 19:30 | Payra | 1 | 00:00
AKSML | 158 | 07:00 | Jamalpur | 139 | 21:00 | PHP | 8 | 03:00
Amnura | 44 | 19:30 | Jashore | 116 | 19:30 | Purbachal | 17 | 19:30
Ashuganj | 42 | 23:00 | Jhenaidah | 109 | 23:00 | Purbasadipur | 118 | 21:00
Bagerhat | 87 | 22:00 | Joydebpur | 173 | 19:30 | Rahim | 30 | 16:00
Bakulia | 96 | 20:00 | Joypurhat | 59 | 22:00 | Rajbari | 62 | 20:00
Banani | 39 | 12:00 | Juldah | 26 | 13:00 | Rajendrapur | 111 | 20:00
Bangabhaban | 18 | 11:00 | Kabirpur | 268 | 16:00 | Rajshahi | 145 | 21:00
Barapukuria | 50 | 22:00 | Kachua | 62 | 20:00 | Rajshahi | 40 | 22:00
Barguna | 18 | 21:00 | Kallyanpur | 96 | 15:00 | Ramganj | 88 | 21:00
Barishal | 106 | 12:00 | Kalurghat | 5 | 12:00 | Rampur | 13 | 19:00
Barishal | 40 | 11:00 | Kamrangirchar | 68 | 13:00 | Rangamati | 10 | 12:00
Baroaulia | 53 | 22:00 | Kaptai | 3.5 | 21:00 | Rangpur | 136 | 19:30
Baroirhat | 62 | 21:00 | Kazla | 78 | 13:00 | Ruppur | 5 | 11:00
Bashundhara | 161 | 15:00 | Keranigonj | 56 | 11:00 | Saidpur | 106 | 20:00
BashundharaCement | 1 | 00:00 | Khagrachori | 24 | 20:00 | Satkhira | 116 | 22:00
Beanibazar | 44 | 19:00 | Khulna | 101 | 20:00 | Satmasjid | 84 | 19:00
Benapole | 50 | 20:00 | Khulshi | 171 | 19:00 | Savar | 169 | 12:00
Bhaluka | 128 | 19:30 | Kishoreganj | 132 | 22:00 | Shahjadpur | 97 | 19:30
Bhandaria | 51 | 20:00 | Kodda | 305 | 15:00 | Shahjibazar | 102 | 22:00
Bhangura | 32 | 20:00 | KSRM | 24.5 | 11:00 | Shahmirpur | 41 | 19:00
Bheramara(GK) | 58 | 23:00 | Kulaura | 34 | 23:00 | Shariatpur | 62 | 22:00
Bhulta | 253 | 23:00 | Kurigram | 58 | 20:00 | Sherpur | 126 | 20:00
Bog-Sherpur | 62 | 22:00 | Kushtia | 136 | 20:00 | Shikalbaha | 24 | 12:00
Bogura | 158 | 23:00 | Lalbag | 90 | 13:00 | Shitalakhya | 116 | 15:00
Borhanuddin | 39 | 00:00 | Lalmonirhat | 42 | 19:30 | Sholosohor | N/A | N/A
Brahmanbaria | 140 | 22:00 | Madanganj | 103 | 21:00 | Shyampur | 168 | 11:00
BSRM | 159 | 17:00 | Madaripur | 87 | 20:00 | Siddhirganj | 114 | 15:00
Cantonment | 135 | 13:00 | Madartek | 68 | 21:00 | Sirajganj | 102 | 20:00
Chandpur | 55 | 21:00 | Madunaghat | 43 | 22:00 | Sonargaon | 89 | 21:00
Chandraghona | 28 | 19:30 | Magura | 53 | 21:00 | Sreemongol | 47 | 23:00
Chapai | 63 | 21:00 | Mahasthangarh | 66 | 23:00 | Srinagar | 39.7 | 22:00
Charsaidpur | 43 | 23:00 | Manikganj | 72 | 21:00 | SSM | 3 | 12:00
Chauddagram | 43 | 23:00 | Maniknagar | 73 | 15:00 | Sunamganj | 4 | 21:00
Chhatak | 6 | 22:00 | Matarbari | 36 | 19:00 | Sylhet | 72 | 15:00
Chowmuhani | 182 | 22:00 | Matuail | 62 | 13:00 | Tangail | 207 | 20:00
Chuadanga | 104 | 22:00 | Millgate | 68 | 15:00 | Thakurgaon | 93 | 21:00
Coxsbazar | 103 | 20:00 | Mirpur | 119 | 16:00 | TK | 25 | 23:00
Cumilla(N) | 131 | 20:00 | Mirsorai | N/A | N/A | Tongi | 116 | 15:00
Cumilla(S) | 139 | 15:00 | Mithapukur | 28 | 09:00 | Ullon | 32 | 19:00
Daudkandi | 120 | 22:00 | Modern | 0 | 00:00 | Uttara | 84 | 15:00
Dhaka | 34 | 13:00 | Mogbazar | 114 | 14:00 | UttaraNew | 15 | 12:00
Dhamrai | 114 | 15:00 | Mongla | 30 | 16:00 | Zigatola | 39 | 15:00
Dhanmondi | 134 | 13:00 | Motijheel | 36 | 14:00
Dohazari | 86 | 20:00 | Munshiganj | 92 | 23:00
Faridpur | 130 | 22:00 | Mymensingh | 208 | 20:00
Fatullah | 68 | 15:00 | Naogaon | 112 | 21:00
Fenchuganj | 42 | 19:30 | Narail | 48 | 19:30
Feni | 93 | 20:00 | Narinda | 65 | 13:00
Ghorashal | 57 | 00:00 | Narshingdi | 156 | 20:00
Goalpara | 27 | 13:00 | Natore | 138 | 21:00
Gollamari | 37 | 01:00 | Nawabganj | 47.3 | 21:00
Gopalganj | 104.4 | 13:00 | Netrakona | 98 | 19:30
GPH | 92 | 19:00 | New | 81 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bhulta | 397 | 22:00 | 380 | 15:00 | Kaliakoir | 398 | 20:00 | 338 | 06:00
| Bibiana | 411 | 22:00 | 402 | 05:00 | Payra | 419 | 06:00 | 407 | 23:00
| BIPTC | 400 | 04:00 | 394 | 15:00
| Gopalganj_I | 414 | 07:00 | 391 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 22:00 | 216 | 00:00 | Hathazari | 237 | 20:00 | 222 | 08:00
| AKSML | 236 | 21:00 | 215 | 07:00 | Ishurdi | 235 | 06:00 | 224 | 19:30
| Aminbazar | 228 | 23:00 | 218 | 15:00 | Jhenaidah | 232 | 18:30 | 216 | 21:00
| Baghabari | 233 | 05:00 | 226 | 12:00 | Kaliakoir | 229 | 06:00 | 218 | 15:00
| Barapukuria | 226 | 03:00 | 212 | 20:00 | Keranigonj | 225 | 22:00 | 216 | 00:00
| Barishal | 241 | 18:30 | 231 | 23:00 | Khulna(S) | 240 | 16:00 | 216 | 02:00
| Bheramara | N/A | N/A | N/A | N/A | Maniknagar | 229 | 22:00 | 219 | 15:00
| Bhulta | 231 | 22:00 | 220 | 15:00 | Meghnaghat | 230 | 00:00 | 222 | 13:00
| Bibiana | 239 | 22:00 | 233 | 00:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 18:30 | 221 | 20:00 | Rajshahi | 233 | 19:00 | 219 | 23:00
| Bogura | 231 | 05:00 | 219 | 20:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 15:00 | 238 | 22:00 | Rampura | 229 | 22:00 | 218 | 15:00
| BSRM | 233 | 19:30 | 222 | 07:00 | Shikalbaha | 238 | 19:30 | 221 | 08:00
| Cumilla(N) | 230 | 20:00 | 224 | 11:00 | Shyampur | 226 | 22:00 | 217 | 15:00
| Fenchuganj | 242 | 22:00 | 236 | 01:00 | Siddhirganj | 230 | 22:00 | 221 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 231 | 06:00 | 225 | 20:00
| GPH | 235 | 20:00 | 220 | 07:00 | Tongi | 226 | 23:00 | 216 | 00:00
| Haripur | 229 | 22:00 | 220 | 00:00
| Hasnabad | 226 | 23:00 | 217 | 00:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 04:00 | 127 | 14:00 | Manikganj | 128 | 17:00 | 122 | 00:00
| Agargaon | 134 | 22:00 | 128 | 15:00 | Maniknagar | 134 | 22:00 | 128 | 15:00
| Agrabad | 140 | 19:30 | 130 | 18:00 | Matarbari | 128 | 20:00 | 122 | 00:00
| AKS | 140 | 20:00 | 128 | 18:00 | Matuail | 133 | 22:00 | 128 | 11:00
| Aminbazar | 134 | 23:00 | 126 | 15:00 | Millgate | 134 | 22:00 | 125 | 15:00
| Amnura | 136 | 19:00 | 120 | 01:00 | Mirpur | 131 | 22:00 | 124 | 00:00
| Ashuganj | 136 | 10:00 | 134 | 01:00 | Mithapukur | 135 | 06:00 | 121 | 20:00
| Bagerhat | 137 | 16:00 | 121 | 12:00 | Modern | 140 | 20:00 | 131 | 18:00
| Bakulia | 139 | 20:00 | 130 | 08:00 | Mogbazar | 135 | 22:00 | 127 | 15:00
| Banani | 133 | 22:00 | 125 | 15:00 | Mongla | 136 | 16:00 | 121 | 12:00
| Bangabhaban | 135 | 23:00 | 128 | 15:00 | Motijheel | 135 | 23:00 | 128 | 15:00
| Barapukuria | 135 | 04:00 | 124 | 20:00 | Munshiganj | 135 | 22:00 | 129 | 00:00
| Barguna | 138 | 03:00 | 130 | 22:00 | Mymensingh | 133 | 10:00 | 125 | 03:00
| Barishal | 138 | 06:00 | 131 | 22:00 | Naogaon | 132 | 18:30 | 121 | 20:00
| Barishal | 139 | 05:00 | 132 | 22:00 | Narail | 135 | 18:30 | 123 | 19:30
| Baroaulia | 142 | 20:00 | 132 | 16:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 131 | 09:00 | 127 | 00:00 | Narshingdi | 130 | 07:00 | 122 | 19:00
| Bashundhara | 134 | 22:00 | 126 | 15:00 | Natore | 135 | 18:30 | 120 | 06:00
| BashundharaCement | 135 | 22:00 | 128 | 00:00 | Nawabganj | 135 | 22:00 | 129 | 00:00
| Beanibazar | 137 | 05:00 | 134 | 00:00 | Netrakona | 131 | 10:00 | 124 | 01:00
| Benapole | 136 | 16:00 | 124 | 21:00 | New | 133 | 22:00 | 127 | 11:00
| Bhaluka | 130 | 11:00 | 120 | 16:00 | Niamatpur | 133 | 08:00 | 118 | 20:00
| Bhandaria | 137 | 10:00 | 126 | 22:00 | Noapara | 137 | 16:00 | 127 | 21:00
| Bhangura | 138 | 05:00 | 131 | 20:00 | Pabna | 135 | 05:00 | 128 | 21:00
| Bheramara | N/A | N/A | N/A | N/A | Palashbari | 133 | 06:00 | 119 | 20:00
| Bheramara(GK) | 139 | 06:00 | 132 | 19:30 | Panchagarh | 135 | 15:00 | 114 | 20:00
| Bhulta | 125 | 19:00 | 120 | 00:00 | Patuakhali | 137 | 05:00 | 131 | 23:00
| Bog-Sherpur | 134 | 06:00 | 126 | 20:00 | Payra | 139 | 06:00 | 133 | 23:00
| Bogura | 137 | 18:30 | 128 | 20:00 | PHP | 131 | 19:00 | 127 | 00:00
| Bogura | 136 | 05:00 | 128 | 20:00 | Purbachal | 133 | 23:00 | 124 | 15:00
| Brahmanbaria | 132 | 06:00 | 128 | 00:00 | Purbasadipur | 135 | 15:00 | 116 | 20:00
| Cantonment | 133 | 22:00 | 126 | 15:00 | Rahim | 134 | 22:00 | 129 | 00:00
| Chandpur | 138 | 16:00 | 132 | 04:00 | Rajbari | 136 | 06:00 | 125 | 23:00
| Chandraghona | 140 | 20:00 | 132 | 18:00 | Rajendrapur | 128 | 14:00 | 119 | 04:00
| Chapai | 135 | 19:00 | 123 | 00:00 | Rajshahi | 132 | 18:30 | 120 | 00:00
| Charsaidpur | 135 | 22:00 | 129 | 00:00 | Rajshahi | 133 | 19:00 | 120 | 02:00
| Chauddagram | 132 | 18:30 | 128 | 00:00 | Ramganj | 134 | 15:00 | 128 | 00:00
| Chhatak | 137 | 16:00 | 134 | 14:00 | Rampur | 138 | 19:30 | 131 | 18:00
| Chowmuhani | 130 | 18:00 | 125 | 00:00 | Rampura | 134 | 22:00 | 127 | 15:00
| Chuadanga | 131 | 18:00 | 118 | 21:00 | Rangamati | 138 | 19:30 | 133 | 06:00
| Coxsbazar | 128 | 11:00 | 120 | 23:00 | Rangpur | 131 | 18:00 | 116 | 20:00
| Cumilla(N) | 134 | 20:00 | 130 | 00:00 | Ruppur | 136 | 06:00 | 130 | 23:00
| Cumilla(S) | 135 | 05:00 | 129 | 00:00 | Saidpur | 133 | 05:00 | 120 | 20:00
| Daudkandi | 131 | 19:00 | 127 | 00:00 | Satkhira | 134 | 00:00 | 121 | 21:00
| Dhaka | 134 | 22:00 | 127 | 14:00 | Satmasjid | 134 | 22:00 | 127 | 15:00
| Dhamrai | 131 | 22:00 | 125 | 15:00 | Savar | 133 | 22:00 | 123 | 00:00
| Dhanmondi | 133 | 19:30 | 128 | 15:00 | Shahjadpur | 140 | 06:00 | 133 | 19:30
| Dohazari | 136 | 19:30 | 130 | 00:00 | Shahjibazar | 135 | 06:00 | 131 | 00:00
| Faridpur | 136 | 06:00 | 127 | 23:00 | Shahmirpur | 140 | 20:00 | 132 | 01:00
| Fatullah | 134 | 22:00 | 128 | 00:00 | Shariatpur | 138 | 06:00 | 128 | 22:00
| Fenchuganj | 139 | 17:00 | 135 | 01:00 | Sherpur | 137 | 11:00 | 122 | 07:00
| Feni | 132 | 20:00 | 127 | 00:00 | Shikalbaha | 140 | 20:00 | 132 | 07:00
| Ghorashal | 137 | 00:00 | 134 | 15:00 | Shikalbaha | 140 | 19:30 | 132 | 08:00
| Goalpara | 136 | 19:00 | 125 | 12:00 | Shitalakhya | 135 | 22:00 | 128 | 00:00
| Gollamari | 138 | 15:00 | 127 | 23:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gopalganj | 138 | 14:00 | 128 | 23:00 | Shyampur | 132 | 22:00 | 127 | 15:00
| Gopalganj_I | 140 | 06:00 | 131 | 23:00 | Shyampur | 133 | 22:00 | 127 | 15:00
| Gulshan | 134 | 22:00 | 126 | 15:00 | Siddhirganj | 134 | 22:00 | 128 | 00:00
| Halishahar | 139 | 19:30 | 131 | 18:00 | Sirajganj | 135 | 04:00 | 127 | 20:00
| Haripur | 134 | 22:00 | 129 | 00:00 | Sonargaon | 133 | 00:00 | 130 | 04:00
| HaripurSBU | 135 | 22:00 | 129 | 00:00 | Sreemongol | 138 | 04:00 | 134 | 00:00
| Hasnabad | 135 | 19:30 | 130 | 15:00 | Srinagar | 135 | 22:00 | 130 | 00:00
| Hathazari | 138 | 19:30 | 132 | 06:00 | SSM | 142 | 20:00 | 132 | 18:30
| Ishurdi | 137 | 18:30 | 131 | 19:30 | Sunamganj | 136 | 16:00 | 135 | 15:00
| Jaldhaka | 133 | 06:00 | 119 | 22:00 | Sylhet | 136 | 05:00 | 134 | 00:00
| Jamalpur | 138 | 11:00 | 125 | 06:00 | Tangail | 133 | 10:00 | 127 | 19:30
| Jashore | 135 | 17:00 | 126 | 01:00 | Thakurgaon | 137 | 15:00 | 111 | 20:00
| Jhenaidah | 136 | 16:00 | 127 | 19:30 | TK | 140 | 19:30 | 133 | 17:00
| Jhenaidah | 137 | 18:30 | 127 | 19:30 | Tongi | 134 | 21:00 | 128 | 15:00
| Joydebpur | 140 | 13:00 | 130 | 16:00 | Ullon | 133 | 05:00 | 126 | 15:00
| Joypurhat | 133 | 18:30 | 120 | 20:00 | Uttara | 132 | 23:00 | 124 | 15:00
| Juldah | 140 | 19:30 | 133 | 04:00 | UttaraNew | 133 | 22:00 | 125 | 00:00
| Kabirpur | 130 | 18:30 | 121 | 15:00 | Zigatola | 135 | 23:00 | 129 | 13:00
| Kachua | 135 | 18:30 | 130 | 01:00
| Kaliakoir | 131 | 12:00 | 127 | 01:00
| Kallyanpur | 133 | 22:00 | 125 | 15:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 364 | 8247 | 3715 | 11962 |  |  |  | QF-LDC-11
0:30 | 189 | 7627 | 3374 | 11001 | Date: | 2022-06-20
1:00 | 14 | 7007 | 3033 | 10040
1:30 | 51 | 6921 | 3016.5 | 9937.5
2:00 | 88 | 6835 | 3000 | 9835
2:30 | 78 | 6788 | 2982 | 9770 | [5 empty] | Gen. at Eve. Peak | 12439 | 12439 MW (21:00 )
3:00 | 68 | 6741 | 2964 | 9705 | [6 empty] | 21:00
3:30 | 55 | 6610 | 2941.5 | 9551.5 | [5 empty] | Gen. at Day Peak | 10336 | 10336 MW (12:00 )
4:00 | 42 | 6479 | 2919 | 9398 | [6 empty] | 12:00
4:30 | 38 | 6351 | 2919.5 | 9270.5 | [5 empty] | Highest Generation | 12439
5:00 | 34 | 6223 | 2920 | 9143 | [6 empty] | 21:00
5:30 | 150 | 5949 | 2915.5 | 8864.5
6:00 | 266 | 5675 | 2911 | 8586
6:30 | 259 | 5713 | 2919.5 | 8632.5
7:00 | 252 | 5751 | 2928 | 8679
7:30 | 296 | 5754 | 2961.5 | 8715.5
8:00 | 340 | 5757 | 2995 | 8752
8:30 | 365 | 5930 | 3017 | 8947
9:00 | 390 | 6103 | 3039 | 9142
9:30 | 330 | 6322 | 3038 | 9360
10:00 | 270 | 6541 | 3037 | 9578
10:30 | 265 | 6659 | 3077 | 9736
11:00 | 260 | 6777 | 3117 | 9894
11:30 | 170 | 7001 | 3114 | 10115
12:00 | 80 | 7225 | 3111 | 10336
12:30 | 100 | 7322.5 | 3189 | 10511.5
13:00 | 120 | 7420 | 3267 | 10687
13:30 | 120 | 7407 | 3223.5 | 10630.5
14:00 | 120 | 7394 | 3180 | 10574
14:30 | 165 | 7486.5 | 3243.5 | 10730
15:00 | 210 | 7579 | 3307 | 10886
15:30 | 220 | 7441.5 | 3291.5 | 10733
16:00 | 230 | 7304 | 3276 | 10580
16:30 | 205 | 7209 | 3203 | 10412
17:00 | 180 | 7114 | 3130 | 10244
17:30 | 165 | 7078 | 3048.5 | 10126.5
18:00 | 150 | 7042 | 2967 | 10009
18:30 | 80 | 7409.5 | 3140 | 10549.5
19:00 | 10 | 7777 | 3313 | 11090
19:30 | 140 | 8531 | 3885 | 12416
20:00 | 260 | 8550 | 3842 | 12392 |  |  |  | Executive Engineer
20:30 | 250 | 8489 | 3926.5 | 12415.5 |  |  |  | Network Operation Division
21:00 | 240 | 8428 | 4011 | 12439
21:30 | 236 | 8369.5 | 4022 | 12391.5
22:00 | 232 | 8311 | 4033 | 12344 |  |  |  |  | Page 6 of 7
22:30 | 278 | 8286.5 | 3925 | 12211.5
23:00 | 324 | 8262 | 3817 | 12079
23:30 | 344 | 8254.5 | 3766 | 12020.5
24:00 | 364 | 8247 | 3715 | 11962
12439 MW (21:00 )
10336 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-20 |  | Energy |  | 252895303
[13 empty] | 2022-06-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4347 | 924 | 2215 | 0 | 3475 | 735 | 105 | 0 | 53 | 108 | 0 | 0
0:30 | 4310 | 924 | 2164.5 | 0 | 2742.5 | 630 | 102.5 | 0 | 26.5 | 101 | 0 | 0 | Date: | 2022-06-20
1:00 | 4273 | 924 | 2114 | 0 | 2010 | 525 | 100 | 0 | 0 | 94 | 0 | 0
1:30 | 4276 | 923.5 | 2097 | 0 | 1920.5 | 525 | 101.5 | 0 | 0 | 94 | 0 | 0 | [8 empty] | Total Energy | 252.8953 | Total Energy Gen 252.895 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.895 MKWHr
2:00 | 4279 | 923 | 2080 | 0 | 1831 | 525 | 103 | 0 | 0 | 94 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4270 | 923.5 | 2050.5 | 0 | 1803.5 | 525 | 103.5 | 0 | 0 | 94 | 0 | 0 | [8 empty] | Energy Requirement | 252.8953
3:00 | 4261 | 924 | 2021 | 0 | 1776 | 525 | 104 | 0 | 0 | 94 | 0 | 0
3:30 | 4251.5 | 923 | 2032.5 | 0 | 1624.5 | 525 | 104 | 0 | 0 | 91 | 0 | 0 | [6 empty] | Shortage
4:00 | 4242 | 922 | 2044 | 0 | 1473 | 525 | 104 | 0 | 0 | 88 | 0 | 0
4:30 | 4233.5 | 922.5 | 2036 | 0 | 1363.5 | 525 | 104 | 0 | 0 | 86 | 0 | 0
5:00 | 4225 | 923 | 2028 | 0 | 1254 | 525 | 104 | 0 | 0 | 84 | 0 | 0
5:30 | 4073 | 923 | 2027 | 0 | 1130.5 | 525 | 104 | 0 | 0 | 81 | 1 | 0
6:00 | 3921 | 923 | 2026 | 0 | 1007 | 525 | 104 | 0 | 0 | 78 | 2 | 0
6:30 | 3959.5 | 923 | 2045.5 | 0 | 997 | 525 | 102 | 0 | 0 | 76 | 4.5 | 0 |  |  |  |  | Coal
7:00 | 3998 | 923 | 2065 | 0 | 987 | 525 | 100 | 0 | 0 | 74 | 7 | 0
7:30 | 3972 | 923 | 2088 | 0 | 1018 | 525 | 100 | 0 | 0 | 79 | 10.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3946 | 923 | 2111 | 0 | 1049 | 525 | 100 | 0 | 0 | 84 | 14 | 0
8:30 | 3948.5 | 923 | 2114 | 0 | 1211.5 | 525 | 100 | 0 | 0 | 88 | 37 | 0
9:00 | 3951 | 923 | 2117 | 0 | 1374 | 525 | 100 | 0 | 0 | 92 | 60 | 0
9:30 | 3912.5 | 923.5 | 2095 | 0 | 1625 | 525 | 101 | 0 | 0 | 96 | 82 | 0
10:00 | 3874 | 924 | 2073 | 0 | 1876 | 525 | 102 | 0 | 0 | 100 | 104 | 0
10:30 | 3883 | 923.5 | 2121.5 | 0 | 1998 | 529.5 | 102 | 0 | 0 | 100 | 78.5 | 0
11:00 | 3892 | 923 | 2170 | 0 | 2120 | 534 | 102 | 0 | 0 | 100 | 53 | 0
11:30 | 3942 | 923.5 | 2150 | 0 | 2290.5 | 549.5 | 102.5 | 0 | 5 | 102 | 50 | 0
12:00 | 3992 | 924 | 2130 | 0 | 2461 | 565 | 103 | 0 | 10 | 104 | 47 | 0
12:30 | 3999.5 | 923.5 | 2145.5 | 0 | 2588.5 | 565 | 103.5 | 0 | 21 | 105 | 60 | 0
13:00 | 4007 | 923 | 2161 | 0 | 2716 | 565 | 104 | 0 | 32 | 106 | 73 | 0
13:30 | 4007 | 923 | 2161 | 0 | 2716 | 565 | 104 | 0 | 32 | 106 | 73 | 0
14:00 | 4007 | 923 | 2161 | 0 | 2716 | 565 | 104 | 0 | 32 | 106 | 73 | 0
14:30 | 4102 | 923 | 2135.5 | 0 | 2797.5 | 530 | 104.5 | 0 | 24.5 | 111 | 58.5 | 0
15:00 | 4197 | 923 | 2110 | 0 | 2879 | 495 | 105 | 0 | 17 | 116 | 44 | 0
15:30 | 4107 | 923.5 | 2081.5 | 0 | 2848.5 | 495 | 105 | 0 | 17 | 108 | 47.5 | 0
16:00 | 4017 | 924 | 2053 | 0 | 2818 | 495 | 105 | 0 | 17 | 100 | 51 | 0
16:30 | 3947 | 924 | 2031.5 | 0 | 2717.5 | 485 | 105 | 0 | 17 | 99 | 51 | 0
17:00 | 3947 | 924 | 2010 | 0 | 2617 | 475 | 105 | 0 | 17 | 98 | 51 | 0
17:30 | 3912 | 923.5 | 1986 | 0 | 2566.5 | 475 | 106.5 | 0 | 25.5 | 100 | 31.5 | 0
18:00 | 3877 | 923 | 1962 | 0 | 2516 | 475 | 108 | 0 | 34 | 102 | 12 | 0
18:30 | 3950.5 | 923 | 1999.5 | 0 | 2763.5 | 510 | 106.5 | 0 | 184.5 | 106 | 6 | 0
19:00 | 4024 | 923 | 2037 | 0 | 3011 | 545 | 105 | 0 | 335 | 110 | 0 | 0
19:30 | 4172 | 924 | 2211 | 0 | 3745 | 675 | 105 | 0 | 472 | 112 | 0 | 0
20:00 | 4196 | 923 | 2103 | 0 | 3791 | 695 | 103 | 0 | 473 | 108 | 0 | 0
20:30 | 4274 | 923.5 | 2142 | 0 | 3753.5 | 705 | 103.5 | 0 | 405 | 109 | 0 | 0
21:00 | 4352 | 924 | 2181 | 0 | 3716 | 715 | 104 | 0 | 337 | 110 | 0 | 0
21:30 | 4336.5 | 924 | 2177 | 0 | 3699 | 730 | 103.5 | 0 | 312.5 | 109 | 0 | 0
22:00 | 4321 | 924 | 2173 | 0 | 3682 | 745 | 103 | 0 | 288 | 108 | 0 | 0
22:30 | 4309 | 924 | 2214 | 0 | 3631.5 | 745 | 103.5 | 0 | 178.5 | 106 | 0 | 0
23:00 | 4297 | 924 | 2255 | 0 | 3581 | 745 | 104 | 0 | 69 | 104 | 0 | 0
23:30 | 4322 | 924 | 2235 | 0 | 3528 | 740 | 104.5 | 0 | 61 | 106 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.1° C
24:00 | 4347 | 924 | 2215 | 0 | 3475 | 735 | 105 | 0 | 53 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 252.895 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.895 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 70 | 73 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 72 | 72 | 73 | 74 | 75 | 75 | 75 | 75 | 78 |  | 75 | 75 | 73 | 74 | 73 | 74 | 75 | 1765347
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 736000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 3 | 17 | 24 | 25 | 25 | 25 | 0 | 175510
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 1 | 4 | 8 | 2 | 6 |  | 4 | 3 | 2 | 1 | 0 | [8 empty] | 33480
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 0 |  |  |  | 71951
12 | Hathazari 100 MW peaking PP | [12 empty] | 16 | 17 | 17 | 17 | 17 | 17 |  | 32 | 32 | 32 | 0 |  |  |  | 149136
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 51 | 51 | 34 | 34 | 34 | 57 | 68 | 68 | 82 | 85 | 88 | 97 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2096763
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [11 empty] | 10 | 16 | 0 |  |  |  | 0 |  | 25 | 37 | 42 | 0 |  |  | 0 | 64432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [22 empty] | 47 | 37 | 39 | 95 | 178000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 280 | 333 | 335 | 335 | 335 | 270 | 240 | 240 |  | 240 | 335 | 335 | 335 | 335 | 335 | 335 | 7462458
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 0 | [6 empty] | 12 | 47 | 95 | 178 | 270 | 275 | 260 | 255 | 248 | 260 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 3618108
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 92 | 92 | 92 | 92 | 92 | 92 | 97 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2074181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 35 | 35 | 35 | 32 | 34 | 31 | 34 | 34 |  | 37 | 37 | 37 | 37 | 37 | 37 | 34 | 802512
33 | Ashuganj 225 MW CCPP | 213 | 213 | 215 | 216 | 216 | 214 | 213 | 214 | 213 | 213 | 214 | 213 | 212 | 182 | 183 | 182 | 182 | 194 |  | 214 | 215 | 216 | 216 | 216 | 214 | 215 | 5046000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 310 | 310 | 270 | 315 | 290 | 310 | 295 | 290 | 295 | 295 | 275 | 300 | 275 | 275 | 280 |  | 305 | 275 | 280 | 300 | 300 | 300 | 300 | 7215000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 300 | 275 | 310 | 290 | 305 | 295 | 290 | 295 | 295 | 280 | 330 | 280 | 280 | 285 |  | 310 | 280 | 280 | 330 | 330 | 330 | 330 | 7697300
| Ashuganj 420 MW CCPP(East) | [14 empty] | 0 | 10 | [10 empty] | 2327
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 52 | 49 | 50 | 50 | 53 | 54 | 53 | 54 | 51 | 53 | 53 |  | 55 | 55 | 56 | 53 | 55 | 56 | 55 | 1279680
36 | Chandpur 150 MW CCPP | 136 | 137 | 136 | 136 | 136 | 136 | 136 | 135 | 136 | 136 | 135 | 136 | 135 | 137 | 136 | 136 | 135 | 135 |  | 136 | 136 | 136 | 135 | 136 | 136 | 135 | 3237460
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 404 | 403 | 402 | 402 | 401 | 402 | 402 | 402 | 402 | 402 | 421 | 415 | 412 | 409 | 414 | 421 | 417 |  | 417 | 421 | 420 | 420 | 423 | 421 | 418 | 9967610
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 |  | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 9298000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 184 | 192 | 192 | 193 | 192 | 192 | 187 | 181 | 167 | 158 | 159 | 151 | 148 | 137 | 143 | 154 | 155 | 154 |  | 160 | 161 | 163 | 163 | 163 | 163 | 160 | 3923520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 1 | 2 | 6 | 7 | 3 | 30 | 54 | 19 | 19 | 9 | 11 | 3 |  | 0 | [6 empty] | 158690
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 43 | 43 | 44 | 44 |  | 44 | 43 | 43 | 44 | 43 | 43 | 43 | 1032000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 0 | [22 empty] | 114224
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 65 | 65 | 63 | 65 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 40 | 40 | 40 |  | 40 | 61 | 40 | 62 | 40 | 40 | 40 | 1306560
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 81 | 40 |  | 84 | 81 | 81 | 84 | 84 | 84 | 84 | 1896000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3069590
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [14 empty] | 0 | 5 | 8 | 13 |  | 16 | 17 | 17 | 18 | 21 | 21 | 21 | 118020
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178380
54 | Hobiganj 11MW PP Cofidence-E |  |  | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235206
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 53 | 53 | 53 | 53 | 50 | 51 | 1242000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 167472
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 280 | 275 | 285 | 270 | 290 | 290 | 300 | 290 | 290 | 280 | 290 | 280 | 300 | 290 | 270 | 290 |  | 290 | 285 | 290 | 285 | 270 | 280 | 295 | 7057000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 220 | 317 | 400 | 400 | 398 | 360 |  | 400 | 400 | 400 | 400 | 400 | 401 | 400 | 8072100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 0 |  |  | 2 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 964065
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 22 |  | 22 | 22 | 22 | 18 | 20 | 19 | 24 | 529200
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 523344
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 418212
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 441504
63 | Impoprt (Tripura) | 94 | 94 | 94 | 88 | 84 | 78 | 74 | 84 | 92 | 100 | 100 | 104 | 106 | 104 | 116 | 100 | 98 | 102 |  | 110 | 112 | 108 | 110 | 108 | 104 | 108 | 2329920
64 | Malancha, Ctg. EPZ (United) | 38 | 31 | 31 | 37 | 39 | 37 | 36 | 8 | 3 | 2 | 2 | 2 | 7 | 4 | 2 | 2 | 6 | 7 |  | 19 | 25 | 30 | 25 | 25 | 38 | 38 | 499200
65 | Feni 22MW PP (Doreen) | [21 empty] | 9 | 0 |  |  | 21 | 25920
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 11 | 11 | 11 | 213300
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 22 | 20 | 15 | 13 | 16 | 32 | 12 | 6 | 8 | 12 | 13 | 16 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 562700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 3 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 479430
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 11 | 11 |  | 11 | 17 | 20 | 20 | 20 | 20 | 20 | 413460
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806760
72 | Rupganj 33 MW PP(Summit)
73 | Ghorashal 108MW PP (Regent) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 53 | 53 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 58 | 58 | 59 | 60 | 59 | 59 | 1330863
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 37 | 31 | 28 | 29 | 29 | 28 | 29 | 29 | 29 | 28 | 29 | 29 | 28 | 29 | 29 | 35 | 95 | 96 |  | 95 | 96 | 96 | 95 | 95 | 95 | 42 | 1198680
| Manikgonj 162MW PP(MPGL) | [8 empty] | 9 | 68 | 108 | 152 | 162 | 162 | 162 | 162 | 108 | 108 |  | 112 | 162 | 162 | 162 | 162 | 162 | 162 | 2194560
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 8 | 16 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 43 | 70 | 92 | 100 | 100 | 100 | 100 | 864960
78 | Gazipur 52 MW PP | 16 | 0 | [5 empty] | 16 | 16 | 49 | 49 | 42 | 42 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 32 | 32 | 742560
79 | Kodda 150MW PP | [19 empty] | 64 | 150 | 133 | 115 | 64 | 32 | 16 | 408480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 90 | 50 | 50 | 50 | 35 | 17 | 17 | 34 | 34 | 34 | 34 | 70 | 70 | 50 | 50 | 50 | 50 | 50 |  | 70 | 90 | 95 | 105 | 105 | 105 | 105 | 1492800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 | 5 | 3 | 4 | 1 | 1 | 1 | 0 | [9 empty] | 24121
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 30 | 35 | 888962
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 51 | 51 | 34 | 34 | 34 | 40 | 94 | 108 | 110 | 110 | 110 | 110 | 110 | 68 | 68 |  | 74 | 110 | 104 | 110 | 110 | 110 | 110 | 2239772
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 285 | 274 | 255 | 270 | 252 | 275 | 295 | 285 | 290 | 275 | 280 | 275 | 275 | 280 | 265 | 275 | 275 | 295 |  | 305 | 275 | 250 | 260 | 255 | 276 | 252 | 6630691
87 | Meghnaghat 100 MW(IEL) | 78 | 77 | 77 | 77 | 77 | 78 | 70 | 72 | 75 | 67 | 61 | 66 | 71 | 73 | 78 | 72 | 70 | 72 |  | 75 | 79 | 79 | 62 | 66 | 79 | 85 | 1766400
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 85 | 54 | 35 | 35 | 34 | 36 | 56 | 92 | 92 | 93 | 89 | 90 | 93 | 93 | 70 |  | 57 | 93 | 90 | 92 | 94 | 93 | 93 | 1937280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 20 | 60 | 80 | 70 | 70 | 80 | 80 | 30 | 30 | 30 |  | 70 | 80 | 80 | 50 | 50 | 50 | 50 | 1110360
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 47 | 50 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1154088
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1184238
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 7 | 7 | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 788688
95 | Patenga 50MW PP (Baraka) | 42 | 45 | 45 | 45 | 45 | 31 | 31 | 33 | 45 | 45 | 45 | 44 | 44 | 44 | 39 | 39 | 39 | 45 |  | 45 | 44 | 44 | 44 | 44 | 45 | 44 | 1028160
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 12 | 45 | 54 | 0 |  |  |  | 76800
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 55 | 55 | 40 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1314308
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 0 |  |  |  | 17 | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 907435
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2707936
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 8250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 49 | 54 | 54 | 35 | 47 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1276560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 140 | 140 | 140 | 140 | 85 | 45 | 45 | 50 | 65 | 84 | 108 | 160 | 180 | 200 | 200 | 160 | 160 | 120 |  | 137 | 185 | 193 | 184 | 184 | 174 | 164 | 3374400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 50 | 50 | 37 | 0 |  |  | 2 | 17 | 30 | 88 | 107 | 107 | 101 | 115 | 119 | 115 | 122 | 117 |  | 112 | 100 | 98 | 104 | 114 | 132 | 134 | 1905264
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 50 | 50 | 30 | 30 | 30 | 75 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 60 | 20 |  | 76 | 76 | 76 | 76 | 90 | 90 | 90 | 1728960
116 | Chandpur 200MW (Desh energy) | 145 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 105 | 155 |  | 157 | 200 | 200 | 200 | 200 | 200 | 200 | 2589120
117 | Ashuganj 150MW PP (Midland) | 90 | 90 | 90 | 90 | 90 | 30 | 30 | 30 | 40 | 78 | 135 | 142 | 140 | 143 | 138 | 142 | 142 | 140 |  | 142 | 145 | 143 | 145 | 145 | 147 | 140 | 2714836
118 | Bibiyana-III 400 MW CCPP | 401 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 401 | 402 | 402 | 402 | 401 | 401 | 402 | 360 | 364 |  | 401 | 400 | 400 | 400 | 400 | 401 | 400 | 9544000
| Jamalpur 115 MW PP (United) | [8 empty] | 8 | 8 | 12 | 24 | 24 | 24 | 38 | 54 | 32 | 32 |  | 42 | 104 | 106 | 106 | 106 | 106 | 106 | 856800
| Anwara 300 MW PP (United) | [9 empty] | 15 | 15 | 45 | 45 | 15 | 15 | 15 | 15 | 15 |  | 100 | 250 | 265 | 230 | 190 | 135 | 135 | 1287164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 98 | 50 | 45 | 30 | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 20 |  | 29 | 100 | 100 | 100 | 100 | 100 | 100 | 2034240
| Anlima Energy Ltd. | 90 | 90 | 90 | 87 | 51 | 34 | 34 | 34 | 73 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 108 | 108 | 108 | 92 | 92 | 108 | 2032363
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 0 | 16 | 10 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438840
Spectra Solar Plant Ltd.
| Chandpur 115(Doreen) | 100 | 101 | 100 | 100 | 100 | 101 | 101 | 100 | 101 | 100 | 101 | 100 | 96 | 93 | 101 | 101 | 101 | 101 |  | 101 | 102 | 100 | 101 | 100 | 100 | 100 | 2416320
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 34 | 34 | 34 | 39 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1270080
120 | Eastern Zone Total | 7007 | 6835 | 6741 | 6479 | 6223 | 5675 | 5751 | 5757 | 6103 | 6541 | 6777 | 7225 | 7420 | 7339 | 7524 | 7249 | 7059 | 6987 |  | 7722 | 8476 | 8495 | 8373 | 8311 | 8262 | 8247 | 172565371
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 45 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 35 | 45 | 45 |  | 93 | 93 | 94 | 93 | 93 | 80 | 80 | 1121280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 17 |  | 37 | 45 | 39 | 39 | 39 |  |  | 163680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 17 | 70 | 70 | 70 | 70 | 35 | 17 |  | 35 | 93 | 93 | 93 | 93 | 93 | 93 | 871680
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 5 | 7 | 42 | 77 | 33 | 3 | 5 | 12 | 17 | 33 | 36 | 8 |  | 0 | [6 empty] | 267840
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 165 | 165 | 163 | 164 | 165 | 165 | 164 | 184 | 184 | 184 | 223 | 223 | 223 | 202 | 203 | 204 | 173 | 173 |  | 173 | 227 | 228 | 227 | 228 | 226 | 226 | 4834873
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 |  |  | 0 | 42432
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 87 | 87 | 86 | 84 | 85 | 85 | 87 | 87 | 87 | 87 | 87 |  | 84 | 87 | 87 | 87 | 87 | 87 | 87 | 2010800
140 | Bhola 33 MW PP (Venture) | 18 | 23 | 21 | 22 | 19 | 17 | 15 | 15 | 15 | 16 | 20 | 18 | 19 | 10 | 15 | 16 | 16 | 17 |  | 21 | 22 | 26 | 26 | 27 | 27 | 26 | 455700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 32 | 32 | 32 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 340875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 924 | 923 | 924 | 922 | 923 | 923 | 923 | 923 | 923 | 924 | 923 | 924 | 923 | 923 | 923 | 924 | 924 | 923 |  | 923 | 924 | 923 | 924 | 924 | 924 | 924 | 22333090
147 | Bheramara 410 MW CCPP | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 320 | 310 | 315 | 315 |  | 324 | 325 | 325 | 320 | 315 | 305 | 295 | 8032896
148 | Payra 1320 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 360 | 390 | 390 | 360 | 320 | 320 | 300 | 300 |  | 370 | 500 | 520 | 540 | 570 | 570 | 560 | 10393400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 174 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4290500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [21 empty] | 18 | 26 | 26 |  |  | 69499
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 2 | 3 | 3 | 4 | 3 | 1 | 3 | 1 | 1 | 0 | [8 empty] | 31140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 169 | 146 | 159 | 172 | 211 | 212 | 211 | 213 | 213 | 206 |  | 160 | 193 | 204 | 214 | 212 | 197 | 193 | 4706964
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 181 | 174 | 174 | 175 | 176 | 183 | 181 | 189 | 178 | 188 | 191 | 177 | 180 | 186 | 174 | 193 | 130 |  | 130 | 175 | 190 | 211 | 211 | 212 | 209 | 4697600
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 370 | 349 | 323 | 328 | 329 | 320 | 332 | 370 | 370 | 367 | 414 | 380 | 390 | 340 | 370 | 309 | 304 | 250 |  | 250 | 395 | 296 | 373 | 377 | 420 | 390 | 8471527
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 22 | 22 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 478560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201240
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 16 | 34 | 34 | 34 | 34 |  | 0 | 130865
167 | Katakhali 50 MW Peaking PP | [19 empty] | 14 | 32 | 32 | 32 | 32 |  |  | 88237
168 | Santahar 50 MW Peaking PP | [19 empty] | 24 | 36 | 38 | 37 | 37 | 37 | 37 | 179162
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 88 | 89 | 88 | 88 | 90 |  | 0 | 338272
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 50 | 57 | 76 | 50 | 50 |  | 54 | 80 | 92 | 94 | 94 | 94 | 94 | 1425600
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 50 | 95 | 113 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1681632
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 49 | 49 | 55 | 67 | 78 | 70 |  | 81 | 86 | 86 | 86 | 93 | 94 | 76 | 1295577
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 3 | 4 | 5 | 6 |  | 6 | 3 |  | 4 | 2 | 1 |  | 0 | [6 empty] | 35427
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 108 | 108 | 72 | 72 |  | 72 | 72 | 52 | 90 | 90 | 90 | 72 | 1339584
178