## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-24 | Friday
|  |  | Date (day): | 2022-06-24 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13558.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14967 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-23 | 2022-06-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 81 | 80 | 80 |  | 28 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 410 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas line problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 400 | 400 | 50 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 80 | 88 | 80 | 88 |  | 12 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 300 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 80 | 70 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 337 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 94 | 85 | 95 |  | 7 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 45 | 51 | 51 |  | 29 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 268 | 285 | 285 | 285 |  | 10 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 122 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 86 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 80 | 25 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 118 | 112 | 135 | 135 |  | 14 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 94 | 94 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 156 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 12 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3091 | 3552 | 3728 | 3891 | 671 | 1255
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 37 | 44 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 79 | 81 | 123 | 123 |  | 107 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI |  | 2022-06-24
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 43 | 0 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 50 | 30 | 54 | 54 |  | 46 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 63 | 83 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 25 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 62 | 80 | 92 |  | 16 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 220 | 265 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 35 | 35 |  | 19 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 50 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 75 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 828 | 1188 | 1278 | 1422 | 311 | 652
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 200 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 355 | 300 | 355 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 335 | 300 | 335 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 299 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 33 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 51 | 52 | 52
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 110 | 150 | 150 | 150 | 45 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 143 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 32 | 49 |  | 3 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 136 | 135 | 135 |  | 28 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 117 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 19 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 156 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 95 | 38 | 94 | 19 |  | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 108 | 116 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 2004 | 2189 | 2077 | 2422 | 364 | 68
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 147 | 154 | 160 | 170 | 32 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 170 | 181 | 180 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 32 | 96 | 107 | 107 |  | 8 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 439 | 475 | 542.6 | 521 | 32 | 16
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 21 | 42 | 42 | 42 |  | 48 | Under maintenance
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 31 | 51 | 51
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 30 | 50 | 50
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 56 | 65 | 65
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 38 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 25 | 25 | 25 | 25
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 315 | 320 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1591 | 1692 | 1748 | 1769 | 330 | 338
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 923 | 940 | 940
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 33 | 103 | 97 | 103 |  | 12 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42 |  | 12 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 305 | 350 | 350 | 60 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 70 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 76 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 70 | 89 |  | 16 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1428 | 1574 | 1690 | 2037 | 60 | 101
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 |  |  | Rampal Transformar O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 27 | 20 | 25
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 83 | 87 | 87 | 107 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 540 | 622 | 622 |  | 622 | Unit-2 S/D
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 222 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 729 | 905 | 1000 | 1005 | 107 | 622
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 29 | 0 | 0 |  | 71 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 175 | 180 | 210 | 10 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 212 | 192 | 200 | 210 | 10 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 351 | 416 | 414 | 414 |  |  | FGMO
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 190 |  | 10 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 94 | 94 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 928 | 1245 | 1134 | 1492 | 453 | 178
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 68 | 91 | 70 | 100 |  | 13 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 50 | 108 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 300 | 374 | 361 | 408 | 269 | 20
|  | Total |  |  |  |  | 22348 | 21396 | 11338 | 13194 | 13558.6 | 14967 | 2597 | 3250
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10941.1872 | 12732.23 | 13084.0696 | 14443.1777
| A. |  | 2022-06-23 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 13212 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9732 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13194 | MW
| 3 | Day peak Generation : |  |  | 11338 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12732.23 | MW
| 4 | Evening peak Generation : |  |  | 13194 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 287.9724 | MKWHr | By Solar | 1.2027 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 155.99 | MKWHr |  | By Oil: | 86.1076 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.4412 | MKWHr |  | By Hydro: | 2.6262 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2597 | MW | Dhaka | 4775.28 | 4775.28 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3250 | MW | Chittagong | 1292.95 | 1292.95 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5847 | MW | Khulna | 1590.8 | 1590.8 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1168.43 | MMCFD |  |  | Rajshahi | 1291.3 | 1291.3 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 176990043.53 | ii) Oil : | Taka | 1127754666.76 | Comilla | 1146 | 1146 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 132209520 | Total | Taka | 1436954230.29 | Mymensingh | 1023 | 1023 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.979 | MKWHr. | Sylhet | 414 | 414 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -162 | MW (E to W) at | 19:30 | hrs | Barisal | 358.9 | 358.9 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -248 | MW at | 22:00 | hrs | Rangpur | 840 | 840 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 12732.23 | 12732.23 |  | 0
| B. |  | 2022-06-24 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14967 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2167 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 278.9923 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9303 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3396 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.265 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.04 |  | (b) Today: | 88.1 |  | (c) Rule Curve: |  | 82.11
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 0 |  | 0 | 420 | 285 | 81 | 0 | 55 | 335 | 0 | 0 | 100 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 30 | 0 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 54 | 67 | 44 | 22 | 38 | 0 | 0 | 0 | 330 | 305 | 182 | 110 | 136 | 35 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 138 | 164 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 51 | 86 | 0 | 120 | 0 | 25 | 9 | 270 | 16 | 11 | 0 | 293 | 0 | 0 | 181 | 0 | 116 | 0 | 90 | 68 | 123 | 402 | 107 | 105 | 105 | 0 | 266 | 54 | 110 | 0 | 37 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 925 | 0 | 280 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 28 | 16 | 0 | 0 | 0 | 34 | 0 | 38 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 203 | 0 | 425 | 93 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 530 | 228 | 0 | 0 | 0 | 0 | 90 |  | 8525 | 3803 | 12328 | 4220 | 925 | 2329 | 0 | 3647 | 705 | 115 | 0 | 249 | 138 | 0 | 0 | 86.86
2:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 409 | 0 |  | 0 | 420 | 260 | 81 | 0 | 55 | 335 | 0 | 0 | 67 | 85 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 30 | 0 | 50 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 54 | 0 | 44 | 22 | 38 | 0 | 0 | 0 | 330 | 305 | 181 | 110 | 137 | 35 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 138 | 175 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 51 | 86 | 0 | 120 | 0 | 25 | 9 | 270 | 16 | 11 | 0 | 291 | 0 | 0 | 181 | 0 | 115 | 0 | 90 | 68 | 118 | 402 | 107 | 105 | 105 | 0 | 155 | 54 | 110 | 0 | 38 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 112 | 55 | 0 |  | 925 | 0 | 280 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 88 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 9 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 204 | 0 | 428 | 93 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 510 | 227 | 0 | 0 | 0 | 0 | 72 |  | 8232 | 3649 | 11881 | 4234 | 925 | 2305 | 0 | 3350 | 685 | 115 | 0 | 129 | 138 | 0 | 0 | 86.9
3:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 0 |  | 0 | 420 | 275 | 82 | 0 | 55 | 335 | 0 | 0 | 28 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 30 | 0 | 50 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 54 | 0 | 44 | 22 | 38 | 0 | 0 | 0 | 330 | 305 | 182 | 110 | 135 | 35 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 134 | 175 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 51 | 82 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 291 | 0 | 0 | 181 | 0 | 123 | 0 | 90 | 68 | 132 | 402 | 108 | 105 | 105 | 0 | 15 | 54 | 110 | 0 | 38 | 100 | 400 | 104 | 0 | 72 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 924 | 0 | 280 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 205 | 0 | 421 | 93 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 470 | 227 | 0 | 0 | 0 | 0 | 52 |  | 7887 | 3499 | 11386 | 4232 | 924 | 2318 | 0 | 3002 | 645 | 115 | 0 | 16 | 134 | 0 | 0 | 86.94
4:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 0 |  | 0 | 420 | 300 | 81 | 0 | 55 | 335 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 0 | 50 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 54 | 0 | 44 | 22 | 38 | 0 | 0 | 0 | 330 | 305 | 182 | 110 | 136 | 35 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 130 | 178 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 52 | 81 | 0 | 120 | 0 | 25 | 9 | 270 | 15 | 11 | 0 | 195 | 0 | 0 | 181 | 0 | 134 | 0 | 90 | 68 | 137 | 401 | 108 | 105 | 105 | 0 | 0 | 54 | 110 | 0 | 38 | 100 | 400 | 104 | 0 | 17 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 924 | 0 | 295 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 206 | 0 | 428 | 35 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 450 | 227 | 0 | 0 | 0 | 0 | 52 |  | 7698 | 3427 | 11125 | 4254 | 924 | 2336 | 0 | 2741 | 625 | 115 | 0 | 0 | 130 | 0 | 0 | 86.98
5:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 0 |  | 0 | 420 | 275 | 82 | 0 | 55 | 280 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 26 | 33 | 0 | 32 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 30 | 0 | 38 | 22 | 38 | 0 | 0 | 0 | 330 | 305 | 182 | 110 | 135 | 35 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 126 | 186 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 52 | 81 | 0 | 120 | 0 | 25 | 9 | 280 | 15 | 11 | 0 | 80 | 0 | 0 | 181 | 0 | 133 | 0 | 90 | 68 | 60 | 401 | 35 | 70 | 105 | 0 | 0 | 54 | 110 | 0 | 38 | 100 | 400 | 92 | 0 | 17 | 90 | 0 | 35 | 0 | 116 | 34 | 0 |  | 924 | 0 | 295 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 206 | 0 | 427 | 17 | 0 | 94 | 0 | 69 | 0 | 0 | 113 | 470 | 227 | 0 | 0 | 0 | 0 | 52 |  | 7210 | 3432 | 10642 | 4212 | 924 | 2320 | 0 | 2292 | 645 | 123 | 0 | 0 | 126 | 0 | 0 | 87.01
6:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 0 |  | 0 | 370 | 275 | 82 | 0 | 55 | 280 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 25 | 33 | 0 | 24 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 30 | 0 | 38 | 22 | 36 | 0 | 0 | 0 | 280 | 270 | 182 | 110 | 135 | 35 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 116 | 178 | 0 | 17 | 0 | 43 | 21 | 53 | 50 | 110 | 0 | 40 | 81 | 0 | 120 | 0 | 23 | 9 | 270 | 16 | 11 | 0 | 45 | 0 | 0 | 181 | 0 | 133 | 1 | 50 | 88 | 60 | 352 | 8 | 52 | 105 | 0 | 0 | 54 | 85 | 0 | 75 | 100 | 360 | 85 | 2 | 17 | 90 | 0 | 35 | 1 | 116 | 34 | 0 |  | 923 | 0 | 305 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 160 | 0 | 340 | 17 | 0 | 70 | 0 | 42 | 0 | 0 | 70 | 470 | 163 | 0 | 0 | 0 | 7 | 34 |  | 6807 | 3109 | 9916 | 3954 | 923 | 2103 | 0 | 2041 | 645 | 123 | 0 | 0 | 116 | 11 | 0 | 87.04
7:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 409 | 0 |  | 0 | 370 | 300 | 77 | 0 | 55 | 335 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 25 | 0 | 24 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 38 | 22 | 27 | 0 | 0 | 0 | 300 | 280 | 193 | 110 | 135 | 35 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 106 | 174 | 0 | 17 | 0 | 43 | 21 | 50 | 50 | 110 | 0 | 63 | 81 | 0 | 120 | 0 | 23 | 9 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 133 | 4 | 50 | 120 | 30 | 352 | 8 | 34 | 91 | 2 | 0 | 35 | 85 | 0 | 94 | 79 | 360 | 73 | 4 | 17 | 90 | 0 | 35 | 3 | 108 | 34 | 0 |  | 924 | 0 | 315 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 160 | 0 | 333 | 17 | 0 | 35 | 0 | 42 | 0 | 1 | 35 | 450 | 163 | 0 | 0 | 0 | 27 | 34 |  | 6693 | 3039 | 9732 | 3985 | 924 | 2124 | 0 | 1804 | 625 | 123 | 0 | 0 | 106 | 41 | 0 | 87.06
8:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 410 | 0 |  | 0 | 370 | 305 | 74 | 0 | 55 | 335 | 0 | 0 | 8 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 25 | 0 | 42 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 34 | 22 | 8 | 0 | 0 | 0 | 280 | 270 | 183 | 110 | 135 | 35 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 114 | 162 | 0 | 17 | 1 | 43 | 21 | 50 | 50 | 110 | 0 | 65 | 81 | 0 | 120 | 0 | 23 | 9 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 133 | 7 | 50 | 120 | 30 | 352 | 8 | 34 | 87 | 3 | 0 | 35 | 85 | 0 | 95 | 70 | 360 | 72 | 19 | 17 | 90 | 0 | 35 | 4 | 109 | 34 | 0 |  | 923 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 191 | 0 | 320 | 0 | 0 | 35 | 0 | 41 | 0 | 2 | 35 | 450 | 164 | 0 | 0 | 1 | 52 | 35 |  | 6675 | 3102 | 9777 | 4001 | 923 | 2100 | 0 | 1786 | 625 | 123 | 0 | 16 | 114 | 89 | 0 | 87.1
9:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 411 | 0 |  | 0 | 400 | 280 | 82 | 0 | 55 | 336 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 33 | 0 | 25 | 25 | 25 | 0 | 42 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 0 | 31 | 22 | 3 | 0 | 0 | 0 | 365 | 300 | 183 | 110 | 135 | 30 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 20 | 130 | 156 | 0 | 17 | 1 | 44 | 21 | 50 | 50 | 110 | 0 | 59 | 0 | 0 | 120 | 0 | 23 | 9 | 310 | 16 | 11 | 0 | 17 | 0 | 0 | 144 | 0 | 135 | 16 | 76 | 120 | 38 | 401 | 11 | 34 | 91 | 4 | 15 | 37 | 100 | 0 | 94 | 82 | 360 | 82 | 30 | 26 | 90 | 0 | 35 | 8 | 116 | 43 | 0 |  | 924 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 210 | 0 | 320 | 5 | 0 | 42 | 0 | 56 | 0 | 3 | 70 | 440 | 164 | 0 | 0 | 3 | 40 | 35 |  | 7031 | 3190 | 10221 | 4231 | 924 | 2039 | 0 | 2038 | 615 | 123 | 0 | 16 | 130 | 105 | 0 | 87.15
10:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 410 | 0 |  | 0 | 400 | 275 | 82 | 0 | 55 | 336 | 0 | 0 | 45 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 0 | 49 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 50 | 0 | 31 | 22 | 8 | 0 | 0 | 0 | 270 | 300 | 182 | 110 | 135 | 32 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 20 | 134 | 152 | 0 | 17 | 1 | 43 | 21 | 50 | 47 | 110 | 0 | 59 | 0 | 0 | 120 | 0 | 23 | 9 | 275 | 8 | 11 | 0 | 132 | 0 | 0 | 172 | 0 | 133 | 0 | 76 | 75 | 103 | 401 | 32 | 70 | 105 | 5 | 30 | 54 | 110 | 0 | 67 | 90 | 360 | 84 | 36 | 108 | 90 | 0 | 35 | 14 | 116 | 55 | 140 |  | 924 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 212 | 0 | 320 | 35 | 0 | 70 | 0 | 69 | 0 | 4 | 70 | 400 | 163 | 0 | 0 | 3 | 48 | 35 |  | 7544 | 3210 | 10754 | 4267 | 924 | 1992 | 0 | 2580 | 575 | 123 | 0 | 48 | 134 | 111 | 0 | 87.2
11:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 411 | 0 |  | 0 | 400 | 255 | 80 | 0 | 45 | 336 | 0 | 0 | 50 | 75 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 0 | 49 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 0 | 31 | 22 | 8 | 0 | 0 | 0 | 270 | 300 | 182 | 110 | 135 | 32 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 31 | 12 | 130 | 146 | 0 | 17 | 2 | 43 | 21 | 50 | 47 | 110 | 0 | 60 | 38 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 173 | 0 | 0 | 171 | 0 | 123 | 11 | 76 | 70 | 122 | 401 | 32 | 70 | 105 | 3 | 30 | 54 | 110 | 0 | 63 | 90 | 360 | 92 | 53 | 112 | 90 | 0 | 35 | 13 | 100 | 55 | 300 |  | 923 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 213 | 0 | 299 | 35 | 0 | 70 | 0 | 68 | 0 | 6 | 70 | 400 | 224 | 0 | 0 | 5 | 61 | 35 |  | 7801 | 3269 | 11070 | 4454 | 923 | 2011 | 0 | 2652 | 575 | 123 | 0 | 48 | 130 | 154 | 0 | 87.24
12:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 411 | 0 |  | 0 | 400 | 300 | 80 | 0 | 45 | 331 | 0 | 0 | 80 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 23 | 25 | 0 | 49 | 0 | 44 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 0 | 31 | 22 | 6 | 0 | 0 | 0 | 280 | 315 | 189 | 110 | 136 | 32 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 12 | 136 | 147 | 0 | 17 | 3 | 44 | 21 | 50 | 50 | 110 | 0 | 55 | 38 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 118 | 8 | 63 | 117 | 125 | 402 | 32 | 70 | 105 | 5 | 30 | 54 | 110 | 0 | 38 | 90 | 360 | 94 | 46 | 156 | 75 | 0 | 35 | 12 | 108 | 55 | 299 |  | 924 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 212 | 0 | 351 | 35 | 0 | 70 | 0 | 68 | 0 | 7 | 70 | 400 | 224 | 0 | 0 | 5 | 98 | 50 |  | 7953 | 3385 | 11338 | 4445 | 924 | 2108 | 0 | 2835 | 575 | 79 | 0 | 52 | 136 | 184 | 0 | 87.28
13:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 409 | 0 |  | 0 | 400 | 250 | 80 | 0 | 45 | 335 | 0 | 0 | 91 | 85 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 23 | 25 | 0 | 48 | 0 | 44 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 9 | 30 | 22 | 9 | 0 | 0 | 0 | 270 | 300 | 212 | 147 | 136 | 32 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 0 | 12 | 144 | 147 | 0 | 17 | 3 | 43 | 21 | 50 | 50 | 110 | 0 | 55 | 61 | 0 | 120 | 0 | 25 | 9 | 300 | 16 | 11 | 0 | 281 | 0 | 0 | 160 | 0 | 116 | 18 | 63 | 120 | 133 | 409 | 56 | 90 | 105 | 6 | 130 | 54 | 110 | 0 | 38 | 90 | 400 | 94 | 20 | 162 | 90 | 0 | 35 | 16 | 101 | 55 | 302 |  | 924 | 0 | 325 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 16 | 17 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 210 | 0 | 304 | 40 | 0 | 80 | 0 | 70 | 0 | 7 | 100 | 420 | 223 | 0 | 0 | 5 | 27 | 108 |  | 8191 | 3446 | 11637 | 4494 | 924 | 2091 | 0 | 3165 | 595 | 79 | 0 | 43 | 144 | 102 | 0 | 87.36
14:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 411 | 0 |  | 0 | 400 | 275 | 80 | 0 | 45 | 334 | 0 | 0 | 93 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 25 | 0 | 32 | 0 | 44 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 40 | 9 | 22 | 7 | 0 | 0 | 0 | 270 | 300 | 183 | 147 | 136 | 31 | 0 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 0 | 21 | 148 | 149 | 0 | 17 | 2 | 44 | 21 | 50 | 49 | 110 | 0 | 45 | 81 | 0 | 120 | 0 | 25 | 9 | 265 | 16 | 11 | 0 | 291 | 0 | 0 | 160 | 0 | 132 | 0 | 63 | 120 | 138 | 365 | 64 | 90 | 105 | 0 | 100 | 54 | 110 | 0 | 37 | 79 | 400 | 94 | 43 | 162 | 90 | 0 | 35 | 20 | 115 | 55 | 302 |  | 923 | 0 | 325 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 170 | 0 | 322 | 70 | 0 | 94 | 0 | 68 | 0 | 7 | 113 | 360 | 225 | 0 | 0 | 4 | 15 | 108 |  | 8202 | 3376 | 11578 | 4351 | 923 | 2117 | 0 | 3175 | 535 | 79 | 0 | 159 | 148 | 91 | 0 | 87.44
15:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 410 | 0 |  | 0 | 400 | 285 | 79 | 0 | 45 | 335 | 0 | 0 | 100 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 25 | 0 | 32 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 31 | 41 | 28 | 22 | 3 | 0 | 0 | 0 | 285 | 320 | 190 | 147 | 138 | 19 | 17 | 0 | 43 | 0 | 49 | 0 | 19 | 8 | 0 | 21 | 148 | 150 | 0 | 17 | 2 | 44 | 20 | 50 | 49 | 110 | 0 | 45 | 81 | 0 | 120 | 0 | 25 | 9 | 300 | 16 | 11 | 0 | 285 | 0 | 0 | 160 | 0 | 123 | 10 | 63 | 120 | 132 | 404 | 65 | 90 | 105 | 2 | 100 | 54 | 110 | 0 | 38 | 64 | 400 | 94 | 30 | 162 | 90 | 0 | 35 | 19 | 116 | 55 | 240 |  | 924 | 0 | 320 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 32 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 182 | 0 | 405 | 62 | 0 | 94 | 0 | 68 | 0 | 6 | 113 | 370 | 220 | 0 | 0 | 4 | 26 | 108 |  | 8263 | 3497 | 11760 | 4349 | 924 | 2257 | 0 | 3205 | 545 | 81 | 0 | 152 | 148 | 99 | 0 | 87.52
16:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 411 | 0 |  | 0 | 400 | 265 | 80 | 0 | 45 | 335 | 0 | 0 | 100 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 25 | 0 | 32 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 39 | 31 | 22 | 2 | 0 | 0 | 0 | 270 | 305 | 179 | 147 | 137 | 19 | 46 | 0 | 43 | 0 | 47 | 0 | 19 | 8 | 33 | 21 | 144 | 150 | 0 | 17 | 1 | 44 | 20 | 50 | 49 | 110 | 0 | 45 | 81 | 0 | 120 | 0 | 24 | 9 | 290 | 16 | 11 | 0 | 283 | 0 | 0 | 160 | 0 | 115 | 9 | 63 | 120 | 133 | 402 | 65 | 105 | 105 | 0 | 100 | 54 | 110 | 0 | 52 | 50 | 400 | 94 | 20 | 162 | 90 | 0 | 35 | 8 | 116 | 55 | 0 |  | 922 | 0 | 315 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 32 | 84 | 21 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 204 | 0 | 365 | 56 | 0 | 94 | 0 | 69 | 0 | 4 | 113 | 400 | 222 | 0 | 0 | 2 | 75 | 108 |  | 8010 | 3584 | 11594 | 4159 | 922 | 2219 | 0 | 3227 | 574 | 81 | 0 | 149 | 144 | 119 | 0 | 87.6
17:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 411 | 0 |  | 0 | 400 | 255 | 72 | 0 | 45 | 335 | 0 | 0 | 76 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 26 | 25 | 0 | 32 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 45 | 36 | 22 | 3 | 0 | 0 | 0 | 280 | 305 | 180 | 148 | 136 | 30 | 50 | 0 | 51 | 0 | 48 | 0 | 19 | 11 | 33 | 21 | 140 | 149 | 0 | 17 | 1 | 44 | 20 | 31 | 30 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 24 | 9 | 270 | 16 | 11 | 0 | 230 | 0 | 0 | 169 | 0 | 112 | 4 | 63 | 145 | 137 | 402 | 45 | 52 | 105 | 1 | 45 | 54 | 100 | 0 | 94 | 50 | 400 | 94 | 11 | 108 | 90 | 0 | 35 | 8 | 116 | 55 | 0 |  | 923 | 0 | 305 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 28 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 204 | 0 | 360 | 35 | 0 | 70 | 0 | 69 | 0 | 2 | 113 | 390 | 222 | 0 | 0 | 1 | 7 | 108 |  | 7766 | 3424 | 11190 | 4191 | 923 | 2163 | 0 | 2938 | 565 | 81 | 0 | 154 | 140 | 35 | 0 | 87.66
18:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 411 | 0 |  | 0 | 400 | 270 | 76 | 0 | 55 | 270 | 0 | 0 | 50 | 64 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 0 | 32 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 42 | 37 | 22 | 14 | 0 | 0 | 0 | 280 | 290 | 180 | 148 | 136 | 31 | 51 | 0 | 51 | 0 | 48 | 0 | 19 | 11 | 33 | 21 | 134 | 155 | 0 | 17 | 0 | 44 | 21 | 31 | 30 | 110 | 0 | 64 | 84 | 0 | 120 | 0 | 24 | 9 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 180 | 0 | 115 | 1 | 40 | 155 | 137 | 352 | 45 | 35 | 105 | 0 | 45 | 54 | 98 | 0 | 94 | 50 | 350 | 54 | 1 | 108 | 90 | 0 | 35 | 2 | 116 | 55 | 0 |  | 923 | 0 | 300 | 0 | 52 | 0 | 0 | 0 | 4 | 0 | 8 | 84 | 19 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 32 | 0 | 13 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 202 | 0 | 304 | 35 | 0 | 70 | 0 | 94 | 0 | 0 | 50 | 390 | 168 | 0 | 0 | 0 | 4 | 108 |  | 7514 | 3285 | 10799 | 4019 | 923 | 2082 | 0 | 2812 | 565 | 81 | 0 | 175 | 134 | 8 | 0 | 87.73
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 411 | 0 |  | 0 | 400 | 305 | 76 | 0 | 55 | 290 | 0 | 0 | 50 | 85 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 0 | 40 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 20 | 51 | 30 | 49 | 37 | 22 | 14 | 0 | 0 | 0 | 310 | 290 | 193 | 150 | 136 | 33 | 51 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 152 | 154 | 0 | 17 | 0 | 44 | 42 | 31 | 30 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 25 | 9 | 275 | 16 | 11 | 0 | 215 | 0 | 0 | 181 | 0 | 98 | 0 | 80 | 158 | 143 | 396 | 48 | 40 | 105 | 0 | 155 | 54 | 110 | 0 | 94 | 50 | 400 | 58 | 0 | 115 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 923 | 0 | 305 | 0 | 103 | 0 | 0 | 0 | 35 | 0 | 40 | 83 | 26 | 16 | 0 | 0 | 0 | 34 | 29 | 72 | 0 | 0 | 32 | 0 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 181 | 0 | 380 | 35 | 0 | 86 | 5 | 95 | 0 | 0 | 90 | 410 | 222 | 0 | 3 | 0 | 0 | 108 |  | 8086 | 3718 | 11804 | 4144 | 923 | 2265 | 0 | 3196 | 585 | 81 | 0 | 458 | 152 | 0 | 0 | 87.85
19:30 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 410 | 0 |  | 0 | 400 | 300 | 88 | 0 | 55 | 337 | 0 | 0 | 70 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 0 | 50 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 30 | 62 | 37 | 22 | 25 | 0 | 0 | 0 | 355 | 335 | 200 | 150 | 136 | 33 | 51 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 156 | 154 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 315 | 16 | 11 | 0 | 285 | 122 | 86 | 181 | 80 | 112 | 0 | 83 | 200 | 143 | 400 | 96 | 105 | 105 | 0 | 220 | 54 | 110 | 0 | 95 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 923 | 0 | 305 | 0 | 103 | 0 | 0 | 0 | 42 | 0 | 40 | 83 | 27 | 16 | 0 | 0 | 0 | 34 | 29 | 89 | 0 | 0 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 70 | 192 | 0 | 416 | 76 | 0 | 94 | 15 | 91 | 0 | 0 | 113 | 540 | 222 | 0 | 17 | 0 | 0 | 108 |  | 9096 | 4098 | 13194 | 4312 | 923 | 2349 | 358 | 3743 | 715 | 81 | 0 | 557 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 408 | 0 |  | 0 | 400 | 270 | 87 | 0 | 55 | 336 | 0 | 0 | 95 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 25 | 0 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 44 | 51 | 30 | 72 | 37 | 22 | 3 | 0 | 0 | 0 | 320 | 305 | 213 | 150 | 136 | 33 | 52 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 150 | 154 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 310 | 16 | 11 | 0 | 291 | 122 | 85 | 181 | 80 | 115 | 0 | 86 | 200 | 143 | 401 | 98 | 105 | 105 | 0 | 259 | 54 | 110 | 0 | 94 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 113 | 55 | 0 |  | 924 | 0 | 305 | 0 | 98 | 0 | 0 | 0 | 35 | 0 | 40 | 87 | 28 | 16 | 0 | 0 | 0 | 34 | 29 | 90 | 0 | 0 | 32 | 0 | 38 | 0 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 60 | 197 | 0 | 390 | 60 | 0 | 94 | 15 | 95 | 0 | 0 | 113 | 560 | 223 | 0 | 17 | 0 | 0 | 108 |  | 9103 | 4053 | 13156 | 4279 | 924 | 2247 | 347 | 3809 | 735 | 113 | 0 | 552 | 150 | 0 | 0 | 87.81
21:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 411 | 0 |  | 0 | 400 | 290 | 86 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 22 | 25 | 28 | 25 | 0 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 44 | 51 | 30 | 91 | 37 | 22 | 30 | 0 | 0 | 0 | 340 | 320 | 210 | 150 | 136 | 33 | 52 | 0 | 43 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 150 | 166 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 285 | 16 | 11 | 0 | 291 | 0 | 50 | 182 | 30 | 113 | 0 | 90 | 200 | 143 | 402 | 100 | 105 | 105 | 0 | 282 | 54 | 110 | 0 | 94 | 50 | 400 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 924 | 0 | 305 | 0 | 105 | 0 | 0 | 0 | 33 | 0 | 40 | 84 | 29 | 0 | 0 | 0 | 0 | 34 | 29 | 90 | 0 | 0 | 32 | 0 | 38 | 0 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 50 | 206 | 0 | 414 | 76 | 0 | 94 | 15 | 95 | 0 | 0 | 113 | 580 | 225 | 0 | 17 | 0 | 0 | 108 |  | 9028 | 4108 | 13136 | 4339 | 924 | 2286 | 130 | 3879 | 755 | 123 | 0 | 550 | 150 | 0 | 0 | 87.85
22:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 411 | 0 |  | 0 | 430 | 300 | 88 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 30 | 91 | 37 | 22 | 30 | 0 | 0 | 0 | 345 | 305 | 209 | 150 | 136 | 33 | 51 | 0 | 51 | 0 | 49 | 0 | 19 | 8 | 32 | 21 | 148 | 164 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 300 | 16 | 11 | 0 | 291 | 0 | 50 | 183 | 30 | 131 | 0 | 76 | 200 | 145 | 401 | 102 | 105 | 105 | 0 | 264 | 54 | 110 | 0 | 94 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 924 | 0 | 300 | 0 | 101 | 0 | 0 | 0 | 33 | 0 | 40 | 84 | 31 | 0 | 0 | 0 | 0 | 34 | 29 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 50 | 207 | 0 | 414 | 76 | 0 | 94 | 15 | 95 | 0 | 0 | 113 | 580 | 226 | 0 | 17 | 0 | 0 | 108 |  | 9090 | 4122 | 13212 | 4325 | 924 | 2373 | 130 | 3879 | 755 | 122 | 0 | 556 | 148 | 0 | 0 | 87.89
23:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 411 | 0 |  | 0 | 450 | 285 | 87 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 20 | 91 | 37 | 22 | 37 | 0 | 0 | 0 | 315 | 305 | 211 | 150 | 136 | 15 | 51 | 0 | 51 | 0 | 34 | 0 | 19 | 8 | 33 | 21 | 150 | 159 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 295 | 16 | 11 | 0 | 291 | 0 | 50 | 183 | 30 | 128 | 0 | 76 | 200 | 145 | 401 | 104 | 105 | 105 | 0 | 268 | 54 | 110 | 0 | 94 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 108 | 55 | 0 |  | 923 | 0 | 295 | 0 | 108 | 0 | 0 | 0 | 33 | 0 | 40 | 86 | 31 | 0 | 0 | 0 | 0 | 34 | 30 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 50 | 207 | 0 | 414 | 76 | 0 | 94 | 15 | 95 | 0 | 0 | 113 | 600 | 226 | 0 | 17 | 0 | 0 | 108 |  | 9017 | 4146 | 13163 | 4272 | 923 | 2380 | 130 | 3870 | 775 | 121 | 0 | 542 | 150 | 0 | 0 | 87.93
24:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 410 | 0 |  | 0 | 450 | 265 | 88 | 0 | 55 | 336 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 39 | 20 | 91 | 37 | 22 | 37 | 0 | 0 | 0 | 315 | 305 | 213 | 150 | 136 | 20 | 51 | 0 | 51 | 0 | 41 | 0 | 19 | 8 | 33 | 21 | 150 | 159 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 57 | 84 | 0 | 120 | 0 | 25 | 9 | 300 | 16 | 11 | 0 | 291 | 0 | 50 | 191 | 30 | 116 | 0 | 76 | 200 | 123 | 401 | 99 | 105 | 105 | 0 | 267 | 54 | 110 | 0 | 40 | 50 | 400 | 95 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 924 | 0 | 295 | 0 | 100 | 0 | 0 | 0 | 33 | 0 | 40 | 87 | 30 | 0 | 0 | 0 | 0 | 34 | 29 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 50 | 206 | 0 | 422 | 75 | 0 | 94 | 15 | 70 | 0 | 0 | 113 | 610 | 227 | 0 | 17 | 0 | 0 | 108 |  | 8928 | 4128 | 13056 | 4276 | 924 | 2373 | 130 | 3760 | 785 | 122 | 0 | 536 | 150 | 0 | 0 | 87.97
KWH | 0 | 0 | 0 | 4378500 | 0 | 1759500 | 0 | 9971710 | 0 |  | 0 | 9492250 | 6773207 | 1957440 | 0 | 1272654 | 7948803 | 0 | 0 | 1491840 | 1469520 | 1459200 | 0 | 0 | 0 | 0 | 1306800 | 1162014 | 973771 | 326808 | 600000 | 578700 | 738400 | 0 | 1006560 | 0 | 1778198 | 848000 | 2300000 | 0 | 327400 | 0 | 0 | 0 | 0 |  | 569760 | 242976 | 289975 | 882960 | 776640 | 8438400 | 508128 | 489120 | 0 | 0 | 0 | 7639500 | 7381000 | 4639000 | 3111272 | 3258510 | 690480 | 1014720 | 0 | 1017118 | 0 | 516824 | 0 | 461232 | 202140 | 513900 | 476120 | 3264960 | 3751680 | 0 | 378540 | 14850 | 1033000 | 581184 | 1078800 | 1056528 | 2694763 | 0 | 1315680 | 1681920 | 0 | 2895300 | 0 | 574280 | 210060 | 7014500 | 372096 | 264000 | 0 | 5286653 | 121139 | 277925 | 4104000 | 193784 | 2970580 | 81945 | 1723200 | 3074880 | 2835272 | 9376000 | 1561200 | 2002800 | 2493199 | 25920 | 2601927 | 1313003 | 2606098 | 0 | 1594320 | 1817280 | 9221400 | 2188800 | 287250 | 2806560 | 2152800 | 0 | 890280 | 121508 | 2726400 | 1241280 | 1552900 |  | 22339636 | 0 | 7607520 | 0 | 1179840 | 0 | 0 | 0 | 198720 | 0 | 409500 | 2112962 | 543226 | 88032 | 0 | 0 | 0 | 226704 | 339623 | 536416 | 0 | 82592 | 341200 | 0 | 295380 | 466800 | 0 | 251910 | 0 | 0 | 4281100 | 0 | 0 | 0 | 0 | 4517918 | 0 | 0 | 289920 | 5065664 | 0 | 9048618 | 1254240 | 0 | 2019264 | 91440 | 1727808 | 0 | 49607 | 2284320 | 12160100 | 5052682 | 0 | 121200 | 38460 | 583200 | 1893312 |  | 200473494 | 87498914 | 287972408 | 102910685 | 22339636 | 53079364 | 882768 | 80777839 | 16441200 | 2626198 | 0 | 4447018 | 3264960 | 1202740 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 2340135 | 0 | 10470295.5 | 0 |  | 0 | 10346552.5 | 7518259.77 | 21884179.2 | 0 | 16862665.5 | 8902659.36 | 0 | 0 | 21810700.8 | 20676146.4 | 23653632 | 0 | 0 | 0 | 0 | 16622496 | 15687189 | 13058269.11 | 245106 | 450000 | 0 | 0 | 0 | 17121585.6 | 0 | 480113.46 | 228960 | 4347000 | 0 | 5352990 | 0 | 0 | 0 | 0 |  | 7435368 | 4052839.68 | 4935374.5 | 11928789.6 | 9847795.2 | 97632288 | 645322.56 | 1628769.6 | 0 | 0 | 0 | 8479845 | 8045290 | 5381240 | 4013540.88 | 3975382.2 | 780242.4 | 1511932.8 | 0 | 1698587.06 | 0 | 8925550.48 | 0 | 631887.84 | 151605 | 899325 | 357090 | 23442412.8 | 4089331.2 | 0 | 514814.4 | 236709 | 1415210 | 767162.88 | 1877112 | 1827793.44 | 3098977.45 | 0 | 2552419.2 | 3834777.6 | 0 | 2924253 | 0 | 855677.2 | 415918.8 | 7014500 | 279072 | 200640 | 0 | 72162813.45 | 2539073.44 | 5744709.75 | 55321920 | 4005515.28 | 41142533 | 957937.05 | 17783424 | 42002860.8 | 37624059.44 | 8625920 | 18984192 | 28960488 | 31538967.35 | 0 | 30546622.98 | 14298602.67 | 27702821.74 | 0 | 20550784.8 | 21407558.4 | 8483688 | 28344960 | 4150762.5 | 35615246.4 | 24498864 | 0 | 11627056.8 | 1452020.6 | 40814208 | 16347657.6 | 0 |  | 67018908 | 0 | 8520422.4 | 0 | 12282134.4 | 0 | 0 | 0 | 3578947.2 | 0 | 5884515 | 2366517.44 | 1053858.44 | 959548.8 | 0 | 0 | 0 | 3801826.08 | 5940006.27 | 8389546.24 | 0 | 1367723.52 | 5769692 | 0 | 4983060.6 | 966276 | 0 | 190695.87 | 0 | 0 | 22647019 | 0 | 0 | 0 | 0 | 5782935.04 | 0 | 0 | 6082521.6 | 5876170.24 | 0 | 8958131.82 | 16856985.6 | 0 | 23887893.12 | 1321308 | 21943161.6 | 0 | 548157.35 | 27731644.8 | 109562501 | 5153735.64 | 0 | 896880 | 434982.6 | 6840936 | 29024472.96 |  | 1116123015.02 | 426623114.63 | 1542746129.65 | 112875507.53 | 67018908 | 64114536 | 18371820.07 | 1035352371.64 | 132209520 | 709073.46 | 0 | 74030475.05 | 23442412.8 | 14621505.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 411 | 0 |  | 0 | 400 | 300 | 80 | 0 | 45 | 331 | 0 | 0 | 80 | 85 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 23 | 25 | 0 | 49 | 0 | 44 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 0 | 31 | 22 | 6 | 0 | 0 | 0 | 280 | 315 | 189 | 110 | 136 | 32 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 0 | 12 | 136 | 147 | 0 | 17 | 3 | 44 | 21 | 50 | 50 | 110 | 0 | 55 | 38 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 118 | 8 | 63 | 117 | 125 | 402 | 32 | 70 | 105 | 5 | 30 | 54 | 110 | 0 | 38 | 90 | 360 | 94 | 46 | 156 | 75 | 0 | 35 | 12 | 108 | 55 | 299 |  | 924 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 212 | 0 | 351 | 35 | 0 | 70 | 0 | 68 | 0 | 7 | 70 | 400 | 224 | 0 | 0 | 5 | 98 | 50 |  | 11338 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 410 | 0 | 0 | 0 | 400 | 300 | 88 | 0 | 55 | 337 | 0 | 0 | 70 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 0 | 50 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 43 | 51 | 30 | 62 | 37 | 22 | 25 | 0 | 0 | 0 | 355 | 335 | 200 | 150 | 136 | 33 | 51 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 156 | 154 | 0 | 20 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 25 | 9 | 315 | 16 | 11 | 0 | 285 | 122 | 86 | 181 | 80 | 112 | 0 | 83 | 200 | 143 | 400 | 96 | 105 | 105 | 0 | 220 | 54 | 110 | 0 | 95 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 923 | 0 | 305 | 0 | 103 | 0 | 0 | 0 | 42 | 0 | 40 | 83 | 27 | 16 | 0 | 0 | 0 | 34 | 29 | 89 | 0 | 0 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 70 | 192 | 0 | 416 | 76 | 0 | 94 | 15 | 91 | 0 | 0 | 113 | 540 | 222 | 0 | 17 | 0 | 0 | 108 |  | 13194 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 412 | 0 | 0 | 0 | 400 | 305 | 88 | 0 | 55 | 335 | 0 | 0 | 100 | 95 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 54 | 92 | 44 | 22 | 30 | 0 | 0 | 0 | 355 | 335 | 215 | 150 | 135 | 35 | 52 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 165 | 170 | 0 | 22 | 0 | 44 | 42 | 51 | 50 | 110 | 0 | 65 | 84 | 0 | 120 | 0 | 25 | 10 | 341 | 16 | 11 | 200 | 285 | 300 | 100 | 200 | 100 | 135 | 0 | 90 | 200 | 150 | 400 | 107 | 105 | 105 | 0 | 300 | 35 | 110 | 0 | 94 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 |  | 115 | 55 |  |  | 940 | 0 | 350 | 0 | 103 | 220 | 0 | 0 | 42 | 60 | 40 | 87 | 25 | 16 | 0 | 0 | 0 | 34 | 0 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 210 | 0 | 0 | 100 | 210 | 0 | 414 | 93 | 190 | 94 | 89 | 100 | 0 | 0 | 113 | 622 | 220 |  | 35 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 412 | 0 | 0 | 0 | 400 | 305 | 80 | 0 | 55 | 335 | 0 | 0 | 100 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 54 | 80 | 44 | 22 | 10 | 0 | 0 | 0 | 300 | 300 | 215 | 150 | 135 | 35 | 52 | 0 | 51 | 0 | 32 | 0 | 21 | 11 | 33 | 21 | 143 | 160 | 0 | 22 | 1.6 | 44 | 42 | 51 | 50 | 110 | 0 | 65 | 84 | 0 | 120 | 0 | 25 | 10 | 320 | 16 | 11 | 100 | 285 | 200 | 100 | 180 | 25 | 135 | 20 | 90 | 150 | 140 | 400 | 107 | 105 | 105 | 5 | 265 | 35 | 110 | 0 | 38 | 100 | 400 | 104 | 50 | 162 | 90 | 0 | 35 | 30 | 115 | 55 |  |  | 940 | 0 | 350 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 200 | 0 | 414 | 93 | 100 | 94 | 70 | 70 | 0 | 8 | 75 | 622 | 220 |  | 35 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 409 | 0 | 0 | 0 | 400 | 280 | 57 | 0 | 55 | 250 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 28 | 33 | 0 | 24 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 37 | 22 | 20 | 0 | 0 | 0 | 280 | 275 | 213 | 150 | 137 | 32 | 50 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 108 | 173 | 0 | 17 | 0 | 43 | 42 | 31 | 30 | 110 | 0 | 20 | 84 | 0 | 120 | 0 | 25 | 9 | 260 | 16 | 11 | 0 | 45 | 0 | 0 | 80 | 0 | 79 | 9 | 20 | 68 | 20 | 350 | 8 | 35 | 68 | 2 | 15 | 35 | 51 | 0 | 38 | 25 | 350 | 36 | 17 | 35 | 90 | 0 | 35 | 5 | 74 | 34 | 0 | 0 | 924 | 0 | 345 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 309 | 0 | 0 | 35 | 0 | 31 | 0 | 2 | 35 | 380 | 174 | 0 | 0 | 2 | 44 | 34 | 0 |  |  |  |  | 86107625 |  | 0
86107625
| Minimum Generation |  | 9732 | 7:00
| Highest Generation |  | 13212 | 22:00
| Day Peak Generation |  | 11338 | 12:00
| Evening Peak Generation |  | 13194 | 19:30
| HVDC Max Flow |  | 925 | 1:00
| HVDC EvPeak Flow |  | 923 | 19:30
| Load factor L.F |  | 90.82%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-24
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11338 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9303 | MW
Evening Peak Generation : |  | 13194 | MW Hour : | 19:30 | Available Max Generation : |  | 14967 | MW
E.P. Demand (at gen end) : |  | 13194 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 13212 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2167 | MW
Total Gen. (MKWH) : |  | 287.9724 | System Load Factor : | 90.82% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -248 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-24
Actual : | 88.1 | Ft.(MSL) , | Rule curve : | 82.11 | Ft.( MSL )
Gas Consumed : | Total = | 1168.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 176990043.53
: |  | Coal : | 132209520 | Oil : | 1127754666.76 | Total : | 1436954230.29
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4459.8768 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1191.6307 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1575.9569 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1410.6277 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1251.0769 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 921.9754 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 508.6523 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 338.5477 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 702.4246 |  |  | 0 | 0%
Total | 0 |  | 12360.769 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit- 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kabirpur 132/33 kV T-1 & T-2 transformers tripped at 09:28 from 33 kV end showing Directional O/C | [5 empty] | About 150 MW power interruption occurred under
relays and was switched on at 09:59. | [5 empty] | Kabirpur S/S area from 09:28 to 09:59.
b) 230 kV Rampur Bay-1 at Hathazari S/S was under shut down from 10:12 to 17:41 for D/W.
c) Hathazari-Sikalbaha 230 kV Ckt-1 was under shut down from 10:12 to 17:29 for D/W.
d) Ishurdi-Pabna 132 kV Ckt was under shut down from 10:11 to 12:28 for D/W.
e) Sreenagar 132/33 kV T-2 transformer was under shut down from 11:13 to 13:45 for red hot at 33 kV end.
f) Gopalganj(O) 132/33 kV T-1 transformer was under shut down from 10:47 to 14:15 for C/M.
g) Kabirpur 132/33 kV T-3 transformer was under shut down from 12:25 to 13:51 for D/W. | [5 empty] | About 50 MW power interruption occurred under
Kabirpur S/S area from 12:25 to 13:51.
h) Ashuganj (East) GT was synchronized at 09:11.
i) Ashuganj 132 kV Bus-2 was under shut down from 11:40 to 13:33 for high temp maintenance.
j) Sreenagar 132/33 kV T-1 transformer was under shut down from 15:05 to 16:30 for R/H maintenance.
k) Bogura 132/33 kV T-4 transformers tripped at 19:59 due to 33 kV feeder fault and was switched on at
20:45.
l) Cox'sbazar 132/33 kV T-2 transformer was under shut down from 00:31(24/06/2022) to 02:55 for D/W. | [5 empty] | About 60 MW power interruption occurred under
Cox'sbazar S/S area from 00:31(24/06/2022) to 02:55
m) Naogaon 132/33 kV T-3 transformer was under shut down from 07:15(24/06/2022) to 08:48 for D/W. | [5 empty] | About 40 MW power interruption occurred under
Naogaon S/S area from 07:15(24/06/2022) to 08:48.
n) Gallamari 132/33 kV T-1 transformer was under shut down at 06:03(24/06/2022) for D/W.
o) Kustia 132/33 kV T-2 transformer was shut down at 07:11(24/06/2022) due to R/H maintenance
at 33 kV PBS feeder by PBS.
p) Sherpur-Sirajganj 132 kV Ckt-1 was under shut down at 07:11(24-06-2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 1759500 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 410 | 9971710
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9492250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 88 | 1957440 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6773207 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1272654
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 326808
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 70 | 1491840 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 337 | 7948803
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1469520 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1306800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1459200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1162014
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 973771 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1178700 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 738400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 0 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1006560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 285 | 5286653 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 122 | 121139 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 86 | 277925 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 80 | 193784 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2970580 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2002800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 2188800 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2806560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 121508
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1241280
| Dhaka area Total |  |  |  | 5847 | 3552 | 71878706
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 327400
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 81945
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 8438400 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 2626198 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2493199
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 242976 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 289975 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 30 | 882960 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 83 | 1723200 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508128
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 489120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 62 | 776640 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25920
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 220 | 2601927 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1313003
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2606098
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1817280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2152800 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1188 | 31697169
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4639000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 355 | 7639500 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 335 | 7381000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 1552900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 690480 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1014720
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 150 | 3111272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1017118
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 2835272 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 516824
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3258510 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3074880
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 461232
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 202140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3264960
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 513900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 476120
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1594320 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 890280 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 116 | 2726400
| Cumilla Area Total |  |  |  | 2885 | 2189 | 46860828
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 154 | 3751680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 378540
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 181 | 4104000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1561200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 287250
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 569760
| Mymensingh Area Total |  |  |  | 614 | 475 | 10667280
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1033000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 581184 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2694763 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 31 | 1078800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 1056528 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1315680
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1681920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2895300 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 25 | 574280
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 372096 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7014500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9376000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 210060
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9221400
| Sylhet Area Total |  |  |  | 2477 | 1692 | 39369511
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 22339636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 103 | 1179840 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 198720 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7607520 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 409500
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 70 | 289920 | Low demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 76 | 1254240 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 91440 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 583200
| Khulna Area Total |  |  |  | 2384 | 1574 | 33954016
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 88032 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 543226 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 83 | 2112962 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 12160100 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5052682
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 121200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 905 | 20078202
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 226704 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 29 | 339623 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 82592 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 341200 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 175 | 4517918
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 192 | 5065664 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 9048618
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 295380 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 466800
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251910
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 536416 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2019264 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2284320
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38460
| Rajshahi Area Total |  |  |  | 2129 | 1245 | 25514869
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4281100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1727808 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 49607
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1893312 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 374 | 7951827
| Total |  |  |  | 21396 | 13194 | 287972408
| Eastern Grid Total |  |  |  | 14205 | 9096 | 200473494
| Western Grid Total |  |  |  | 7191 | 4098 | 87498914
| National Grid Total |  |  |  | 21396 | 13194 | 287972408
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-23
(a) ENTIRE EASTERN GRID : |  | 8651.23 | MW | (b) ENTIRE WESTERN GRID : |  | 4081 | MW
i) Dhaka area |  | 4775.28 | MW | i) Khulna area |  | 1590.8 | MW
ii) Chittagong area |  | 1292.95 | MW | ii) Rajshahi area |  | 1291.3 | MW
iii) Comilla area |  | 1146 | MW | iii) Barisal area |  | 358.9 | MW
iv) Mymensingh area |  | 1023 | MW | iv) Rangpur area |  | 840 | MW
v) Sylhet area |  | 414 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12732.23 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 13:00 | Hasnabad | 87 | 23:00 | Palashbari | 116 | 01:00
Agargaon | 90 | 13:00 | Hathazari | 96 | 20:00 | Panchagarh | 61 | 21:00
Agrabad | 78 | 16:00 | Ishurdi | 81 | 20:00 | Patuakhali | 117 | 23:00
AKS | 10 | 05:00 | Jaldhaka | 67 | 20:00 | Payra | 0.95 | 12:00
AKSML | 127 | 13:00 | Jamalpur | 149 | 20:00 | PHP | 5 | 03:00
Amnura | 56 | 22:00 | Jashore | 134 | 20:00 | Purbachal | 19 | 19:00
Ashuganj | 30 | 00:00 | Jhenaidah | 118 | 22:00 | Purbasadipur | 126 | 20:00
Bagerhat | 104 | 19:30 | Joydebpur | 175 | 19:30 | Rahim | 32 | 00:00
Bakulia | 128 | 23:00 | Joypurhat | 67 | 21:00 | Rajbari | 66 | 19:30
Banani | 55 | 11:00 | Juldah | 23 | 13:00 | Rajendrapur | 112 | 16:00
Bangabhaban | 20 | 10:00 | Kabirpur | 246 | 22:00 | Rajshahi | 146 | 20:00
Barapukuria | 52 | 22:00 | Kachua | 72 | 21:00 | Rajshahi | 39 | 23:00
Barguna | 20 | 23:00 | Kallyanpur | 96 | 00:00 | Ramganj | 116 | 22:00
Barishal | 111 | 19:30 | Kalurghat | 6 | 10:00 | Rampur | 22 | 19:30
Barishal | 46 | 21:00 | Kamrangirchar | 70 | 12:00 | Rangamati | 12 | 19:00
Baroaulia | 63 | 09:00 | Kaptai | 4.2 | 19:00 | Rangpur | 146 | 21:00
Baroirhat | 58 | 00:00 | Kazla | 84 | 19:30 | Ruppur | 5 | 10:00
Bashundhara | 155 | 12:00 | Keranigonj | 62 | 19:30 | Saidpur | 111 | 20:00
BashundharaCement | 6 | 21:00 | Khagrachori | 28 | 20:00 | Satkhira | 117 | 00:00
Beanibazar | 55 | 20:00 | Khulna | 107 | 13:00 | Satmasjid | 90 | 13:00
Benapole | 64 | 00:00 | Khulshi | 180 | 14:00 | Savar | 205 | 16:00
Bhaluka | 144 | 00:00 | Kishoreganj | 140 | 22:00 | Shahjadpur | 98 | 22:00
Bhandaria | 56 | 23:00 | Kodda | 305 | 10:00 | Shahjibazar | 107 | 22:00
Bhangura | 34 | 20:00 | KSRM | 28.75 | 19:30 | Shahmirpur | 48.6 | 19:00
Bheramara(GK) | 63 | 22:00 | Kulaura | 40 | 00:00 | Shariatpur | 72 | 22:00
Bhulta | 257 | 11:00 | Kurigram | 60 | 20:00 | Sherpur | 134 | 00:00
Bog-Sherpur | 62 | 23:00 | Kushtia | 140 | 19:30 | Shikalbaha | 26 | 13:00
Bogura | 158 | 00:00 | Lalbag | 95 | 13:00 | Shitalakhya | 126 | 15:00
Borhanuddin | 38 | 21:00 | Lalmonirhat | 46 | 20:00 | Sholosohor | N/A | N/A
Brahmanbaria | 152 | 00:00 | Madanganj | 104 | 21:00 | Shyampur | 164 | 00:00
BSRM | 165 | 18:00 | Madaripur | 100 | 22:00 | Siddhirganj | 122 | 16:00
Cantonment | 141 | 12:00 | Madartek | 76 | 22:00 | Sirajganj | 109 | 21:00
Chandpur | 67 | 20:00 | Madunaghat | 55 | 19:30 | Sonargaon | 100 | 00:00
Chandraghona | 30 | 20:00 | Magura | 52 | 21:00 | Sreemongol | 52 | 20:00
Chapai | 71 | 21:00 | Mahasthangarh | 66 | 20:00 | Srinagar | 43.39 | 22:00
Charsaidpur | 45 | 23:00 | Manikganj | 78 | 20:00 | SSM | 14 | 00:00
Chauddagram | 50 | 00:00 | Maniknagar | 81 | 13:00 | Sunamganj | 17 | 22:00
Chhatak | 19 | 21:00 | Matarbari | 38 | 21:00 | Sylhet | 117 | 19:00
Chowmuhani | 194 | 23:00 | Matuail | 64 | 10:00 | Tangail | 217 | 22:00
Chuadanga | 101 | 23:00 | Millgate | 60 | 11:00 | Thakurgaon | 97 | 21:00
Coxsbazar | 107 | 23:00 | Mirpur | 137 | 19:30 | TK | 28.5 | 22:00
Cumilla(N) | 143 | 22:00 | Mirsorai | N/A | N/A | Tongi | 116 | 15:00
Cumilla(S) | 156 | 19:30 | Mithapukur | 38 | 19:30 | Ullon | 35 | 19:30
Daudkandi | 132 | 00:00 | Modern | 0 | 00:00 | Uttara | 92 | 13:00
Dhaka | 35 | 12:00 | Mogbazar | 124 | 12:00 | UttaraNew | 16 | 12:00
Dhamrai | 116 | 13:00 | Mongla | 42 | 12:00 | Zigatola | 42 | 13:00
Dhanmondi | 146 | 13:00 | Motijheel | 34 | 11:00
Dohazari | 94 | 20:00 | Munshiganj | 102 | 22:00
Faridpur | 144 | 21:00 | Mymensingh | 211 | 20:00
Fatullah | 66 | 09:00 | Naogaon | 114 | 23:00
Fenchuganj | 38 | 20:00 | Narail | 44 | 00:00
Feni | 118 | 20:00 | Narinda | 75 | 20:00
Ghorashal | 63 | 00:00 | Narshingdi | 181 | 00:00
Goalpara | 27 | 13:00 | Natore | 140 | 22:00
Gollamari | 44 | 19:30 | Nawabganj | 51.6 | 22:00
Gopalganj | 98.4 | 22:00 | Netrakona | 110 | 21:00
GPH | 22 | 03:00 | New | 83.4 | 11:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 396 | 06:00 | 377 | 12:00 | Kaliakoir | 396 | 04:00 | 385 | 12:00
| Bibiana | 412 | 02:00 | 403 | 12:00 | Payra | 419 | 18:30 | 408 | 01:00
| BIPTC | 398 | 07:00 | 392 | 00:00
| Gopalganj_I | 413 | 18:30 | 395 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 02:00 | 216 | 12:00 | Hathazari | 239 | 21:00 | 222 | 12:00
| AKSML | 237 | 20:00 | 220 | 12:00 | Ishurdi | 236 | 18:30 | 213 | 06:00
| Aminbazar | 226 | 00:00 | 216 | 11:00 | Jhenaidah | 234 | 18:30 | 219 | 23:00
| Baghabari | 233 | 06:00 | 226 | 23:00 | Kaliakoir | 227 | 04:00 | 219 | 12:00
| Barapukuria | 230 | 18:30 | 215 | 00:00 | Keranigonj | 225 | 02:00 | 215 | 12:00
| Barishal | 241 | 07:00 | 224 | 23:00 | Khulna(S) | 242 | 18:30 | 226 | 01:00
| Bheramara | 233 | 18:30 | 224 | 00:00 | Maniknagar | 228 | 06:00 | 219 | 12:00
| Bhulta | 230 | 01:00 | 220 | 12:00 | Meghnaghat | 230 | 00:00 | 225 | 09:00
| Bibiana | 241 | 07:00 | 234 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 18:30 | 224 | 01:00 | Rajshahi | 234 | 18:00 | 222 | 19:30
| Bogura | 233 | 18:30 | 220 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 08:00 | 233 | 23:00 | Rampura | 228 | 03:00 | 218 | 12:00
| BSRM | 235 | 20:00 | 221 | 12:00 | Shikalbaha | 239 | 22:00 | 224 | 12:00
| Cumilla(N) | 231 | 08:00 | 224 | 12:00 | Shyampur | 226 | 02:00 | 217 | 12:00
| Fenchuganj | 243 | 07:00 | 237 | 15:00 | Siddhirganj | 230 | 01:00 | 221 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 18:30 | 227 | 00:00
| GPH | 235 | 22:00 | 219 | 07:00 | Tongi | 227 | 21:00 | 219 | 09:00
| Haripur | 227 | 00:00 | 219 | 11:00
| Hasnabad | 227 | 20:00 | 217 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 03:00 | 125 | 12:00 | Manikganj | 130 | 08:00 | 123 | 15:00
| Agargaon | 135 | 04:00 | 127 | 12:00 | Maniknagar | 135 | 04:00 | 127 | 12:00
| Agrabad | 139 | 20:00 | 129 | 11:00 | Matarbari | 127 | 20:00 | 118 | 12:00
| AKS | 137 | 02:00 | 135 | 03:00 | Matuail | 133 | 01:00 | 126 | 12:00
| Aminbazar | 132 | 00:00 | 127 | 07:00 | Millgate | 134 | 01:00 | 127 | 12:00
| Amnura | 134 | 18:30 | 125 | 02:00 | Mirpur | 135 | 03:00 | 125 | 12:00
| Ashuganj | 138 | 06:00 | 135 | 00:00 | Mithapukur | 136 | 18:30 | 123 | 01:00
| Bagerhat | 135 | 18:30 | 124 | 04:00 | Modern | 139 | 22:00 | 128 | 12:00
| Bakulia | 139 | 21:00 | 129 | 12:00 | Mogbazar | 136 | 04:00 | 127 | 12:00
| Banani | 134 | 01:00 | 128 | 12:00 | Mongla | 134 | 18:30 | 125 | 01:00
| Bangabhaban | 134 | 00:00 | 127 | 12:00 | Motijheel | 134 | 00:00 | 127 | 12:00
| Barapukuria | 137 | 18:00 | 127 | 00:00 | Munshiganj | 135 | 20:00 | 128 | 12:00
| Barguna | 137 | 06:00 | 130 | 21:00 | Mymensingh | 133 | 16:00 | 124 | 19:00
| Barishal | 138 | 07:00 | 130 | 21:00 | Naogaon | 134 | 18:30 | 122 | 00:00
| Barishal | 139 | 07:00 | 132 | 19:30 | Narail | 136 | 06:00 | 126 | 23:00
| Baroaulia | 140 | 20:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 133 | 06:00 | 126 | 04:00 | Narshingdi | 133 | 07:00 | 122 | 12:00
| Bashundhara | 134 | 00:00 | 126 | 12:00 | Natore | 135 | 18:30 | 127 | 19:30
| BashundharaCement | 134 | 01:00 | 128 | 09:00 | Nawabganj | 136 | 03:00 | 129 | 12:00
| Beanibazar | 137 | 06:00 | 131 | 19:00 | Netrakona | 133 | 18:00 | 119 | 19:00
| Benapole | 136 | 18:30 | 126 | 04:00 | New | 134 | 01:00 | 127 | 12:00
| Bhaluka | 132 | 18:30 | 119 | 19:00 | Niamatpur | 133 | 18:30 | 120 | 23:00
| Bhandaria | 137 | 08:00 | 125 | 21:00 | Noapara | 139 | 18:30 | 129 | 01:00
| Bhangura | 139 | 18:30 | 132 | 00:00 | Pabna | 136 | 18:30 | 126 | 12:00
| Bheramara | 137 | 18:30 | 132 | 00:00 | Palashbari | 134 | 18:00 | 121 | 00:00
| Bheramara(GK) | 140 | 18:30 | 133 | 00:00 | Panchagarh | 136 | 18:00 | 118 | 19:30
| Bhulta | 125 | 20:00 | 121 | 07:00 | Patuakhali | 136 | 06:00 | 132 | 01:00
| Bog-Sherpur | 135 | 18:00 | 128 | 00:00 | Payra | 138 | 09:00 | 134 | 21:00
| Bogura | 136 | 17:00 | 129 | 00:00 | PHP | 132 | 06:00 | 126 | 02:00
| Bogura | 140 | 20:00 | 130 | 00:00 | Purbachal | 135 | 01:00 | 126 | 08:00
| Brahmanbaria | 133 | 06:00 | 127 | 00:00 | Purbasadipur | 138 | 18:00 | 121 | 00:00
| Cantonment | 134 | 03:00 | 126 | 12:00 | Rahim | 134 | 20:00 | 129 | 11:00
| Chandpur | 138 | 06:00 | 133 | 01:00 | Rajbari | 135 | 18:30 | 126 | 21:00
| Chandraghona | 140 | 21:00 | 130 | 12:00 | Rajendrapur | 130 | 06:00 | 122 | 15:00
| Chapai | 134 | 18:00 | 127 | 01:00 | Rajshahi | 133 | 18:00 | 124 | 02:00
| Charsaidpur | 135 | 20:00 | 129 | 09:00 | Rajshahi | 133 | 17:00 | 125 | 03:00
| Chauddagram | 133 | 09:00 | 128 | 02:00 | Ramganj | 135 | 09:00 | 126 | 01:00
| Chhatak | 137 | 02:00 | 133 | 19:00 | Rampur | 137 | 20:00 | 132 | 05:00
| Chowmuhani | 132 | 18:00 | 126 | 01:00 | Rampura | 134 | 03:00 | 126 | 12:00
| Chuadanga | 134 | 09:00 | 121 | 23:00 | Rangamati | 139 | 21:00 | 129 | 12:00
| Coxsbazar | 127 | 19:30 | 115 | 11:00 | Rangpur | 134 | 18:30 | 120 | 19:30
| Cumilla(N) | 134 | 20:00 | 130 | 12:00 | Ruppur | 136 | 18:00 | 131 | 23:00
| Cumilla(S) | 135 | 05:00 | 126 | 12:00 | Saidpur | 136 | 18:00 | 122 | 23:00
| Daudkandi | 132 | 18:30 | 123 | 10:00 | Satkhira | 136 | 18:30 | 124 | 02:00
| Dhaka | 135 | 06:00 | 126 | 12:00 | Satmasjid | 135 | 03:00 | 127 | 12:00
| Dhamrai | 132 | 06:00 | 126 | 09:00 | Savar | 133 | 02:00 | 126 | 12:00
| Dhanmondi | 134 | 06:00 | 127 | 12:00 | Shahjadpur | 140 | 18:00 | 135 | 11:00
| Dohazari | 137 | 20:00 | 126 | 12:00 | Shahjibazar | 135 | 04:00 | 132 | 00:00
| Faridpur | 134 | 06:00 | 126 | 21:00 | Shahmirpur | 141 | 21:00 | 130 | 12:00
| Fatullah | 135 | 20:00 | 127 | 12:00 | Shariatpur | 137 | 10:00 | 127 | 21:00
| Fenchuganj | 140 | 06:00 | 135 | 19:00 | Sherpur | 137 | 16:00 | 126 | 19:00
| Feni | 139 | 03:00 | 127 | 15:00 | Shikalbaha | 141 | 20:00 | 133 | 05:00
| Ghorashal | 139 | 20:00 | 136 | 15:00 | Shikalbaha | 141 | 22:00 | 131 | 12:00
| Goalpara | 139 | 18:30 | 128 | 01:00 | Shitalakhya | 135 | 02:00 | 129 | 11:00
| Gollamari | 136 | 08:00 | 124 | 21:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gopalganj | 136 | 08:00 | 126 | 21:00 | Shyampur | 134 | 20:00 | 127 | 09:00
| Gopalganj_I | 138 | 07:00 | 129 | 23:00 | Shyampur | 135 | 20:00 | 127 | 12:00
| Gulshan | 134 | 02:00 | 125 | 12:00 | Siddhirganj | 133 | 00:00 | 128 | 12:00
| Halishahar | 139 | 20:00 | 128 | 12:00 | Sirajganj | 136 | 18:30 | 129 | 19:30
| Haripur | 134 | 20:00 | 129 | 11:00 | Sonargaon | 134 | 00:00 | 128 | 07:00
| HaripurSBU | 134 | 20:00 | 129 | 12:00 | Sreemongol | 137 | 04:00 | 134 | 00:00
| Hasnabad | 135 | 00:00 | 131 | 13:00 | Srinagar | 136 | 02:00 | 129 | 12:00
| Hathazari | 140 | 21:00 | 131 | 12:00 | SSM | 142 | 20:00 | 132 | 11:00
| Ishurdi | 138 | 18:30 | 132 | 01:00 | Sunamganj | 136 | 03:00 | 132 | 22:00
| Jaldhaka | 133 | 17:00 | 117 | 19:30 | Sylhet | 136 | 02:00 | 133 | 19:30
| Jamalpur | 139 | 16:00 | 131 | 00:00 | Tangail | 134 | 05:00 | 126 | 21:00
| Jashore | 137 | 18:30 | 127 | 01:00 | Thakurgaon | 136 | 18:00 | 120 | 23:00
| Jhenaidah | 137 | 07:00 | 128 | 23:00 | TK | 140 | 20:00 | 130 | 12:00
| Jhenaidah | 139 | 18:30 | 129 | 01:00 | Tongi | 136 | 07:00 | 130 | 09:00
| Joydebpur | 141 | 20:00 | 131 | 08:00 | Ullon | 134 | 04:00 | 126 | 12:00
| Joypurhat | 135 | 18:30 | 116 | 22:00 | Uttara | 132 | 02:00 | 124 | 15:00
| Juldah | 141 | 21:00 | 130 | 12:00 | UttaraNew | 132 | 01:00 | 126 | 08:00
| Kabirpur | 132 | 05:00 | 124 | 15:00 | Zigatola | 135 | 02:00 | 129 | 12:00
| Kachua | 136 | 18:30 | 130 | 02:00
| Kaliakoir | 134 | 06:00 | 129 | 12:00
| Kallyanpur | 133 | 23:00 | 125 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 236 | 8928 | 4128 | 13056 |  |  |  | QF-LDC-11
0:30 | 223 | 8726.5 | 3965.5 | 12692 | Date: | 2022-06-23
1:00 | 210 | 8525 | 3803 | 12328
1:30 | 221 | 8378.5 | 3726 | 12104.5
2:00 | 232 | 8232 | 3649 | 11881
2:30 | 209 | 8059.5 | 3574 | 11633.5 | [5 empty] | Gen. at Eve. Peak | 13194 | 13194 MW (19:30 )
3:00 | 186 | 7887 | 3499 | 11386 | [6 empty] | 19:30
3:30 | 172 | 7792.5 | 3463 | 11255.5 | [5 empty] | Gen. at Day Peak | 11338 | 11338 MW (12:00 )
4:00 | 158 | 7698 | 3427 | 11125 | [6 empty] | 12:00
4:30 | 103 | 7454 | 3429.5 | 10883.5 | [5 empty] | Highest Generation | 13212
5:00 | 48 | 7210 | 3432 | 10642 | [6 empty] | 22:00
5:30 | 37 | 7008.5 | 3270.5 | 10279
6:00 | 26 | 6807 | 3109 | 9916
6:30 | 22 | 6750 | 3074 | 9824
7:00 | 18 | 6693 | 3039 | 9732
7:30 | 104 | 6684 | 3070.5 | 9754.5
8:00 | 190 | 6675 | 3102 | 9777
8:30 | 210 | 6853 | 3146 | 9999
9:00 | 230 | 7031 | 3190 | 10221
9:30 | 191 | 7287.5 | 3200 | 10487.5
10:00 | 152 | 7544 | 3210 | 10754
10:30 | 158 | 7672.5 | 3239.5 | 10912
11:00 | 164 | 7801 | 3269 | 11070
11:30 | 147 | 7877 | 3327 | 11204
12:00 | 130 | 7953 | 3385 | 11338
12:30 | 97 | 8072 | 3415.5 | 11487.5
13:00 | 64 | 8191 | 3446 | 11637
13:30 | 42 | 8196.5 | 3411 | 11607.5
14:00 | 20 | 8202 | 3376 | 11578
14:30 | 92 | 8232.5 | 3436.5 | 11669
15:00 | 164 | 8263 | 3497 | 11760
15:30 | 191 | 8136.5 | 3540.5 | 11677
16:00 | 218 | 8010 | 3584 | 11594
16:30 | 241 | 7888 | 3504 | 11392
17:00 | 264 | 7766 | 3424 | 11190
17:30 | 265 | 7640 | 3354.5 | 10994.5
18:00 | 266 | 7514 | 3285 | 10799
18:30 | 268 | 7800 | 3501.5 | 11301.5
19:00 | 270 | 8086 | 3718 | 11804
19:30 | 162 | 9096 | 4098 | 13194
20:00 | 214 | 9103 | 4053 | 13156 |  |  |  | Executive Engineer
20:30 | 216 | 9065.5 | 4080.5 | 13146 |  |  |  | Network Operation Division
21:00 | 218 | 9028 | 4108 | 13136
21:30 | 233 | 9059 | 4115 | 13174
22:00 | 248 | 9090 | 4122 | 13212 |  |  |  |  | Page 6 of 7
22:30 | 241 | 9053.5 | 4134 | 13187.5
23:00 | 234 | 9017 | 4146 | 13163
23:30 | 235 | 8972.5 | 4137 | 13109.5
24:00 | 236 | 8928 | 4128 | 13056
13194 MW (19:30 )
11338 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-23 |  | Energy |  | 287972408
[13 empty] | 2022-06-23 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4276 | 924 | 2373 | 130 | 3760 | 785 | 122 | 0 | 536 | 150 | 0 | 0
0:30 | 4248 | 924.5 | 2351 | 65 | 3703.5 | 745 | 118.5 | 0 | 392.5 | 144 | 0 | 0 | Date: | 2022-06-23
1:00 | 4220 | 925 | 2329 | 0 | 3647 | 705 | 115 | 0 | 249 | 138 | 0 | 0
1:30 | 4227 | 925 | 2317 | 0 | 3498.5 | 695 | 115 | 0 | 189 | 138 | 0 | 0 | [7 empty] | Total Energy | 287.9724 | Total Energy Gen 287.972 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 287.972 MKWHr
2:00 | 4234 | 925 | 2305 | 0 | 3350 | 685 | 115 | 0 | 129 | 138 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4233 | 924.5 | 2311.5 | 0 | 3176 | 665 | 115 | 0 | 72.5 | 136 | 0 | 0 | [7 empty] | Energy Requirement | 287.9724
3:00 | 4232 | 924 | 2318 | 0 | 3002 | 645 | 115 | 0 | 16 | 134 | 0 | 0
3:30 | 4243 | 924 | 2327 | 0 | 2871.5 | 635 | 115 | 0 | 8 | 132 | 0 | 0 | [5 empty] | Shortage
4:00 | 4254 | 924 | 2336 | 0 | 2741 | 625 | 115 | 0 | 0 | 130 | 0 | 0
4:30 | 4233 | 924 | 2328 | 0 | 2516.5 | 635 | 119 | 0 | 0 | 128 | 0 | 0
5:00 | 4212 | 924 | 2320 | 0 | 2292 | 645 | 123 | 0 | 0 | 126 | 0 | 0
5:30 | 4083 | 923.5 | 2211.5 | 0 | 2166.5 | 645 | 123 | 0 | 0 | 121 | 5.5 | 0
6:00 | 3954 | 923 | 2103 | 0 | 2041 | 645 | 123 | 0 | 0 | 116 | 11 | 0
6:30 | 3969.5 | 923.5 | 2113.5 | 0 | 1922.5 | 635 | 123 | 0 | 0 | 111 | 26 | 0 |  |  |  | Coal
7:00 | 3985 | 924 | 2124 | 0 | 1804 | 625 | 123 | 0 | 0 | 106 | 41 | 0
7:30 | 3993 | 923.5 | 2112 | 0 | 1795 | 625 | 123 | 0 | 8 | 110 | 65 | 0 |  |  | Oil |  |  |  | ,
8:00 | 4001 | 923 | 2100 | 0 | 1786 | 625 | 123 | 0 | 16 | 114 | 89 | 0
8:30 | 4116 | 923.5 | 2069.5 | 0 | 1912 | 620 | 123 | 0 | 16 | 122 | 97 | 0
9:00 | 4231 | 924 | 2039 | 0 | 2038 | 615 | 123 | 0 | 16 | 130 | 105 | 0
9:30 | 4249 | 924 | 2015.5 | 0 | 2309 | 595 | 123 | 0 | 32 | 132 | 108 | 0
10:00 | 4267 | 924 | 1992 | 0 | 2580 | 575 | 123 | 0 | 48 | 134 | 111 | 0
10:30 | 4360.5 | 923.5 | 2001.5 | 0 | 2616 | 575 | 123 | 0 | 48 | 132 | 132.5 | 0
11:00 | 4454 | 923 | 2011 | 0 | 2652 | 575 | 123 | 0 | 48 | 130 | 154 | 0
11:30 | 4449.5 | 923.5 | 2059.5 | 0 | 2743.5 | 575 | 101 | 0 | 50 | 133 | 169 | 0
12:00 | 4445 | 924 | 2108 | 0 | 2835 | 575 | 79 | 0 | 52 | 136 | 184 | 0
12:30 | 4469.5 | 924 | 2099.5 | 0 | 3000 | 585 | 79 | 0 | 47.5 | 140 | 143 | 0
13:00 | 4494 | 924 | 2091 | 0 | 3165 | 595 | 79 | 0 | 43 | 144 | 102 | 0
13:30 | 4494 | 924 | 2091 | 0 | 3165 | 595 | 79 | 0 | 43 | 144 | 102 | 0
14:00 | 4494 | 924 | 2091 | 0 | 3165 | 595 | 79 | 0 | 43 | 144 | 102 | 0
14:30 | 4421.5 | 924 | 2174 | 0 | 3185 | 570 | 80 | 0 | 97.5 | 146 | 100.5 | 0
15:00 | 4349 | 924 | 2257 | 0 | 3205 | 545 | 81 | 0 | 152 | 148 | 99 | 0
15:30 | 4254 | 923 | 2238 | 0 | 3216 | 559.5 | 81 | 0 | 150.5 | 146 | 109 | 0
16:00 | 4159 | 922 | 2219 | 0 | 3227 | 574 | 81 | 0 | 149 | 144 | 119 | 0
16:30 | 4191 | 922.5 | 2191 | 0 | 3082.5 | 569.5 | 81 | 0 | 151.5 | 142 | 77 | 0
17:00 | 4191 | 923 | 2163 | 0 | 2938 | 565 | 81 | 0 | 154 | 140 | 35 | 0
17:30 | 4105 | 923 | 2122.5 | 0 | 2875 | 565 | 81 | 0 | 164.5 | 137 | 21.5 | 0
18:00 | 4019 | 923 | 2082 | 0 | 2812 | 565 | 81 | 0 | 175 | 134 | 8 | 0
18:30 | 4081.5 | 923 | 2173.5 | 0 | 3004 | 575 | 81 | 0 | 316.5 | 143 | 4 | 0
19:00 | 4144 | 923 | 2265 | 0 | 3196 | 585 | 81 | 0 | 458 | 152 | 0 | 0
19:30 | 4312 | 923 | 2349 | 358 | 3743 | 715 | 81 | 0 | 557 | 156 | 0 | 0
20:00 | 4279 | 924 | 2247 | 347 | 3809 | 735 | 113 | 0 | 552 | 150 | 0 | 0
20:30 | 4309 | 924 | 2266.5 | 238.5 | 3844 | 745 | 118 | 0 | 551 | 150 | 0 | 0
21:00 | 4339 | 924 | 2286 | 130 | 3879 | 755 | 123 | 0 | 550 | 150 | 0 | 0
21:30 | 4332 | 924 | 2329.5 | 130 | 3879 | 755 | 122.5 | 0 | 553 | 149 | 0 | 0
22:00 | 4325 | 924 | 2373 | 130 | 3879 | 755 | 122 | 0 | 556 | 148 | 0 | 0
22:30 | 4298.5 | 923.5 | 2376.5 | 130 | 3874.5 | 765 | 121.5 | 0 | 549 | 149 | 0 | 0
23:00 | 4272 | 923 | 2380 | 130 | 3870 | 775 | 121 | 0 | 542 | 150 | 0 | 0
23:30 | 4274 | 923.5 | 2376.5 | 130 | 3815 | 780 | 121.5 | 0 | 539 | 150 | 0 | 0 | Max Temp. in Dhaka |  | 33.2° C
24:00 | 4276 | 924 | 2373 | 130 | 3760 | 785 | 122 | 0 | 536 | 150 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 287.972 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 287.972 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 80 | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 44 | 44 | 44 | 46 | 46 | 46 | 46 |  | 46 | 46 | 78 | 88 | 87 | 86 | 87 | 1778198
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [10 empty] | 16 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 327400
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 4 | 7 | 16 |  | 11 | 8 | 18 | 0 | 10 | 9 | 4 | 1 | [8 empty] | 81945
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 39 | 289975
12 | Hathazari 100 MW peaking PP | [19 empty] | 20 | 43 | 44 | 44 | 51 | 51 | 51 | 242976
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 91 | 87 | 91 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2493199
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [13 empty] | 49 | 49 | 47 | 48 | 48 |  | 49 | 49 | 49 | 49 | 49 | 34 | 41 | 516824
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 280 | 280 | 335 | 335 | 336 | 336 | 336 | 331 | 335 | 334 | 335 | 335 | 335 | 270 |  | 290 | 337 | 336 | 335 | 337 | 337 | 336 | 7948803
18 | Kodda 300 MW PP Unit-2 (Summit) | 293 | 291 | 291 | 195 | 80 | 45 | 15 | 15 | 17 | 132 | 173 | 268 | 281 | 291 | 285 | 283 | 230 | 195 |  | 215 | 285 | 291 | 291 | 291 | 291 | 291 | 5286653
19 | Ashuganj 195MW PP (APSCL-United) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 147 | 147 | 147 | 147 | 148 | 148 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3111272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 32 | 32 | 32 | 32 | 31 | 19 | 19 | 30 | 31 |  | 33 | 33 | 33 | 33 | 33 | 15 | 20 | 690480
33 | Ashuganj 225 MW CCPP | 182 | 181 | 182 | 182 | 182 | 182 | 193 | 183 | 183 | 182 | 182 | 189 | 212 | 183 | 190 | 179 | 180 | 180 |  | 193 | 200 | 213 | 210 | 209 | 211 | 213 | 4639000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 270 | 280 | 270 | 300 | 300 | 300 | 315 | 300 | 300 | 320 | 305 | 305 | 290 |  | 290 | 335 | 305 | 320 | 305 | 305 | 305 | 7381000
| Ashuganj 450 MW CCPP(North) | 330 | 330 | 330 | 330 | 330 | 280 | 300 | 280 | 365 | 270 | 270 | 280 | 270 | 270 | 285 | 270 | 280 | 280 |  | 310 | 355 | 320 | 340 | 345 | 315 | 315 | 7639500
| Ashuganj 420 MW CCPP(East) | [9 empty] | 140 | 300 | 299 | 302 | 302 | 240 | 0 | [10 empty] | 1552900
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 50 | 51 | 51 | 51 | 52 | 52 | 52 | 5 | 0 |  |  | 17 | 46 | 50 | 51 |  | 51 | 51 | 52 | 52 | 51 | 51 | 51 | 1014720
36 | Chandpur 150 MW CCPP | 136 | 137 | 135 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 136 | 136 | 136 | 138 | 137 | 136 | 136 |  | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 3258510
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 409 | 408 | 408 | 408 | 408 | 409 | 410 | 411 | 410 | 411 | 411 | 409 | 411 | 410 | 411 | 411 | 411 |  | 411 | 410 | 408 | 411 | 411 | 411 | 410 | 9971710
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 430 | 450 | 450 | 9492250
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 164 | 175 | 175 | 178 | 186 | 178 | 174 | 162 | 156 | 152 | 146 | 147 | 147 | 149 | 150 | 150 | 149 | 155 |  | 154 | 154 | 154 | 166 | 164 | 159 | 159 | 3751680
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 4 | 19 | 30 | 36 | 53 | 46 | 20 | 43 | 30 | 20 | 11 | 1 |  | 0 | [6 empty] | 287250
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 44 | 43 | 44 | 44 | 44 | 44 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1033000
45 | Fenchugonj CCPP Phase-2 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 21 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 581184
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 51 | 51 | 52 | 52 | 40 | 63 | 65 | 59 | 59 | 60 | 55 | 55 | 45 | 45 | 45 | 63 | 64 |  | 63 | 56 | 56 | 56 | 56 | 56 | 57 | 1315680
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 82 | 81 | 81 | 81 | 81 | 81 |  | 0 | 38 | 38 | 61 | 81 | 81 | 81 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1681920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2895300
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 25 | 25 | 25 | 25 | 25 | 23 | 23 | 23 | 23 | 23 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 574280
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 210060
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 1078800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 15 | 15 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 372096
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 270 | 280 | 270 | 280 | 270 | 290 | 290 | 310 | 275 | 280 | 280 | 300 | 265 | 300 | 290 | 270 | 270 |  | 275 | 315 | 310 | 285 | 300 | 295 | 300 | 7014500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 400 | 400 | 400 | 400 | 400 | 350 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9221400
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 33 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 45 | 55 | 55 | 55 | 973771
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 569760
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508128
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 326808
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 378540
63 | Impoprt (Tripura) | 138 | 138 | 134 | 130 | 126 | 116 | 106 | 114 | 130 | 134 | 130 | 136 | 144 | 148 | 148 | 144 | 140 | 134 |  | 152 | 156 | 150 | 150 | 148 | 150 | 150 | 3264960
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 36 | 27 | 8 | 3 | 8 | 8 | 6 | 9 | 7 | 3 | 2 | 3 | 14 |  | 14 | 25 | 3 | 30 | 30 | 37 | 37 | 489120
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 461232
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 202140
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 |  |  | 31 | 0 | 0 | 0 |  | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 32 | 33 | 33 | 513900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 0 |  | 20 | 20 | 12 | 12 | 12 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 22 | 23 | 23 | 24 | 25 | 25 | 26 | 28 |  | 20 | 20 | 28 | 28 | 28 | 28 | 28 | 578700
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 738400
72 | Rupganj 33 MW PP(Summit)
73 | Ghorashal 108MW PP (Regent) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 68 | 68 | 70 | 70 | 70 | 71 | 75 | 76 | 78 |  | 81 | 81 | 81 | 79 | 79 | 79 | 79 | 1759500
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 37 | 38 | 38 | 38 | 38 | 75 | 94 | 95 | 94 | 67 | 63 | 38 | 38 | 37 | 38 | 52 | 94 | 94 |  | 94 | 95 | 94 | 94 | 94 | 94 | 40 | 1594320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 72 | 17 | 17 | 17 | 17 | 17 | 26 | 108 | 112 | 156 | 162 | 162 | 162 | 162 | 108 | 108 |  | 115 | 162 | 162 | 162 | 162 | 162 | 162 | 2806560
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 67 | 28 | 8 | 8 | 8 | 8 | 8 | 9 | 45 | 50 | 80 | 91 | 93 | 100 | 100 | 76 | 50 |  | 50 | 70 | 95 | 100 | 100 | 100 | 100 | 1491840
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 32 | 24 | 24 | 42 | 42 | 49 | 49 | 49 | 48 | 32 | 32 | 32 | 32 | 32 |  | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 1006560
79 | Kodda 150MW PP | 115 | 82 | 16 | 0 |  |  |  | 16 | 16 | 48 | 48 | 48 | 0 | 48 | 48 | 48 | 48 | 48 |  | 98 | 150 | 150 | 150 | 150 | 150 | 150 | 1459200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 70 | 52 | 34 | 34 | 34 | 70 | 70 | 70 | 90 | 90 | 90 | 105 | 52 | 35 |  | 40 | 105 | 105 | 105 | 105 | 105 | 105 | 2002800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 5 | 3 | 5 | 6 | 0 | 2 | 0 | 1 | 0 | [8 empty] | 25920
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 37 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1313003
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 85 | 85 | 85 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 98 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2606098
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 285 | 260 | 275 | 300 | 275 | 275 | 300 | 305 | 280 | 275 | 255 | 300 | 250 | 275 | 285 | 265 | 255 | 270 |  | 305 | 300 | 270 | 290 | 300 | 285 | 265 | 6773207
87 | Meghnaghat 100 MW(IEL) | 81 | 81 | 82 | 81 | 82 | 82 | 77 | 74 | 82 | 82 | 80 | 80 | 80 | 80 | 79 | 80 | 72 | 76 |  | 76 | 88 | 87 | 86 | 88 | 87 | 88 | 1957440
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 92 | 85 | 73 | 72 | 82 | 84 | 92 | 94 | 94 | 94 | 94 | 94 | 94 | 54 |  | 58 | 94 | 94 | 93 | 94 | 94 | 95 | 2188800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 54 | 54 | 54 | 54 | 30 | 30 | 10 | 10 | 50 | 50 | 50 | 50 | 55 | 10 | 31 | 50 | 40 | 40 |  | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 882960
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 49 | 49 | 49 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1056528
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 |  | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 1017118
94 | Gagnagar 102 MW PP (Digital Power) | 85 | 85 | 32 | 16 | 7 | 7 | 7 | 7 | 16 | 32 | 75 | 85 | 85 | 85 | 85 | 85 | 64 | 64 |  | 85 | 94 | 94 | 94 | 94 | 94 | 94 | 1469520
95 | Patenga 50MW PP (Baraka) | 44 | 44 | 44 | 44 | 38 | 38 | 38 | 34 | 31 | 31 | 31 | 31 | 30 | 9 | 28 | 31 | 36 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 8438400
96 | Chattogram 108 MW PP (ECPV) | 67 | 0 | [10 empty] | 9 | 40 | 41 | 39 | 45 | 42 |  | 49 | 62 | 72 | 91 | 91 | 91 | 91 | 776640
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1272654
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1162014
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2694763
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 14850
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1306800
104 | Keranigonj 300 MW PP (APR) | [20 empty] | 122 | 122 |  |  |  |  | 121139
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 86 | 85 | 50 | 50 | 50 | 50 | 277925
106 | Mymensingh 200 MW PP (United) | 181 | 181 | 181 | 181 | 181 | 181 | 140 | 140 | 144 | 172 | 171 | 170 | 160 | 160 | 160 | 160 | 169 | 180 |  | 181 | 181 | 181 | 182 | 183 | 183 | 191 | 4104000
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 80 | 80 | 30 | 30 | 30 | 30 | 193784
114 | Kodda 149 MW PP Unit-1 (Summit) | 116 | 115 | 123 | 134 | 133 | 133 | 133 | 133 | 135 | 133 | 123 | 118 | 116 | 132 | 123 | 115 | 112 | 115 |  | 98 | 112 | 115 | 113 | 131 | 128 | 116 | 2970580
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 76 | 76 | 76 | 63 | 63 | 63 | 63 | 63 | 63 | 40 |  | 80 | 83 | 86 | 90 | 76 | 76 | 76 | 1723200
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 88 | 120 | 120 | 120 | 75 | 70 | 117 | 120 | 120 | 120 | 120 | 145 | 155 |  | 158 | 200 | 200 | 200 | 200 | 200 | 200 | 3074880
117 | Ashuganj 150MW PP (Midland) | 123 | 118 | 132 | 137 | 60 | 60 | 30 | 30 | 38 | 103 | 122 | 125 | 133 | 138 | 132 | 133 | 137 | 137 |  | 143 | 143 | 143 | 143 | 145 | 145 | 123 | 2835272
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 401 | 352 | 352 | 352 | 401 | 401 | 401 | 402 | 409 | 365 | 404 | 402 | 402 | 352 |  | 396 | 400 | 401 | 402 | 401 | 401 | 401 | 9376000
| Jamalpur 115 MW PP (United) | 107 | 107 | 108 | 108 | 35 | 8 | 8 | 8 | 11 | 32 | 32 | 32 | 56 | 64 | 65 | 65 | 45 | 45 |  | 48 | 96 | 98 | 100 | 102 | 104 | 99 | 1561200
| Anwara 300 MW PP (United) | 266 | 155 | 15 | [5 empty] | 15 | 30 | 30 | 30 | 130 | 100 | 100 | 100 | 45 | 45 |  | 155 | 220 | 259 | 282 | 264 | 268 | 267 | 2601927
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 79 | 70 | 82 | 90 | 90 | 90 | 90 | 79 | 64 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1817280
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2152800
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 890280
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 3 | 4 | 8 | 14 | 13 | 12 | 16 | 20 | 19 | 8 | 8 | 2 | [8 empty] | 121508
| Chandpur 115(Doreen) | 116 | 112 | 116 | 116 | 116 | 116 | 108 | 109 | 116 | 116 | 100 | 108 | 101 | 115 | 116 | 116 | 116 | 116 |  | 116 | 116 | 113 | 116 | 116 | 108 | 116 | 2726400
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 34 | 34 | 34 | 34 | 43 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1241280
120 | Eastern Zone Total | 8525 | 8232 | 7887 | 7698 | 7210 | 6807 | 6693 | 6675 | 7031 | 7544 | 7801 | 7953 | 8191 | 8202 | 8263 | 8010 | 7766 | 7514 |  | 8086 | 9096 | 9103 | 9028 | 9090 | 9017 | 8928 | 200473494
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 52 |  | 103 | 103 | 98 | 105 | 101 | 108 | 100 | 1179840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 35 | 42 | 35 | 33 | 33 | 33 | 33 | 198720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 35 | 17 | 17 | 17 |  | 5 | 35 | 35 | 35 | 40 | 70 | 62 | 56 | 35 | 35 |  | 35 | 76 | 60 | 76 | 76 | 76 | 75 | 1254240
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 7 | 27 | 52 | 40 | 48 | 61 | 98 | 27 | 15 | 26 | 75 | 7 | 4 | [8 empty] | 583200
131
132 | United Payra Power Ltd. | [19 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 121200
133 | Bhola Nutan Biddut BD LTD (GAS) | 228 | 227 | 227 | 227 | 227 | 163 | 163 | 164 | 164 | 163 | 224 | 224 | 223 | 225 | 220 | 222 | 222 | 168 |  | 222 | 222 | 223 | 225 | 226 | 226 | 227 | 5052682
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 0 | [15 empty] | 16 | 16 | 16 | 0 |  |  |  | 88032
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 86 | 85 | 86 | 84 | 82 | 84 | 84 | 84 |  | 83 | 83 | 87 | 84 | 84 | 86 | 87 | 2112962
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 26 | 25 | 24 | 22 | 17 | 18 | 18 | 17 | 18 | 20 | 19 | 19 | 22 | 21 | 19 | 19 |  | 26 | 27 | 28 | 29 | 31 | 31 | 30 | 543226
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [10 empty] | 70 | 60 | 50 | 50 | 50 | 50 | 289920
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 8 | 8 | 32 | 32 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 409500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 91440
146 | Bheramara HVDC | 925 | 925 | 924 | 924 | 924 | 923 | 924 | 923 | 924 | 924 | 923 | 924 | 924 | 923 | 924 | 922 | 923 | 923 |  | 923 | 923 | 924 | 924 | 924 | 923 | 924 | 22339636
147 | Bheramara 410 MW CCPP | 280 | 280 | 280 | 295 | 295 | 305 | 315 | 330 | 330 | 330 | 330 | 330 | 325 | 325 | 320 | 315 | 305 | 300 |  | 305 | 305 | 305 | 305 | 300 | 295 | 295 | 7607520
148 | Payra 1320 MW | 530 | 510 | 470 | 450 | 470 | 470 | 450 | 450 | 440 | 400 | 400 | 400 | 420 | 360 | 370 | 400 | 390 | 390 |  | 410 | 540 | 560 | 580 | 580 | 600 | 610 | 12160100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 174 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4281100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 0 | [17 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 226704
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 3 | 5 | 5 | 5 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 38460
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 172 | 172 | 172 | 172 | 178 | 150 | 150 | 169 | 202 | 184 | 185 | 183 | 191 | 160 | 165 | 206 | 206 | 188 |  | 160 | 175 | 179 | 186 | 184 | 184 | 182 | 4517918
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 203 | 204 | 205 | 206 | 206 | 160 | 160 | 191 | 210 | 212 | 213 | 212 | 210 | 170 | 182 | 204 | 204 | 202 |  | 181 | 192 | 197 | 206 | 207 | 207 | 206 | 5065664
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 425 | 428 | 421 | 428 | 427 | 340 | 333 | 320 | 320 | 320 | 299 | 351 | 304 | 322 | 405 | 365 | 360 | 304 |  | 380 | 416 | 390 | 414 | 414 | 414 | 422 | 9048618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 4 | 26 | 38 | 31 | 30 | 30 | 30 |  | 29 | 29 | 29 | 29 | 29 | 30 | 29 | 339623
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 21 | 21 |  | 21 | 22 | 0 | 0 | 22 | 22 | 22 | 466800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251910
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 0 | [9 empty] | 16 | [13 empty] | 82592
167 | Katakhali 50 MW Peaking PP | 24 | 9 | 0 | [9 empty] | 17 | 24 | 24 | 24 | 28 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 341200
168 | Santahar 50 MW Peaking PP | 38 | 38 | 0 | [14 empty] | 13 |  | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 295380
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | 38 | 0 | [17 empty] | 72 | 89 | 90 | 90 | 90 | 90 | 90 | 536416
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 70 | 35 | 35 | 42 | 70 | 70 | 70 | 80 | 94 | 94 | 94 | 70 | 70 |  | 86 | 94 | 94 | 94 | 94 | 94 | 94 | 2019264
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 70 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 113 | 50 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2284320
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 70 | 69 | 42 | 42 | 41 | 56 | 69 | 68 | 68 | 70 | 68 | 68 | 69 | 69 | 94 |  | 95 | 91 | 95 | 95 | 95 | 95 | 70 | 1727808
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 7 | 7 | 6 | 4 | 2 | 0 | [8 empty] | 49607
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 72 | 52 | 52 | 52 | 34 | 34 | 35 | 35 | 35 | 35 | 50 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1893312
178