## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-26 | Sunday
|  |  | Date (day): | 2022-06-26 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13379.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14920 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-25 | 2022-06-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 87 | 84 | 87 |  | 21 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 411 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 142 | 0 | 0 | 360 |  | Gas line problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 80 | 89 | 80 | 89 |  | 11 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 305 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 75 | 98 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 270 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 85 | 95
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 53 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 238 | 278 | 270 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 27 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 30 | 25 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 79 | 134 | 134 | 134 |  | 15 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2988 | 3443 | 3766 | 3945 | 621 | 1249
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 43 | 43 | 43 |  | 7 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 123 | 125 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 34 | 0 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 30 | 30 | 30 | 30 |  | 70 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 23 | 82 | 80 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 230 | 300 | 265 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 34 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 76 | 77 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1122 | 1366 | 1154 | 1305 | 411 | 659
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 208 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 345 | 350 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 330 | 300 | 360 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 133 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 14 | 14 | 15 | 15 |  | 30 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 48 | 52 | 50 | 50
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 180 | 189 | 180 | 190
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 117 | 140 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 49 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 136 | 135 | 136 |  | 27 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 150 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 94 | 60 | 94 |  | 19 | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 116 | 99 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 2020 | 2178 | 2124 | 2472 | 300 | 95
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 176 | 129 | 120 | 130 | 72 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 177 | 200 | 180 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 92 | 108 | 110 | 110
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 540 | 481 | 503.6 | 484 | 72 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 330 |  | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 33 | 33 | 33
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 30 | 30 | 30
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 31 | 30 | 32 |  | 33 | Unit-8 Under maint.
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 81 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Flood in Sylhet
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 25 | 25 | 25 | 25
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Machine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 370 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1567 | 1634 | 1665 | 1698 | 330 | 380
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 883 | 940 | 940
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 112 | 63 | 20 | 60 |  | 55 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 40 |  | 14 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 385 | 400 | 400
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 70 | 90 |  | 15 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 100 | 0
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1423 | 1503 | 1663 | 2043 | 0 | 145
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 |  |  | Rampal Transformar O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 29 | 20 | 29 |  | 11 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 75 | 85 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 330 | 600 | 622 | 622 |  | 622 | Unit-2 S/D
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 223 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 645 | 953 | 998 | 1007 | 109 | 633
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 100 | 100 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 35 |  | 36 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 24 | 24 | 24 |  | 26 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 212 | 215 | 180 | 210
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 215 | 200 | 220
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 332 | 414 | 414 |  |  | FGMO
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 38 |  | 12 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 113 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1167 | 1376 | 1145 | 1558 | 433 | 122
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 68 | 102 | 70 | 100 |  | 13 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 108 | 108 | 108
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 284 | 385 | 361 | 408 | 269 | 13
|  | Total |  |  |  |  | 22348 | 21396 | 11756 | 13319 | 13379.6 | 14920 | 2545 | 3304
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11362.1621 | 12872.8 | 12931.3698 | 14420.1649
| A. |  | 2022-06-25 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13319 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9902 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13319 | MW
| 3 | Day peak Generation : |  |  | 11756 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12872.8 | MW
| 4 | Evening peak Generation : |  |  | 13319 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 283.7733 | MKWHr | By Solar | 1.3058 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 160.8351 | MKWHr |  | By Oil: | 78.081 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.6701 | MKWHr |  | By Hydro: | 2.9712 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2545 | MW | Dhaka | 4707.87 | 4707.87 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3304 | MW | Chittagong | 1391.3 | 1391.3 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5849 | MW | Khulna | 1555.2 | 1555.2 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1201.6 | MMCFD |  |  | Rajshahi | 1351.6 | 1351.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 183916096.494 | ii) Oil : | Taka | 1025715274.69 | Comilla | 1161 | 1161 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 125233265 | Total | Taka | 1334864636.184 | Mymensingh | 1025 | 1025 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.395 | MKWHr. | Sylhet | 445 | 445 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -202 | MW (E to W) at | 21:00 | hrs | Barisal | 357.83 | 357.83 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -206 | MW at | 22:00 | hrs | Rangpur | 878 | 878 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.3° C |  |  | Total | 12872.8 | 12872.8 |  | 0
| B. |  | 2022-06-26 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14920 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11900 | MW
| 4 | Reserve(Generation end) |  |  |  | 920 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 298.2826 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10295 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6989 | MKWHr. | ii) HVDC Flow at Peak Time |  | 883 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2112 | MKWHr. | iii) Maximum HVDC Flow : |  | 922 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.66 |  | (b) Today: | 88.94 |  | (c) Rule Curve: |  | 82.38
.

## YesterdayGen
2022-06-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 240 | 89 | 0 | 48 | 337 | 0 | 0 | 100 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 37 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 182 | 177 | 136 | 25 | 52 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 136 | 194 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 32 | 84 | 0 | 120 | 0 | 25 | 9 | 290 | 16 | 11 | 0 | 274 | 0 | 0 | 187 | 0 | 100 | 0 | 90 | 184 | 143 | 401 | 102 | 105 | 105 | 0 | 210 | 54 | 110 | 0 | 47 | 76 | 400 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 922 | 0 | 410 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 215 | 0 | 425 | 53 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 580 | 225 | 0 | 17 | 0 | 0 | 72 |  | 8515 | 3926 | 12441 | 4419 | 922 | 2378 | 0 | 3574 | 755 | 123 | 0 | 134 | 136 | 0 | 0 | 88.61
2:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 408 | 0 |  | 0 | 450 | 275 | 88 | 0 | 45 | 337 | 0 | 0 | 90 | 32 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 32 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 182 | 177 | 137 | 23 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 132 | 191 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 32 | 84 | 0 | 120 | 0 | 24 | 9 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 96 | 0 | 90 | 155 | 142 | 402 | 102 | 105 | 105 | 0 | 95 | 54 | 110 | 0 | 38 | 50 | 400 | 93 | 0 | 108 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 904 | 0 | 405 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 24 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 217 | 0 | 421 | 17 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 560 | 226 | 0 | 17 | 0 | 0 | 52 |  | 8091 | 3803 | 11894 | 4413 | 904 | 2385 | 0 | 3101 | 735 | 124 | 0 | 100 | 132 | 0 | 0 | 88.62
3:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 268 | 89 | 0 | 55 | 337 | 0 | 0 | 20 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 30 | 0 | 37 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 182 | 177 | 136 | 23 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 128 | 192 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 98 | 0 | 90 | 155 | 143 | 401 | 102 | 105 | 105 | 0 | 45 | 54 | 110 | 0 | 38 | 50 | 400 | 75 | 0 | 108 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 903 | 0 | 405 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 24 | 85 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 217 | 0 | 422 | 0 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 560 | 226 | 0 | 17 | 0 | 0 | 52 |  | 7897 | 3748 | 11645 | 4410 | 903 | 2389 | 0 | 2924 | 735 | 124 | 0 | 32 | 128 | 0 | 0 | 88.63
4:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 270 | 89 | 0 | 55 | 335 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 0 | 0 | 90 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 30 | 0 | 37 | 20 | 42 | 0 | 0 | 0 | 310 | 305 | 182 | 177 | 136 | 23 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 193 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 275 | 16 | 11 | 0 | 60 | 0 | 0 | 193 | 0 | 96 | 0 | 90 | 155 | 143 | 401 | 55 | 105 | 105 | 0 | 15 | 54 | 110 | 0 | 38 | 50 | 400 | 84 | 0 | 36 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 911 | 0 | 410 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 217 | 0 | 422 | 0 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 520 | 226 | 0 | 0 | 0 | 0 | 52 |  | 7509 | 3681 | 11190 | 4411 | 911 | 2385 | 0 | 2537 | 695 | 125 | 0 | 0 | 126 | 0 | 0 | 88.64
5:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 265 | 85 | 0 | 55 | 335 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 0 | 0 | 90 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 37 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 182 | 178 | 137 | 23 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 118 | 193 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 170 | 0 | 97 | 0 | 90 | 155 | 142 | 401 | 25 | 105 | 105 | 0 | 0 | 54 | 110 | 0 | 38 | 50 | 400 | 93 | 0 | 17 | 90 | 0 | 35 | 0 | 111 | 55 | 0 |  | 911 | 0 | 410 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 216 | 0 | 425 | 0 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 480 | 224 | 0 | 0 | 0 | 0 | 32 |  | 7389 | 3618 | 11007 | 4416 | 911 | 2397 | 0 | 2386 | 654 | 125 | 0 | 0 | 118 | 0 | 0 | 88.65
6:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 270 | 80 | 0 | 55 | 280 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 29 | 33 | 0 | 0 | 0 | 90 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 30 | 0 | 37 | 20 | 42 | 0 | 0 | 0 | 270 | 310 | 182 | 180 | 137 | 23 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 112 | 192 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 62 | 2 | 90 | 100 | 90 | 376 | 0 | 70 | 105 | 0 | 0 | 17 | 110 | 0 | 38 | 50 | 360 | 55 | 2 | 17 | 90 | 0 | 35 | 2 | 116 | 34 | 0 |  | 911 | 0 | 410 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 421 | 0 | 0 | 50 | 0 | 46 | 0 | 0 | 50 | 410 | 225 | 0 | 0 | 0 | 2 | 32 |  | 6822 | 3343 | 10165 | 4181 | 911 | 2388 | 0 | 1855 | 585 | 125 | 0 | 0 | 112 | 8 | 0 | 88.66
7:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 280 | 80 | 0 | 40 | 280 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 29 | 33 | 0 | 0 | 0 | 90 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 30 | 0 | 37 | 20 | 40 | 0 | 0 | 0 | 280 | 275 | 183 | 180 | 136 | 23 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 32 | 17 | 104 | 190 | 0 | 20 | 0 | 43 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 52 | 3 | 76 | 100 | 50 | 370 | 0 | 50 | 105 | 1 | 0 | 17 | 110 | 0 | 38 | 50 | 360 | 55 | 14 | 17 | 90 | 0 | 35 | 5 | 106 | 34 | 0 |  | 910 | 0 | 360 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 421 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 50 | 340 | 226 | 0 | 0 | 1 | 11 | 34 |  | 6682 | 3220 | 9902 | 4073 | 910 | 2404 | 0 | 1736 | 515 | 125 | 0 | 0 | 104 | 35 | 0 | 88.67
8:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 300 | 80 | 0 | 40 | 333 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 20 | 0 | 25 | 29 | 33 | 0 | 0 | 0 | 91 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 30 | 0 | 37 | 20 | 12 | 0 | 0 | 0 | 350 | 340 | 207 | 180 | 136 | 23 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 24 | 17 | 116 | 187 | 0 | 20 | 1 | 44 | 42 | 34 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 9 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 50 | 11 | 63 | 100 | 50 | 397 | 0 | 50 | 105 | 2 | 0 | 17 | 110 | 0 | 39 | 50 | 378 | 55 | 24 | 17 | 90 | 0 | 35 | 17 | 116 | 34 | 0 |  | 911 | 0 | 320 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 186 | 0 | 414 | 0 | 0 | 50 | 0 | 34 | 0 | 1 | 60 | 280 | 220 | 0 | 0 | 1 | 25 | 34 |  | 6992 | 3122 | 10114 | 4268 | 911 | 2403 | 0 | 1753 | 455 | 126 | 0 | 0 | 116 | 82 | 0 | 88.68
9:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 408 | 0 |  | 0 | 450 | 280 | 80 | 0 | 40 | 300 | 0 | 0 | 20 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 0 | 17 | 0 | 91 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 30 | 0 | 37 | 20 | 4 | 0 | 0 | 0 | 310 | 315 | 213 | 180 | 136 | 12 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 12 | 124 | 190 | 0 | 20 | 2 | 44 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 290 | 16 | 11 | 0 | 43 | 0 | 0 | 150 | 0 | 65 | 12 | 63 | 115 | 81 | 402 | 25 | 80 | 105 | 4 | 80 | 40 | 110 | 0 | 39 | 55 | 395 | 87 | 27 | 72 | 90 | 0 | 35 | 16 | 116 | 51 | 0 |  | 910 | 0 | 320 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 208 | 0 | 414 | 6 | 0 | 78 | 0 | 60 | 0 | 3 | 113 | 270 | 220 | 0 | 0 | 3 | 13 | 34 |  | 7366 | 3271 | 10637 | 4251 | 910 | 2352 | 0 | 2350 | 444 | 126 | 0 | 0 | 124 | 80 | 0 | 88.7
10:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 409 | 0 |  | 0 | 450 | 295 | 79 | 0 | 40 | 331 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 0 | 50 | 0 | 91 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 37 | 21 | 4 | 0 | 0 | 0 | 345 | 345 | 208 | 180 | 135 | 12 | 49 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 31 | 18 | 130 | 185 | 0 | 20 | 1 | 44 | 42 | 34 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 285 | 16 | 11 | 0 | 150 | 0 | 0 | 150 | 0 | 78 | 14 | 76 | 112 | 114 | 365 | 45 | 105 | 105 | 4 | 80 | 54 | 110 | 0 | 38 | 78 | 392 | 93 | 22 | 108 | 90 | 0 | 35 | 26 | 116 | 55 | 0 |  | 896 | 0 | 320 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 180 | 0 | 414 | 35 | 0 | 94 | 0 | 68 | 0 | 3 | 113 | 270 | 222 | 0 | 0 | 4 | 103 | 34 |  | 7783 | 3357 | 11140 | 4253 | 896 | 2352 | 0 | 2761 | 445 | 126 | 0 | 0 | 130 | 177 | 0 | 88.72
11:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 406 | 0 |  | 0 | 400 | 305 | 80 | 0 | 40 | 335 | 0 | 0 | 60 | 78 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 0 | 49 | 0 | 90 | 35 | 100 | 0 | 10 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 12 | 37 | 22 | 4 | 0 | 0 | 0 | 310 | 315 | 180 | 180 | 136 | 12 | 47 | 0 | 43 | 0 | 15 | 0 | 19 | 11 | 27 | 18 | 134 | 189 | 0 | 20 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 23 | 9 | 280 | 16 | 11 | 0 | 214 | 0 | 0 | 170 | 0 | 79 | 5 | 76 | 120 | 122 | 402 | 72 | 90 | 105 | 5 | 170 | 54 | 107 | 0 | 39 | 76 | 400 | 93 | 45 | 136 | 90 | 0 | 35 | 22 | 116 | 55 | 133 |  | 896 | 0 | 360 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 205 | 0 | 385 | 35 | 0 | 94 | 0 | 68 | 0 | 6 | 113 | 280 | 224 | 0 | 0 | 5 | 75 | 34 |  | 8207 | 3507 | 11714 | 4494 | 896 | 2280 | 0 | 3060 | 455 | 125 | 0 | 106 | 134 | 164 | 0 | 88.74
12:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 409 | 0 |  | 0 | 400 | 298 | 80 | 0 | 40 | 300 | 0 | 0 | 75 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 0 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 23 | 37 | 22 | 2 | 0 | 0 | 0 | 310 | 315 | 181 | 180 | 136 | 14 | 48 | 0 | 51 | 0 | 24 | 0 | 19 | 11 | 16 | 18 | 138 | 176 | 0 | 17 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 100 | 0 | 25 | 9 | 280 | 16 | 0 | 0 | 238 | 0 | 0 | 177 | 0 | 79 | 20 | 90 | 120 | 117 | 370 | 92 | 90 | 105 | 2 | 230 | 54 | 93 | 0 | 38 | 76 | 394 | 93 | 52 | 144 | 90 | 0 | 35 | 31 | 116 | 0 | 133 |  | 896 | 0 | 360 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 211 | 0 | 380 | 35 | 0 | 94 | 0 | 68 | 0 | 7 | 113 | 330 | 221 | 0 | 0 | 2 | 20 | 34 |  | 8237 | 3519 | 11756 | 4402 | 896 | 2270 | 0 | 3174 | 505 | 123 | 0 | 112 | 138 | 136 | 0 | 88.76
13:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 411 | 0 |  | 0 | 450 | 275 | 80 | 0 | 40 | 335 | 0 | 0 | 80 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 0 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 36 | 36 | 22 | 10 | 0 | 0 | 0 | 310 | 315 | 181 | 177 | 136 | 14 | 49 | 0 | 51 | 0 | 25 | 0 | 19 | 11 | 16 | 20 | 138 | 161 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 300 | 16 | 11 | 0 | 242 | 0 | 0 | 171 | 0 | 77 | 7 | 90 | 120 | 120 | 404 | 107 | 90 | 105 | 4 | 265 | 54 | 93 | 0 | 39 | 66 | 400 | 92 | 10 | 162 | 90 | 0 | 35 | 18 | 116 | 0 | 173 |  | 897 | 0 | 405 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 0 | 0 | 100 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 209 | 0 | 414 | 35 | 0 | 94 | 0 | 68 | 0 | 7 | 113 | 350 | 220 | 0 | 0 | 3 | 36 | 34 |  | 8471 | 3606 | 12077 | 4583 | 897 | 2357 | 0 | 3217 | 525 | 121 | 0 | 152 | 138 | 87 | 0 | 88.77
14:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 410 | 0 |  | 0 | 400 | 265 | 80 | 0 | 40 | 250 | 0 | 0 | 80 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 37 | 22 | 7 | 0 | 0 | 0 | 310 | 270 | 181 | 177 | 137 | 17 | 48 | 0 | 51 | 0 | 36 | 0 | 19 | 11 | 25 | 18 | 142 | 152 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 23 | 9 | 265 | 16 | 11 | 0 | 242 | 0 | 0 | 170 | 0 | 79 | 12 | 90 | 120 | 127 | 403 | 107 | 105 | 105 | 5 | 300 | 54 | 92 | 0 | 38 | 65 | 360 | 93 | 51 | 162 | 90 | 0 | 20 | 21 | 116 | 0 | 225 |  | 899 | 0 | 340 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 0 | 0 | 80 | 0 | 34 | 5 | 0 | 0 | 16 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 202 | 0 | 353 | 47 | 0 | 100 | 0 | 68 | 0 | 2 | 113 | 330 | 185 | 0 | 0 | 4 | 105 | 34 |  | 8392 | 3424 | 11816 | 4356 | 899 | 2162 | 0 | 3266 | 505 | 121 | 0 | 163 | 142 | 202 | 0 | 88.78
15:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 409 | 0 |  | 0 | 400 | 276 | 80 | 0 | 40 | 330 | 0 | 0 | 91 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 55 | 22 | 25 | 28 | 33 | 0 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 65 | 37 | 22 | 5 | 0 | 0 | 0 | 310 | 270 | 183 | 177 | 135 | 17 | 48 | 0 | 51 | 0 | 41 | 0 | 16 | 11 | 33 | 18 | 148 | 145 | 0 | 20 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 24 | 9 | 280 | 16 | 11 | 0 | 242 | 0 | 0 | 170 | 0 | 78 | 14 | 90 | 120 | 130 | 403 | 107 | 105 | 105 | 2 | 300 | 54 | 61 | 0 | 36 | 55 | 380 | 93 | 43 | 162 | 90 | 0 | 21 | 8 | 115 | 0 | 270 |  | 899 | 0 | 340 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 0 | 0 | 80 | 0 | 34 | 6 | 0 | 0 | 34 | 24 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 185 | 0 | 394 | 53 | 0 | 113 | 0 | 68 | 0 | 2 | 113 | 330 | 175 | 0 | 0 | 1 | 32 | 35 |  | 8477 | 3367 | 11844 | 4447 | 899 | 2214 | 0 | 3238 | 505 | 121 | 0 | 169 | 148 | 103 | 0 | 88.79
16:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 407 | 0 |  | 0 | 400 | 260 | 74 | 0 | 40 | 330 | 0 | 0 | 86 | 94 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 0 | 48 | 0 | 86 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 26 | 41 | 22 | 5 | 0 | 0 | 0 | 320 | 275 | 206 | 178 | 136 | 11 | 48 | 0 | 51 | 0 | 41 | 0 | 16 | 11 | 33 | 18 | 140 | 135 | 0 | 20 | 1 | 43 | 42 | 34 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 24 | 10 | 305 | 16 | 11 | 0 | 240 | 0 | 0 | 170 | 0 | 70 | 9 | 90 | 120 | 132 | 365 | 107 | 105 | 105 | 1 | 245 | 54 | 36 | 0 | 36 | 50 | 390 | 99 | 19 | 162 | 90 | 0 | 28 | 12 | 116 | 0 | 270 |  | 892 | 0 | 270 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 20 | 0 | 0 | 80 | 0 | 34 | 6 | 0 | 0 | 8 | 24 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 177 | 0 | 350 | 53 | 0 | 113 | 0 | 68 | 0 | 2 | 113 | 330 | 175 | 0 | 0 | 0 | 69 | 77 |  | 8280 | 3323 | 11603 | 4395 | 892 | 2183 | 0 | 3117 | 505 | 121 | 0 | 137 | 140 | 113 | 0 | 88.8
17:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 411 | 31 |  | 0 | 400 | 266 | 70 | 0 | 40 | 300 | 0 | 0 | 68 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 0 | 48 | 0 | 86 | 35 | 95 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 42 | 22 | 8 | 0 | 0 | 0 | 310 | 270 | 208 | 178 | 135 | 11 | 50 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 18 | 138 | 132 | 0 | 20 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 24 | 10 | 270 | 16 | 11 | 0 | 240 | 0 | 0 | 170 | 0 | 60 | 4 | 90 | 120 | 132 | 364 | 45 | 90 | 105 | 1 | 155 | 54 | 50 | 0 | 36 | 50 | 395 | 104 | 3 | 162 | 90 | 0 | 35 | 14 | 116 | 0 | 130 |  | 889 | 0 | 270 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 18 | 0 | 0 | 80 | 0 | 34 | 23 | 0 | 0 | 8 | 24 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 350 | 17 | 0 | 50 | 0 | 72 | 0 | 2 | 70 | 330 | 202 | 0 | 0 | 0 | 35 | 107 |  | 7870 | 3219 | 11089 | 4207 | 889 | 2221 | 0 | 2787 | 505 | 121 | 0 | 162 | 138 | 59 | 0 | 88.81
18:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 411 | 31 |  | 0 | 300 | 285 | 67 | 0 | 55 | 240 | 0 | 0 | 40 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 48 | 0 | 88 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 42 | 22 | 13 | 0 | 0 | 0 | 315 | 270 | 208 | 178 | 136 | 12 | 50 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 20 | 128 | 130 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 20 | 30 | 0 | 120 | 0 | 24 | 10 | 280 | 16 | 11 | 0 | 258 | 0 | 0 | 178 | 0 | 101 | 1 | 20 | 120 | 132 | 364 | 45 | 105 | 105 | 0 | 155 | 54 | 76 | 0 | 36 | 50 | 400 | 84 | 2 | 162 | 90 | 0 | 35 | 2 | 114 | 0 | 0 |  | 889 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 85 | 18 | 0 | 0 | 80 | 0 | 34 | 32 | 0 | 0 | 8 | 24 | 0 | 20 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 150 | 0 | 270 | 17 | 0 | 50 | 0 | 90 | 0 | 1 | 70 | 330 | 164 | 0 | 0 | 0 | 8 | 107 |  | 7545 | 3097 | 10642 | 4003 | 889 | 1983 | 0 | 2820 | 505 | 123 | 0 | 177 | 128 | 14 | 0 | 88.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 410 | 35 |  | 0 | 400 | 300 | 80 | 0 | 55 | 300 | 0 | 0 | 48 | 94 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 0 | 48 | 0 | 88 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 19 | 51 | 30 | 16 | 42 | 22 | 18 | 0 | 0 | 0 | 340 | 335 | 204 | 180 | 135 | 12 | 53 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 20 | 148 | 130 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 30 | 30 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 0 | 260 | 0 | 0 | 200 | 0 | 135 | 0 | 50 | 124 | 137 | 400 | 64 | 105 | 105 | 0 | 280 | 54 | 76 | 0 | 40 | 82 | 390 | 55 | 0 | 162 | 90 | 0 | 35 | 0 | 105 | 0 | 0 |  | 884 | 0 | 310 | 0 | 35 | 0 | 0 | 0 | 33 | 10 | 8 | 84 | 25 | 16 | 0 | 80 | 0 | 34 | 35 | 40 | 0 | 8 | 27 | 0 | 38 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 145 | 0 | 326 | 17 | 0 | 50 | 0 | 95 | 0 | 0 | 90 | 350 | 184 | 0 | 0 | 0 | 0 | 107 |  | 8291 | 3377 | 11668 | 4179 | 884 | 2197 | 0 | 3194 | 525 | 123 | 0 | 418 | 148 | 0 | 0 | 88.85
19:30 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 410 | 35 |  | 0 | 400 | 240 | 89 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 0 | 48 | 0 | 88 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 29 | 51 | 30 | 80 | 43 | 22 | 21 | 0 | 0 | 0 | 310 | 270 | 209 | 187 | 135 | 12 | 53 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 20 | 150 | 131 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 9 | 275 | 16 | 11 | 50 | 275 | 45 | 50 | 200 | 50 | 134 | 0 | 90 | 200 | 140 | 400 | 108 | 105 | 105 | 0 | 300 | 54 | 85 | 0 | 95 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 100 | 0 | 0 |  | 884 | 0 | 355 | 0 | 48 | 0 | 0 | 0 | 45 | 10 | 40 | 86 | 28 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 50 | 161 | 0 | 414 | 80 | 14 | 70 | 0 | 95 | 0 | 0 | 113 | 490 | 222 | 0 | 0 | 0 | 0 | 109 |  | 8978 | 4100 | 13078 | 4278 | 884 | 2326 | 259 | 3830 | 665 | 123 | 0 | 563 | 150 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 410 | 38 |  | 0 | 400 | 260 | 88 | 0 | 55 | 335 | 0 | 0 | 94 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 0 | 49 | 0 | 88 | 35 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 24 | 31 | 51 | 30 | 79 | 43 | 22 | 22 | 0 | 0 | 0 | 310 | 270 | 210 | 185 | 136 | 12 | 54 | 0 | 51 | 0 | 49 | 0 | 19 | 11 | 33 | 21 | 154 | 131 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 32 | 84 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 20 | 278 | 20 | 30 | 200 | 30 | 134 | 0 | 90 | 190 | 140 | 400 | 108 | 105 | 105 | 0 | 300 | 54 | 109 | 0 | 91 | 100 | 400 | 98 | 0 | 162 | 90 | 0 | 35 | 0 | 98 | 0 | 0 |  | 884 | 0 | 355 | 0 | 63 | 0 | 0 | 0 | 39 | 0 | 40 | 87 | 28 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 220 | 0 | 414 | 66 | 0 | 110 | 0 | 95 | 0 | 0 | 113 | 520 | 223 | 0 | 0 | 0 | 0 | 108 |  | 8925 | 4151 | 13076 | 4350 | 884 | 2355 | 100 | 3874 | 695 | 123 | 0 | 541 | 154 | 0 | 0 | 88.84
21:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 411 | 142 |  | 0 | 400 | 305 | 89 | 0 | 55 | 270 | 0 | 0 | 98 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 51 | 30 | 82 | 43 | 22 | 28 | 0 | 0 | 0 | 345 | 330 | 208 | 189 | 136 | 14 | 52 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 150 | 129 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 0 | 278 | 0 | 27 | 200 | 30 | 134 | 0 | 90 | 200 | 140 | 402 | 108 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 77 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 99 | 0 | 0 |  | 883 | 0 | 385 | 0 | 63 | 0 | 0 | 0 | 39 | 0 | 40 | 85 | 29 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 215 | 0 | 332 | 93 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 600 | 223 | 0 | 0 | 0 | 0 | 108 |  | 9102 | 4217 | 13319 | 4435 | 883 | 2429 | 57 | 3921 | 775 | 125 | 0 | 544 | 150 | 0 | 0 | 88.85
22:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 411 | 293 |  | 0 | 400 | 270 | 83 | 0 | 55 | 270 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 51 | 30 | 40 | 43 | 22 | 34 | 0 | 0 | 0 | 315 | 305 | 210 | 189 | 135 | 15 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 148 | 120 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 10 | 290 | 16 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 134 | 0 | 90 | 200 | 142 | 402 | 108 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 55 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 109 | 0 | 0 |  | 870 | 0 | 355 | 0 | 63 | 0 | 0 | 0 | 39 | 0 | 16 | 86 | 30 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 215 | 0 | 340 | 93 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 600 | 225 | 0 | 0 | 0 | 0 | 108 |  | 9056 | 4162 | 13218 | 4344 | 870 | 2576 | 0 | 3838 | 775 | 123 | 0 | 544 | 148 | 0 | 0 | 88.86
23:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 408 | 0 |  | 0 | 450 | 295 | 72 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 89 | 35 | 100 | 0 | 5 | 0 | 0 | 0 | 0 |  | 24 | 34 | 51 | 30 | 0 | 43 | 22 | 37 | 0 | 0 | 0 | 350 | 345 | 208 | 189 | 136 | 15 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 18 | 154 | 120 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 25 | 10 | 305 | 16 | 11 | 0 | 271 | 54 | 0 | 200 | 0 | 114 | 0 | 90 | 200 | 143 | 403 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 50 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 0 | 0 |  | 875 | 0 | 390 | 0 | 64 | 0 | 0 | 0 | 39 | 0 | 16 | 81 | 32 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 16 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 214 | 0 | 414 | 93 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 610 | 223 | 0 | 0 | 0 | 0 | 108 |  | 8962 | 4272 | 13234 | 4505 | 875 | 2447 | 54 | 3754 | 785 | 124 | 0 | 536 | 154 | 0 | 0 | 88.87
24:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 275 | 70 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 89 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 51 | 30 | 1 | 43 | 22 | 37 | 0 | 0 | 0 | 320 | 305 | 210 | 189 | 136 | 28 | 54 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 18 | 152 | 122 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 25 | 10 | 300 | 16 | 11 | 0 | 276 | 155 | 40 | 200 | 80 | 80 | 0 | 90 | 182 | 143 | 402 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 50 | 401 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 0 | 0 |  | 875 | 0 | 355 | 0 | 30 | 0 | 0 | 0 | 39 | 0 | 16 | 84 | 31 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 25 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 214 | 0 | 418 | 92 | 0 | 113 | 0 | 69 | 0 | 0 | 113 | 620 | 226 | 0 | 0 | 0 | 0 | 72 |  | 8976 | 4143 | 13119 | 4324 | 875 | 2426 | 275 | 3613 | 795 | 124 | 0 | 535 | 152 | 0 | 0 | 88.88
KWH | 0 | 0 | 0 | 4353000 | 0 | 1974863 | 0 | 9955330 | 450000 |  | 0 | 9771000 | 6714996 | 1943040 | 0 | 1162884 | 7387185 | 0 | 0 | 1417046 | 1609056 | 1436160 | 0 | 0 | 0 | 0 | 1292400 | 1189189 | 1141237 | 350100 | 600000 | 622080 | 799400 | 0 | 918720 | 0 | 2131195 | 840000 | 2300000 | 0 | 321242 | 0 | 0 | 0 | 0 |  | 553680 | 199888 | 265439 | 742440 | 464640 | 938400 | 499824 | 585120 | 0 | 0 | 0 | 7919600 | 7334000 | 4742000 | 4365818 | 3265040 | 403920 | 1203840 | 0 | 1130674 | 0 | 549128 | 0 | 446004 | 248400 | 737800 | 458800 | 3211200 | 3831360 | 0 | 426780 | 12950 | 1031000 | 984944 | 811200 | 780984 | 2662773 | 0 | 730752 | 1902720 | 0 | 2861430 | 0 | 576960 | 211860 | 7112500 | 385248 | 251040 | 35904 | 4707053 | 219009 | 77051 | 4248000 | 100107 | 2181168 | 122715 | 1931520 | 3492960 | 2977454 | 9379000 | 1845600 | 2328000 | 2544218 | 30000 | 4147527 | 1256536 | 2366899 | 0 | 1218840 | 1479360 | 9383000 | 2137920 | 328030 | 3054240 | 2152800 | 0 | 849600 | 194597 | 2731200 | 591480 | 1272500 |  | 21698909 | 0 | 8744256 | 0 | 1805760 | 0 | 0 | 0 | 199680 | 11520 | 217875 | 1976145 | 534162 | 110112 | 0 | 1227000 | 0 | 368880 | 256712 | 452408 | 0 | 214496 | 265648 | 0 | 294710 | 492000 | 0 | 227592 | 0 | 0 | 4288800 | 0 | 0 | 0 | 0 | 4933836 | 0 | 0 | 25920 | 5009018 | 0 | 9313745 | 973920 | 28541 | 2227104 | 0 | 1724755 | 0 | 36931 | 2485728 | 11381300 | 5162455 | 0 | 62400 | 31200 | 549360 | 1535808 |  | 194904567 | 88868686 | 283773253 | 105077384 | 21698909 | 55757670 | 486532 | 73294307 | 15670100 | 2971195 | 0 | 4300173 | 3211200 | 1305783 | 0
Fuel Cost | 0 | 0 | 0 | 6485970 | 0 | 2626567.79 | 0 | 10453096.5 | 486000 |  | 0 | 10650390 | 7453645.56 | 21723187.2 | 0 | 15408213 | 8273647.2 | 0 | 0 | 20717212.52 | 22639417.92 | 23280153.6 | 0 | 0 | 0 | 0 | 16439328 | 16054051.5 | 15303988.17 | 262575 | 450000 | 0 | 0 | 0 | 15627427.2 | 0 | 575422.65 | 226800 | 4347000 | 0 | 5252306.7 | 0 | 0 | 0 | 0 |  | 7225524 | 3334131.84 | 4517771.78 | 10030364.4 | 5891635.2 | 10857288 | 634776.48 | 1948449.6 | 0 | 0 | 0 | 8790756 | 7994060 | 5500720 | 5631905.22 | 3983348.8 | 456429.6 | 1793721.6 | 0 | 1888225.58 | 0 | 9483440.56 | 0 | 611025.48 | 186300 | 1291150 | 344100 | 23056416 | 4176182.4 | 0 | 580420.8 | 206423 | 1412470 | 1300126.08 | 1411488 | 1351102.32 | 3062188.95 | 0 | 1417658.88 | 4338201.6 | 0 | 2890044.3 | 0 | 859670.4 | 419482.8 | 7112500 | 288936 | 190790.4 | 752547.84 | 64251273.45 | 4590428.64 | 1592644.17 | 57263040 | 2069211.69 | 30209176.8 | 1434538.35 | 19933286.4 | 47713833.6 | 39510814.58 | 8628680 | 22442496 | 33662880 | 32184357.7 | 0 | 48691966.98 | 13683677.04 | 25160136.37 | 0 | 15710847.6 | 17426860.8 | 8632360 | 27686064 | 4740033.5 | 38758305.6 | 24498864 | 0 | 11095776 | 2325434.15 | 40886064 | 7789791.6 | 0 |  | 65096727 | 0 | 9793566.72 | 0 | 18797961.6 | 0 | 0 | 0 | 3596236.8 | 207360 | 3130863.75 | 2213282.4 | 1036274.28 | 1200220.8 | 0 | 2454000 | 0 | 6186117.6 | 4489892.88 | 7075661.12 | 0 | 3552053.76 | 4492107.68 | 0 | 4971757.7 | 1018440 | 0 | 172287.144 | 0 | 0 | 22687752 | 0 | 0 | 0 | 0 | 6315310.08 | 0 | 0 | 543801.6 | 5810460.88 | 0 | 9220607.55 | 13089484.8 | 598504.77 | 26346640.32 | 0 | 21904388.5 | 0 | 408087.55 | 30176737.92 | 102545513 | 5265704.1 | 0 | 461760 | 352872 | 6443992.8 | 23543936.64 |  | 1024531017.44 | 415200365.744 | 1439731383.184 | 116341531.144 | 65096727 | 67574565.35 | 10147138.71 | 943933504.42 | 125233265 | 802222.65 | 0 | 71634631.56 | 23056416 | 15911381.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 409 | 0 |  | 0 | 400 | 298 | 80 | 0 | 40 | 300 | 0 | 0 | 75 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 0 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 23 | 37 | 22 | 2 | 0 | 0 | 0 | 310 | 315 | 181 | 180 | 136 | 14 | 48 | 0 | 51 | 0 | 24 | 0 | 19 | 11 | 16 | 18 | 138 | 176 | 0 | 17 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 100 | 0 | 25 | 9 | 280 | 16 | 0 | 0 | 238 | 0 | 0 | 177 | 0 | 79 | 20 | 90 | 120 | 117 | 370 | 92 | 90 | 105 | 2 | 230 | 54 | 93 | 0 | 38 | 76 | 394 | 93 | 52 | 144 | 90 | 0 | 35 | 31 | 116 | 0 | 133 |  | 896 | 0 | 360 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 211 | 0 | 380 | 35 | 0 | 94 | 0 | 68 | 0 | 7 | 113 | 330 | 221 | 0 | 0 | 2 | 20 | 34 |  | 11756 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 411 | 142 | 0 | 0 | 400 | 305 | 89 | 0 | 55 | 270 | 0 | 0 | 98 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 34 | 51 | 30 | 82 | 43 | 22 | 28 | 0 | 0 | 0 | 345 | 330 | 208 | 189 | 136 | 14 | 52 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 150 | 129 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 0 | 278 | 0 | 27 | 200 | 30 | 134 | 0 | 90 | 200 | 140 | 402 | 108 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 77 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 99 | 0 | 0 |  | 883 | 0 | 385 | 0 | 63 | 0 | 0 | 0 | 39 | 0 | 40 | 85 | 29 | 16 | 0 | 100 | 0 | 34 | 35 | 90 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 215 | 0 | 332 | 93 | 0 | 113 | 0 | 102 | 0 | 0 | 113 | 600 | 223 | 0 | 0 | 0 | 0 | 108 |  | 13319 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 412 | 0 | 0 | 0 | 450 | 305 | 89 | 0 | 55 | 335 | 0 | 0 | 100 | 95 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 50 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 30 | 90 | 43 | 22 | 20 | 0 | 0 | 0 | 360 | 360 | 215 | 190 | 136 | 15 | 50 | 0 | 51 | 0 | 50 | 0 | 21 | 11 | 33 | 21 | 165 | 130 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 32 | 84 | 0 | 120 | 0 | 25 | 10 | 341 | 16 | 11 | 200 | 280 | 300 | 100 | 200 | 100 | 134 | 0 | 90 | 200 | 150 | 400 | 110 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 100 | 400 | 104 | 0 | 162 | 90 | 0 | 35 |  | 115 | 55 |  |  | 940 | 0 | 400 | 0 | 60 | 220 | 0 | 0 | 40 | 60 | 40 | 85 | 29 | 16 | 0 | 0 | 0 | 34 | 35 | 90 | 0 | 34 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 210 | 0 | 0 | 100 | 220 | 0 | 414 | 93 | 200 | 113 | 90 | 100 | 0 | 0 | 113 | 622 | 220 |  | 35 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 412 | 0 | 0 | 0 | 450 | 305 | 80 | 0 | 55 | 335 | 0 | 0 | 100 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 50 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 30 | 80 | 43 | 22 | 10 | 0 | 0 | 0 | 350 | 300 | 215 | 180 | 135 | 15 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 143 | 120 | 0 | 20 | 1.6 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 10 | 310 | 16 | 11 | 100 | 270 | 200 | 100 | 180 | 25 | 134 | 20 | 90 | 150 | 140 | 400 | 110 | 105 | 105 | 5 | 265 | 34 | 110 | 0 | 60 | 100 | 400 | 104 | 50 | 162 | 90 | 0 | 35 | 30 | 115 | 55 |  |  | 940 | 0 | 400 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 40 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 200 | 0 | 414 | 93 | 100 | 113 | 70 | 70 | 0 | 8 | 75 | 622 | 220 |  | 35 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 | 0 | 0 | 400 | 300 | 72 | 0 | 55 | 300 | 0 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 29 | 33 | 0 | 24 | 0 | 89 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 30 | 0 | 44 | 22 | 4 | 0 | 0 | 0 | 360 | 305 | 210 | 189 | 138 | 28 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 120 | 110 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 75 | 0 | 120 | 0 | 24 | 10 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 181 | 0 | 79 | 12 | 90 | 100 | 100 | 387 | 19 | 70 | 87 | 2 | 80 | 54 | 110 | 0 | 39 | 50 | 360 | 104 | 25 | 72 | 0 | 0 | 35 | 15 | 116 | 41 | 0 | 0 | 888 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 158 | 0 | 391 | 17 | 0 | 50 | 0 | 70 | 0 | 1 | 70 | 450 | 204 | 0 | 0 | 2 | 54 | 34 | 0 |  |  |  |  | 78081012 |  | 0
78081012
| Minimum Generation |  | 9902 | 7:00
| Highest Generation |  | 13319 | 21:00
| Day Peak Generation |  | 11756 | 12:00
| Evening Peak Generation |  | 13319 | 21:00
| HVDC Max Flow |  | 922 | 1:00
| HVDC EvPeak Flow |  | 883 | 21:00
| Load factor L.F |  | 88.77%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-26
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11756 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10295 | MW
Evening Peak Generation : |  | 13319 | MW Hour : | 21:00 | Available Max Generation : |  | 14920 | MW
E.P. Demand (at gen end) : |  | 13319 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13319 | MW Hour : | 21:00 | Reserve(Generation end) |  | 920 | MW
Total Gen. (MKWH) : |  | 283.7733 | System Load Factor : | 88.77% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -206 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-26
Actual : | 88.94 | Ft.(MSL) , | Rule curve : | 82.38 | Ft.( MSL )
Gas Consumed : | Total = | 1201.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 183916096.494
: |  | Coal : | 125233265 | Oil : | 1025715274.69 | Total : | 1334864636.184
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4884.17 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1315.3829 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1724.4595 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1544.9872 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1368.9361 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1006.834 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 558.1532 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 365.6553 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 770.7829 |  |  | 0 | 0%
Total | 0 |  | 13539.3611 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Halishahar-Kulshi 132 kV Ckt-3 tripped at 08:25 showing dist.Z1,B-phase from both end and was
switched on at 10:40.
b) Chattak 132/33 kV T-1 transformer tripped at 11:35 due to 33 kV Sunamganj feeder fault and was
switched on at 11:40.
c) Baghabari-100 MW was synchronized at 10:27 and shut down at 06:45(26/6/22) due to gas shortage.
d) Bhulta 132/33 kV T-1 & T-2 transformers tripped at 11:42 showing E/F relay and were switched on at 11:58. | [5 empty] | About 248 MW power interruption occurred under
Bhulta S/S area from 11:42 to 11:58.
e) Haripur-360 MW CCPP GT & ST were synchronized at 16:01 & 20:38 respectively and tripped at 22:11
due to gas valve problem.
f) Siddirganj-Matuail 132 kV Ckt tripped at 13:48 showing E/F relay and was switched on at 14:18. | [5 empty] | About 65 MW power interruption occurred under
Matuail S/S area from 13:48 to 14:18.
g) Siddirganj S/S-Siddirganj peaking 132 kV Ckt tripped at 13:48 showing no relay and was switched on at 14:05.
h) Maniknagar-Matuail 132 kV Ckt tripped at 13:49 showing E/F relay.
i) Naogaon 132/33 kV T-3 transformer was shut down at 14:05 for changing riser of 33 kV and was switched | [5 empty] | About 25 MW power interruption occurred under
on at 15:55. | [5 empty] | Naogaon S/S area from 14:05 to 15:55.
j) Benapole 132/33 kV T-1 & T-2 transformer tripped at 18:38 showing O/C & E/F relays due to 33 kV
Navaron & Chutipara PBS feeder fault and were switched on at 18:48.
k) Gallamari 132/33 kV T-1 transformer is under shut since 06:09(26/6/22) for D/W.
l) Raozan #1 tripped at 23:58 for boiler problem.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4353000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 87 | 1974863 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 411 | 9955330
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 142 | 450000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9771000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 89 | 1943040 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 305 | 6714996 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1162884
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 350100
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 98 | 1417046
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 7387185 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1609056 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1292400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1436160
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1189189
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1141237
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1222080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 799400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 0 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 918720 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 4707053 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 219009 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 27 | 77051 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 30 | 100107 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 2181168 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2328000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2137920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3054240
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 194597
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 591480 | 33 kV feeder problem.
| Dhaka area Total |  |  |  | 5847 | 3443 | 70678311
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 321242
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 122715
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 938400 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 2971195 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2544218
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 199888 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 265439 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 30 | 742440 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1931520 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499824
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 585120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 464640 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 4147527
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1256536
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2366899
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 77 | 1479360
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2152800 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1366 | 25319763
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4742000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7919600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7334000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 1272500 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 14 | 403920 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1203840
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 189 | 4365818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1130674
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 2977454 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 549128
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3265040 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3492960
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 446004
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 248400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 3211200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 737800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 458800 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 35904 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 1218840 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 849600 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 2731200 | Engine problem
| Cumilla Area Total |  |  |  | 2885 | 2178 | 48594682
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 129 | 3831360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 426780
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 4248000
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 1845600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 328030
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 553680
| Mymensingh Area Total |  |  |  | 614 | 481 | 11246400
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1031000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 984944 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2662773 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 33 | 811200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 780984 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 251040
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 31 | 730752 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1902720
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2861430 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 25 | 576960 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 385248 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7112500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9379000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 211860
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9383000
| Sylhet Area Total |  |  |  | 2477 | 1634 | 39065411
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 883 | 21698909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 63 | 1805760 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 199680 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 11520 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 385 | 8744256
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 217875
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 25920 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 973920 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 549360
| Khulna Area Total |  |  |  | 2384 | 1503 | 34227200
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 110112 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 29 | 534162 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 1976145 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 11381300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 5162455
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 62400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 953 | 19226574
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 100 | 1227000
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 368880
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 256712
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 214496 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 265648 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 215 | 4933836
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 215 | 5009018 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 332 | 9313745
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 294710 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 492000
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227592
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 452408
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 28541 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2227104
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2485728
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31200
| Rajshahi Area Total |  |  |  | 2129 | 1376 | 27828618
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4288800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 1724755 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36931
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1535808
| Rangpur Area Total |  |  |  | 720 | 385 | 7586294
| Total |  |  |  | 21396 | 13319 | 283773253
| Eastern Grid Total |  |  |  | 14205 | 9102 | 194904567
| Western Grid Total |  |  |  | 7191 | 4217 | 88868686
| National Grid Total |  |  |  | 21396 | 13319 | 283773253
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-25
(a) ENTIRE EASTERN GRID : |  | 8730.17 | MW | (b) ENTIRE WESTERN GRID : |  | 4142.63 | MW
i) Dhaka area |  | 4707.87 | MW | i) Khulna area |  | 1555.2 | MW
ii) Chittagong area |  | 1391.3 | MW | ii) Rajshahi area |  | 1351.6 | MW
iii) Comilla area |  | 1161 | MW | iii) Barisal area |  | 357.83 | MW
iv) Mymensingh area |  | 1025 | MW | iv) Rangpur area |  | 878 | MW
v) Sylhet area |  | 445 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12872.8 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 31 | 19:00 | Hasnabad | 91 | 21:00 | Noapara | 50 | 19:30
Agargaon | 80 | 11:00 | Hathazari | 98 | 19:30 | Pabna | 106 | 19:30
Agrabad | 74 | 19:00 | Ish-D | N/A | N/A | Palashbari | 118 | 22:00
AKS | 22 | 23:00 | Ishurdi | 76 | 20:00 | Panchagarh | 59 | 22:00
AKSML | 134 | 16:00 | Jaldhaka | 64 | 20:00 | Patuakhali | 115.5 | 22:00
Amnura | 50 | 02:00 | Jamalpur | 154 | 00:00 | Payra | 0.93 | 11:00
Ashuganj | 42 | 14:00 | Jashore | 111 | 00:00 | PHP | 5 | 18:30
Bagerhat | 98 | 20:00 | Jhenaidah | 112 | 00:00 | Purbachal | 19 | 14:00
Bakulia | 121 | 19:00 | Joydebpur | 186 | 21:00 | Purbasadipur | 123 | 00:00
Banani | 51 | 12:00 | Joypurhat | 67 | 21:00 | Rahim | 26 | 10:00
Bangabhaban | 10 | 10:00 | Juldah | 26 | 12:00 | Rajbari | 64 | 19:30
Barapukuria | 53 | 22:00 | Kabirpur | 265 | 16:00 | Rajendrapur | 115 | 12:00
Barguna | 20 | 23:00 | Kachua | 74 | 22:00 | Rajshahi | 141 | 20:00
Barishal | 113 | 19:30 | Kallyanpur | 99 | 19:30 | Rajshahi | 38 | 00:00
Barishal | 46 | 21:00 | Kalurghat | 6 | 10:00 | Ramganj | 120 | 22:00
Baroaulia | 73 | 13:00 | Kamrangirchar | 78 | 09:00 | Rampur | 21.5 | 19:30
Baroirhat | 50 | 19:30 | Kaptai | 4 | 18:30 | Rangamati | 14 | 19:30
Bashundhara | 154 | 14:00 | Kazla | 84 | 16:00 | Rangpur | 153 | 23:00
BashundharaCement | 7 | 15:00 | Keranigonj | 50 | 13:00 | Ruppur | 3 | 18:00
Beanibazar | 68 | 23:00 | Khagrachori | 26 | 14:00 | Saidpur | 107 | 20:00
Benapole | 72 | 20:00 | Khulna | 91 | 13:00 | Satkhira | 114 | 00:00
Bhaluka | 152 | 12:00 | Khulshi | 175 | 13:00 | Satmasjid | 99 | 19:30
Bhandaria | 54 | 00:00 | Kishoreganj | 146 | 00:00 | Savar | 185 | 12:00
Bhangura | 33 | 21:00 | Kodda | 320 | 19:30 | Shahjadpur | 96 | 22:00
Bheramara(GK) | 60 | 20:00 | KSRM | 27.9 | 21:00 | Shahjibazar | 118 | 22:00
Bhulta | 252 | 02:00 | Kulaura | 46 | 21:00 | Shahmirpur | 43 | 18:30
Bog-Sherpur | 64 | 20:00 | Kurigram | 68 | 21:00 | Shariatpur | 70 | 00:00
Bogura | 154 | 00:00 | Kushtia | 137 | 20:00 | Sherpur | 132 | 22:00
Borhanuddin | 37 | 21:00 | Lalbag | 93 | 13:00 | Shikalbaha | 27 | 18:30
Brahmanbaria | 160 | 00:00 | Lalmonirhat | 50 | 20:00 | Shitalakhya | 124 | 12:00
BSRM | 165 | 11:00 | Madanganj | 105 | 00:00 | Sholosohor | N/A | N/A
Cantonment | 129 | 12:00 | Madaripur | 95 | 00:00 | Shyampur | 156 | 10:00
Chandpur | 63 | 23:00 | Madartek | 76 | 21:00 | Siddhirganj | 120 | 09:00
Chandraghona | 32 | 19:00 | Madunaghat | 57 | 19:00 | Sirajganj | 104 | 19:30
Chapai | 65 | 01:00 | Magura | 54 | 00:00 | Sonargaon | 95 | 15:00
Charsaidpur | 45 | 21:00 | Mahasthangarh | 70 | 00:00 | Sreemongol | 48 | 20:00
Chauddagram | 49 | 23:00 | Manikganj | 80 | 21:00 | Srinagar | 42.83 | 22:00
Chhatak | 22 | 20:00 | Maniknagar | 60 | 12:00 | SSM | 10 | 23:00
Chowmuhani | 188 | 19:30 | Matarbari | 36 | 21:00 | Sunamganj | 20 | 19:00
Chuadanga | 100 | 20:00 | Matuail | 66 | 12:00 | Sylhet | 127 | 19:30
Coxsbazar | 108 | 22:00 | Millgate | 62 | 11:00 | Tangail | 205 | 00:00
Cumilla(N) | 147 | 19:30 | Mirpur | 142 | 19:00 | Thakurgaon | 99 | 20:00
Cumilla(S) | 154 | 20:00 | Mirsorai | N/A | N/A | TK | 28.9 | 21:00
Daudkandi | 136 | 22:00 | Mithapukur | 30 | 02:00 | Tongi | 126 | 12:00
Dhaka | 30 | 12:00 | Modern | 0 | 00:00 | Ullon | 44 | 19:30
Dhamrai | 114 | 12:00 | Mogbazar | 116 | 12:00 | Uttara | 87 | 13:00
Dhanmondi | 129 | 12:00 | Mongla | 44 | 11:00 | UttaraNew | 16 | 12:00
Dohazari | 92 | 20:00 | Motijheel | 34 | 11:00 | Zigatola | 43 | 19:30
Faridpur | 140 | 21:00 | Munshiganj | 106 | 00:00
Fatullah | 68 | 12:00 | Mymensingh | 213 | 20:00
Fenchuganj | 39 | 23:00 | Naogaon | 118 | 20:00
Feni | 123 | 19:30 | Narail | 52 | 21:00
Ghorashal | 61 | 00:00 | Narinda | 67 | 12:00
Goalpara | 26 | 00:00 | Narshingdi | 172 | 21:00
Gollamari | 49 | 15:00 | Natore | 139 | 20:00
Gopalganj | 92 | 22:00 | Natore-D | N/A | N/A
GPH | 93 | 21:00 | Nawabganj | 51.6 | 22:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 400 | 05:00 | 381 | 15:00 | Kaliakoir | 396 | 15:00 | 382 | 13:00
| Bibiana | 412 | 01:00 | 402 | 10:00 | Payra | 421 | 09:00 | 405 | 23:00
| BIPTC | 400 | 06:00 | 393 | 00:00
| Gopalganj_I | 415 | 18:00 | 392 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 01:00 | 217 | 13:00 | Hathazari | 236 | 18:00 | 227 | 08:00
| AKSML | 236 | 01:00 | 218 | 08:00 | Ishurdi | 237 | 18:00 | 224 | 21:00
| Aminbazar | 228 | 01:00 | 219 | 10:00 | Jhenaidah | 233 | 06:00 | 214 | 21:00
| Baghabari | 235 | 17:00 | 226 | 21:00 | Kaliakoir | 227 | 18:00 | 220 | 15:00
| Barapukuria | 229 | 18:00 | 214 | 21:00 | Keranigonj | 228 | 01:00 | 217 | 10:00
| Barishal | 235 | 09:00 | 222 | 23:00 | Khulna(S) | 242 | 06:00 | 221 | 22:00
| Bheramara | 235 | 05:00 | 222 | 21:00 | Maniknagar | 231 | 01:00 | 220 | 12:00
| Bhulta | 233 | 01:00 | 222 | 12:00 | Meghnaghat | 232 | 00:00 | 227 | 15:00
| Bibiana | 243 | 03:00 | 233 | 10:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 05:00 | 221 | 21:00 | Rajshahi | 234 | 18:00 | 219 | 00:00
| Bogura | 232 | 18:30 | 220 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 09:00 | 229 | 20:00 | Rampura | 230 | 01:00 | 220 | 15:00
| BSRM | 235 | 00:00 | 224 | 08:00 | Shikalbaha | 238 | 18:30 | 229 | 08:00
| Cumilla(N) | 232 | 04:00 | 225 | 10:00 | Shyampur | 229 | 01:00 | 219 | 10:00
| Fenchuganj | 242 | 18:00 | 237 | 08:00 | Siddhirganj | 234 | 02:00 | 224 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 18:00 | 226 | 00:00
| GPH | 238 | 19:30 | 224 | 08:00 | Tongi | 228 | 00:00 | 218 | 08:00
| Haripur | 229 | 00:00 | 220 | 11:00
| Hasnabad | 228 | 00:00 | 218 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 03:00 | 127 | 15:00 | Mahasthangarh | 135 | 18:00 | 125 | 01:00
| Agargaon | 136 | 01:00 | 128 | 12:00 | Manikganj | 129 | 18:00 | 120 | 23:00
| Agrabad | 139 | 19:30 | 131 | 08:00 | Maniknagar | 136 | 01:00 | 129 | 10:00
| AKS | 137 | 00:00 | 130 | 15:00 | Matarbari | 126 | 14:00 | 119 | 04:00
| Aminbazar | 133 | 01:00 | 127 | 07:00 | Matuail | 135 | 02:00 | 128 | 13:00
| Amnura | 134 | 17:00 | 122 | 01:00 | Millgate | 137 | 01:00 | 127 | 11:00
| Ashuganj | 137 | 05:00 | 134 | 23:00 | Mirpur | 139 | 23:00 | 124 | 11:00
| Bagerhat | 134 | 06:00 | 121 | 23:00 | Mithapukur | 134 | 18:00 | 122 | 00:00
| Bakulia | 139 | 19:30 | 133 | 08:00 | Modern | 139 | 19:00 | 132 | 10:00
| Banani | 137 | 02:00 | 127 | 10:00 | Mogbazar | 138 | 00:00 | 129 | 11:00
| Bangabhaban | 137 | 04:00 | 129 | 09:00 | Mongla | 131 | 06:00 | 119 | 23:00
| Barapukuria | 137 | 18:00 | 126 | 21:00 | Motijheel | 137 | 04:00 | 128 | 11:00
| Barguna | 139 | 07:00 | 130 | 23:00 | Munshiganj | 136 | 03:00 | 130 | 10:00
| Barishal | 139 | 03:00 | 130 | 23:00 | Mymensingh | 133 | 05:00 | 121 | 23:00
| Barishal | 141 | 06:00 | 132 | 23:00 | Naogaon | 133 | 18:30 | 120 | 00:00
| Baroaulia | 141 | 20:00 | 134 | 10:00 | Narail | 135 | 18:00 | 124 | 22:00
| Baroirhat | 132 | 07:00 | 128 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bashundhara | 138 | 01:00 | 126 | 12:00 | Narshingdi | 137 | 21:00 | 123 | 11:00
| BashundharaCement | 135 | 00:00 | 128 | 10:00 | Natore | 135 | 18:00 | 126 | 00:00
| Beanibazar | 136 | 07:00 | 127 | 23:00 | Natore-D | N/A | N/A | N/A | N/A
| Benapole | 137 | 05:00 | 122 | 23:00 | Nawabganj | 138 | 03:00 | 130 | 12:00
| Bhaluka | 130 | 03:00 | 117 | 23:00 | Netrakona | 132 | 16:00 | 120 | 23:00
| Bhandaria | 139 | 07:00 | 125 | 21:00 | New | 137 | 00:00 | 128 | 12:00
| Bhangura | 140 | 18:00 | 132 | 00:00 | Niamatpur | 132 | 18:00 | 117 | 22:00
| Bheramara | 137 | 05:00 | 131 | 21:00 | Noapara | 138 | 05:00 | 124 | 22:00
| Bheramara(GK) | 137 | 06:00 | 131 | 21:00 | Pabna | 136 | 06:00 | 129 | 00:00
| Bhulta | 127 | 02:00 | 120 | 15:00 | Palashbari | 134 | 18:00 | 120 | 00:00
| Bog-Sherpur | 136 | 18:00 | 127 | 00:00 | Panchagarh | 133 | 18:00 | 115 | 19:30
| Bogura | 137 | 18:00 | 126 | 23:00 | Patuakhali | 137 | 04:00 | 130 | 23:00
| Bogura | 136 | 18:00 | 128 | 00:00 | Payra | 139 | 06:00 | 133 | 22:00
| Brahmanbaria | 131 | 04:00 | 128 | 00:00 | PHP | 133 | 09:00 | 127 | 23:00
| Cantonment | 135 | 01:00 | 127 | 12:00 | Purbachal | 138 | 01:00 | 126 | 12:00
| Chandpur | 139 | 20:00 | 135 | 00:00 | Purbasadipur | 134 | 18:00 | 120 | 19:30
| Chandraghona | 140 | 20:00 | 134 | 09:00 | Rahim | 135 | 00:00 | 130 | 11:00
| Chapai | 135 | 18:00 | 127 | 22:00 | Rajbari | 135 | 09:00 | 124 | 23:00
| Charsaidpur | 136 | 00:00 | 129 | 10:00 | Rajendrapur | 129 | 04:00 | 118 | 11:00
| Chauddagram | 132 | 06:00 | 129 | 00:00 | Rajshahi | 133 | 18:00 | 123 | 00:00
| Chhatak | 134 | 03:00 | 130 | 22:00 | Rajshahi | 133 | 18:00 | 124 | 00:00
| Chowmuhani | 130 | 07:00 | 125 | 00:00 | Ramganj | 135 | 20:00 | 128 | 00:00
| Chuadanga | 131 | 06:00 | 110 | 22:00 | Rampur | 138 | 19:30 | 131 | 08:00
| Coxsbazar | 128 | 09:00 | 118 | 03:00 | Rampura | 135 | 01:00 | 127 | 15:00
| Cumilla(N) | 136 | 18:30 | 132 | 10:00 | Rangamati | 138 | 01:00 | 133 | 08:00
| Cumilla(S) | 136 | 18:30 | 128 | 15:00 | Rangpur | 133 | 18:00 | 120 | 00:00
| Daudkandi | 133 | 18:00 | 129 | 11:00 | Ruppur | 136 | 05:00 | 130 | 21:00
| Dhaka | 135 | 01:00 | 127 | 16:00 | Saidpur | 134 | 18:00 | 121 | 21:00
| Dhamrai | 133 | 01:00 | 125 | 12:00 | Satkhira | 134 | 06:00 | 119 | 23:00
| Dhanmondi | 135 | 01:00 | 128 | 11:00 | Satmasjid | 136 | 01:00 | 128 | 10:00
| Dohazari | 136 | 19:30 | 129 | 04:00 | Savar | 135 | 01:00 | 126 | 08:00
| Faridpur | 135 | 09:00 | 125 | 23:00 | Shahjadpur | 140 | 17:00 | 134 | 00:00
| Fatullah | 135 | 01:00 | 129 | 10:00 | Shahjibazar | 135 | 06:00 | 130 | 23:00
| Fenchuganj | 138 | 04:00 | 134 | 13:00 | Shahmirpur | 140 | 20:00 | 130 | 21:00
| Feni | 134 | 18:30 | 128 | 00:00 | Shariatpur | 137 | 09:00 | 124 | 23:00
| Ghorashal | 137 | 00:00 | 137 | 00:00 | Sherpur | 139 | 16:00 | 127 | 21:00
| Goalpara | 139 | 05:00 | 126 | 23:00 | Shikalbaha | 141 | 19:30 | 134 | 08:00
| Gollamari | 134 | 18:00 | 122 | 23:00 | Shikalbaha | 140 | 18:30 | 135 | 05:00
| Gopalganj | 135 | 09:00 | 124 | 23:00 | Shitalakhya | 137 | 01:00 | 128 | 10:00
| Gopalganj_I | 138 | 05:00 | 128 | 23:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gulshan | 135 | 01:00 | 127 | 11:00 | Shyampur | 133 | 00:00 | 129 | 10:00
| Halishahar | 140 | 19:30 | 132 | 10:00 | Shyampur | 134 | 01:00 | 128 | 10:00
| Haripur | 135 | 00:00 | 130 | 11:00 | Siddhirganj | 134 | 00:00 | 128 | 10:00
| HaripurSBU | 135 | 02:00 | 129 | 10:00 | Sirajganj | 136 | 18:00 | 127 | 00:00
| Hasnabad | 137 | 02:00 | 130 | 10:00 | Sonargaon | 134 | 00:00 | 129 | 10:00
| Hathazari | 141 | 19:30 | 133 | 08:00 | Sreemongol | 137 | 06:00 | 134 | 00:00
| Ish-D | N/A | N/A | N/A | N/A | Srinagar | 137 | 02:00 | 129 | 12:00
| Ishurdi | 137 | 06:00 | 130 | 21:00 | SSM | 141 | 00:00 | 138 | 07:00
| Jaldhaka | 132 | 18:00 | 117 | 22:00 | Sunamganj | 135 | 05:00 | 130 | 14:00
| Jamalpur | 139 | 02:00 | 129 | 10:00 | Sylhet | 135 | 04:00 | 131 | 14:00
| Jashore | 136 | 05:00 | 123 | 22:00 | Tangail | 133 | 02:00 | 124 | 23:00
| Jhenaidah | 138 | 05:00 | 125 | 22:00 | Thakurgaon | 135 | 18:00 | 118 | 23:00
| Jhenaidah | 137 | 06:00 | 126 | 21:00 | TK | 140 | 14:00 | 134 | 06:00
| Joydebpur | 143 | 00:00 | 135 | 10:00 | Tongi | 136 | 00:00 | 129 | 10:00
| Joypurhat | 134 | 18:30 | 117 | 21:00 | Ullon | 135 | 01:00 | 127 | 11:00
| Juldah | 141 | 19:30 | 134 | 10:00 | Uttara | 134 | 03:00 | 123 | 13:00
| Kabirpur | 134 | 00:00 | 122 | 10:00 | UttaraNew | 137 | 01:00 | 126 | 10:00
| Kachua | 136 | 20:00 | 132 | 22:00 | Zigatola | 137 | 02:00 | 128 | 13:00
| Kaliakoir | 131 | 18:00 | 126 | 14:00
Page 7 of 7

## L-Curve
Date | 2022-06-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 118 | 8976 | 4143 | 13119 |  |  |  | QF-LDC-11
0:30 | 160 | 8745.5 | 4034.5 | 12780 | Date: | 2022-06-25
1:00 | 202 | 8515 | 3926 | 12441
1:30 | 192 | 8303 | 3864.5 | 12167.5
2:00 | 182 | 8091 | 3803 | 11894
2:30 | 162 | 7994 | 3775.5 | 11769.5 | [5 empty] | Gen. at Eve. Peak | 13319 | 13319 MW (21:00 )
3:00 | 142 | 7897 | 3748 | 11645 | [6 empty] | 21:00
3:30 | 108 | 7703 | 3714.5 | 11417.5 | [5 empty] | Gen. at Day Peak | 11756 | 11756 MW (12:00 )
4:00 | 74 | 7509 | 3681 | 11190 | [6 empty] | 12:00
4:30 | 58 | 7449 | 3649.5 | 11098.5 | [5 empty] | Highest Generation | 13319
5:00 | 42 | 7389 | 3618 | 11007 | [6 empty] | 21:00
5:30 | 109 | 7105.5 | 3480.5 | 10586
6:00 | 176 | 6822 | 3343 | 10165
6:30 | 130 | 6752 | 3281.5 | 10033.5
7:00 | 84 | 6682 | 3220 | 9902
7:30 | 82 | 6837 | 3171 | 10008
8:00 | 80 | 6992 | 3122 | 10114
8:30 | 96 | 7179 | 3196.5 | 10375.5
9:00 | 112 | 7366 | 3271 | 10637
9:30 | 150 | 7574.5 | 3314 | 10888.5
10:00 | 188 | 7783 | 3357 | 11140
10:30 | 195 | 7995 | 3432 | 11427
11:00 | 202 | 8207 | 3507 | 11714
11:30 | 130 | 8222 | 3513 | 11735
12:00 | 58 | 8237 | 3519 | 11756
12:30 | 38 | 8354 | 3562.5 | 11916.5
13:00 | 18 | 8471 | 3606 | 12077
13:30 | 33 | 8431.5 | 3515 | 11946.5
14:00 | 48 | 8392 | 3424 | 11816
14:30 | 60 | 8434.5 | 3395.5 | 11830
15:00 | 72 | 8477 | 3367 | 11844
15:30 | 57 | 8378.5 | 3345 | 11723.5
16:00 | 42 | 8280 | 3323 | 11603
16:30 | 96 | 8075 | 3271 | 11346
17:00 | 150 | 7870 | 3219 | 11089
17:30 | 150 | 7707.5 | 3158 | 10865.5
18:00 | 150 | 7545 | 3097 | 10642
18:30 | 115 | 7918 | 3237 | 11155
19:00 | 80 | 8291 | 3377 | 11668
19:30 | 70 | 8978 | 4100 | 13078
20:00 | 76 | 8925 | 4151 | 13076 |  |  |  | Executive Engineer
20:30 | 139 | 9013.5 | 4184 | 13197.5 |  |  |  | Network Operation Division
21:00 | 202 | 9102 | 4217 | 13319
21:30 | 204 | 9079 | 4189.5 | 13268.5
22:00 | 206 | 9056 | 4162 | 13218 |  |  |  |  | Page 6 of 7
22:30 | 141 | 9009 | 4217 | 13226
23:00 | 76 | 8962 | 4272 | 13234
23:30 | 97 | 8969 | 4207.5 | 13176.5
24:00 | 118 | 8976 | 4143 | 13119
13319 MW (21:00 )
11756 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-25 |  | Energy |  | 283773253
[13 empty] | 2022-06-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4324 | 875 | 2426 | 275 | 3613 | 795 | 124 | 0 | 535 | 152 | 0 | 0
0:30 | 4371.5 | 898.5 | 2402 | 137.5 | 3593.5 | 775 | 123.5 | 0 | 334.5 | 144 | 0 | 0 | Date: | 2022-06-25
1:00 | 4419 | 922 | 2378 | 0 | 3574 | 755 | 123 | 0 | 134 | 136 | 0 | 0
1:30 | 4416 | 913 | 2381.5 | 0 | 3337.5 | 745 | 123.5 | 0 | 117 | 134 | 0 | 0 | [8 empty] | Total Energy | 283.7733 | Total Energy Gen 283.773 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 283.773 MKWHr
2:00 | 4413 | 904 | 2385 | 0 | 3101 | 735 | 124 | 0 | 100 | 132 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4411.5 | 903.5 | 2387 | 0 | 3012.5 | 735 | 124 | 0 | 66 | 130 | 0 | 0 | [8 empty] | Energy Requirement | 283.7733
3:00 | 4410 | 903 | 2389 | 0 | 2924 | 735 | 124 | 0 | 32 | 128 | 0 | 0
3:30 | 4410.5 | 907 | 2387 | 0 | 2730.5 | 715 | 124.5 | 0 | 16 | 127 | 0 | 0 | [6 empty] | Shortage
4:00 | 4411 | 911 | 2385 | 0 | 2537 | 695 | 125 | 0 | 0 | 126 | 0 | 0
4:30 | 4413.5 | 911 | 2391 | 0 | 2461.5 | 674.5 | 125 | 0 | 0 | 122 | 0 | 0
5:00 | 4416 | 911 | 2397 | 0 | 2386 | 654 | 125 | 0 | 0 | 118 | 0 | 0
5:30 | 4298.5 | 911 | 2392.5 | 0 | 2120.5 | 619.5 | 125 | 0 | 0 | 115 | 4 | 0
6:00 | 4181 | 911 | 2388 | 0 | 1855 | 585 | 125 | 0 | 0 | 112 | 8 | 0
6:30 | 4127 | 910.5 | 2396 | 0 | 1795.5 | 550 | 125 | 0 | 0 | 108 | 21.5 | 0 |  |  |  |  | Coal
7:00 | 4073 | 910 | 2404 | 0 | 1736 | 515 | 125 | 0 | 0 | 104 | 35 | 0
7:30 | 4170.5 | 910.5 | 2403.5 | 0 | 1744.5 | 485 | 125.5 | 0 | 0 | 110 | 58.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4268 | 911 | 2403 | 0 | 1753 | 455 | 126 | 0 | 0 | 116 | 82 | 0
8:30 | 4259.5 | 910.5 | 2377.5 | 0 | 2051.5 | 449.5 | 126 | 0 | 0 | 120 | 81 | 0
9:00 | 4251 | 910 | 2352 | 0 | 2350 | 444 | 126 | 0 | 0 | 124 | 80 | 0
9:30 | 4252 | 903 | 2352 | 0 | 2555.5 | 444.5 | 126 | 0 | 0 | 127 | 128.5 | 0
10:00 | 4253 | 896 | 2352 | 0 | 2761 | 445 | 126 | 0 | 0 | 130 | 177 | 0
10:30 | 4373.5 | 896 | 2316 | 0 | 2910.5 | 450 | 125.5 | 0 | 53 | 132 | 170.5 | 0
11:00 | 4494 | 896 | 2280 | 0 | 3060 | 455 | 125 | 0 | 106 | 134 | 164 | 0
11:30 | 4448 | 896 | 2275 | 0 | 3117 | 480 | 124 | 0 | 109 | 136 | 150 | 0
12:00 | 4402 | 896 | 2270 | 0 | 3174 | 505 | 123 | 0 | 112 | 138 | 136 | 0
12:30 | 4492.5 | 896.5 | 2313.5 | 0 | 3195.5 | 515 | 122 | 0 | 132 | 138 | 111.5 | 0
13:00 | 4583 | 897 | 2357 | 0 | 3217 | 525 | 121 | 0 | 152 | 138 | 87 | 0
13:30 | 4583 | 897 | 2357 | 0 | 3217 | 525 | 121 | 0 | 152 | 138 | 87 | 0
14:00 | 4583 | 897 | 2357 | 0 | 3217 | 525 | 121 | 0 | 152 | 138 | 87 | 0
14:30 | 4515 | 898 | 2285.5 | 0 | 3227.5 | 515 | 121 | 0 | 160.5 | 143 | 95 | 0
15:00 | 4447 | 899 | 2214 | 0 | 3238 | 505 | 121 | 0 | 169 | 148 | 103 | 0
15:30 | 4421 | 895.5 | 2198.5 | 0 | 3177.5 | 505 | 121 | 0 | 153 | 144 | 108 | 0
16:00 | 4395 | 892 | 2183 | 0 | 3117 | 505 | 121 | 0 | 137 | 140 | 113 | 0
16:30 | 4207 | 890.5 | 2202 | 0 | 2952 | 505 | 121 | 0 | 149.5 | 139 | 86 | 0
17:00 | 4207 | 889 | 2221 | 0 | 2787 | 505 | 121 | 0 | 162 | 138 | 59 | 0
17:30 | 4105 | 889 | 2102 | 0 | 2803.5 | 505 | 122 | 0 | 169.5 | 133 | 36.5 | 0
18:00 | 4003 | 889 | 1983 | 0 | 2820 | 505 | 123 | 0 | 177 | 128 | 14 | 0
18:30 | 4091 | 886.5 | 2090 | 0 | 3007 | 515 | 123 | 0 | 297.5 | 138 | 7 | 0
19:00 | 4179 | 884 | 2197 | 0 | 3194 | 525 | 123 | 0 | 418 | 148 | 0 | 0
19:30 | 4278 | 884 | 2326 | 259 | 3830 | 665 | 123 | 0 | 563 | 150 | 0 | 0
20:00 | 4350 | 884 | 2355 | 100 | 3874 | 695 | 123 | 0 | 541 | 154 | 0 | 0
20:30 | 4392.5 | 883.5 | 2392 | 78.5 | 3897.5 | 735 | 124 | 0 | 542.5 | 152 | 0 | 0
21:00 | 4435 | 883 | 2429 | 57 | 3921 | 775 | 125 | 0 | 544 | 150 | 0 | 0
21:30 | 4389.5 | 876.5 | 2502.5 | 28.5 | 3879.5 | 775 | 124 | 0 | 544 | 149 | 0 | 0
22:00 | 4344 | 870 | 2576 | 0 | 3838 | 775 | 123 | 0 | 544 | 148 | 0 | 0
22:30 | 4424.5 | 872.5 | 2511.5 | 27 | 3796 | 780 | 123.5 | 0 | 540 | 151 | 0 | 0
23:00 | 4505 | 875 | 2447 | 54 | 3754 | 785 | 124 | 0 | 536 | 154 | 0 | 0
23:30 | 4414.5 | 875 | 2436.5 | 164.5 | 3683.5 | 790 | 124 | 0 | 535.5 | 153 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.3° C
24:00 | 4324 | 875 | 2426 | 275 | 3613 | 795 | 124 | 0 | 535 | 152 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 283.773 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 283.773 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 89 | 89 | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 90 | 88 | 86 | 86 | 86 | 86 | 86 | 88 |  | 88 | 88 | 88 | 90 | 88 | 89 | 89 | 2131195
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [8 empty] | 10 | 25 | 25 | 25 | 25 | 8 | 8 | 8 |  | 8 | 16 | 22 | 25 | 25 | 5 | 25 | 321242
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 3 | 11 | 12 | 14 | 5 | 20 | 7 | 12 | 14 | 9 | 4 | 1 |  | 0 | [6 empty] | 122715
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 265439
12 | Hathazari 100 MW peaking PP | [17 empty] | 0 |  | 19 | 29 | 31 | 34 | 34 | 34 | 34 | 199888
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2544218
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 0 | 50 | 20 | 0 |  |  |  | 35904
14 | Titas 50 MW Peaking PP | [10 empty] | 15 | 24 | 25 | 36 | 41 | 41 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 549128
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 337 | 337 | 337 | 335 | 335 | 280 | 280 | 333 | 300 | 331 | 335 | 300 | 335 | 250 | 330 | 330 | 300 | 240 |  | 300 | 335 | 335 | 270 | 270 | 335 | 335 | 7387185
18 | Kodda 300 MW PP Unit-2 (Summit) | 274 | 195 | 195 | 60 | 15 | 15 | 15 | 15 | 43 | 150 | 214 | 238 | 242 | 242 | 242 | 240 | 240 | 258 |  | 260 | 275 | 278 | 278 | 275 | 271 | 276 | 4707053
19 | Ashuganj 195MW PP (APSCL-United) | 177 | 177 | 177 | 177 | 178 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 177 | 177 | 177 | 178 | 178 | 178 |  | 180 | 187 | 185 | 189 | 189 | 189 | 189 | 4365818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4353000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 12 | 12 | 12 | 14 | 14 | 17 | 17 | 11 | 11 | 12 |  | 12 | 12 | 12 | 14 | 15 | 15 | 28 | 403920
33 | Ashuganj 225 MW CCPP | 182 | 182 | 182 | 182 | 182 | 182 | 183 | 207 | 213 | 208 | 180 | 181 | 181 | 181 | 183 | 206 | 208 | 208 |  | 204 | 209 | 210 | 208 | 210 | 208 | 210 | 4742000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 305 | 310 | 310 | 275 | 340 | 315 | 345 | 315 | 315 | 315 | 270 | 270 | 275 | 270 | 270 |  | 335 | 270 | 270 | 330 | 305 | 345 | 305 | 7334000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 270 | 280 | 350 | 310 | 345 | 310 | 310 | 310 | 310 | 310 | 320 | 310 | 315 |  | 340 | 310 | 310 | 345 | 315 | 350 | 320 | 7919600
| Ashuganj 420 MW CCPP(East) | [10 empty] | 133 | 133 | 173 | 225 | 270 | 270 | 130 | 0 | [7 empty] | 0 | 1272500
35 | Ashuganj 55 MW PP (Precision) | 52 | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 49 | 49 | 47 | 48 | 49 | 48 | 48 | 48 | 50 | 50 |  | 53 | 53 | 54 | 52 | 53 | 53 | 54 | 1203840
36 | Chandpur 150 MW CCPP | 136 | 137 | 136 | 136 | 137 | 137 | 136 | 136 | 136 | 135 | 136 | 136 | 136 | 137 | 135 | 136 | 135 | 136 |  | 135 | 135 | 136 | 136 | 135 | 136 | 136 | 3265040
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 410 | 408 | 409 | 409 | 410 | 409 | 410 | 410 | 408 | 409 | 406 | 409 | 411 | 410 | 409 | 407 | 411 | 411 |  | 410 | 410 | 410 | 411 | 411 | 408 | 410 | 9955330
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 450 | 400 | 400 | 400 | 400 | 300 |  | 400 | 400 | 400 | 400 | 400 | 450 | 450 | 9771000
41 | Haripur 360MW CCPP(HPL) | [15 empty] | 0 | 31 | 31 |  | 35 | 35 | 38 | 142 | 293 |  | 0 | 450000
42 | RPCL 210MW CCPP | 194 | 191 | 192 | 193 | 193 | 192 | 190 | 187 | 190 | 185 | 189 | 176 | 161 | 152 | 145 | 135 | 132 | 130 |  | 130 | 131 | 131 | 129 | 120 | 120 | 122 | 3831360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 14 | 24 | 27 | 22 | 45 | 52 | 10 | 51 | 43 | 19 | 3 | 2 |  | 0 | [6 empty] | 328030
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 44 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1031000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 984944
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 30 | 31 | 31 | 30 | 30 | 31 | 31 | 31 | 30 | 30 | 20 |  | 30 | 31 | 32 | 31 | 31 | 30 | 31 | 730752
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 30 |  | 30 | 84 | 84 | 81 | 84 | 81 | 81 | 1902720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2861430
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 | 25 | 25 | 23 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 576960
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 211860
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251040
55 | Fenchugonj 51 MW PP (Barakatullah) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 34 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 385248
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 280 | 275 | 290 | 280 | 290 | 310 | 290 | 285 | 280 | 280 | 300 | 265 | 280 | 305 | 270 | 280 |  | 280 | 275 | 280 | 280 | 290 | 305 | 300 | 7112500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 360 | 360 | 378 | 395 | 392 | 400 | 394 | 400 | 360 | 380 | 390 | 395 | 400 |  | 390 | 400 | 400 | 400 | 400 | 400 | 401 | 9383000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1141237
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 23 | 23 | 24 | 10 | 10 | 10 | 18 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 553680
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499824
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 |  | 0 | 22 | 22 | 22 | 22 | 350100
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 426780
63 | Impoprt (Tripura) | 136 | 132 | 128 | 126 | 118 | 112 | 104 | 116 | 124 | 130 | 134 | 138 | 138 | 142 | 148 | 140 | 138 | 128 |  | 148 | 150 | 154 | 150 | 148 | 154 | 152 | 3211200
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 12 | 4 | 4 | 4 | 2 | 10 | 7 | 5 | 5 | 8 | 13 |  | 18 | 21 | 22 | 28 | 34 | 37 | 37 | 585120
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 446004
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 248400
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 24 | 33 | 31 | 27 | 16 | 16 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 737800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 12 | 18 | 18 | 18 | 20 | 18 | 18 | 18 | 18 | 20 |  | 20 | 20 | 21 | 21 | 21 | 18 | 18 | 458800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 20 | 0 | 0 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 622080
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 799400
72 | Rupganj 33 MW PP(Summit)
73 | Ghorashal 108MW PP (Regent) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 78 | 84 | 80 | 81 | 81 | 78 | 80 | 86 | 86 |  | 87 | 87 | 87 | 87 | 87 | 87 | 84 | 1974863
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 47 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 39 | 38 | 39 | 38 | 39 | 38 | 36 | 36 | 36 | 36 |  | 40 | 95 | 91 | 94 | 94 | 94 | 94 | 1218840
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 108 | 36 | 17 | 17 | 17 | 17 | 72 | 108 | 136 | 144 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3054240
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 90 | 20 |  |  |  |  | 0 | 20 | 50 | 60 | 75 | 80 | 80 | 91 | 86 | 68 | 40 |  | 48 | 100 | 94 | 98 | 100 | 100 | 100 | 1417046
78 | Gazipur 52 MW PP | 50 | 50 | 50 | [5 empty] | 17 | 50 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 |  | 48 | 48 | 49 | 50 | 50 | 50 | 50 | 918720
79 | Kodda 150MW PP | 98 | 64 | 32 | [7 empty] | 64 | 64 | 98 | 64 | 64 | 32 | 32 | 16 |  | 82 | 150 | 150 | 150 | 150 | 150 | 150 | 1436160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 70 | 50 | 50 | 80 | 105 | 90 | 90 | 90 | 105 | 105 | 105 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2328000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 2 | 4 | 5 | 2 | 1 | 1 | 0 | [8 empty] | 30000
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1256536
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 107 | 93 | 93 | 92 | 61 | 36 | 50 | 76 |  | 76 | 85 | 109 | 110 | 110 | 110 | 110 | 2366899
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 240 | 275 | 268 | 270 | 265 | 270 | 280 | 300 | 280 | 295 | 305 | 298 | 275 | 265 | 276 | 260 | 266 | 285 |  | 300 | 240 | 260 | 305 | 270 | 295 | 275 | 6714996
87 | Meghnaghat 100 MW(IEL) | 89 | 88 | 89 | 89 | 85 | 80 | 80 | 80 | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 74 | 70 | 67 |  | 80 | 89 | 88 | 89 | 83 | 72 | 70 | 1943040
| Meghnaghat 104 MW PP (OPCL) | 93 | 93 | 75 | 84 | 93 | 55 | 55 | 55 | 87 | 93 | 93 | 93 | 92 | 93 | 93 | 99 | 104 | 84 |  | 55 | 104 | 98 | 104 | 104 | 104 | 104 | 2137920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 742440
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 780984
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1130674
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 32 | 16 | 16 | 16 | 32 | 32 | 40 | 40 | 40 | 78 | 94 | 94 | 94 | 94 | 94 | 64 | 64 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1609056
95 | Patenga 50MW PP (Baraka) | 37 | 32 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 37 | 37 | 41 | 42 | 42 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 938400
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 12 | 23 | 36 | 75 | 65 | 26 | 0 | 0 |  | 16 | 80 | 79 | 82 | 40 |  | 1 | 464640
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 48 | 45 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1162884
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1189189
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2662773
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 12950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1292400
104 | Keranigonj 300 MW PP (APR) | [20 empty] | 45 | 20 | 0 |  | 54 | 155 | 219009
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 50 | 30 | 27 |  |  | 40 | 77051
106 | Mymensingh 200 MW PP (United) | 187 | 192 | 192 | 193 | 170 | 140 | 140 | 140 | 150 | 150 | 170 | 177 | 171 | 170 | 170 | 170 | 170 | 178 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4248000
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 50 | 30 | 30 |  |  | 80 | 100107
114 | Kodda 149 MW PP Unit-1 (Summit) | 100 | 96 | 98 | 96 | 97 | 62 | 52 | 50 | 65 | 78 | 79 | 79 | 77 | 79 | 78 | 70 | 60 | 101 |  | 135 | 134 | 134 | 134 | 134 | 114 | 80 | 2181168
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 63 | 63 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 20 |  | 50 | 90 | 90 | 90 | 90 | 90 | 90 | 1931520
116 | Chandpur 200MW (Desh energy) | 184 | 155 | 155 | 155 | 155 | 100 | 100 | 100 | 115 | 112 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 124 | 200 | 190 | 200 | 200 | 200 | 182 | 3492960
117 | Ashuganj 150MW PP (Midland) | 143 | 142 | 143 | 143 | 142 | 90 | 50 | 50 | 81 | 114 | 122 | 117 | 120 | 127 | 130 | 132 | 132 | 132 |  | 137 | 140 | 140 | 140 | 142 | 143 | 143 | 2977454
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 401 | 401 | 401 | 376 | 370 | 397 | 402 | 365 | 402 | 370 | 404 | 403 | 403 | 365 | 364 | 364 |  | 400 | 400 | 400 | 402 | 402 | 403 | 402 | 9379000
| Jamalpur 115 MW PP (United) | 102 | 102 | 102 | 55 | 25 | 0 |  |  | 25 | 45 | 72 | 92 | 107 | 107 | 107 | 107 | 45 | 45 |  | 64 | 108 | 108 | 108 | 108 | 115 | 115 | 1845600
| Anwara 300 MW PP (United) | 210 | 95 | 45 | 15 | 0 |  |  |  | 80 | 80 | 170 | 230 | 265 | 300 | 300 | 245 | 155 | 155 |  | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 4147527
| Juldah unit-2 (Acorn) | 76 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 78 | 76 | 76 | 66 | 65 | 55 | 50 | 50 | 50 |  | 82 | 100 | 100 | 77 | 55 | 50 | 50 | 1479360
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2152800
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 21 | 28 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 849600
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 17 | 16 | 26 | 22 | 31 | 18 | 21 | 8 | 12 | 14 | 2 |  | 0 | [6 empty] | 194597
| Chandpur 115(Doreen) | 116 | 116 | 116 | 116 | 111 | 116 | 106 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 115 | 116 | 116 | 114 |  | 105 | 100 | 98 | 99 | 109 | 116 | 116 | 2731200
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 34 | 34 | 34 | 51 | 55 | 55 | [14 empty] | 0 | 591480
120 | Eastern Zone Total | 8515 | 8091 | 7897 | 7509 | 7389 | 6822 | 6682 | 6992 | 7366 | 7783 | 8207 | 8237 | 8471 | 8392 | 8477 | 8280 | 7870 | 7545 |  | 8291 | 8978 | 8925 | 9102 | 9056 | 8962 | 8976 | 194904567
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 110 | 110 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 113 | 112 | 81 | 15 | 15 | 15 | 21 | 16 |  | 35 | 48 | 63 | 63 | 63 | 64 | 30 | 1805760
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 0 |  | 33 | 45 | 39 | 39 | 39 | 39 | 39 | 199680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 17 | [6 empty] | 6 | 35 | 35 | 35 | 35 | 47 | 53 | 53 | 17 | 17 |  | 17 | 80 | 66 | 93 | 93 | 93 | 92 | 973920
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 11 | 25 | 13 | 103 | 75 | 20 | 36 | 105 | 32 | 69 | 35 | 8 |  | 0 | [6 empty] | 549360
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | [22 empty] | 0 | 62400
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 226 | 226 | 226 | 224 | 225 | 226 | 220 | 220 | 222 | 224 | 221 | 220 | 185 | 175 | 175 | 202 | 164 |  | 184 | 222 | 223 | 223 | 225 | 223 | 226 | 5162455
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | [18 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 110112
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 85 | 87 | 87 | 86 | 86 | 69 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 84 | 85 |  | 84 | 86 | 87 | 85 | 86 | 81 | 84 | 1976145
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 26 | 25 | 24 | 21 | 18 | 18 | 16 | 18 | 18 | 19 | 19 | 21 | 21 | 20 | 18 | 18 |  | 25 | 28 | 28 | 29 | 30 | 32 | 31 | 534162
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [10 empty] | 50 | 0 |  |  |  | 0 | 25920
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 24 | 24 | [16 empty] | 8 | 40 | 40 | 40 | 16 | 16 | 16 | 217875
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 2 |  | 10 | 10 | 0 |  |  |  |  | 11520
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 922 | 904 | 903 | 911 | 911 | 911 | 910 | 911 | 910 | 896 | 896 | 896 | 897 | 899 | 899 | 892 | 889 | 889 |  | 884 | 884 | 884 | 883 | 870 | 875 | 875 | 21698909
147 | Bheramara 410 MW CCPP | 410 | 405 | 405 | 410 | 410 | 410 | 360 | 320 | 320 | 320 | 360 | 360 | 405 | 340 | 340 | 270 | 270 | 270 |  | 310 | 355 | 355 | 385 | 355 | 390 | 355 | 8744256
148 | Payra 1320 MW | 580 | 560 | 560 | 520 | 480 | 410 | 340 | 280 | 270 | 270 | 280 | 330 | 350 | 330 | 330 | 330 | 330 | 330 |  | 350 | 490 | 520 | 600 | 600 | 610 | 620 | 11381300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 174 | 175 | 175 | 175 | 174 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4288800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [10 empty] | 80 | 100 | 100 | 80 | 80 | 80 | 80 | 80 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 1227000
| Baghabari 50 MW Peaking PP | [13 empty] | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 368880
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 3 | 4 | 5 | 2 | 3 | 4 | 1 | 0 | 0 | 0 | [8 empty] | 31200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 215 | 217 | 217 | 217 | 216 | 180 | 180 | 180 | 210 | 189 | 207 | 212 | 211 | 166 | 133 | 170 | 170 | 159 |  | 140 | 199 | 207 | 215 | 215 | 214 | 215 | 4933836
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 215 | 217 | 217 | 217 | 216 | 180 | 180 | 186 | 208 | 180 | 205 | 211 | 209 | 202 | 185 | 177 | 160 | 150 |  | 145 | 161 | 220 | 215 | 215 | 214 | 214 | 5009018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 425 | 421 | 422 | 422 | 425 | 421 | 421 | 414 | 414 | 414 | 385 | 380 | 414 | 353 | 394 | 350 | 350 | 270 |  | 326 | 414 | 414 | 332 | 340 | 414 | 418 | 9313745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [12 empty] | 5 | 5 | 6 | 6 | 23 | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 256712
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 19 | 19 | 20 | 20 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 492000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 227592
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [13 empty] | 16 | 34 | 8 | 8 | 8 |  | 8 | 34 | 34 | 34 | 34 | 34 | 25 | 214496
167 | Katakhali 50 MW Peaking PP | [10 empty] | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 27 | 32 | 24 | 24 | 24 | 16 | 16 | 265648
168 | Santahar 50 MW Peaking PP | 36 | 36 | [15 empty] | 20 |  | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 294710
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 40 | 90 | 90 | 90 | 90 | 90 | 90 | 452408
171 | Baghabari 200 MW PP (Paramount) | [20 empty] | 14 | 0 |  |  |  | 0 | 28541
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 50 | 50 | 50 | 78 | 94 | 94 | 94 | 94 | 100 | 113 | 113 | 50 | 50 |  | 50 | 70 | 110 | 113 | 113 | 113 | 113 | 2227104
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 60 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2485728
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 68 | 68 | 68 | 68 | 68 | 46 | 34 | 34 | 60 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 72 | 90 |  | 95 | 95 | 95 | 102 | 102 | 102 | 69 | 1724755
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 3 | 6 | 7 | 7 | 2 | 2 | 2 | 2 | 1 |  | 0 | [6 empty] | 36931
178 | Energypac Power Venture Thakurgaon Ltd. | 72 | 52 | 52 | 52 | 32 | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 77 | 107 | 107 |  | 107 | 109 | 108 | 108 | 108 | 108 | 72 | 1535808
178