## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-27 | Monday
|  |  | Date (day): | 2022-06-27 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13648.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14960 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-26 | 2022-06-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 91 | 85 | 91 |  | 17 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 409 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 312 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 64 | 79 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 270 | 280 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 91 | 91 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 330 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 85 | 95 |  | 7 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 50 | 45 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 274 | 275 | 270 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 78 | 255 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 25 | 85 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 40 | 80 | 25 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 80 | 134 | 134 | 134 |  | 15 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 42 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3352 | 4086 | 4052 | 4258 | 291 | 1275
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 0 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 37 | 43 | 43 |  | 7 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 124 | 125 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 0 | 50 |  | 48 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 30 | 30 | 30 | 30 |  | 70 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 27 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 75 | 87 | 80 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 246 | 284 | 265 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 65 | 64 | 64 | 64 |  | 36 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 72 | 72 | 72 | 72 |  | 44 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1059 | 1209 | 1120 | 1251 | 411 | 713
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 206 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 345 | 330 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 335 | 330 | 360 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 33 | 33 | 33 |  | 12 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 52 | 53 | 50 | 50
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 189 | 189 | 180 | 190
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 123 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 49 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 136 | 135 | 136 |  | 27 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 160 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 94 | 94 | 94 |  | 19 | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 116 | 115 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1944 | 2290 | 2186 | 2490 | 300 | 77
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 81 | 105 | 120 | 130 | 72 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 176 | 200 | 180 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 83 | 93 | 110 | 110 |  | 5 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 434 | 443 | 504.6 | 483 | 72 | 13
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 33 | 33 | 33 |  | 18 | Engine problem
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 30 | 30 | 30 |  | 20 | Engine problem
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 32 |  | 33 | Unit-8 Under maint.
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 22 | 25 | 25 | 25
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Machine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 396 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1656 | 1644 | 1665 | 1698 | 0 | 748
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 888 | 859 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 78 | 20 | 80 |  | 35 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 37 |  | 17 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 120 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 225 | 180 | 180 | 230 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 44 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 64 | 92 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 70 | 90 |  | 15 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 48 | 0 | 100 | 0
|  | Khulna 330 MW CCPP |  | HSD | BPDB | 330 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1389 | 1382 | 1553 | 1830 | 230 | 128
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 |  |  | Rampal Transformar O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 30 | 20 | 29 |  | 11 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 81 | 85 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 620 | 622 | 622 |  | 622 | Unit-2 S/D
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 224 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 763 | 992 | 998 | 1007 | 109 | 633
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 35 |  | 36 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 8 | 8 |  | 42 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 209 | 176 | 180 | 210
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 188 | 200 | 220
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 406 | 414 | 414 | 414 |  |  | FGMO
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 40 | 100 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1052 | 1271 | 1183 | 1539 | 433 | 141
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 96 | 96 | 96 |  | 17 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 108 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 284 | 379 | 387 | 404 | 269 | 24
|  | Total |  |  |  |  | 22348 | 21396 | 11933 | 13696 | 13648.6 | 14960 | 2115 | 3752
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11518.4903 | 13220.25 | 13174.4965 | 14440.3432
| A. |  | 2022-06-26 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13696 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10295 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13696 | MW
| 3 | Day peak Generation : |  |  | 11933 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13220.25 | MW
| 4 | Evening peak Generation : |  |  | 13696 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 293.1145 | MKWHr | By Solar | 1.3857 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 157.3392 | MKWHr |  | By Oil: | 89.4035 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.4275 | MKWHr |  | By Hydro: | 2.888 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2115 | MW | Dhaka | 4868 | 4868 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3752 | MW | Chittagong | 1376.25 | 1376.25 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5867 | MW | Khulna | 1583 | 1583 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1141.65 | MMCFD |  |  | Rajshahi | 1411.2 | 1411.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 178962546.142 | ii) Oil : | Taka | 1220984989.33 | Comilla | 1226 | 1226 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 141075251 | Total | Taka | 1541022786.472 | Mymensingh | 1018 | 1018 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.6805 | MKWHr. | Sylhet | 474 | 474 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -444 | MW (E to W) at | 21:00 | hrs | Barisal | 391.8 | 391.8 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -536 | MW at | 22:00 | hrs | Rangpur | 872 | 872 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 13220.25 | 13220.25 |  | 0
| B. |  | 2022-06-27 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14960 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1060 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 297.4804 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10574 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2473 | MKWHr. | ii) HVDC Flow at Peak Time |  | 859 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4234 | MKWHr. | iii) Maximum HVDC Flow : |  | 889 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.94 |  | (b) Today: | 89.04 |  | (c) Rule Curve: |  | 82.38
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. |  | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 255 | 70 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 88 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 30 | 50 | 43 | 22 | 37 | 0 | 0 | 0 | 315 | 305 | 214 | 189 | 135 | 28 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 18 | 146 | 122 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 25 | 10 | 275 | 16 | 11 | 0 | 276 | 53 | 50 | 200 | 50 | 80 | 0 | 90 | 120 | 140 | 401 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 55 | 50 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 0 | 0 |  | 874 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 39 | 0 | 0 | 87 | 30 | 16 | 0 | 100 | 0 | 34 | 35 | 0 | 0 | 25 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 216 | 0 | 423 | 93 | 0 | 113 | 0 | 69 | 0 | 0 | 113 | 620 | 224 | 0 | 0 | 0 | 0 | 72 |  |  | 8659 | 4026 | 12685 | 4325 | 874 | 2382 | 153 | 3527 | 795 | 123 | 0 | 360 | 146 | 0 | 0 | 88.89
2:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 285 | 70 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 88 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 30 | 88 | 43 | 22 | 39 | 0 | 0 | 0 | 320 | 305 | 211 | 189 | 137 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 142 | 122 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 24 | 10 | 270 | 16 | 11 | 0 | 273 | 0 | 0 | 200 | 0 | 79 | 0 | 90 | 120 | 138 | 402 | 115 | 105 | 105 | 0 | 300 | 54 | 103 | 0 | 45 | 50 | 401 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 21 | 0 |  | 888 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 9 | 0 | 0 | 86 | 30 | 0 | 0 | 90 | 0 | 34 | 35 | 0 | 0 | 25 | 5 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 212 | 0 | 391 | 93 | 0 | 113 | 0 | 69 | 0 | 0 | 113 | 560 | 226 | 0 | 0 | 0 | 0 | 72 |  |  | 8520 | 3884 | 12404 | 4319 | 888 | 2379 | 0 | 3548 | 735 | 123 | 0 | 270 | 142 | 0 | 0 | 88.9
3:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 255 | 70 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 50 | 0 | 89 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 86 | 39 | 22 | 39 | 0 | 0 | 0 | 320 | 305 | 211 | 187 | 136 | 28 | 53 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 138 | 133 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 78 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 0 | 276 | 0 | 0 | 200 | 0 | 80 | 0 | 90 | 120 | 137 | 402 | 115 | 105 | 105 | 0 | 230 | 54 | 110 | 0 | 37 | 50 | 400 | 104 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 887 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 0 | 0 | 80 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 167 | 0 | 364 | 93 | 0 | 113 | 0 | 69 | 0 | 0 | 113 | 550 | 227 | 0 | 0 | 0 | 0 | 52 |  |  | 8399 | 3644 | 12043 | 4277 | 887 | 2326 | 0 | 3464 | 725 | 124 | 0 | 102 | 138 | 0 | 0 | 88.91
4:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 280 | 70 | 0 | 55 | 337 | 0 | 0 | 100 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 33 | 0 | 90 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 43 | 22 | 39 | 0 | 0 | 0 | 320 | 305 | 212 | 189 | 136 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 134 | 133 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 32 | 75 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 0 | 274 | 0 | 0 | 195 | 0 | 80 | 0 | 90 | 120 | 137 | 401 | 115 | 105 | 105 | 0 | 190 | 54 | 110 | 0 | 37 | 50 | 400 | 95 | 0 | 162 | 0 | 0 | 35 | 0 | 116 | 55 | 0 |  | 889 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 163 | 0 | 368 | 93 | 0 | 113 | 0 | 69 | 0 | 0 | 113 | 550 | 227 | 0 | 0 | 0 | 0 | 52 |  |  | 8071 | 3615 | 11686 | 4261 | 889 | 2354 | 0 | 3150 | 725 | 125 | 0 | 48 | 134 | 0 | 0 | 88.92
5:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 450 | 250 | 70 | 0 | 55 | 338 | 0 | 0 | 100 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 16 | 0 | 90 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 315 | 305 | 213 | 187 | 136 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 130 | 140 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 32 | 75 | 0 | 120 | 0 | 24 | 10 | 280 | 16 | 11 | 0 | 274 | 0 | 0 | 200 | 0 | 80 | 0 | 90 | 120 | 137 | 401 | 24 | 105 | 105 | 0 | 190 | 54 | 110 | 0 | 38 | 50 | 400 | 92 | 0 | 160 | 0 | 0 | 35 | 0 | 116 | 55 | 0 |  | 888 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 163 | 0 | 346 | 93 | 0 | 95 | 0 | 69 | 0 | 0 | 113 | 510 | 225 | 0 | 0 | 0 | 0 | 52 |  |  | 7863 | 3537 | 11400 | 4268 | 888 | 2296 | 0 | 2992 | 685 | 125 | 0 | 16 | 130 | 0 | 0 | 88.93
6:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 408 | 0 |  | 0 | 400 | 275 | 71 | 0 | 55 | 300 | 0 | 0 | 72 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 8 | 0 | 89 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 44 | 22 | 39 | 0 | 0 | 0 | 315 | 305 | 212 | 187 | 136 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 118 | 133 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 75 | 0 | 120 | 0 | 25 | 10 | 265 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 79 | 1 | 50 | 120 | 100 | 364 | 24 | 70 | 102 | 0 | 80 | 54 | 102 | 0 | 38 | 50 | 360 | 100 | 3 | 108 | 0 | 0 | 35 | 1 | 116 | 55 | 0 |  | 887 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 160 | 0 | 356 | 35 | 0 | 50 | 0 | 69 | 0 | 0 | 70 | 470 | 196 | 0 | 0 | 0 | 6 | 34 |  |  | 7120 | 3300 | 10420 | 4127 | 887 | 2236 | 0 | 2256 | 645 | 124 | 0 | 16 | 118 | 11 | 0 | 88.94
7:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 400 | 285 | 72 | 0 | 55 | 300 | 0 | 0 | 24 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 29 | 33 | 0 | 9 | 0 | 89 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 44 | 22 | 25 | 0 | 0 | 0 | 320 | 305 | 212 | 189 | 136 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 114 | 122 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 75 | 0 | 120 | 0 | 24 | 10 | 285 | 16 | 11 | 0 | 63 | 0 | 0 | 130 | 0 | 79 | 5 | 70 | 119 | 100 | 370 | 8 | 70 | 90 | 1 | 80 | 54 | 110 | 0 | 38 | 50 | 360 | 104 | 8 | 72 | 0 | 0 | 35 | 6 | 112 | 55 | 0 |  | 889 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 159 | 0 | 378 | 17 | 0 | 50 | 0 | 69 | 0 | 0 | 70 | 460 | 201 | 0 | 0 | 0 | 27 | 34 |  |  | 7024 | 3271 | 10295 | 4080 | 889 | 2277 | 0 | 2113 | 635 | 124 | 0 | 16 | 114 | 47 | 0 | 88.95
8:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 400 | 300 | 72 | 0 | 55 | 300 | 0 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 29 | 33 | 0 | 24 | 0 | 89 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 0 | 44 | 22 | 4 | 0 | 0 | 0 | 360 | 305 | 210 | 189 | 138 | 28 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 120 | 110 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 75 | 0 | 120 | 0 | 24 | 10 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 181 | 0 | 79 | 12 | 90 | 100 | 100 | 387 | 19 | 70 | 87 | 2 | 80 | 54 | 110 | 0 | 39 | 50 | 360 | 104 | 25 | 72 | 0 | 0 | 35 | 15 | 116 | 41 | 0 |  | 888 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 158 | 0 | 391 | 17 | 0 | 50 | 0 | 70 | 0 | 1 | 70 | 450 | 204 | 0 | 0 | 2 | 54 | 34 |  |  | 7138 | 3300 | 10438 | 4119 | 888 | 2281 | 0 | 2154 | 625 | 124 | 0 | 16 | 120 | 111 | 0 | 88.96
9:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 409 | 0 |  | 0 | 420 | 255 | 73 | 0 | 55 | 335 | 0 | 0 | 30 | 50 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 0 | 33 | 0 | 89 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 30 | 0 | 43 | 22 | 3 | 0 | 0 | 0 | 320 | 305 | 211 | 187 | 138 | 28 | 53 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 16 | 17 | 126 | 106 | 0 | 21 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 75 | 0 | 120 | 0 | 24 | 10 | 300 | 16 | 11 | 0 | 55 | 0 | 0 | 189 | 0 | 79 | 16 | 90 | 100 | 107 | 403 | 83 | 70 | 100 | 4 | 80 | 54 | 110 | 0 | 39 | 50 | 400 | 104 | 47 | 110 | 0 | 0 | 35 | 25 | 116 | 42 | 0 |  | 889 | 0 | 410 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 185 | 0 | 378 | 27 | 0 | 62 | 0 | 69 | 0 | 1 | 100 | 430 | 222 | 0 | 0 | 3 | 84 | 34 |  |  | 7421 | 3426 | 10847 | 4216 | 889 | 2267 | 0 | 2422 | 605 | 124 | 0 | 16 | 126 | 182 | 0 | 88.97
10:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 411 | 0 |  | 0 | 420 | 255 | 65 | 0 | 55 | 331 | 0 | 0 | 83 | 85 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 25 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 10 | 44 | 22 | 2 | 0 | 0 | 0 | 315 | 305 | 210 | 189 | 137 | 28 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 24 | 17 | 136 | 95 | 0 | 21 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 78 | 0 | 120 | 0 | 21 | 10 | 275 | 16 | 11 | 0 | 252 | 0 | 0 | 188 | 0 | 77 | 18 | 76 | 100 | 118 | 403 | 83 | 105 | 105 | 4 | 100 | 54 | 110 | 0 | 38 | 50 | 400 | 104 | 49 | 162 | 52 | 0 | 35 | 29 | 116 | 55 | 0 |  | 888 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 179 | 0 | 380 | 70 | 0 | 94 | 0 | 65 | 0 | 1 | 113 | 400 | 223 | 0 | 0 | 4 | 83 | 34 |  |  | 7829 | 3475 | 11304 | 4185 | 888 | 2254 | 0 | 2936 | 575 | 124 | 0 | 16 | 136 | 190 | 0 | 88.97
11:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 410 | 0 |  | 0 | 450 | 295 | 64 | 0 | 55 | 330 | 0 | 0 | 91 | 85 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 25 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 49 | 43 | 22 | 2 | 0 | 0 | 0 | 345 | 330 | 209 | 189 | 136 | 28 | 49 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 24 | 18 | 136 | 95 | 0 | 21 | 2 | 44 | 42 | 34 | 30 | 110 | 0 | 29 | 78 | 0 | 120 | 0 | 21 | 10 | 290 | 16 | 11 | 0 | 271 | 0 | 0 | 177 | 0 | 80 | 20 | 76 | 100 | 123 | 404 | 83 | 105 | 105 | 4 | 155 | 54 | 110 | 0 | 38 | 56 | 400 | 104 | 50 | 162 | 72 | 0 | 35 | 36 | 116 | 0 | 0 |  | 888 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 180 | 0 | 411 | 70 | 0 | 94 | 0 | 68 | 0 | 4 | 113 | 400 | 221 | 0 | 0 | 5 | 44 | 34 |  |  | 8067 | 3453 | 11520 | 4218 | 888 | 2365 | 0 | 3033 | 575 | 124 | 0 | 16 | 136 | 165 | 0 | 88.97
12:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 405 | 0 |  | 0 | 450 | 270 | 64 | 0 | 40 | 330 | 0 | 0 | 91 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 43 | 22 | 3 | 0 | 0 | 0 | 340 | 320 | 205 | 189 | 136 | 27 | 52 | 0 | 51 | 0 | 41 | 0 | 21 | 8 | 14 | 19 | 142 | 81 | 0 | 21 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 22 | 10 | 310 | 16 | 11 | 0 | 274 | 78 | 25 | 176 | 40 | 80 | 20 | 76 | 100 | 125 | 401 | 83 | 90 | 105 | 6 | 246 | 54 | 110 | 0 | 38 | 65 | 396 | 104 | 48 | 162 | 72 | 0 | 0 | 35 | 116 | 42 | 0 |  | 888 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 195 | 0 | 406 | 64 | 0 | 94 | 0 | 70 | 0 | 5 | 113 | 440 | 221 | 0 | 0 | 5 | 48 | 34 |  |  | 8445 | 3488 | 11933 | 4150 | 888 | 2358 | 143 | 3171 | 615 | 124 | 0 | 174 | 142 | 168 | 0 | 88.98
13:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 405 | 0 |  | 0 | 450 | 285 | 64 | 0 | 40 | 333 | 0 | 0 | 91 | 94 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 9 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 43 | 22 | 4 | 0 | 0 | 0 | 315 | 305 | 207 | 187 | 136 | 27 | 51 | 0 | 51 | 0 | 49 | 0 | 21 | 8 | 8 | 21 | 142 | 70 | 0 | 21 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 23 | 10 | 285 | 16 | 11 | 50 | 274 | 120 | 85 | 176 | 80 | 79 | 19 | 76 | 100 | 128 | 402 | 83 | 105 | 105 | 1 | 262 | 54 | 110 | 0 | 38 | 65 | 400 | 104 | 0 | 162 | 72 | 0 | 19 | 34 | 116 | 55 | 0 |  | 876 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 22 | 200 | 0 | 377 | 54 | 0 | 94 | 0 | 68 | 0 | 6 | 113 | 460 | 221 | 0 | 0 | 5 | 61 | 34 |  |  | 8579 | 3484 | 12063 | 4083 | 876 | 2322 | 357 | 3210 | 635 | 124 | 0 | 186 | 142 | 128 | 0 | 88.98
14:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 411 | 0 |  | 0 | 450 | 295 | 64 | 0 | 55 | 330 | 0 | 0 | 95 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 13 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 11 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 42 | 22 | 7 | 0 | 0 | 0 | 320 | 305 | 205 | 189 | 138 | 27 | 50 | 0 | 51 | 0 | 49 | 0 | 21 | 8 | 16 | 21 | 150 | 70 | 0 | 21 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 81 | 0 | 120 | 0 | 23 | 10 | 280 | 16 | 11 | 20 | 273 | 57 | 85 | 186 | 80 | 79 | 17 | 76 | 100 | 132 | 402 | 83 | 105 | 105 | 5 | 282 | 54 | 110 | 0 | 37 | 65 | 400 | 104 | 22 | 162 | 72 | 0 | 35 | 9 | 116 | 55 | 0 |  | 877 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 22 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 16 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 10 | 208 | 0 | 418 | 64 | 0 | 94 | 0 | 70 | 0 | 6 | 113 | 450 | 210 | 0 | 0 | 0 | 30 | 34 |  |  | 8611 | 3477 | 12088 | 4096 | 877 | 2361 | 252 | 3310 | 625 | 124 | 0 | 202 | 150 | 91 | 0 | 88.98
15:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 404 | 0 |  | 0 | 450 | 286 | 64 | 0 | 55 | 330 | 0 | 0 | 99 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 42 | 22 | 3 | 0 | 0 | 0 | 325 | 315 | 204 | 189 | 136 | 27 | 49 | 0 | 51 | 0 | 40 | 0 | 21 | 8 | 25 | 20 | 152 | 71 | 0 | 21 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 23 | 10 | 300 | 16 | 11 | 70 | 275 | 255 | 85 | 167 | 80 | 79 | 14 | 76 | 100 | 128 | 402 | 73 | 105 | 105 | 1 | 283 | 54 | 110 | 0 | 37 | 65 | 398 | 104 | 17 | 162 | 72 | 0 | 35 | 9 | 115 | 55 | 0 |  | 875 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 24 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 39 | 208 | 0 | 414 | 73 | 8 | 94 | 0 | 70 | 0 | 5 | 113 | 470 | 218 | 0 | 0 | 4 | 71 | 34 |  |  | 8838 | 3548 | 12386 | 4074 | 875 | 2372 | 537 | 3298 | 645 | 124 | 0 | 187 | 152 | 122 | 0 | 88.99
16:00 | 0 | 0 | 0 | 180 | 0 | 83 | 0 | 406 | 0 |  | 0 | 450 | 262 | 64 | 0 | 55 | 331 | 0 | 0 | 98 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 86 | 35 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 24 | 22 | 3 | 0 | 0 | 0 | 315 | 305 | 206 | 187 | 136 | 28 | 50 | 0 | 51 | 0 | 40 | 0 | 21 | 11 | 33 | 20 | 154 | 72 | 0 | 21 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 23 | 10 | 290 | 16 | 11 | 100 | 275 | 140 | 85 | 186 | 80 | 79 | 9 | 76 | 100 | 127 | 403 | 73 | 105 | 87 | 2 | 283 | 54 | 110 | 0 | 48 | 65 | 400 | 104 | 10 | 162 | 72 | 0 | 35 | 16 | 116 | 55 | 0 |  | 874 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 19 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 10 | 201 | 0 | 414 | 74 | 10 | 94 | 0 | 70 | 0 | 4 | 113 | 490 | 217 | 0 | 0 | 3 | 57 | 23 |  |  | 8711 | 3496 | 12207 | 4051 | 874 | 2332 | 425 | 3282 | 665 | 121 | 0 | 201 | 154 | 102 | 0 | 88.99
17:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 408 | 58 |  | 0 | 450 | 265 | 64 | 0 | 55 | 331 | 0 | 0 | 98 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 86 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 24 | 22 | 8 | 0 | 0 | 0 | 315 | 305 | 206 | 187 | 136 | 27 | 49 | 0 | 51 | 0 | 40 | 0 | 21 | 11 | 33 | 20 | 152 | 73 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 23 | 10 | 280 | 16 | 11 | 0 | 275 | 0 | 50 | 200 | 25 | 79 | 4 | 76 | 128 | 128 | 403 | 84 | 105 | 87 | 2 | 283 | 54 | 110 | 0 | 94 | 64 | 400 | 104 | 11 | 162 | 72 | 0 | 35 | 10 | 116 | 55 | 0 |  | 874 | 0 | 270 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 24 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 193 | 0 | 414 | 74 | 0 | 94 | 0 | 80 | 0 | 2 | 113 | 450 | 212 | 0 | 0 | 0 | 37 | 35 |  |  | 8572 | 3435 | 12007 | 4033 | 874 | 2389 | 75 | 3431 | 625 | 121 | 0 | 241 | 152 | 66 | 0 | 88.99
18:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 411 | 57 |  | 0 | 400 | 280 | 71 | 0 | 55 | 280 | 0 | 0 | 65 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 10 | 33 | 0 | 41 | 0 | 88 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 80 | 27 | 22 | 12 | 0 | 0 | 0 | 280 | 275 | 182 | 140 | 136 | 27 | 48 | 0 | 51 | 0 | 46 | 0 | 21 | 11 | 33 | 20 | 140 | 88 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 86 | 0 | 120 | 0 | 25 | 10 | 270 | 16 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 128 | 1 | 90 | 200 | 127 | 371 | 95 | 105 | 87 | 0 | 190 | 54 | 110 | 0 | 94 | 64 | 360 | 104 | 0 | 108 | 72 | 0 | 35 | 2 | 116 | 55 | 0 |  | 875 | 0 | 250 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 24 | 0 | 38 | 21 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 180 | 0 | 370 | 90 | 0 | 50 | 0 | 89 | 0 | 1 | 70 | 420 | 163 | 0 | 0 | 0 | 6 | 80 |  |  | 8123 | 3259 | 11382 | 3781 | 875 | 2177 | 0 | 3394 | 596 | 123 | 0 | 286 | 140 | 10 | 0 | 89
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 411 | 131 |  | 0 | 450 | 295 | 75 | 0 | 55 | 331 | 0 | 0 | 65 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 10 | 33 | 0 | 41 | 0 | 88 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 4 | 34 | 30 | 84 | 42 | 22 | 16 | 0 | 0 | 0 | 295 | 310 | 206 | 187 | 136 | 32 | 50 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 33 | 20 | 162 | 106 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 30 | 86 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 20 | 275 | 29 | 25 | 200 | 26 | 127 | 0 | 90 | 200 | 132 | 402 | 103 | 105 | 97 | 0 | 190 | 54 | 110 | 0 | 94 | 64 | 390 | 104 | 0 | 119 | 72 | 0 | 26 | 0 | 116 | 55 | 0 |  | 875 | 0 | 240 | 0 | 73 | 0 | 0 | 0 | 36 | 0 | 32 | 86 | 26 | 16 | 0 | 0 | 0 | 34 | 28 | 85 | 0 | 0 | 24 | 0 | 38 | 21 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 2 | 160 | 0 | 380 | 92 | 3 | 50 | 15 | 95 | 0 | 0 | 90 | 420 | 215 | 0 | 4 | 0 | 0 | 109 |  |  | 8768 | 3596 | 12364 | 3937 | 875 | 2486 | 105 | 3600 | 595 | 123 | 0 | 481 | 162 | 0 | 0 | 89.01
19:30 | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 409 | 235 |  | 0 | 450 | 280 | 80 | 0 | 55 | 335 | 0 | 0 | 80 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 15 | 33 | 0 | 41 | 0 | 88 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 25 | 34 | 30 | 87 | 43 | 22 | 12 | 0 | 0 | 0 | 310 | 305 | 209 | 187 | 136 | 32 | 50 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 9 | 160 | 108 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 86 | 0 | 120 | 0 | 25 | 10 | 260 | 16 | 11 | 190 | 275 | 300 | 85 | 200 | 81 | 133 | 0 | 90 | 200 | 132 | 402 | 103 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 95 | 64 | 386 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 116 | 55 | 0 |  | 875 | 0 | 240 | 0 | 66 | 0 | 0 | 0 | 42 | 0 | 40 | 86 | 28 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 24 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 100 | 190 | 0 | 414 | 93 | 90 | 70 | 15 | 95 | 0 | 0 | 113 | 560 | 223 | 0 | 17 | 0 | 0 | 109 |  |  | 9547 | 4093 | 13640 | 3995 | 875 | 2596 | 846 | 3796 | 735 | 123 | 0 | 514 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 407 | 292 |  | 0 | 450 | 267 | 78 | 0 | 55 | 335 | 0 | 0 | 85 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 20 | 55 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 90 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 30 | 87 | 43 | 22 | 9 | 0 | 0 | 0 | 310 | 305 | 209 | 184 | 136 | 32 | 52 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 162 | 108 | 0 | 21 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 31 | 86 | 0 | 120 | 0 | 25 | 10 | 280 | 16 | 11 | 170 | 275 | 186 | 85 | 200 | 80 | 134 | 0 | 90 | 200 | 127 | 402 | 103 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 94 | 64 | 372 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 240 | 0 | 73 | 0 | 0 | 0 | 37 | 0 | 40 | 84 | 28 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 60 | 185 | 0 | 414 | 92 | 110 | 85 | 15 | 96 | 0 | 0 | 113 | 570 | 175 | 0 | 17 | 0 | 0 | 108 |  |  | 9531 | 4037 | 13568 | 3990 | 860 | 2609 | 691 | 3835 | 745 | 125 | 0 | 551 | 162 | 0 | 0 | 89
21:00 | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 409 | 312 |  | 0 | 450 | 280 | 79 | 0 | 55 | 330 | 0 | 0 | 91 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 0 | 41 | 0 | 90 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 30 | 87 | 37 | 22 | 27 | 0 | 0 | 0 | 345 | 335 | 206 | 189 | 136 | 33 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 160 | 105 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 10 | 290 | 16 | 11 | 80 | 275 | 255 | 85 | 200 | 80 | 134 | 0 | 90 | 200 | 123 | 404 | 93 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 94 | 64 | 395 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 115 | 55 | 0 |  | 859 | 0 | 225 | 0 | 78 | 0 | 0 | 0 | 37 | 0 | 32 | 85 | 30 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 44 | 188 | 0 | 414 | 92 | 40 | 94 | 15 | 96 | 0 | 0 | 113 | 620 | 224 | 0 | 17 | 0 | 0 | 108 |  |  | 9672 | 4024 | 13696 | 4060 | 859 | 2725 | 584 | 3845 | 795 | 125 | 0 | 543 | 160 | 0 | 0 | 89.01
22:00 | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 412 | 312 |  | 0 | 450 | 275 | 79 | 0 | 55 | 332 | 0 | 0 | 88 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 0 | 41 | 0 | 90 | 35 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 30 | 87 | 37 | 22 | 37 | 0 | 0 | 0 | 330 | 325 | 205 | 190 | 135 | 33 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 158 | 106 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 10 | 300 | 16 | 11 | 80 | 275 | 255 | 85 | 200 | 80 | 132 | 0 | 90 | 200 | 138 | 404 | 103 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 94 | 64 | 400 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 109 | 55 | 0 |  | 860 | 0 | 220 | 0 | 65 | 10 | 0 | 0 | 37 | 0 | 32 | 85 | 30 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 60 | 174 | 0 | 414 | 93 | 40 | 94 | 0 | 96 | 0 | 0 | 113 | 622 | 224 | 0 | 17 | 0 | 0 | 108 |  |  | 9692 | 4002 | 13694 | 4021 | 860 | 2741 | 600 | 3839 | 797 | 125 | 10 | 543 | 158 | 0 | 0 | 89.01
23:00 | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 408 | 330 |  | 0 | 450 | 295 | 71 | 0 | 55 | 330 | 0 | 0 | 83 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 0 | 42 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 30 | 87 | 36 | 22 | 38 | 0 | 0 | 0 | 325 | 320 | 207 | 190 | 136 | 33 | 52 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 162 | 105 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 31 | 84 | 0 | 120 | 0 | 25 | 10 | 320 | 16 | 11 | 190 | 275 | 301 | 85 | 187 | 80 | 132 | 0 | 90 | 200 | 142 | 402 | 103 | 105 | 105 | 0 | 215 | 54 | 110 | 0 | 94 | 64 | 400 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 115 | 55 | 0 |  | 861 | 0 | 220 | 0 | 65 | 10 | 0 | 0 | 37 | 0 | 32 | 85 | 31 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 71 | 167 | 0 | 414 | 93 | 51 | 94 | 0 | 96 | 0 | 0 | 106 | 622 | 224 | 0 | 17 | 0 | 0 | 90 |  |  | 9681 | 3986 | 13667 | 3993 | 861 | 2800 | 778 | 3739 | 797 | 35 | 10 | 492 | 162 | 0 | 0 | 89.01
24:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 410 | 330 |  | 0 | 450 | 295 | 75 | 0 | 55 | 326 | 0 | 0 | 91 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 0 | 42 | 0 | 88 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 30 | 88 | 37 | 22 | 39 | 0 | 0 | 0 | 285 | 257 | 105 | 68 | 137 | 33 | 53 | 0 | 51 | 0 | 41 | 0 | 21 | 11 | 33 | 21 | 160 | 105 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 10 | 320 | 16 | 11 | 198 | 275 | 305 | 85 | 185 | 80 | 85 | 0 | 90 | 170 | 107 | 404 | 103 | 105 | 105 | 0 | 215 | 54 | 110 | 0 | 52 | 64 | 396 | 102 | 0 | 162 | 72 | 0 | 35 | 0 | 116 | 55 | 0 |  | 859 | 0 | 215 | 0 | 22 | 15 | 0 | 0 | 37 | 0 | 32 | 84 | 31 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 100 | 167 | 0 | 414 | 93 | 120 | 94 | 0 | 70 | 0 | 0 | 113 | 620 | 224 | 0 | 17 | 0 | 0 | 72 |  |  | 9287 | 3996 | 13283 | 3767 | 859 | 2676 | 888 | 3516 | 795 | 123 | 15 | 484 | 160 | 0 | 0 | 89.01
KWH | 0 | 0 | 0 | 4384800 | 0 | 1994727 | 0 | 9932800 | 1660000 |  | 0 | 9965500 | 6715665 | 1686720 | 0 | 1302848 | 7844676 | 0 | 0 | 1976976 | 1840464 | 2349120 | 0 | 0 | 0 | 0 | 1269000 | 1251700 | 1095478 | 500004 | 600000 | 532440 | 774500 | 0 | 902400 | 0 | 2073965 | 814000 | 0 | 0 | 302961 | 0 | 0 | 0 | 0 |  | 590160 | 153696 | 280743 | 756240 | 1375680 | 973440 | 515808 | 491040 | 0 | 0 | 0 | 8049600 | 7547000 | 4980000 | 4482909 | 3251910 | 686160 | 1251840 | 0 | 1155785 | 0 | 633328 | 0 | 495540 | 226260 | 701800 | 455820 | 3423360 | 2403840 | 0 | 447444 | 13400 | 1032000 | 974560 | 810000 | 799848 | 2657127 | 0 | 733536 | 1929600 | 0 | 2892530 | 0 | 567360 | 240840 | 7073500 | 372816 | 264000 | 903360 | 5823598 | 2077647 | 926880 | 4459200 | 877469 | 2243232 | 147960 | 1973760 | 3287520 | 3029309 | 9522000 | 2001600 | 2391600 | 2437999 | 36361 | 5251527 | 1368926 | 2666325 | 0 | 1364160 | 1383360 | 9382000 | 2610240 | 290340 | 3610080 | 1358673 | 0 | 835560 | 206044 | 2787840 | 1195920 | 0 |  | 21247272 | 0 | 7872192 | 0 | 632640 | 12050 | 0 | 0 | 260640 | 3713 | 243000 | 2050435 | 552848 | 111840 | 0 | 489000 | 0 | 267568 | 333686 | 505520 | 0 | 101184 | 186661 | 0 | 332800 | 493440 | 0 | 222426 | 0 | 0 | 4286700 | 0 | 0 | 0 | 0 | 5009118 | 0 | 0 | 500160 | 4657582 | 0 | 9529527 | 1766400 | 422405 | 2151936 | 45072 | 1814428 | 0 | 37277 | 2541120 | 13140800 | 5163082 | 0 | 112800 | 35820 | 618480 | 1451136 |  |  | 203911754 | 89202758 | 293114512 | 99804597 | 21247272 | 57534638 | 5707921 | 78376052 | 17427500 | 2887965 | 12050 | 5307475 | 3423360 | 1385682 | 0
Fuel Cost | 0 | 0 | 0 | 6533352 | 0 | 2652986.91 | 0 | 10429440 | 1792800 |  | 0 | 10862395 | 7454388.15 | 18857529.6 | 0 | 17262736 | 8786037.12 | 0 | 0 | 28903389.12 | 25895328.48 | 38079235.2 | 0 | 0 | 0 | 0 | 16141680 | 16897950 | 14690359.98 | 375003 | 450000 | 0 | 0 | 0 | 15349824 | 0 | 559970.55 | 219780 | 0 | 0 | 4953412.35 | 0 | 0 | 0 | 0 |  | 7701588 | 2563649.28 | 4778245.86 | 10216802.4 | 17443622.4 | 11262700.8 | 655076.16 | 1635163.2 | 0 | 0 | 0 | 8935056 | 8226230 | 5776800 | 5782952.61 | 3967330.2 | 775360.8 | 1865241.6 | 0 | 1930160.95 | 0 | 10937574.56 | 0 | 678889.8 | 169695 | 1228150 | 341865 | 24579724.8 | 2620185.6 | 0 | 608523.84 | 213596 | 1413840 | 1286419.2 | 1409400 | 1383737.04 | 3055696.05 | 0 | 1423059.84 | 4399488 | 0 | 2921455.3 | 0 | 845366.4 | 476863.2 | 7073500 | 279612 | 200640 | 18934425.6 | 79492112.7 | 43547481.12 | 19158609.6 | 60110016 | 18137284.23 | 31068763.2 | 1729652.4 | 20369203.2 | 44907523.2 | 40198930.43 | 8760240 | 24339456 | 34582536 | 30840687.35 | 0 | 61652926.98 | 14907604.14 | 28343034.75 | 0 | 17584022.4 | 16295980.8 | 8631440 | 33802608 | 4195413 | 45811915.2 | 15461698.74 | 0 | 10912413.6 | 2462225.8 | 41733964.8 | 15750266.4 | 0 |  | 63741816 | 0 | 8816855.04 | 0 | 6585782.4 | 198825 | 0 | 0 | 4694126.4 | 66834 | 3491910 | 2296487.2 | 1072525.12 | 1219056 | 0 | 978000 | 0 | 4487115.36 | 5836168.14 | 7906332.8 | 0 | 1675607.04 | 3156437.51 | 0 | 5614336 | 1021420.8 | 0 | 168376.482 | 0 | 0 | 22676643 | 0 | 0 | 0 | 0 | 6411671.04 | 0 | 0 | 10493356.8 | 5402795.12 | 0 | 9434231.73 | 23740416 | 8857832.85 | 25457402.88 | 651290.4 | 23043235.6 | 0 | 411910.85 | 30849196.8 | 118398608 | 5266343.64 | 0 | 834720 | 405124.2 | 7254770.4 | 22245914.88 |  |  | 1201933294.99 | 444863475.482 | 1646796770.472 | 109547885.742 | 63741816 | 69414660.4 | 119128990.2 | 1013537119.02 | 141075251 | 779750.55 | 198825 | 88120055.11 | 24579724.8 | 16672692.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 405 | 0 |  | 0 | 450 | 270 | 64 | 0 | 40 | 330 | 0 | 0 | 91 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 0 | 41 | 0 | 89 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 43 | 22 | 3 | 0 | 0 | 0 | 340 | 320 | 205 | 189 | 136 | 27 | 52 | 0 | 51 | 0 | 41 | 0 | 21 | 8 | 14 | 19 | 142 | 81 | 0 | 21 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 81 | 0 | 120 | 0 | 22 | 10 | 310 | 16 | 11 | 0 | 274 | 78 | 25 | 176 | 40 | 80 | 20 | 76 | 100 | 125 | 401 | 83 | 90 | 105 | 6 | 246 | 54 | 110 | 0 | 38 | 65 | 396 | 104 | 48 | 162 | 72 | 0 | 0 | 35 | 116 | 42 | 0 |  | 888 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 195 | 0 | 406 | 64 | 0 | 94 | 0 | 70 | 0 | 5 | 113 | 440 | 221 | 0 | 0 | 5 | 48 | 34 |  |  | 11933 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 409 | 312 | 0 | 0 | 450 | 280 | 79 | 0 | 55 | 330 | 0 | 0 | 91 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 0 | 41 | 0 | 90 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 30 | 87 | 37 | 22 | 27 | 0 | 0 | 0 | 345 | 335 | 206 | 189 | 136 | 33 | 53 | 0 | 51 | 0 | 49 | 0 | 21 | 11 | 33 | 21 | 160 | 105 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 10 | 290 | 16 | 11 | 80 | 275 | 255 | 85 | 200 | 80 | 134 | 0 | 90 | 200 | 123 | 404 | 93 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 94 | 64 | 395 | 104 | 0 | 162 | 72 | 0 | 35 | 0 | 115 | 55 | 0 |  | 859 | 0 | 225 | 0 | 78 | 0 | 0 | 0 | 37 | 0 | 32 | 85 | 30 | 16 | 0 | 0 | 0 | 34 | 28 | 90 | 0 | 8 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 44 | 188 | 0 | 414 | 92 | 40 | 94 | 15 | 96 | 0 | 0 | 113 | 620 | 224 | 0 | 17 | 0 | 0 | 108 |  |  | 13696 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 91 | 0 | 412 | 330 | 0 | 0 | 450 | 305 | 80 | 0 | 55 | 335 | 0 | 0 | 100 | 95 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 41 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 30 | 90 | 43 | 22 | 20 | 0 | 0 | 0 | 360 | 360 | 215 | 190 | 136 | 33 | 50 | 0 | 51 | 0 | 50 | 0 | 21 | 11 | 33 | 21 | 165 | 130 | 0 | 21 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 32 | 84 | 0 | 120 | 0 | 25 | 10 | 341 | 16 | 11 | 200 | 280 | 300 | 100 | 200 | 100 | 134 | 0 | 90 | 200 | 150 | 400 | 110 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 64 | 400 | 104 | 0 | 162 | 72 | 0 | 35 |  | 115 | 55 |  |  | 930 | 0 | 180 | 0 | 80 | 220 | 0 | 0 | 37 | 60 | 40 | 85 | 29 | 16 | 0 | 0 | 0 | 34 | 35 | 90 | 0 | 8 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 210 | 0 | 0 | 100 | 220 | 0 | 414 | 93 | 200 | 113 | 90 | 96 | 0 | 0 | 113 | 622 | 220 |  | 35 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 412 | 300 | 0 | 0 | 450 | 305 | 80 | 0 | 55 | 335 | 0 | 0 | 100 | 85 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 41 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 30 | 80 | 43 | 22 | 10 | 0 | 0 | 0 | 330 | 330 | 215 | 180 | 135 | 33 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 143 | 120 | 0 | 21 | 1.6 | 44 | 42 | 33 | 30 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 25 | 10 | 310 | 16 | 11 | 100 | 270 | 200 | 100 | 180 | 25 | 134 | 20 | 90 | 150 | 140 | 400 | 110 | 105 | 105 | 5 | 265 | 54 | 110 | 0 | 94 | 64 | 400 | 104 | 50 | 162 | 72 | 0 | 35 | 30 | 115 | 55 |  |  | 930 | 0 | 180 | 0 | 20 | 120 | 0 | 0 | 0 | 0 | 40 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 200 | 0 | 414 | 93 | 100 | 113 | 70 | 96 | 0 | 8 | 113 | 622 | 220 |  | 35 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 409 | 300 | 0 | 0 | 450 | 295 | 80 | 0 | 55 | 324 | 0 | 0 | 40 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 18 | 33 | 25 | 41 | 0 | 46 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 30 | 10 | 37 | 22 | 7 | 0 | 0 | 0 | 300 | 300 | 120 | 8 | 136 | 27 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 126 | 99 | 0 | 21 | 1 | 44 | 42 | 34 | 30 | 110 | 0 | 31 | 78 | 0 | 120 | 0 | 25 | 9 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 180 | 0 | 79 | 9 | 90 | 51 | 40 | 398 | 24 | 90 | 105 | 3 | 210 | 54 | 110 | 0 | 38 | 50 | 370 | 53 | 15 | 90 | 72 | 0 | 35 | 16 | 116 | 55 | 0 | 0 | 911 | 0 | 185 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 165 | 0 | 310 | 17 | 0 | 50 | 0 | 70 | 0 | 0 | 50 | 450 | 220 | 0 | 0 | 2 | 57 | 34 | 0 | 0 |  |  |  |  | 89403498 |  | 0
89403498
| Minimum Generation |  | 10295 | 7:00
| Highest Generation |  | 13696 | 21:00
| Day Peak Generation |  | 11933 | 12:00
| Evening Peak Generation |  | 13696 | 21:00
| HVDC Max Flow |  | 889 | 4:00
| HVDC EvPeak Flow |  | 859 | 21:00
| Load factor L.F |  | 89.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-27
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11933 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10574 | MW
Evening Peak Generation : |  | 13696 | MW Hour : | 21:00 | Available Max Generation : |  | 14960 | MW
E.P. Demand (at gen end) : |  | 13696 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13900 | MW
Maximum Generation : |  | 13696 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1060 | MW
Total Gen. (MKWH) : |  | 293.1145 | System Load Factor : | 89.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -536 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-27
Actual : | 89.04 | Ft.(MSL) , | Rule curve : | 82.38 | Ft.( MSL )
Gas Consumed : | Total = | 1141.65 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 178962546.142
: |  | Coal : | 141075251 | Oil : | 1220984989.33 | Total : | 1541022786.472
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4843.3052 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1303.464 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1710.1568 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1532.0467 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1357.5848 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 998.661 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 553.3856 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 363.0445 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 764.1992 |  |  | 0 | 0%
Total | 0 |  | 13425.8479 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 08:51 to 13:22 for C/M.
b) Chandraghona 132/33 kV T-2 transformer was under shut down from 10:46 to 16:17 for D/W.
c) Netrokona 132/33 kV T-1 transformer was under shut down from 10:10 to 10:48 for D/W.
d) Tongi-Uttara 3 rd phase 132 kV Cable was under shut down from 11:00 to 13:22 for protection work.
e) Sikalbaha 132/33 kV T-3 transformer was under shut down from 10:02 to 11:26 due to R/H maintenance
by PDB.
f) Payra-Gopalganj 400 kV Ckt-1 was closed at 13:12 and again open at 13:55 due to high voltage.
g) Gopalganj-Rampal 400 kV Ckt-2(New) was charged at 13:22 from Gopalganj end and again opened at
13:47 due to high voltage.
h) Mymensingh-Kishoreganj 132 kV Ckt-2 tripped at 12:55 from both ends showing Dist.Z2,C-φ at Mymensingh
end & Z1, C-φ relay at Kishoreganj end and was switched on at 12:58.
i) Shahjadpur 132/33 kV T-3 transformer was under shut down from 12:43 to 14:19 due to R/H maintenance.
j) Rajshahi(old) 132/33 kV T-2 transformer was under shut down from 15:26 to 16:44 due to R/H maintenance | [5 empty] | About 35 MW power interruption occurred under
at 33 kV feeder by NESCO. | [5 empty] | Rajshahi(Old) S/S area from 15:26 to 16:44.
k) Payra 400/132 kV ATR-1 transformer is under shut down since 16:05 due to fire protection work system
work by Payra P.P.
l) Barapukuria 132/33 kV T-3 transformer was under shut down from 17:16 to 17:59 due to R/H maintenance | [5 empty] | About 10 MW power interruption occurred under
at 33 kV DS by NESCO. | [5 empty] | Barapukuria S/S area from 17:16 to 17:59.
m) Mongla 132/33 kV T-1 & T-2 transformer tripped at 18:56 showing E/F due to 33 kV New Port(WZPDCL) | [5 empty] | About 36 MW power interruption occurred under
feeder fault and were switched on at 19:06. | [5 empty] | Mongla S/S area from 18:56 to 19:06.
n) After maintenance Haripur 360 MW GT was synchronized at 16:13 & ST at 18:44.
o) Khulna 225 MW CCPP GT was synchronized at 21:24 & ST at 03:23(27/06/2022).
p) Mymensingh 132/33 kV T-3 transformer was under shut down from 21:27 to 22:15 due to R/H at 33 kV
Bus DS.
q) Kaptai Hydro Unit-2&3 tripped at 22:35 due to Governor System problem and were synchronized at
23:07(unit-2) & 23:23(unit-3).
r) Keraniganj-Nawabganj 132 kV Ckt-2 tripped at 02:09(27/06/2022) from both ends showing O/C at Keraniganj | [5 empty] | About 45 MW power interruption occurred under
end & Dist. Z1,Z2, 3-φ, SOTF at Nawabganj end as R-φ PT at Nawabganj end got burst. | [5 empty] | Nawabganj S/S area from 02:09(27/06/2022) to 04:11.
s) Keraniganj-Nawabganj 132 kV Ckt-1 tripped at 02:09(27/06/2022) from Keraniganj end showing Dist. Z2
L/O and was switched on at 04:11(27/06/2022).
t) Madunaghat-Sholoshahar 132 kV Ckt tripped at 0:45(27/06/2022) from Sholoshahar end showing L/O
and was switched on at 05:00(27/06/2022).
u) Natore-Rajshahi(Old) 132 kV Ckt-2 is under shut down since 06:07(27/06/2022) due to Bus DS
replacement work at Natore end.
v) Natore-Rajshahi(Old) 132 kV Ckt-1 was under shut down from 07:01(27/06/2022) to 09:01(27/06/2022)
due to C/M of reserve Bus DS.
w) Natore 132 kV main Bus was under shut down from 06:39(27/06/2022) to 09:01(27/06/2022) due to | [5 empty] | About 85 MW power interruption has been running under
Bus DS of Rajshahi(old)-2 replacement. | [5 empty] | Natore S/S area since 06:39(27/06/2022).
x) Sonargaon 132/33 kV T-2 transformer along with 33 kV Bus were under shut down from | [5 empty] | About 20 MW power interruption occurred under
07:27(27/06/2022) to 10:32(27/06/2022) for C/M. | [5 empty] | Sonargaon S/S area from 07:27(27/06/2022) to 10:32.
y) Gollamari 132/33 kV T-1 transformer was shut down at 06:12(27/06/2022) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4384800
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 1994727 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9932800
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 312 | 1660000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9965500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 79 | 1686720 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 6715665 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1302848
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 500004
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 91 | 1976976 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7844676
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1840464 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1269000
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2349120
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1251700
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1095478
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1132440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 774500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 0 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 902400 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 5823598 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 255 | 2077647 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 85 | 926880 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 80 | 877469 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 2243232 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2391600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2610240
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3610080
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 206044
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1195920 | 33 kV feeder problem.
| Dhaka area Total |  |  |  | 5847 | 4086 | 80542528
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 302961 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 147960
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 973440 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 2887965 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2437999
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 153696 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 280743 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 30 | 756240 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1973760 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515808
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 491040
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 1375680 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36361
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 284 | 5251527 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1368926
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2666325
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 64 | 1383360
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 1358673 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1209 | 24362464
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4980000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 8049600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 335 | 7547000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 686160 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 53 | 1251840
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 189 | 4482909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1155785
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 3029309 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 633328
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3251910 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3287520
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 495540
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3423360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 701800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 455820 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 80 | 903360 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 1364160 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 835560 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2787840
| Cumilla Area Total |  |  |  | 2885 | 2290 | 49549061
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2403840 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 447444
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 4459200
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 2001600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 290340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 590160
| Mymensingh Area Total |  |  |  | 614 | 443 | 10205984
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1032000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 974560 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2657127 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 33 | 810000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 799848 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 733536 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1929600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2892530 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 25 | 567360 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 372816 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7073500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9522000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9382000
| Sylhet Area Total |  |  |  | 2477 | 1644 | 39251717
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 859 | 21247272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 78 | 632640 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 260640 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 12050 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 3713 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 7872192 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 243000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 44 | 500160 | Low demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 1766400 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 45072 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 618480
| Khulna 330 MW CCPP |  | BPDB | 330 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1382 | 33201619
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 111840 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 552848 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2050435 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 620 | 13140800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 5163082
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 112800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 992 | 21131805
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 489000
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 267568
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 333686
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 101184 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 186661 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 176 | 5009118
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4657582 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9529527
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 332800 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 493440
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 222426
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 505520 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 40 | 422405 | Low demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2151936 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2541120
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35820
| Rajshahi Area Total |  |  |  | 2129 | 1271 | 27279793
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4286700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 96 | 1814428 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37277
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1451136 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 379 | 7589541
| Total |  |  |  | 21396 | 13696 | 293114512
| Eastern Grid Total |  |  |  | 14205 | 9672 | 203911754
| Western Grid Total |  |  |  | 7191 | 4024 | 89202758
| National Grid Total |  |  |  | 21396 | 13696 | 293114512
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-26
(a) ENTIRE EASTERN GRID : |  | 8962.25 | MW | (b) ENTIRE WESTERN GRID : |  | 4258 | MW
i) Dhaka area |  | 4868 | MW | i) Khulna area |  | 1583 | MW
ii) Chittagong area |  | 1376.25 | MW | ii) Rajshahi area |  | 1411.2 | MW
iii) Comilla area |  | 1226 | MW | iii) Barisal area |  | 391.8 | MW
iv) Mymensingh area |  | 1018 | MW | iv) Rangpur area |  | 872 | MW
v) Sylhet area |  | 474 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13220.25 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 19:00 | Hasnabad | 88 | 22:00 | Noapara | 51 | 22:00
Agargaon | 97 | 13:00 | Hathazari | 99 | 20:00 | Pabna | 108 | 13:00
Agrabad | 80 | 15:00 | Ish-D | N/A | N/A | Palashbari | 124 | 23:00
AKS | 23 | 09:00 | Ishurdi | 79 | 22:00 | Panchagarh | 58 | 22:00
AKSML | 135 | 18:00 | Jaldhaka | 64 | 21:00 | Patuakhali | 119 | 23:00
Amnura | 53 | 21:00 | Jamalpur | 155 | 00:00 | Payra | 0.98 | 11:00
Ashuganj | 43 | 12:00 | Jashore | 121 | 23:00 | PHP | 3 | 00:00
Bagerhat | 106 | 19:30 | Jhenaidah | 118 | 23:00 | Purbachal | 19 | 15:00
Bakulia | 127 | 16:00 | Joydebpur | 194 | 20:00 | Purbasadipur | 130 | 22:00
Banani | 61 | 15:00 | Joypurhat | 64 | 00:00 | Rahim | 10 | 21:00
Bangabhaban | 22 | 10:00 | Juldah | 28 | 00:00 | Rajbari | 64 | 21:00
Barapukuria | 53 | 21:00 | Kabirpur | 276 | 12:00 | Rajendrapur | 122 | 21:00
Barguna | 20 | 21:00 | Kachua | 76 | 22:00 | Rajshahi | 171 | 20:00
Barishal | 116 | 19:30 | Kallyanpur | 102 | 16:00 | Rajshahi | 40 | 23:00
Barishal | 54 | 19:30 | Kalurghat | 6 | 10:00 | Ramganj | 116 | 23:00
Baroaulia | 73 | 22:00 | Kamrangirchar | 73 | 13:00 | Rampur | 23 | 20:00
Baroirhat | 52 | 19:30 | Kaptai | 4 | 21:00 | Rangamati | 14 | 19:00
Bashundhara | 165 | 14:00 | Kazla | 86 | 16:00 | Rangpur | 144 | 19:30
BashundharaCement | 7 | 00:00 | Keranigonj | 68 | 17:00 | Ruppur | 4.4 | 11:00
Beanibazar | 68 | 22:00 | Khagrachori | 28 | 19:30 | Saidpur | 110 | 22:00
Benapole | 60 | 22:00 | Khulna | 105 | 13:00 | Satkhira | 120 | 23:00
Bhaluka | 162 | 19:30 | Khulshi | 185 | 14:00 | Satmasjid | 105 | 19:30
Bhandaria | 58 | 21:00 | Kishoreganj | 146 | 22:00 | Savar | 197 | 16:00
Bhangura | 36 | 20:00 | Kodda | 339 | 14:00 | Shahjadpur | 111 | 21:00
Bheramara(GK) | 59 | 20:00 | KSRM | 19.7 | 01:00 | Shahjibazar | 114 | 00:00
Bhulta | 241 | 22:00 | Kulaura | 46 | 20:00 | Shahmirpur | 46.5 | 19:00
Bog-Sherpur | 62 | 20:00 | Kurigram | 61 | 21:00 | Shariatpur | 74 | 21:00
Bogura | 161 | 21:00 | Kushtia | 136 | 19:30 | Sherpur | 128 | 01:00
Borhanuddin | 46 | 23:00 | Lalbag | 98 | 13:00 | Shikalbaha | 32 | 01:00
Brahmanbaria | 170 | 23:00 | Lalmonirhat | 49 | 21:00 | Shitalakhya | 112 | 10:00
BSRM | 159 | 18:00 | Madanganj | 105 | 21:00 | Sholosohor | N/A | N/A
Cantonment | 152 | 14:00 | Madaripur | 98 | 21:00 | Shyampur | 168 | 10:00
Chandpur | 67 | 23:00 | Madartek | 85 | 21:00 | Siddhirganj | 130 | 12:00
Chandraghona | 32 | 22:00 | Madunaghat | 59 | 19:30 | Sirajganj | 102 | 22:00
Chapai | 69 | 21:00 | Magura | 60 | 22:00 | Sonargaon | 96 | 00:00
Charsaidpur | 44 | 23:00 | Mahasthangarh | 70 | 23:00 | Sreemongol | 58 | 19:30
Chauddagram | 52 | 22:00 | Manikganj | 84 | 20:00 | Srinagar | 45.39 | 22:00
Chhatak | 26 | 22:00 | Maniknagar | 77 | 13:00 | SSM | 19 | 23:00
Chowmuhani | 198 | 19:30 | Matarbari | 36 | 19:00 | Sunamganj | 34 | 20:00
Chuadanga | 107 | 23:00 | Matuail | 67 | 10:00 | Sylhet | 136 | 19:00
Coxsbazar | 115 | 20:00 | Millgate | 64 | 12:00 | Tangail | 205 | 21:00
Cumilla(N) | 148 | 21:00 | Mirpur | 136 | 17:00 | Thakurgaon | 97 | 22:00
Cumilla(S) | 162 | 19:00 | Mirsorai | N/A | N/A | TK | 30.5 | 23:00
Daudkandi | 143 | 22:00 | Mithapukur | 38 | 18:30 | Tongi | 129 | 15:00
Dhaka | 40 | 13:00 | Modern | 0 | 00:00 | Ullon | 45 | 23:00
Dhamrai | 130 | 20:00 | Mogbazar | 135 | 13:00 | Uttara | 94 | 16:00
Dhanmondi | 159 | 13:00 | Mongla | 44 | 11:00 | UttaraNew | 18 | 14:00
Dohazari | 104 | 20:00 | Motijheel | 39 | 13:00 | Zigatola | 45 | 16:00
Faridpur | 149 | 22:00 | Munshiganj | 110 | 01:00
Fatullah | 67 | 12:00 | Mymensingh | 207 | 00:00
Fenchuganj | 42 | 23:00 | Naogaon | 122 | 20:00
Feni | 129 | 19:30 | Narail | 50 | 21:00
Ghorashal | 140 | 10:00 | Narinda | 75 | 16:00
Goalpara | 28 | 23:00 | Narshingdi | 186 | 01:00
Gollamari | 44 | 19:30 | Natore | 142 | 20:00
Gopalganj | 96.4 | 23:00 | Natore-D | N/A | N/A
GPH | 93 | 14:00 | Nawabganj | 55 | 22:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 402 | 03:00 | 387 | 11:00 | Kaliakoir | 399 | 04:00 | 381 | 15:00
| Bibiana | 411 | 06:00 | 402 | 19:00 | Payra | 417 | 18:30 | 405 | 00:00
| BIPTC | 401 | 08:00 | 394 | 00:00
| Gopalganj_I | 414 | 18:30 | 392 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 05:00 | 216 | 11:00 | Hathazari | 237 | 01:00 | 223 | 07:00
| AKSML | 241 | 01:00 | 217 | 09:00 | Ishurdi | 237 | 06:00 | 224 | 21:00
| Aminbazar | 229 | 04:00 | 218 | 12:00 | Jhenaidah | 238 | 17:00 | 215 | 00:00
| Baghabari | 234 | 18:00 | 226 | 00:00 | Kaliakoir | 231 | 04:00 | 220 | 11:00
| Barapukuria | 228 | 18:00 | 211 | 21:00 | Keranigonj | 229 | 05:00 | 216 | 11:00
| Barishal | 232 | 18:30 | 222 | 00:00 | Khulna(S) | 242 | 09:00 | 219 | 01:00
| Bheramara | 235 | 06:00 | 222 | 21:00 | Maniknagar | 231 | 06:00 | 221 | 11:00
| Bhulta | 234 | 05:00 | 222 | 11:00 | Meghnaghat | 233 | 05:00 | 227 | 10:00
| Bibiana | 240 | 06:00 | 234 | 14:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 06:00 | 221 | 21:00 | Rajshahi | 233 | 09:00 | 220 | 21:00
| Bogura | 232 | 18:30 | 217 | 23:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 238 | 18:30 | 230 | 02:00 | Rampura | 230 | 04:00 | 220 | 11:00
| BSRM | 235 | 01:00 | 220 | 09:00 | Shikalbaha | 239 | 02:00 | 224 | 09:00
| Cumilla(N) | 233 | 20:00 | 226 | 10:00 | Shyampur | 230 | 05:00 | 218 | 11:00
| Fenchuganj | 242 | 06:00 | 237 | 16:00 | Siddhirganj | 232 | 04:00 | 223 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:00 | 225 | 21:00
| GPH | 238 | 01:00 | 220 | 09:00 | Tongi | 230 | 03:00 | 220 | 12:00
| Haripur | 228 | 05:00 | 220 | 12:00
| Hasnabad | 227 | 04:00 | 218 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 05:00 | 127 | 11:00 | Mahasthangarh | 135 | 18:00 | 123 | 21:00
| Agargaon | 137 | 05:00 | 127 | 11:00 | Manikganj | 128 | 04:00 | 122 | 15:00
| Agrabad | 139 | 18:30 | 130 | 08:00 | Maniknagar | 136 | 03:00 | 129 | 11:00
| AKS | 137 | 20:00 | 128 | 08:00 | Matarbari | 128 | 18:30 | 115 | 04:00
| Aminbazar | 133 | 04:00 | 126 | 12:00 | Matuail | 134.5 | 20:00 | 129 | 11:00
| Amnura | 134 | 18:00 | 125 | 01:00 | Millgate | 136 | 04:00 | 126 | 11:00
| Ashuganj | 138 | 10:00 | 134 | 00:00 | Mirpur | 132 | 04:00 | 125 | 15:00
| Bagerhat | 135 | 09:00 | 120 | 01:00 | Mithapukur | 135 | 18:30 | 119 | 21:00
| Bakulia | 139 | 01:00 | 131 | 09:00 | Modern | 139 | 18:00 | 130 | 04:00
| Banani | 136 | 03:00 | 126 | 11:00 | Mogbazar | 136 | 04:00 | 127 | 12:00
| Bangabhaban | 136 | 05:00 | 129 | 10:00 | Mongla | 134 | 10:00 | 119 | 01:00
| Barapukuria | 136 | 18:00 | 124 | 00:00 | Motijheel | 138 | 07:00 | 129 | 10:00
| Barguna | 138 | 18:00 | 130 | 00:00 | Munshiganj | 136 | 20:00 | 130 | 12:00
| Barishal | 138 | 18:00 | 131 | 00:00 | Mymensingh | 134 | 09:00 | 116 | 23:00
| Barishal | 140 | 18:30 | 132 | 23:00 | Naogaon | 133 | 18:00 | 119 | 21:00
| Baroaulia | 140 | 18:00 | 133 | 06:00 | Narail | 136 | 01:00 | 125 | 00:00
| Baroirhat | 134 | 18:30 | 128 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bashundhara | 136 | 02:00 | 125 | 12:00 | Narshingdi | 139 | 01:00 | 124 | 11:00
| BashundharaCement | 137 | 00:00 | 122 | 08:00 | Natore | 135 | 18:00 | 125 | 21:00
| Beanibazar | 134 | 06:00 | 127 | 22:00 | Natore-D | N/A | N/A | N/A | N/A
| Benapole | 136 | 18:30 | 122 | 00:00 | Nawabganj | 137 | 03:00 | 129 | 11:00
| Bhaluka | 133 | 09:00 | 112 | 21:00 | Netrakona | 134 | 13:00 | 116 | 23:00
| Bhandaria | 138 | 18:30 | 126 | 00:00 | New | 138 | 19:00 | 126 | 12:00
| Bhangura | 139 | 19:00 | 132 | 21:00 | Niamatpur | 132 | 18:30 | 113 | 23:00
| Bheramara | 137 | 06:00 | 131 | 21:00 | Noapara | 137 | 18:00 | 124 | 01:00
| Bheramara(GK) | 138 | 16:00 | 131 | 00:00 | Pabna | 136 | 06:00 | 128 | 21:00
| Bhulta | 126 | 05:00 | 121 | 10:00 | Palashbari | 132 | 18:30 | 117 | 21:00
| Bog-Sherpur | 136 | 18:30 | 125 | 21:00 | Panchagarh | 135 | 18:30 | 114 | 00:00
| Bogura | 137 | 18:00 | 125 | 21:00 | Patuakhali | 137 | 18:00 | 131 | 00:00
| Bogura | 137 | 19:00 | 126 | 23:00 | Payra | 138 | 08:00 | 133 | 00:00
| Brahmanbaria | 133 | 06:00 | 127 | 23:00 | PHP | 133 | 17:00 | 126 | 04:00
| Cantonment | 136 | 05:00 | 125 | 11:00 | Purbachal | 137 | 04:00 | 125 | 12:00
| Chandpur | 141 | 18:00 | 134 | 23:00 | Purbasadipur | 135 | 18:30 | 116 | 00:00
| Chandraghona | 139 | 18:00 | 132 | 09:00 | Rahim | 135 | 23:00 | 130 | 11:00
| Chapai | 135 | 18:00 | 125 | 21:00 | Rajbari | 134 | 18:30 | 124 | 00:00
| Charsaidpur | 137 | 05:00 | 130 | 11:00 | Rajendrapur | 127 | 06:00 | 118 | 15:00
| Chauddagram | 134 | 18:00 | 128 | 00:00 | Rajshahi | 133 | 17:00 | 124 | 21:00
| Chhatak | 134 | 05:00 | 129 | 23:00 | Rajshahi | 134 | 18:00 | 128 | 04:00
| Chowmuhani | 133 | 18:00 | 126 | 00:00 | Ramganj | 134 | 18:00 | 131 | 11:00
| Chuadanga | 133 | 18:00 | 118 | 00:00 | Rampur | 137 | 19:00 | 131 | 07:00
| Coxsbazar | 125 | 07:00 | 115 | 23:00 | Rampura | 135 | 04:00 | 127 | 11:00
| Cumilla(N) | 136 | 19:30 | 132 | 09:00 | Rangamati | 139 | 18:30 | 131 | 10:00
| Cumilla(S) | 136 | 18:30 | 126 | 14:00 | Rangpur | 133 | 18:30 | 118 | 00:00
| Daudkandi | 138 | 20:00 | 129 | 00:00 | Ruppur | 137 | 18:30 | 130 | 21:00
| Dhaka | 136 | 05:00 | 127 | 12:00 | Saidpur | 134 | 18:30 | 119 | 21:00
| Dhamrai | 134 | 05:00 | 124 | 15:00 | Satkhira | 136 | 18:30 | 118 | 01:00
| Dhanmondi | 135 | 01:00 | 129 | 12:00 | Satmasjid | 137 | 05:00 | 126 | 11:00
| Dohazari | 137 | 18:30 | 127 | 19:00 | Savar | 135 | 03:00 | 125 | 11:00
| Faridpur | 135 | 18:30 | 125 | 00:00 | Shahjadpur | 140 | 18:00 | 133 | 21:00
| Fatullah | 135 | 00:00 | 128 | 11:00 | Shahjibazar | 135 | 06:00 | 129 | 23:00
| Fenchuganj | 138 | 06:00 | 133 | 23:00 | Shahmirpur | 140 | 18:30 | 131 | 09:00
| Feni | 134 | 18:00 | 127 | 23:00 | Shariatpur | 136 | 18:30 | 125 | 00:00
| Ghorashal | 137 | 00:00 | 136 | 01:00 | Sherpur | 138 | 10:00 | 122 | 23:00
| Goalpara | 138 | 18:00 | 125 | 01:00 | Shikalbaha | 140 | 18:30 | 131 | 09:00
| Gollamari | 134 | 18:00 | 123 | 00:00 | Shikalbaha | 140 | 02:00 | 132 | 09:00
| Gopalganj | 136 | 18:30 | 125 | 00:00 | Shitalakhya | 136 | 02:00 | 130 | 12:00
| Gopalganj_I | 138 | 18:30 | 129 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gulshan | 136 | 05:00 | 126 | 11:00 | Shyampur | 133 | 02:00 | 128 | 11:00
| Halishahar | 139 | 02:00 | 129 | 08:00 | Shyampur | 135 | 01:00 | 128 | 11:00
| Haripur | 135 | 23:00 | 130 | 11:00 | Siddhirganj | 135 | 04:00 | 129 | 11:00
| HaripurSBU | 136 | 04:00 | 130 | 11:00 | Sirajganj | 136 | 19:00 | 127 | 21:00
| Hasnabad | 136 | 01:00 | 132 | 09:00 | Sonargaon | 137 | 19:30 | 131 | 11:00
| Hathazari | 140 | 18:30 | 132 | 07:00 | Sreemongol | 138 | 07:00 | 132 | 23:00
| Ish-D | N/A | N/A | N/A | N/A | Srinagar | 138 | 05:00 | 130 | 12:00
| Ishurdi | 137 | 06:00 | 130 | 21:00 | SSM | 141 | 20:00 | 135 | 05:00
| Jaldhaka | 133 | 18:30 | 115 | 21:00 | Sunamganj | 134 | 06:00 | 127 | 19:00
| Jamalpur | 141 | 13:00 | 125 | 22:00 | Sylhet | 135 | 06:00 | 131 | 19:00
| Jashore | 137 | 18:30 | 123 | 00:00 | Tangail | 133 | 05:00 | 124 | 23:00
| Jhenaidah | 137 | 09:00 | 126 | 01:00 | Thakurgaon | 137 | 19:00 | 114 | 23:00
| Jhenaidah | 138 | 09:00 | 126 | 00:00 | TK | 139 | 22:00 | 130 | 09:00
| Joydebpur | 144 | 14:00 | 136 | 15:00 | Tongi | 137 | 03:00 | 129 | 12:00
| Joypurhat | 135 | 18:30 | 115 | 23:00 | Ullon | 135 | 01:00 | 126 | 12:00
| Juldah | 140 | 17:00 | 132 | 06:00 | Uttara | 133 | 04:00 | 124 | 11:00
| Kabirpur | 137 | 03:00 | 122 | 11:00 | UttaraNew | 136 | 03:00 | 124 | 11:00
| Kachua | 136 | 07:00 | 132 | 00:00 | Zigatola | 137 | 04:00 | 129 | 11:00
| Kaliakoir | 133 | 05:00 | 127 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 372 | 9287 | 3996 | 13283 |  |  |  | QF-LDC-11
0:30 | 241 | 8973 | 4011 | 12984 | Date: | 2022-06-26
1:00 | 110 | 8659 | 4026 | 12685
1:30 | 155 | 8589.5 | 3955 | 12544.5
2:00 | 200 | 8520 | 3884 | 12404
2:30 | 229 | 8459.5 | 3764 | 12223.5 | [5 empty] | Gen. at Eve. Peak | 13696 | 13696 MW (21:00 )
3:00 | 258 | 8399 | 3644 | 12043 | [6 empty] | 21:00
3:30 | 216 | 8235 | 3629.5 | 11864.5 | [5 empty] | Gen. at Day Peak | 11933 | 11933 MW (12:00 )
4:00 | 174 | 8071 | 3615 | 11686 | [6 empty] | 12:00
4:30 | 150 | 7967 | 3576 | 11543 | [5 empty] | Highest Generation | 13696
5:00 | 126 | 7863 | 3537 | 11400 | [6 empty] | 21:00
5:30 | 66 | 7491.5 | 3418.5 | 10910
6:00 | 6 | 7120 | 3300 | 10420
6:30 | 37 | 7072 | 3285.5 | 10357.5
7:00 | 68 | 7024 | 3271 | 10295
7:30 | 115 | 7081 | 3285.5 | 10366.5
8:00 | 162 | 7138 | 3300 | 10438
8:30 | 248 | 7279.5 | 3363 | 10642.5
9:00 | 334 | 7421 | 3426 | 10847
9:30 | 338 | 7625 | 3450.5 | 11075.5
10:00 | 342 | 7829 | 3475 | 11304
10:30 | 329 | 7948 | 3464 | 11412
11:00 | 316 | 8067 | 3453 | 11520
11:30 | 229 | 8256 | 3470.5 | 11726.5
12:00 | 142 | 8445 | 3488 | 11933
12:30 | 81 | 8512 | 3486 | 11998
13:00 | 20 | 8579 | 3484 | 12063
13:30 | 10 | 8595 | 3480.5 | 12075.5
14:00 | 0 | 8611 | 3477 | 12088
14:30 | 43 | 8724.5 | 3512.5 | 12237
15:00 | 86 | 8838 | 3548 | 12386
15:30 | 97 | 8774.5 | 3522 | 12296.5
16:00 | 108 | 8711 | 3496 | 12207
16:30 | 113 | 8641.5 | 3465.5 | 12107
17:00 | 118 | 8572 | 3435 | 12007
17:30 | 141 | 8347.5 | 3347 | 11694.5
18:00 | 164 | 8123 | 3259 | 11382
18:30 | 214 | 8445.5 | 3427.5 | 11873
19:00 | 264 | 8768 | 3596 | 12364
19:30 | 204 | 9547 | 4093 | 13640
20:00 | 208 | 9531 | 4037 | 13568 |  |  |  | Executive Engineer
20:30 | 326 | 9601.5 | 4030.5 | 13632 |  |  |  | Network Operation Division
21:00 | 444 | 9672 | 4024 | 13696
21:30 | 490 | 9682 | 4013 | 13695
22:00 | 536 | 9692 | 4002 | 13694 |  |  |  |  | Page 6 of 7
22:30 | 500 | 9686.5 | 3994 | 13680.5
23:00 | 464 | 9681 | 3986 | 13667
23:30 | 418 | 9484 | 3991 | 13475
24:00 | 372 | 9287 | 3996 | 13283
13696 MW (21:00 )
11933 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-26 |  | Energy |  | 293114512
[13 empty] | 2022-06-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3767 | 859 | 2676 | 888 | 3516 | 795 | 123 | 15 | 484 | 160 | 0 | 0
0:30 | 4046 | 866.5 | 2529 | 520.5 | 3521.5 | 795 | 123 | 7.5 | 422 | 153 | 0 | 0 | Date: | 2022-06-26
1:00 | 4325 | 874 | 2382 | 153 | 3527 | 795 | 123 | 0 | 360 | 146 | 0 | 0
1:30 | 4322 | 881 | 2380.5 | 76.5 | 3537.5 | 765 | 123 | 0 | 315 | 144 | 0 | 0 | [8 empty] | Total Energy | 293.1145 | Total Energy Gen 293.115 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 293.115 MKWHr
2:00 | 4319 | 888 | 2379 | 0 | 3548 | 735 | 123 | 0 | 270 | 142 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4298 | 887.5 | 2352.5 | 0 | 3506 | 730 | 123.5 | 0 | 186 | 140 | 0 | 0 | [8 empty] | Energy Requirement | 293.1145
3:00 | 4277 | 887 | 2326 | 0 | 3464 | 725 | 124 | 0 | 102 | 138 | 0 | 0
3:30 | 4269 | 888 | 2340 | 0 | 3307 | 725 | 124.5 | 0 | 75 | 136 | 0 | 0 | [6 empty] | Shortage
4:00 | 4261 | 889 | 2354 | 0 | 3150 | 725 | 125 | 0 | 48 | 134 | 0 | 0
4:30 | 4264.5 | 888.5 | 2325 | 0 | 3071 | 705 | 125 | 0 | 32 | 132 | 0 | 0
5:00 | 4268 | 888 | 2296 | 0 | 2992 | 685 | 125 | 0 | 16 | 130 | 0 | 0
5:30 | 4197.5 | 887.5 | 2266 | 0 | 2624 | 665 | 124.5 | 0 | 16 | 124 | 5.5 | 0
6:00 | 4127 | 887 | 2236 | 0 | 2256 | 645 | 124 | 0 | 16 | 118 | 11 | 0
6:30 | 4103.5 | 888 | 2256.5 | 0 | 2184.5 | 640 | 124 | 0 | 16 | 116 | 29 | 0 |  |  |  |  | Coal
7:00 | 4080 | 889 | 2277 | 0 | 2113 | 635 | 124 | 0 | 16 | 114 | 47 | 0
7:30 | 4099.5 | 888.5 | 2279 | 0 | 2133.5 | 630 | 124 | 0 | 16 | 117 | 79 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4119 | 888 | 2281 | 0 | 2154 | 625 | 124 | 0 | 16 | 120 | 111 | 0
8:30 | 4167.5 | 888.5 | 2274 | 0 | 2288 | 615 | 124 | 0 | 16 | 123 | 146.5 | 0
9:00 | 4216 | 889 | 2267 | 0 | 2422 | 605 | 124 | 0 | 16 | 126 | 182 | 0
9:30 | 4200.5 | 888.5 | 2260.5 | 0 | 2679 | 590 | 124 | 0 | 16 | 131 | 186 | 0
10:00 | 4185 | 888 | 2254 | 0 | 2936 | 575 | 124 | 0 | 16 | 136 | 190 | 0
10:30 | 4201.5 | 888 | 2309.5 | 0 | 2984.5 | 575 | 124 | 0 | 16 | 136 | 177.5 | 0
11:00 | 4218 | 888 | 2365 | 0 | 3033 | 575 | 124 | 0 | 16 | 136 | 165 | 0
11:30 | 4184 | 888 | 2361.5 | 71.5 | 3102 | 595 | 124 | 0 | 95 | 139 | 166.5 | 0
12:00 | 4150 | 888 | 2358 | 143 | 3171 | 615 | 124 | 0 | 174 | 142 | 168 | 0
12:30 | 4116.5 | 882 | 2340 | 250 | 3190.5 | 625 | 124 | 0 | 180 | 142 | 148 | 0
13:00 | 4083 | 876 | 2322 | 357 | 3210 | 635 | 124 | 0 | 186 | 142 | 128 | 0
13:30 | 4083 | 876 | 2322 | 357 | 3210 | 635 | 124 | 0 | 186 | 142 | 128 | 0
14:00 | 4083 | 876 | 2322 | 357 | 3210 | 635 | 124 | 0 | 186 | 142 | 128 | 0
14:30 | 4078.5 | 875.5 | 2347 | 447 | 3254 | 640 | 124 | 0 | 186.5 | 147 | 125 | 0
15:00 | 4074 | 875 | 2372 | 537 | 3298 | 645 | 124 | 0 | 187 | 152 | 122 | 0
15:30 | 4062.5 | 874.5 | 2352 | 481 | 3290 | 655 | 122.5 | 0 | 194 | 153 | 112 | 0
16:00 | 4051 | 874 | 2332 | 425 | 3282 | 665 | 121 | 0 | 201 | 154 | 102 | 0
16:30 | 4033 | 874 | 2360.5 | 250 | 3356.5 | 645 | 121 | 0 | 221 | 153 | 84 | 0
17:00 | 4033 | 874 | 2389 | 75 | 3431 | 625 | 121 | 0 | 241 | 152 | 66 | 0
17:30 | 3907 | 874.5 | 2283 | 37.5 | 3412.5 | 610.5 | 122 | 0 | 263.5 | 146 | 38 | 0
18:00 | 3781 | 875 | 2177 | 0 | 3394 | 596 | 123 | 0 | 286 | 140 | 10 | 0
18:30 | 3859 | 875 | 2331.5 | 52.5 | 3497 | 595.5 | 123 | 0 | 383.5 | 151 | 5 | 0
19:00 | 3937 | 875 | 2486 | 105 | 3600 | 595 | 123 | 0 | 481 | 162 | 0 | 0
19:30 | 3995 | 875 | 2596 | 846 | 3796 | 735 | 123 | 0 | 514 | 160 | 0 | 0
20:00 | 3990 | 860 | 2609 | 691 | 3835 | 745 | 125 | 0 | 551 | 162 | 0 | 0
20:30 | 4025 | 859.5 | 2667 | 637.5 | 3840 | 770 | 125 | 0 | 547 | 161 | 0 | 0
21:00 | 4060 | 859 | 2725 | 584 | 3845 | 795 | 125 | 0 | 543 | 160 | 0 | 0
21:30 | 4040.5 | 859.5 | 2733 | 592 | 3842 | 796 | 125 | 5 | 543 | 159 | 0 | 0
22:00 | 4021 | 860 | 2741 | 600 | 3839 | 797 | 125 | 10 | 543 | 158 | 0 | 0
22:30 | 4007 | 860.5 | 2770.5 | 689 | 3789 | 797 | 80 | 10 | 517.5 | 160 | 0 | 0
23:00 | 3993 | 861 | 2800 | 778 | 3739 | 797 | 35 | 10 | 492 | 162 | 0 | 0
23:30 | 3880 | 860 | 2738 | 833 | 3627.5 | 796 | 79 | 12.5 | 488 | 161 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 3767 | 859 | 2676 | 888 | 3516 | 795 | 123 | 15 | 484 | 160 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 293.115 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 293.115 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 88 | 89 | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 88 |  | 88 | 88 | 90 | 90 | 90 | 0 | 88 | 2073965
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 814000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | [6 empty] | 1 | 8 | 8 | 8 | 11 | 17 | 18 | 25 | 25 |  | 17 | 17 | 17 | 0 | 7 | 17 | 17 | 302961
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 12 | 16 | 18 | 20 | 20 | 19 | 17 | 14 | 9 | 4 | 1 |  | 0 | [6 empty] | 147960
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 34 | 34 | 51 | 51 | 51 | 51 | 51 | 280743
12 | Hathazari 100 MW peaking PP | [19 empty] | 4 | 25 | 43 | 51 | 51 | 0 |  | 153696
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 102 | 90 | 87 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 87 | 87 | 87 |  | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 2437999
| Daudkandi 200 MW PP (B.Trac) | [12 empty] | 50 | 20 | 70 | 100 | 0 |  |  | 20 | 190 | 170 | 80 | 80 | 190 | 198 | 903360
14 | Titas 50 MW Peaking PP | 49 | [10 empty] | 41 | 49 | 49 | 40 | 40 | 40 | 46 |  | 48 | 49 | 49 | 49 | 49 | 49 | 41 | 633328
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 337 | 335 | 337 | 337 | 338 | 300 | 300 | 300 | 335 | 331 | 330 | 330 | 333 | 330 | 330 | 331 | 331 | 280 |  | 331 | 335 | 335 | 330 | 332 | 330 | 326 | 7844676
18 | Kodda 300 MW PP Unit-2 (Summit) | 276 | 273 | 276 | 274 | 274 | 95 | 63 | 45 | 55 | 252 | 271 | 274 | 274 | 273 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 5823598
19 | Ashuganj 195MW PP (APSCL-United) | 189 | 189 | 187 | 189 | 187 | 187 | 189 | 189 | 187 | 189 | 189 | 189 | 187 | 189 | 189 | 187 | 187 | 140 |  | 187 | 187 | 184 | 189 | 190 | 190 | 68 | 4482909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4384800
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 28 | 27 | 27 |  | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 686160
33 | Ashuganj 225 MW CCPP | 214 | 211 | 211 | 212 | 213 | 212 | 212 | 210 | 211 | 210 | 209 | 205 | 207 | 205 | 204 | 206 | 206 | 182 |  | 206 | 209 | 209 | 206 | 205 | 207 | 105 | 4980000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 330 | 320 | 305 | 305 | 315 | 305 | 305 | 275 |  | 310 | 305 | 305 | 335 | 325 | 320 | 257 | 7547000
| Ashuganj 450 MW CCPP(North) | 315 | 320 | 320 | 320 | 315 | 315 | 320 | 360 | 320 | 315 | 345 | 340 | 315 | 320 | 325 | 315 | 315 | 280 |  | 295 | 310 | 310 | 345 | 330 | 325 | 285 | 8049600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 53 | 54 | 53 | 54 | 54 | 54 | 54 | 55 | 53 | 52 | 49 | 52 | 51 | 50 | 49 | 50 | 49 | 48 |  | 50 | 50 | 52 | 53 | 53 | 52 | 53 | 1251840
36 | Chandpur 150 MW CCPP | 135 | 137 | 136 | 136 | 136 | 136 | 136 | 138 | 138 | 137 | 136 | 136 | 136 | 138 | 136 | 136 | 136 | 136 |  | 136 | 136 | 136 | 136 | 135 | 136 | 137 | 3251910
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 410 | 409 | 410 | 409 | 409 | 408 | 409 | 410 | 409 | 411 | 410 | 405 | 405 | 411 | 404 | 406 | 408 | 411 |  | 411 | 409 | 407 | 409 | 412 | 408 | 410 | 9932800
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9965500
41 | Haripur 360MW CCPP(HPL) | [16 empty] | 58 | 57 |  | 131 | 235 | 292 | 312 | 312 | 330 | 330 | 1660000
42 | RPCL 210MW CCPP | 122 | 122 | 133 | 133 | 140 | 133 | 122 | 110 | 106 | 95 | 95 | 81 | 70 | 70 | 71 | 72 | 73 | 88 |  | 106 | 108 | 108 | 105 | 106 | 105 | 105 | 2403840
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 8 | 25 | 47 | 49 | 50 | 48 | 0 | 22 | 17 | 10 | 11 | 0 | [8 empty] | 290340
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 44 | 44 | 44 |  | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 1032000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 974560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 31 | 31 | 32 | 32 | 31 | 31 | 30 | 30 | 31 | 29 | 30 | 30 | 31 | 30 | 30 | 30 | 30 |  | 30 | 31 | 31 | 30 | 31 | 31 | 30 | 733536
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 84 | 86 |  | 86 | 86 | 86 | 84 | 84 | 84 | 84 | 1929600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2892530
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 25 | 24 | 25 | 25 | 24 | 25 | 24 | 24 | 24 | 21 | 21 | 22 | 23 | 23 | 23 | 23 | 23 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 567360
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 372816
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 270 | 280 | 280 | 280 | 265 | 285 | 280 | 300 | 275 | 290 | 310 | 285 | 280 | 300 | 290 | 280 | 270 |  | 280 | 260 | 280 | 290 | 300 | 320 | 320 | 7073500
| Bibiyana South 400 MW | 400 | 401 | 400 | 400 | 400 | 360 | 360 | 360 | 400 | 400 | 400 | 396 | 400 | 400 | 398 | 400 | 400 | 360 |  | 390 | 386 | 372 | 395 | 400 | 400 | 396 | 9382000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1095478
59 | Tangail Palli Power Gen 22 MW | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 590160
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515808
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500004
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 447444
63 | Impoprt (Tripura) | 146 | 142 | 138 | 134 | 130 | 118 | 114 | 120 | 126 | 136 | 136 | 142 | 142 | 150 | 152 | 154 | 152 | 140 |  | 162 | 160 | 162 | 160 | 158 | 162 | 160 | 3423360
64 | Malancha, Ctg. EPZ (United) | 37 | 39 | 39 | 39 | 39 | 39 | 25 | 4 | 3 | 2 | 2 | 3 | 4 | 7 | 3 | 3 | 8 | 12 |  | 16 | 12 | 9 | 27 | 37 | 38 | 39 | 491040
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 495540
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 24 | 24 | 14 | 8 | 16 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 701800
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 20 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 19 | 21 | 21 | 20 | 20 | 20 | 20 |  | 20 | 9 | 21 | 21 | 21 | 21 | 21 | 455820
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 25 | 25 | 20 | 9 | 13 | 20 | 20 | 20 | 10 |  | 10 | 15 | 20 | 25 | 25 | 28 | 20 | 532440
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 774500
72 | Rupganj 33 MW PP(Summit)
73 | Ghorashal 108MW PP (Regent) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 80 | 84 | 84 | 81 | 83 | 84 | 53 |  | 90 | 90 | 91 | 91 | 91 | 91 | 87 | 1994727
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 55 | 45 | 37 | 37 | 38 | 38 | 38 | 39 | 39 | 38 | 38 | 38 | 38 | 37 | 37 | 48 | 94 | 94 |  | 94 | 95 | 94 | 94 | 94 | 94 | 52 | 1364160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 160 | 108 | 72 | 72 | 110 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 108 |  | 119 | 162 | 162 | 162 | 162 | 162 | 162 | 3610080
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 72 | 24 | 16 | 30 | 83 | 91 | 91 | 91 | 95 | 99 | 98 | 98 | 65 |  | 65 | 80 | 85 | 91 | 88 | 83 | 91 | 1976976
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 33 | 16 | 8 | 9 | 24 | 33 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 902400
79 | Kodda 150MW PP | 150 | 150 | 82 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 133 | 133 | 133 | 133 | 133 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2349120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 | 70 | 105 | 105 | 90 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2391600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 6 | 1 | 5 | 1 | 2 | 2 | 0 | [8 empty] | 36361
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1368926
| Karnaphuli Power Ltd. | 110 | 103 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2666325
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 255 | 285 | 255 | 280 | 250 | 275 | 285 | 300 | 255 | 255 | 295 | 270 | 285 | 295 | 286 | 262 | 265 | 280 |  | 295 | 280 | 267 | 280 | 275 | 295 | 295 | 6715665
87 | Meghnaghat 100 MW(IEL) | 70 | 70 | 70 | 70 | 70 | 71 | 72 | 72 | 73 | 65 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 71 |  | 75 | 80 | 78 | 79 | 79 | 71 | 75 | 1686720
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 95 | 92 | 100 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 102 | 2610240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 756240
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 799848
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1155785
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 50 | 16 | 16 | 16 | 16 | 50 | 85 | 85 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1840464
95 | Patenga 50MW PP (Baraka) | 43 | 43 | 39 | 43 | 44 | 44 | 44 | 44 | 43 | 44 | 43 | 43 | 43 | 42 | 42 | 24 | 24 | 27 |  | 42 | 43 | 43 | 37 | 37 | 36 | 37 | 973440
96 | Chattogram 108 MW PP (ECPV) | 50 | 88 | 86 | [6 empty] | 10 | 49 | 75 | 80 | 80 | 80 | 80 | 80 | 80 |  | 84 | 87 | 87 | 87 | 87 | 87 | 88 | 1375680
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1302848
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 0 | 20 | 55 | 55 | 55 | 55 | 1251700
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2657127
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1269000
104 | Keranigonj 300 MW PP (APR) | 53 | [10 empty] | 78 | 120 | 57 | 255 | 140 |  |  |  | 29 | 300 | 186 | 255 | 255 | 301 | 305 | 2077647
105 | Bramhangoan 100 MW PP (Aggreko) | 50 | [10 empty] | 25 | 85 | 85 | 85 | 85 | 50 |  |  | 25 | 85 | 85 | 85 | 85 | 85 | 85 | 926880
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 195 | 200 | 120 | 130 | 181 | 189 | 188 | 177 | 176 | 176 | 186 | 167 | 186 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 187 | 185 | 4459200
112 | Aurahati 100MW PP (Aggreko) | 50 | [10 empty] | 40 | 80 | 80 | 80 | 80 | 25 |  |  | 26 | 81 | 80 | 80 | 80 | 80 | 80 | 877469
114 | Kodda 149 MW PP Unit-1 (Summit) | 80 | 79 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 77 | 80 | 80 | 79 | 79 | 79 | 79 | 79 | 128 |  | 127 | 133 | 134 | 134 | 132 | 132 | 85 | 2243232
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 50 | 70 | 90 | 90 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1973760
116 | Chandpur 200MW (Desh energy) | 120 | 120 | 120 | 120 | 120 | 120 | 119 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 128 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 3287520
117 | Ashuganj 150MW PP (Midland) | 140 | 138 | 137 | 137 | 137 | 100 | 100 | 100 | 107 | 118 | 123 | 125 | 128 | 132 | 128 | 127 | 128 | 127 |  | 132 | 132 | 127 | 123 | 138 | 142 | 107 | 3029309
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 402 | 401 | 401 | 364 | 370 | 387 | 403 | 403 | 404 | 401 | 402 | 402 | 402 | 403 | 403 | 371 |  | 402 | 402 | 402 | 404 | 404 | 402 | 404 | 9522000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 24 | 24 | 8 | 19 | 83 | 83 | 83 | 83 | 83 | 83 | 73 | 73 | 84 | 95 |  | 103 | 103 | 103 | 93 | 103 | 103 | 103 | 2001600
| Anwara 300 MW PP (United) | 300 | 300 | 230 | 190 | 190 | 80 | 80 | 80 | 80 | 100 | 155 | 246 | 262 | 282 | 283 | 283 | 283 | 190 |  | 190 | 284 | 284 | 284 | 284 | 215 | 215 | 5251527
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 65 | 65 | 65 | 65 | 65 | 64 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1383360
| Anlima Energy Ltd. | 90 | 90 | 90 | [5 empty] | 0 | 52 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1358673
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 19 | 35 | 35 | 35 | 35 | 35 |  | 26 | 35 | 35 | 35 | 35 | 35 | 35 | 835560
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 15 | 25 | 29 | 36 | 35 | 34 | 9 | 9 | 16 | 10 | 2 |  | 0 | [6 empty] | 206044
| Chandpur 115(Doreen) | 116 | 116 | 116 | 116 | 116 | 116 | 112 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 115 | 116 | 116 | 116 |  | 116 | 116 | 116 | 115 | 109 | 115 | 116 | 2787840
| Kanchan Purbachal Power Generation Ltd. |  | 21 | 55 | 55 | 55 | 55 | 55 | 41 | 42 | 55 |  | 42 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1195920
120 | Eastern Zone Total | 8659 | 8520 | 8399 | 8071 | 7863 | 7120 | 7024 | 7138 | 7421 | 7829 | 8067 | 8445 | 8579 | 8611 | 8838 | 8711 | 8572 | 8123 |  | 8768 | 9547 | 9531 | 9672 | 9692 | 9681 | 9287 | 203911754
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 22 |  | 73 | 66 | 73 | 78 | 65 | 65 | 22 | 632640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 39 | 9 | [17 empty] | 36 | 42 | 37 | 37 | 37 | 37 | 37 | 260640
| Khulna 225 MW CCPP | [23 empty] | 10 | 10 | 15 | 12050
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 93 | 93 | 35 | 17 | 17 | 27 | 70 | 70 | 64 | 54 | 64 | 73 | 74 | 74 | 90 |  | 92 | 93 | 92 | 92 | 93 | 93 | 93 | 1766400
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 27 | 54 | 84 | 83 | 44 | 48 | 61 | 30 | 71 | 57 | 37 | 6 | [8 empty] | 618480
131
132 | United Payra Power Ltd. | [19 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 112800
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 226 | 227 | 227 | 225 | 196 | 201 | 204 | 222 | 223 | 221 | 221 | 221 | 210 | 218 | 217 | 212 | 163 |  | 215 | 223 | 175 | 224 | 224 | 224 | 224 | 5163082
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | [18 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 111840
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 86 | 86 | 86 | 87 | 87 | 86 | 82 | 85 | 84 | 82 | 81 | 84 | 83 | 83 | 83 | 85 | 85 |  | 86 | 86 | 84 | 85 | 85 | 85 | 84 | 2050435
140 | Bhola 33 MW PP (Venture) | 30 | 30 | 28 | 27 | 26 | 24 | 21 | 19 | 11 | 20 | 20 | 21 | 21 | 22 | 24 | 19 | 20 | 18 |  | 26 | 28 | 28 | 30 | 30 | 31 | 31 | 552848
141 | Noapara 100 MW PP (Bangla Trac) | [12 empty] | 22 | 10 | 39 | 10 |  |  |  | 2 | 100 | 60 | 44 | 60 | 71 | 100 | 500160
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 40 | 40 | 32 | 32 | 32 | 32 | 243000
143 | Gopalganj 100 MW Peaking PP | [26 empty] | 3713
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 | 15 | 0 |  |  | 45072
146 | Bheramara HVDC | 874 | 888 | 887 | 889 | 888 | 887 | 889 | 888 | 889 | 888 | 888 | 888 | 876 | 877 | 875 | 874 | 874 | 875 |  | 875 | 875 | 860 | 859 | 860 | 861 | 859 | 21247272
147 | Bheramara 410 MW CCPP | 350 | 355 | 355 | 355 | 370 | 370 | 370 | 370 | 410 | 400 | 385 | 365 | 345 | 330 | 310 | 290 | 270 | 250 |  | 240 | 240 | 240 | 225 | 220 | 220 | 215 | 7872192
148 | Payra 1320 MW | 620 | 560 | 550 | 550 | 510 | 470 | 460 | 450 | 430 | 400 | 400 | 440 | 460 | 450 | 470 | 490 | 450 | 420 |  | 420 | 560 | 570 | 620 | 622 | 622 | 620 | 13140800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 176 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4286700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 100 | 90 | 80 | 70 | 60 | 45 | [20 empty] | 489000
| Baghabari 50 MW Peaking PP | 34 | 34 | [17 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 267568
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 0 | 4 | 3 | 0 | 0 | [8 empty] | 35820
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 216 | 217 | 216 | 216 | 216 | 217 | 216 | 216 | 213 | 214 | 212 | 209 | 210 | 210 | 191 | 193 | 202 | 187 |  | 164 | 181 | 182 | 176 | 171 | 163 | 160 | 5009118
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 216 | 212 | 167 | 163 | 163 | 160 | 159 | 158 | 185 | 179 | 180 | 195 | 200 | 208 | 208 | 201 | 193 | 180 |  | 160 | 190 | 185 | 188 | 174 | 167 | 167 | 4657582
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 423 | 391 | 364 | 368 | 346 | 356 | 378 | 391 | 378 | 380 | 411 | 406 | 377 | 418 | 414 | 414 | 414 | 370 |  | 380 | 414 | 414 | 414 | 414 | 414 | 414 | 9529527
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 35 | 35 | 20 | [9 empty] | 4 | 4 | 6 | 6 | 27 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 333686
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 19 | 19 | 18 | 20 | 19 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 493440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 222426
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | [18 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 101184
167 | Katakhali 50 MW Peaking PP | 16 | 5 | [11 empty] | 16 | 8 | 22 | 24 | 24 |  | 24 | 24 | 32 | 16 | 16 | 16 | 16 | 186661
168 | Santahar 50 MW Peaking PP | 37 | 37 | [15 empty] | 38 |  | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 332800
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 85 | 90 | 90 | 90 | 90 | 90 | 90 | 505520
171 | Baghabari 200 MW PP (Paramount) | [14 empty] | 8 | 10 |  |  |  | 3 | 90 | 110 | 40 | 40 | 51 | 120 | 422405
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 95 | 50 | 50 | 50 | 62 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 50 |  | 50 | 70 | 85 | 94 | 94 | 94 | 94 | 2151936
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 90 | 113 | 113 | 113 | 113 | 106 | 113 | 2541120
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 70 | 69 | 65 | 68 | 70 | 68 | 70 | 70 | 70 | 80 | 89 |  | 95 | 95 | 96 | 96 | 96 | 96 | 70 | 1814428
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 4 | 5 | 6 | 6 | 5 | 4 | 2 | 1 | [8 empty] | 37277
178 | Energypac Power Venture Thakurgaon Ltd. | 72 | 72 | 52 | 52 | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 23 | 35 | 80 |  | 109 | 109 | 108 | 108 | 108 | 90 | 72 | 1451136
178