## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-06-30 | Thursday
|  |  | Date (day): | 2022-06-30 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13012.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14241 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-29 | 2022-06-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 35 | 280 | 280 | 280 |  | 85
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 59 | 67 | 67 | 67 |  | 41 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 337 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 300 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | Gas shortage due to dirty fuel
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 79 | 79 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 125 | 125 | 150 |  |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M & Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 91 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 337 | 0 | 0
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 95 | 95 |  | 7 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 49 | 49 | 49 |  | 3 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 228 | 248 | 260 | 260 |  | 40 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 125 | 205 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 85 | 80 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 82 | 80 | 25 | 80 |  |  | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 78 | 132 | 134 | 134 |  | 15 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 75 | 93 | 95 | 95 |  |  | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 90 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 10 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3525 | 3796 | 3610 | 3760 | 291 | 1029
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 37 | 37 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 124 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 97 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 60 | 0 | 60 |  | 38 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 20 | 20 | 20 | 20 |  | 80 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 76 | 76 | 76 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 24 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 79 | 83 | 80 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 200 | 295 | 265 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 50 | 50 |  | 50 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 106 |  | 10 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1083 | 1317 | 1194 | 1361 | 311 | 699
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 211 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 300 | 300 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 270 | 300 | 330 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 15 | 15 | 30 | 30 | 15 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 143 | 140 | 143
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 7 | 50 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 135 | 135 | 135 | 136 |  | 27 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 200 | 150 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 146 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 94 | 94 | 94 |  | 19 | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 116 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1603 | 2045 | 1906 | 2163 | 552 | 65
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 72 | 105 | 120 | 120 | 82 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 180 | 180 | 180 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 93 | 93 | 93 |  | 22 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 21 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 307 | 422 | 488.6 | 437 | 82 | 30
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 33 | 33 | 33 |  | 18 | Engine problem
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 30 | 30 | 30 |  | 20 | Engine problem
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 57 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 25 | 24 | 25 | 25
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24 |  | 1 | Machine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 401 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1681 | 1690 | 1703 | 1734 | 0 | 707
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 874 | 851 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 49 | 20 | 80 |  | 35 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 0 | 34 |  | 20 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 214 | 222 | 120 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 175 | 160 | 200 | 200 | 210 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 75 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 70 | 90 |  | 15 | Engine problem
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 51 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1413 | 1514 | 1573 | 1847 | 210 | 131
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 17 | 16 | 16 |  |  | Rampal Transformar S/D
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 28 | 20 | 28 |  | 12 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 86 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 600 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 225 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 763 | 973 | 998 | 1006 | 109 | 12
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 23 | 0 | 35 |  | 36 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 8 | 8 |  | 42 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 213 | 207 | 150 | 200
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 159 | 200 | 220
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 380 | 414 | 414 |  |  | FGMO
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 15 | 90 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 159 | 100 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 113 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1050 | 1358 | 1153 | 1529 | 433 | 141
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 105 | 96 | 96 |  | 17 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 280 | 370 | 387 | 404 | 269 | 24
|  | Total |  |  |  |  | 22678 | 21396 | 11705 | 13485 | 13012.6 | 14241 | 2257 | 2838
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11160.1207 | 12857.26 | 12406.8507 | 13578.0675
| A. |  | 2022-06-29 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13485 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 10384 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13485 | MW
| 3 | Day peak Generation : |  |  | 11705 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12857.26 | MW
| 4 | Evening peak Generation : |  |  | 13485 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 289.4789 | MKWHr | By Solar | 0.98134 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 145.9176 | MKWHr |  | By Oil: | 97.9835 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.6264 | MKWHr |  | By Hydro: | 2.9749 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2257 | MW | Dhaka | 4840 | 4840 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2838 | MW | Chittagong | 1310.7 | 1310.7 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5095 | MW | Khulna | 1573.4 | 1573.4 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1103.58 | MMCFD |  |  | Rajshahi | 1351.2 | 1351.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 165237008.84 | ii) Oil : | Taka | 1391059144.34 | Comilla | 1137 | 1137 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 142857296 | Total | Taka | 1699153449.18 | Mymensingh | 1027 | 1027 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.755 | MKWHr. | Sylhet | 431 | 431 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -108 | MW (E to W) at | 20:00 | hrs | Barisal | 390.96 | 390.96 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -454 | MW at | 3:00 | hrs | Rangpur | 796 | 796 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 12857.26 | 12857.26 |  | 0
| B. |  | 2022-06-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14241 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11700 | MW
| 4 | Reserve(Generation end) |  |  |  | 341 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 298.3876 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10144 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.6218 | MKWHr. | ii) HVDC Flow at Peak Time |  | 851 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3734 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.12 |  | (b) Today: | 89.07 |  | (c) Rule Curve: |  | 83.73
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-06-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 412 | 329 |  | 0 | 225 | 261 | 79 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 88 | 37 | 22 | 39 | 0 | 0 | 0 | 300 | 300 | 197 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 152 | 151 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 52 | 86 | 0 | 120 | 0 | 23 | 10 | 285 | 24 | 0 | 200 | 268 | 300 | 83 | 115 | 82 | 60 | 0 | 90 | 163 | 133 | 400 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 37 | 50 | 400 | 94 | 0 | 54 | 108 | 0 | 35 | 0 | 113 | 55 | 0 |  | 798 | 0 | 130 | 0 | 16 | 223 | 0 | 0 | 32 | 0 | 8 | 87 | 31 | 32 | 0 | 0 | 0 | 0 | 28 | 90 | 0 | 0 | 24 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 99 | 124 | 0 | 321 | 75 | 186 | 94 | 26 | 70 | 0 | 0 | 113 | 622 | 225 | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 9061 | 3881 | 12942 | 4124 | 798 | 2153 | 950 | 3189 | 796 | 123 | 223 | 434 | 152 | 0 | 0 | 89.12
2:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 411 | 337 |  | 0 | 225 | 260 | 79 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 88 | 37 | 22 | 39 | 0 | 0 | 0 | 300 | 300 | 196 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 148 | 144 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 52 | 84 | 0 | 120 | 0 | 22 | 10 | 260 | 24 | 11 | 200 | 263 | 220 | 82 | 115 | 82 | 60 | 0 | 90 | 100 | 131 | 400 | 56 | 105 | 105 | 0 | 176 | 54 | 102 | 0 | 38 | 50 | 401 | 79 | 0 | 54 | 108 | 0 | 35 | 0 | 115 | 55 | 0 |  | 798 | 0 | 135 | 0 | 16 | 224 | 0 | 0 | 32 | 0 | 8 | 87 | 30 | 16 | 0 | 0 | 0 | 0 | 29 | 43 | 0 | 0 | 24 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 99 | 124 | 0 | 250 | 75 | 179 | 94 | 0 | 70 | 0 | 0 | 113 | 622 | 225 | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 8819 | 3721 | 12540 | 4133 | 798 | 2060 | 862 | 3058 | 797 | 123 | 224 | 337 | 148 | 0 | 0 | 89.12
3:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 411 | 337 |  | 0 | 225 | 285 | 78 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 87 | 37 | 22 | 39 | 0 | 0 | 0 | 300 | 300 | 202 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 148 | 130 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 51 | 75 | 0 | 120 | 0 | 22 | 10 | 280 | 24 | 11 | 110 | 275 | 162 | 82 | 115 | 82 | 60 | 0 | 90 | 100 | 113 | 400 | 56 | 105 | 105 | 0 | 176 | 54 | 103 | 0 | 38 | 50 | 400 | 94 | 0 | 54 | 108 | 0 | 35 | 0 | 106 | 55 | 0 |  | 798 | 0 | 140 | 0 | 16 | 222 | 0 | 0 | 32 | 0 | 8 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 24 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 119 | 0 | 250 | 75 | 50 | 94 | 0 | 70 | 0 | 0 | 113 | 600 | 223 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 8696 | 3388 | 12084 | 4122 | 798 | 2093 | 486 | 3023 | 775 | 123 | 222 | 294 | 148 | 0 | 0 | 89.12
4:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 411 | 331 |  | 0 | 225 | 270 | 78 | 0 | 50 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 87 | 37 | 22 | 40 | 0 | 0 | 0 | 300 | 300 | 207 | 8 | 134 | 15 | 5 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 144 | 134 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 52 | 75 | 0 | 120 | 0 | 22 | 10 | 275 | 24 | 11 | 0 | 273 | 55 | 81 | 115 | 82 | 69 | 0 | 90 | 100 | 117 | 400 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 38 | 50 | 400 | 94 | 0 | 54 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 798 | 0 | 170 | 0 | 16 | 220 | 0 | 0 | 32 | 0 | 8 | 88 | 29 | 16 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 24 | 0 | 36 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 121 | 0 | 251 | 75 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 580 | 223 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 8460 | 3352 | 11812 | 4166 | 798 | 2069 | 218 | 3025 | 755 | 123 | 220 | 294 | 144 | 0 | 0 | 89.12
5:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 410 | 339 |  | 0 | 225 | 237 | 78 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 87 | 37 | 22 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 134 | 132 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 51 | 75 | 0 | 120 | 0 | 22 | 10 | 265 | 24 | 11 | 0 | 273 | 0 | 0 | 115 | 0 | 78 | 0 | 90 | 100 | 128 | 399 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 38 | 50 | 390 | 94 | 0 | 54 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 815 | 0 | 175 | 0 | 16 | 223 | 0 | 0 | 7 | 0 | 8 | 87 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 144 | 0 | 300 | 75 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 560 | 221 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 8171 | 3351 | 11522 | 4067 | 815 | 2079 | 0 | 3050 | 735 | 123 | 351 | 296 | 134 | 0 | 0 | 89.12
6:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 400 | 342 |  | 0 | 225 | 268 | 78 | 0 | 55 | 250 | 0 | 0 | 73 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 37 | 20 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 126 | 121 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 52 | 75 | 0 | 90 | 0 | 22 | 10 | 270 | 24 | 11 | 0 | 145 | 0 | 0 | 115 | 0 | 79 | 0 | 76 | 85 | 128 | 369 | 56 | 105 | 105 | 0 | 80 | 54 | 95 | 0 | 38 | 50 | 361 | 94 | 1 | 54 | 90 | 0 | 35 | 1 | 95 | 55 | 0 |  | 816 | 0 | 190 | 0 | 16 | 223 | 0 | 0 | 0 | 0 | 8 | 87 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 178 | 0 | 300 | 35 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 500 | 165 | 0 | 0 | 0 | 4 | 35 | 0 | 0 |  | 7474 | 3212 | 10686 | 3922 | 816 | 2059 | 0 | 2542 | 675 | 123 | 353 | 194 | 126 | 6 | 0 | 89.12
7:00 | 0 | 0 | 0 | 180 | 200 | 59 | 0 | 403 | 337 |  | 0 | 225 | 240 | 78 | 0 | 55 | 250 | 0 | 0 | 20 | 50 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 37 | 20 | 38 | 0 | 0 | 0 | 300 | 300 | 213 | 8 | 145 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 118 | 108 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 51 | 75 | 0 | 90 | 0 | 23 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 115 | 0 | 76 | 2 | 90 | 100 | 100 | 370 | 56 | 105 | 105 | 1 | 45 | 54 | 92 | 0 | 38 | 50 | 370 | 75 | 7 | 54 | 90 | 0 | 35 | 7 | 95 | 34 | 0 |  | 910 | 0 | 200 | 0 | 16 | 190 | 0 | 0 | 0 | 0 | 8 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 183 | 0 | 300 | 17 | 0 | 94 | 0 | 70 | 0 | 0 | 70 | 460 | 165 | 0 | 0 | 1 | 24 | 35 | 0 | 0 |  | 7182 | 3205 | 10387 | 3947 | 910 | 2032 | 0 | 2228 | 635 | 123 | 320 | 162 | 118 | 42 | 0 | 89.12
8:00 | 0 | 0 | 0 | 180 | 200 | 62 | 0 | 411 | 303 |  | 0 | 225 | 265 | 78 | 0 | 55 | 250 | 0 | 0 | 20 | 50 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 37 | 20 | 6 | 0 | 0 | 0 | 355 | 305 | 210 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 124 | 108 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 50 | 75 | 0 | 90 | 0 | 23 | 10 | 280 | 24 | 11 | 0 | 55 | 0 | 0 | 115 | 0 | 78 | 8 | 90 | 100 | 108 | 370 | 56 | 105 | 105 | 2 | 45 | 54 | 92 | 0 | 38 | 50 | 370 | 89 | 16 | 54 | 90 | 0 | 35 | 7 | 95 | 34 | 0 |  | 911 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 350 | 17 | 0 | 94 | 0 | 70 | 0 | 1 | 70 | 410 | 201 | 0 | 0 | 2 | 38 | 34 | 0 | 0 |  | 7220 | 3164 | 10384 | 3983 | 911 | 2075 | 0 | 2241 | 585 | 125 | 250 | 146 | 124 | 74 | 0 | 89.12
9:00 | 0 | 0 | 0 | 180 | 40 | 62 | 0 | 410 | 348 |  | 0 | 225 | 281 | 79 | 0 | 55 | 335 | 0 | 0 | 23 | 65 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 15 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 1 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 37 | 20 | 4 | 0 | 0 | 0 | 300 | 320 | 201 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 16 | 20 | 130 | 72 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 51 | 75 | 0 | 120 | 0 | 23 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 115 | 0 | 78 | 12 | 76 | 100 | 122 | 401 | 56 | 105 | 105 | 2 | 50 | 54 | 92 | 0 | 38 | 50 | 400 | 94 | 21 | 54 | 90 | 0 | 35 | 13 | 95 | 34 | 0 |  | 910 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 171 | 0 | 414 | 17 | 0 | 94 | 0 | 70 | 0 | 0 | 90 | 410 | 226 | 0 | 0 | 2 | 29 | 34 | 0 | 0 |  | 7334 | 3267 | 10601 | 3891 | 910 | 2253 | 0 | 2331 | 585 | 123 | 250 | 178 | 130 | 80 | 0 | 89.12
10:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 411 | 312 |  | 0 | 225 | 300 | 79 | 0 | 55 | 335 | 0 | 0 | 55 | 94 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 23 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 54 | 37 | 20 | 2 | 0 | 0 | 0 | 300 | 340 | 199 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 18 | 20 | 124 | 72 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 50 | 75 | 0 | 120 | 0 | 23 | 10 | 300 | 24 | 11 | 0 | 230 | 0 | 0 | 114 | 0 | 79 | 19 | 76 | 100 | 127 | 402 | 56 | 105 | 105 | 4 | 201 | 54 | 92 | 0 | 38 | 50 | 400 | 94 | 22 | 54 | 90 | 0 | 35 | 13 | 95 | 34 | 0 |  | 874 | 0 | 190 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 85 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 181 | 0 | 414 | 55 | 0 | 94 | 0 | 63 | 0 | 1 | 113 | 400 | 224 | 0 | 0 | 0 | 24 | 34 | 0 | 0 |  | 7799 | 3252 | 11051 | 3860 | 874 | 2213 | 0 | 2833 | 575 | 123 | 250 | 245 | 124 | 84 | 0 | 89.12
11:00 | 0 | 0 | 0 | 180 | 20 | 59 | 0 | 411 | 312 |  | 0 | 225 | 285 | 79 | 0 | 55 | 331 | 0 | 0 | 86 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 5 | 15 | 25 | 27 | 33 | 25 | 44 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 78 | 37 | 20 | 2 | 0 | 0 | 0 | 300 | 320 | 188 | 8 | 137 | 15 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 18 | 18 | 132 | 72 | 0 | 22 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 60 | 75 | 0 | 120 | 0 | 23 | 10 | 300 | 24 | 11 | 0 | 240 | 21 | 50 | 114 | 50 | 76 | 12 | 76 | 68 | 135 | 401 | 55 | 105 | 105 | 4 | 207 | 54 | 92 | 0 | 38 | 50 | 400 | 75 | 17 | 72 | 90 | 0 | 35 | 11 | 96 | 34 | 0 |  | 874 | 0 | 180 | 0 | 16 | 210 | 0 | 0 | 0 | 0 | 8 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 177 | 0 | 414 | 73 | 0 | 94 | 0 | 70 | 0 | 1 | 113 | 400 | 225 | 0 | 0 | 4 | 38 | 34 | 0 | 0 |  | 7904 | 3442 | 11346 | 3846 | 874 | 2208 | 121 | 2846 | 575 | 126 | 398 | 320 | 132 | 88 | 0 | 89.11
12:00 | 0 | 0 | 0 | 180 | 35 | 59 | 0 | 410 | 326 |  | 0 | 225 | 295 | 79 | 0 | 55 | 333 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 79 | 30 | 20 | 4 | 0 | 0 | 0 | 300 | 335 | 187 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 7 | 0 | 19 | 8 | 8 | 18 | 134 | 72 | 0 | 22 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 58 | 78 | 0 | 120 | 0 | 25 | 9 | 300 | 24 | 11 | 0 | 228 | 125 | 85 | 114 | 82 | 78 | 12 | 76 | 68 | 137 | 403 | 55 | 105 | 105 | 1 | 200 | 54 | 92 | 0 | 38 | 50 | 394 | 75 | 21 | 90 | 90 | 0 | 35 | 10 | 95 | 34 | 0 |  | 874 | 0 | 175 | 0 | 16 | 214 | 0 | 0 | 0 | 0 | 8 | 83 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 171 | 0 | 414 | 75 | 0 | 94 | 0 | 70 | 0 | 1 | 113 | 420 | 224 | 0 | 0 | 5 | 51 | 34 | 0 | 0 |  | 8199 | 3506 | 11705 | 3852 | 874 | 2236 | 292 | 2914 | 595 | 125 | 427 | 367 | 134 | 102 | 0 | 89.11
13:00 | 0 | 0 | 0 | 180 | 35 | 61 | 0 | 411 | 332 |  | 0 | 225 | 265 | 79 | 0 | 55 | 335 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 80 | 30 | 20 | 7 | 0 | 0 | 0 | 300 | 305 | 187 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 33 | 0 | 19 | 8 | 6 | 18 | 138 | 71 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 58 | 78 | 0 | 120 | 0 | 25 | 9 | 305 | 24 | 11 | 40 | 228 | 154 | 85 | 114 | 82 | 78 | 8 | 64 | 68 | 138 | 402 | 55 | 105 | 105 | 0 | 212 | 54 | 92 | 0 | 38 | 50 | 400 | 75 | 18 | 90 | 90 | 0 | 35 | 17 | 95 | 0 | 0 |  | 873 | 0 | 170 | 0 | 16 | 214 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 4 | 23 | 0 | 0 | 5 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 164 | 0 | 404 | 75 | 36 | 94 | 0 | 70 | 0 | 1 | 113 | 450 | 226 | 0 | 0 | 5 | 70 | 34 | 0 | 0 |  | 8210 | 3585 | 11795 | 3801 | 873 | 2212 | 397 | 2882 | 625 | 125 | 425 | 408 | 138 | 120 | 0 | 89.11
14:00 | 0 | 0 | 0 | 180 | 70 | 65 | 0 | 413 | 332 |  | 0 | 225 | 265 | 73 | 0 | 55 | 335 | 0 | 0 | 92 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 80 | 24 | 20 | 6 | 0 | 0 | 0 | 300 | 305 | 187 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 42 | 0 | 19 | 8 | 16 | 18 | 140 | 72 | 0 | 22 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 61 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 24 | 11 | 0 | 235 | 22 | 30 | 114 | 30 | 79 | 14 | 64 | 68 | 138 | 402 | 55 | 105 | 105 | 1 | 212 | 54 | 92 | 0 | 38 | 50 | 400 | 93 | 30 | 108 | 90 | 0 | 35 | 20 | 95 | 0 | 0 |  | 874 | 0 | 165 | 0 | 16 | 216 | 0 | 0 | 0 | 0 | 8 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 6 | 23 | 0 | 0 | 16 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 162 | 0 | 404 | 90 | 0 | 94 | 0 | 70 | 0 | 1 | 113 | 430 | 226 | 0 | 0 | 2 | 14 | 34 | 0 | 0 |  | 8051 | 3496 | 11547 | 3863 | 874 | 2200 | 82 | 2930 | 605 | 123 | 428 | 431 | 140 | 83 | 0 | 89.11
15:00 | 0 | 0 | 0 | 180 | 65 | 65 | 0 | 414 | 348 |  | 0 | 225 | 280 | 72 | 0 | 55 | 335 | 0 | 0 | 99 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 16 | 49 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 79 | 24 | 20 | 6 | 0 | 0 | 0 | 300 | 320 | 189 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 42 | 0 | 22 | 8 | 25 | 20 | 138 | 71 | 0 | 22 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 62 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 24 | 11 | 0 | 255 | 87 | 70 | 115 | 30 | 78 | 17 | 76 | 68 | 138 | 401 | 55 | 88 | 105 | 1 | 212 | 46 | 92 | 0 | 38 | 50 | 400 | 75 | 13 | 108 | 90 | 0 | 35 | 18 | 94 | 0 | 0 |  | 873 | 0 | 160 | 0 | 16 | 219 | 0 | 0 | 0 | 0 | 8 | 85 | 17 | 16 | 0 | 0 | 0 | 0 | 6 | 23 | 0 | 0 | 16 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 156 | 0 | 386 | 93 | 0 | 94 | 0 | 70 | 0 | 4 | 113 | 440 | 224 | 0 | 0 | 1 | 13 | 34 | 0 | 0 |  | 8185 | 3478 | 11663 | 3875 | 873 | 2209 | 187 | 2926 | 615 | 122 | 431 | 431 | 138 | 68 | 0 | 89.11
16:00 | 0 | 0 | 0 | 180 | 124 | 65 | 0 | 405 | 351 |  | 0 | 225 | 250 | 79 | 0 | 55 | 336 | 0 | 35 | 99 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 10 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 79 | 25 | 20 | 4 | 0 | 0 | 0 | 300 | 305 | 189 | 8 | 136 | 15 | 5 | 0 | 51 | 0 | 42 | 0 | 22 | 11 | 27 | 20 | 136 | 70 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 22 | 10 | 280 | 24 | 11 | 0 | 260 | 15 | 30 | 116 | 0 | 77 | 6 | 76 | 68 | 138 | 400 | 55 | 90 | 105 | 0 | 212 | 54 | 92 | 0 | 55 | 50 | 400 | 75 | 18 | 108 | 90 | 0 | 35 | 7 | 95 | 9 | 0 |  | 871 | 0 | 160 | 0 | 16 | 221 | 0 | 0 | 17 | 0 | 8 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 152 | 0 | 385 | 92 | 0 | 94 | 0 | 70 | 0 | 2 | 113 | 450 | 224 | 0 | 0 | 1 | 22 | 34 | 0 | 0 |  | 8106 | 3509 | 11615 | 3954 | 871 | 2171 | 45 | 2934 | 625 | 121 | 435 | 481 | 136 | 56 | 0 | 89.11
17:00 | 0 | 0 | 0 | 180 | 175 | 62 | 0 | 412 | 341 |  | 0 | 225 | 140 | 79 | 0 | 55 | 280 | 0 | 62 | 80 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 76 | 35 | 21 | 8 | 0 | 0 | 0 | 300 | 305 | 192 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 31 | 20 | 138 | 71 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 24 | 10 | 270 | 24 | 11 | 0 | 258 | 0 | 0 | 116 | 0 | 89 | 3 | 50 | 105 | 140 | 401 | 55 | 70 | 85 | 1 | 213 | 35 | 85 | 0 | 85 | 50 | 400 | 72 | 12 | 152 | 90 | 0 | 35 | 1 | 96 | 36 | 0 |  | 869 | 0 | 160 | 0 | 16 | 150 | 0 | 0 | 23 | 0 | 8 | 84 | 19 | 0 | 0 | 0 | 0 | 0 | 26 | 22 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 376 | 53 | 0 | 50 | 0 | 87 | 0 | 1 | 70 | 440 | 222 | 0 | 0 | 0 | 17 | 34 | 0 | 0 |  | 8009 | 3258 | 11267 | 3985 | 869 | 2038 | 0 | 2894 | 615 | 121 | 320 | 422 | 138 | 35 | 0 | 89.11
18:00 | 0 | 0 | 0 | 180 | 240 | 62 | 0 | 402 | 303 |  | 0 | 225 | 140 | 79 | 0 | 55 | 280 | 0 | 0 | 60 | 94 | 98 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 27 | 33 | 25 | 49 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 76 | 36 | 21 | 12 | 0 | 0 | 0 | 300 | 310 | 190 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 31 | 20 | 128 | 71 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 40 | 50 | 0 | 120 | 0 | 24 | 10 | 300 | 24 | 11 | 0 | 253 | 0 | 0 | 181 | 0 | 133 | 0 | 50 | 186 | 145 | 362 | 93 | 70 | 68 | 0 | 287 | 35 | 68 | 0 | 85 | 50 | 350 | 72 | 3 | 162 | 68 | 0 | 35 | 1 | 94 | 46 | 0 |  | 869 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 22 | 0 | 8 | 84 | 20 | 0 | 0 | 0 | 0 | 0 | 27 | 22 | 0 | 0 | 24 | 0 | 22 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 334 | 53 | 0 | 50 | 0 | 105 | 0 | 0 | 50 | 470 | 167 | 0 | 0 | 0 | 3 | 90 | 0 | 0 |  | 8039 | 3199 | 11238 | 3855 | 869 | 1904 | 0 | 3193 | 645 | 122 | 250 | 395 | 128 | 7 | 0 | 89.1
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 62 | 0 | 392 | 300 |  | 0 | 225 | 148 | 79 | 0 | 55 | 336 | 0 | 0 | 72 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 53 | 51 | 20 | 85 | 36 | 21 | 11 | 0 | 0 | 0 | 300 | 325 | 202 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 148 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 62 | 84 | 0 | 120 | 0 | 24 | 10 | 290 | 24 | 11 | 32 | 243 | 92 | 85 | 180 | 60 | 133 | 0 | 76 | 200 | 143 | 400 | 93 | 90 | 80 | 0 | 300 | 43 | 81 | 0 | 92 | 50 | 394 | 80 | 0 | 162 | 76 | 0 | 35 | 0 | 107 | 55 | 0 |  | 868 | 0 | 160 | 0 | 49 | 145 | 0 | 0 | 26 | 0 | 40 | 84 | 29 | 16 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 36 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 156 | 0 | 380 | 55 | 3 | 64 | 15 | 105 | 0 | 0 | 90 | 510 | 221 | 0 | 11 | 0 | 0 | 90 | 0 | 0 |  | 8956 | 3675 | 12631 | 4129 | 868 | 2043 | 272 | 3535 | 685 | 123 | 283 | 683 | 148 | 0 | 0 | 89.1
19:30 | 0 | 0 | 0 | 180 | 280 | 66 | 0 | 336 | 300 |  | 0 | 225 | 145 | 80 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 53 | 51 | 20 | 85 | 36 | 21 | 19 | 0 | 0 | 0 | 300 | 300 | 205 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 56 | 84 | 0 | 120 | 0 | 24 | 10 | 310 | 24 | 11 | 200 | 243 | 202 | 80 | 180 | 80 | 133 | 0 | 76 | 200 | 144 | 402 | 93 | 105 | 105 | 0 | 295 | 54 | 110 | 0 | 95 | 50 | 400 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 115 | 55 | 0 |  | 851 | 0 | 160 | 0 | 49 | 180 | 0 | 0 | 45 | 0 | 40 | 84 | 28 | 16 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 38 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 50 | 158 | 0 | 380 | 93 | 130 | 94 | 15 | 105 | 0 | 0 | 113 | 590 | 221 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 9346 | 4127 | 13473 | 4058 | 851 | 2071 | 742 | 3775 | 765 | 123 | 376 | 762 | 146 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 337 | 300 |  | 0 | 225 | 125 | 79 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 60 | 51 | 20 | 83 | 37 | 21 | 24 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 57 | 84 | 0 | 120 | 0 | 24 | 10 | 300 | 24 | 11 | 200 | 248 | 205 | 80 | 180 | 80 | 132 | 0 | 76 | 200 | 143 | 400 | 93 | 105 | 97 | 0 | 295 | 54 | 110 | 0 | 94 | 50 | 401 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 851 | 0 | 160 | 0 | 49 | 222 | 0 | 0 | 34 | 0 | 40 | 86 | 28 | 17 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 50 | 159 | 0 | 380 | 93 | 159 | 94 | 15 | 105 | 0 | 0 | 113 | 600 | 225 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 9270 | 4215 | 13485 | 4023 | 851 | 2051 | 774 | 3769 | 775 | 124 | 429 | 750 | 146 | 0 | 0 | 89.1
21:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 292 | 303 |  | 0 | 225 | 125 | 80 | 0 | 55 | 250 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 60 | 51 | 20 | 84 | 37 | 21 | 25 | 0 | 0 | 0 | 280 | 270 | 208 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 59 | 86 | 0 | 120 | 0 | 24 | 10 | 290 | 16 | 11 | 200 | 260 | 306 | 80 | 179 | 81 | 133 | 0 | 76 | 200 | 142 | 401 | 93 | 105 | 88 | 0 | 300 | 54 | 110 | 0 | 97 | 50 | 400 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 851 | 0 | 160 | 0 | 49 | 220 | 0 | 0 | 38 | 0 | 40 | 85 | 27 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 40 | 159 | 0 | 380 | 93 | 136 | 94 | 15 | 105 | 0 | 0 | 113 | 622 | 224 | 0 | 35 | 0 | 0 | 90 | 0 | 0 |  | 9204 | 4249 | 13453 | 3881 | 851 | 2045 | 843 | 3779 | 798 | 124 | 439 | 766 | 146 | 0 | 0 | 89.1
22:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 270 | 235 |  | 0 | 225 | 120 | 79 | 0 | 55 | 250 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 60 | 51 | 20 | 86 | 37 | 21 | 34 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 135 | 30 | 5 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 142 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 60 | 86 | 0 | 120 | 0 | 24 | 10 | 260 | 16 | 11 | 200 | 260 | 201 | 80 | 179 | 81 | 132 | 0 | 76 | 200 | 138 | 400 | 93 | 105 | 102 | 0 | 300 | 54 | 110 | 0 | 98 | 50 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 112 | 55 | 0 |  | 855 | 0 | 165 | 0 | 49 | 222 | 0 | 0 | 38 | 0 | 40 | 86 | 27 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 50 | 161 | 0 | 385 | 93 | 182 | 94 | 15 | 105 | 0 | 0 | 113 | 622 | 227 | 0 | 35 | 0 | 0 | 90 | 0 | 0 |  | 9005 | 4331 | 13336 | 3888 | 855 | 1959 | 794 | 3787 | 798 | 125 | 442 | 766 | 142 | 0 | 0 | 89.1
23:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 288 | 200 |  | 0 | 225 | 115 | 80 | 0 | 55 | 230 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 5 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 20 | 87 | 37 | 22 | 38 | 0 | 0 | 0 | 280 | 270 | 206 | 8 | 135 | 35 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 56 | 86 | 0 | 120 | 0 | 24 | 10 | 280 | 23 | 11 | 160 | 257 | 190 | 80 | 178 | 81 | 133 | 0 | 76 | 200 | 140 | 402 | 93 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 97 | 50 | 400 | 95 | 0 | 162 | 90 | 0 | 35 | 0 | 115 | 55 | 0 |  | 854 | 0 | 165 | 0 | 49 | 221 | 0 | 0 | 38 | 0 | 40 | 84 | 30 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 50 | 162 | 0 | 380 | 93 | 185 | 94 | 15 | 105 | 0 | 0 | 113 | 622 | 222 | 0 | 35 | 0 | 0 | 90 | 0 | 0 |  | 8949 | 4322 | 13271 | 3891 | 854 | 1936 | 746 | 3799 | 797 | 124 | 440 | 757 | 146 | 0 | 0 | 89.1
24:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 294 | 201 |  | 0 | 225 | 110 | 81 | 0 | 55 | 150 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 20 | 87 | 37 | 22 | 39 | 0 | 0 | 0 | 280 | 270 | 207 | 8 | 122 | 35 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 142 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 51 | 86 | 0 | 120 | 0 | 24 | 10 | 320 | 23 | 11 | 200 | 260 | 300 | 80 | 116 | 80 | 99 | 0 | 76 | 200 | 138 | 401 | 56 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 91 | 50 | 400 | 94 | 0 | 54 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 855 | 0 | 165 | 0 | 16 | 222 | 0 | 0 | 38 | 0 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 8 | 24 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 79 | 162 | 0 | 381 | 93 | 187 | 94 | 32 | 104 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 34 | 0 | 0 |  | 8807 | 4280 | 13087 | 3802 | 855 | 1972 | 926 | 3501 | 797 | 125 | 437 | 745 | 142 | 0 | 0 | 89.1
KWH | 0 | 0 | 0 | 4334400 | 3952709 | 1451091 | 0 | 9363460 | 7496000 |  | 0 | 5088550 | 5420305 | 1890240 | 0 | 1333332 | 7370458 | 0 | 83000 | 1980480 | 2085984 | 2621280 | 0 | 0 | 0 | 0 | 1027080 | 1212314 | 854013 | 390492 | 600000 | 611820 | 824500 | 585600 | 1176480 | 0 | 2134865 | 840000 | 2200000 | 0 | 519885 | 0 | 0 | 0 | 0 |  | 554640 | 365296 | 319086 | 397440 | 1656000 | 843800 | 493296 | 513600 | 0 | 0 | 0 | 7531500 | 7393000 | 4856000 | 217454 | 3216190 | 436248 | 143520 | 0 | 1136349 | 0 | 748680 | 0 | 488124 | 240300 | 647000 | 488310 | 3373440 | 2330880 | 0 | 498960 | 6100 | 1032000 | 994456 | 804000 | 824976 | 2675945 | 0 | 1361856 | 1892160 | 0 | 2821560 | 0 | 552300 | 243180 | 7072500 | 562584 | 247000 | 1603008 | 5607816 | 2568200 | 1157988 | 3122400 | 1105239 | 2191968 | 115560 | 1847040 | 3019200 | 3194909 | 9496000 | 1552800 | 2442000 | 2443854 | 22441 | 4865127 | 1323001 | 2381125 | 0 | 1377600 | 1204800 | 9362700 | 2094720 | 195550 | 2351520 | 2234345 | 0 | 889200 | 151337 | 2447040 | 1028520 | 0 |  | 20621818 | 0 | 4070880 | 0 | 547200 | 4767360 | 0 | 0 | 391680 | 0 | 379875 | 2073435 | 544444 | 439680 | 0 | 0 | 0 | 201808 | 343379 | 794568 | 0 | 3104 | 345329 | 0 | 387800 | 484560 | 0 | 184840 | 0 | 0 | 4289400 | 0 | 0 | 0 | 0 | 500928 | 3729763 | 0 | 540480 | 4012764 | 0 | 8530072 | 1725120 | 1473421 | 2196192 | 147312 | 1925308 | 0 | 14729 | 2548128 | 13337000 | 5169355 | 0 | 254400 | 29220 | 446400 | 1202112 | 0 | 0 |  | 200825076 | 88653864 | 289478940 | 95657250 | 20621818 | 50260361 | 8448336 | 74519104 | 17626400 | 2974865 | 8497123 | 6518906 | 3373440 | 981337 | 0
Fuel Cost | 0 | 0 | 0 | 6458256 | 4427034.08 | 1929951.03 | 0 | 9831633 | 8095680 |  | 0 | 5546519.5 | 6016538.55 | 21132883.2 | 0 | 17666649 | 8254912.96 | 0 | 145250 | 28954617.6 | 29349794.88 | 42490948.8 | 0 | 0 | 0 | 0 | 13064457.6 | 16366239 | 11452314.33 | 292869 | 450000 | 0 | 0 | 0 | 20011924.8 | 0 | 576413.55 | 226800 | 4158000 | 0 | 8500119.75 | 0 | 0 | 0 | 0 |  | 7238052 | 6093137.28 | 5430843.72 | 5369414.4 | 20998080 | 9762766 | 626485.92 | 1710288 | 0 | 0 | 0 | 8359965 | 8058370 | 5632960 | 280515.66 | 3923751.8 | 492960.24 | 213844.8 | 0 | 1897702.83 | 0 | 12929703.6 | 0 | 668729.88 | 180225 | 1132250 | 366232.5 | 24221299.2 | 2540659.2 | 0 | 678585.6 | 97234 | 1413840 | 1312681.92 | 1398960 | 1427208.48 | 3077336.75 | 0 | 2642000.64 | 4314124.8 | 0 | 2849775.6 | 0 | 822927 | 481496.4 | 7072500 | 421938 | 187720 | 33599047.68 | 76546688.4 | 53829472 | 23935611.96 | 42089952 | 22845290.13 | 30358756.8 | 1350896.4 | 19061452.8 | 41242272 | 42396442.43 | 8736320 | 18882048 | 35311320 | 30914753.1 | 0 | 57116590.98 | 14407480.89 | 25311358.75 | 0 | 17757264 | 14192544 | 8613684 | 27126624 | 2825697.5 | 29840788.8 | 25426846.1 | 0 | 11612952 | 1808477.15 | 36632188.8 | 13545608.4 | 0 |  | 61865454 | 0 | 4559385.6 | 0 | 5696352 | 78661440 | 0 | 0 | 7054156.8 | 0 | 5458803.75 | 2322247.2 | 1056221.36 | 4792512 | 0 | 0 | 0 | 3384320.16 | 6005698.71 | 12427043.52 | 0 | 51402.24 | 5839513.39 | 0 | 6542186 | 1003039.2 | 0 | 139923.88 | 0 | 0 | 22690926 | 0 | 0 | 0 | 0 | 641187.84 | 65121661.98 | 0 | 11339270.4 | 4654806.24 | 0 | 8444771.28 | 23185612.8 | 30897638.37 | 25980951.36 | 2128658.4 | 24451411.6 | 0 | 162755.45 | 30934273.92 | 120166370 | 5272742.1 | 0 | 1882560 | 330478.2 | 5236272 | 18428376.96 | 0 | 0 |  | 1189044801.92 | 608810424.71 | 1797855226.63 | 105174641.1 | 61865454 | 60062367.74 | 176446330.54 | 962632159.84 | 142857296 | 803213.55 | 143783101.98 | 108197551.98 | 24221299.2 | 11811810.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 35 | 59 | 0 | 410 | 326 |  | 0 | 225 | 295 | 79 | 0 | 55 | 333 | 0 | 0 | 91 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 79 | 30 | 20 | 4 | 0 | 0 | 0 | 300 | 335 | 187 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 7 | 0 | 19 | 8 | 8 | 18 | 134 | 72 | 0 | 22 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 58 | 78 | 0 | 120 | 0 | 25 | 9 | 300 | 24 | 11 | 0 | 228 | 125 | 85 | 114 | 82 | 78 | 12 | 76 | 68 | 137 | 403 | 55 | 105 | 105 | 1 | 200 | 54 | 92 | 0 | 38 | 50 | 394 | 75 | 21 | 90 | 90 | 0 | 35 | 10 | 95 | 34 | 0 |  | 874 | 0 | 175 | 0 | 16 | 214 | 0 | 0 | 0 | 0 | 8 | 83 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 171 | 0 | 414 | 75 | 0 | 94 | 0 | 70 | 0 | 1 | 113 | 420 | 224 | 0 | 0 | 5 | 51 | 34 | 0 | 0 |  | 11705 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 337 | 300 | 0 | 0 | 225 | 125 | 79 | 0 | 55 | 337 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 51 | 20 | 83 | 37 | 21 | 24 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 135 | 15 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 57 | 84 | 0 | 120 | 0 | 24 | 10 | 300 | 24 | 11 | 200 | 248 | 205 | 80 | 180 | 80 | 132 | 0 | 76 | 200 | 143 | 400 | 93 | 105 | 97 | 0 | 295 | 54 | 110 | 0 | 94 | 50 | 401 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 851 | 0 | 160 | 0 | 49 | 222 | 0 | 0 | 34 | 0 | 40 | 86 | 28 | 17 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 0 | 32 | 0 | 37 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 50 | 159 | 0 | 380 | 93 | 159 | 94 | 15 | 105 | 0 | 0 | 113 | 600 | 225 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 13485 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 412 | 330 | 0 | 0 | 225 | 150 | 80 | 0 | 55 | 0 | 0 | 0 | 100 | 95 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 51 | 20 | 90 | 37 | 22 | 30 | 0 | 0 | 0 | 300 | 330 | 215 | 8 | 136 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 21 | 11 | 33 | 21 | 165 | 120 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 60 | 84 | 0 | 120 | 0 | 25 | 10 | 341 | 24 | 11 | 200 | 260 | 300 | 100 | 180 | 80 | 134 | 0 | 76 | 200 | 143 | 400 | 93 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 94 | 50 | 400 | 95 | 0 | 162 | 106 | 0 | 35 |  | 115 | 55 |  |  | 930 | 0 | 200 | 0 | 80 | 220 | 0 | 0 | 34 | 60 | 40 | 85 | 28 | 16 | 0 | 0 | 0 | 34 | 35 | 90 | 0 | 8 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 0 | 200 | 0 | 100 | 220 | 0 | 414 | 93 | 200 | 113 | 90 | 96 | 0 | 0 | 113 | 622 | 220 |  | 35 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 412 | 330 | 0 | 0 | 225 | 125 | 80 | 0 | 55 | 0 | 0 | 0 | 100 | 95 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 80 | 37 | 22 | 10 | 0 | 0 | 0 | 300 | 300 | 215 | 8 | 135 | 30 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 143 | 120 | 0 | 22 | 1.6 | 44 | 42 | 33 | 30 | 110 | 0 | 60 | 84 | 0 | 120 | 0 | 25 | 10 | 310 | 24 | 11 | 100 | 260 | 200 | 100 | 180 | 25 | 134 | 20 | 76 | 150 | 140 | 400 | 93 | 105 | 105 | 5 | 265 | 54 | 110 | 0 | 94 | 50 | 400 | 95 | 50 | 162 | 90 | 0 | 35 | 30 | 115 | 55 |  |  | 930 | 0 | 200 | 0 | 20 | 120 | 0 | 0 | 0 | 0 | 40 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 414 | 93 | 100 | 113 | 70 | 96 | 0 | 8 | 113 | 622 | 220 |  | 35 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 404 | 335 | 0 | 0 | 225 | 120 | 67 | 0 | 55 | 0 | 0 | 0 | 14 | 70 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 13 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 14 | 32 | 19 | 14 | 0 | 0 | 0 | 280 | 270 | 212 | 8 | 122 | 31 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 31 | 20 | 112 | 95 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 40 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 23 | 0 | 0 | 100 | 0 | 0 | 114 | 0 | 78 | 0 | 76 | 68 | 76 | 400 | 56 | 90 | 105 | 2 | 125 | 54 | 73 | 0 | 48 | 50 | 400 | 85 | 12 | 54 | 90 | 0 | 35 | 5 | 116 | 55 | 0 | 0 | 910 | 0 | 185 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 8 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 165 | 0 | 406 | 22 | 0 | 35 | 0 | 70 | 0 | 2 | 70 | 450 | 203 | 0 | 0 | 0 | 46 | 34 | 0 | 0 | 0 |  |  |  |  | 97983469 |  | 0
97983469
| Minimum Generation |  | 10384 | 8:00
| Highest Generation |  | 13485 | 20:00
| Day Peak Generation |  | 11705 | 12:00
| Evening Peak Generation |  | 13485 | 20:00
| HVDC Max Flow |  | 911 | 8:00
| HVDC EvPeak Flow |  | 851 | 20:00
| Load factor L.F |  | 89.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-06-30
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11705 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10144 | MW
Evening Peak Generation : |  | 13485 | MW Hour : | 20:00 | Available Max Generation : |  | 14241 | MW
E.P. Demand (at gen end) : |  | 13485 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13900 | MW
Maximum Generation : |  | 13485 | MW Hour : | 20:00 | Reserve(Generation end) |  | 341 | MW
Total Gen. (MKWH) : |  | 289.4789 | System Load Factor : | 89.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -454 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-06-30
Actual : | 89.07 | Ft.(MSL) , | Rule curve : | 83.73 | Ft.( MSL )
Gas Consumed : | Total = | 1103.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165237008.84
: |  | Coal : | 142857296 | Oil : | 1391059144.34 | Total : | 1699153449.18
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4785.2485 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1286.5308 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1689.837 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1513.662 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1341.4579 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 987.0497 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 546.6123 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 359.3353 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 754.8456 |  |  | 0 | 0%
Total | 0 |  | 13264.5791 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bashundhara-Tongi 132 kV Ckt-1 was under shut down from 09:47 to 11:42 for C/M.
b) Aminbazar-Kallyanpur 132 kV Ckt-1 was under shut down from 10:31 to 15:19 for D/W.
c) Gallamari 132/33 kV T-1 transformer was under shut down 09:07 to 18:14 for D/W.
d) Ghorasal unit-7 GT was shut down at 09:07 and was synchronized at 10:59.
e) Ghorasal unit-7 ST was synchronized at 13:36.
f) Ghorasal unit-4 P/P-Ghorasal GIS 230 kV Ckt was under shut down from 12:30 to 15:46 for project work.
g) Kodda 132/33 kV T-3 transformer was shut down from 20:30 to 21:50 due to red hot maintained at | [5 empty] | About 20 MW power interruption occurred under
33 kV DS. | [5 empty] | Kodda S/S area from 20:30 to 21:50.
h) Hasnabad 132/33 kV T-2 transformer tripped at 20:45 showing O/C relays at 33 kV end & 33 kV | [5 empty] | About 19 MW power interruption occurred under
Dohar(PBS) feeder fault and was switched on at 21:00. | [5 empty] | Hasnabad S/S area from 20:45 to 21:00.
i) Siddhirganj EGCB 335 MW GT & ST was shut down at 00:19(29-06-2022) due to gas shortage.
j) Cox'sBazar 132/33 kV T-2 transformer was under shut down since 06:23(30-06-222) for C/M. | [5 empty] | About 36 MW power interruption occurred under
k) Cox'sBazar 132/33 kV T-1 transformer was under shut down since 06:23(30-06-222) for D/W. | [5 empty] | Cox's Bazar S/S area since 06:23.
l) Gallamari 132/33 kV T-1 transformer was under shut down since 06:13(30-06-222) for C/M.
m) Shahjibazar 132/33 kV T-4 transformer was under shut down from 07:07(30-06-222) to 07:56 | [5 empty] | About 45 MW power interruption occurred under
(30-06-222) due to red hot maintained at 33 kV DS. | [5 empty] | Shahjibazar S/S area from 07:07(30-06-2022) to 07:56.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4334400
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 3952709 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 67 | 1451091 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 337 | 9363460 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 300 | 7496000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5088550 | Gas shortage due to dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 79 | 1890240 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 5420305 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1333332
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 390492
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 83000 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 100 | 1980480
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 337 | 7370458
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2085984 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1027080
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2621280 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1212314
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 854013 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1211820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 824500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 585600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1176480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 248 | 5607816 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 205 | 2568200
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 1157988 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 80 | 1105239 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2191968 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2442000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 2094720 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2351520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 151337
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1028520
| Dhaka area Total |  |  |  | 5847 | 3796 | 82452896
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2200000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 519885
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 115560
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 843800 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 124 | 2974865 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 2443854 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 365296 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 319086 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 20 | 397440 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1847040 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 493296
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 513600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 83 | 1656000 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22441
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 295 | 4865127
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1323001
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2381125
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1204800 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2234345 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1317 | 26720561
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 4856000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7531500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7393000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 15 | 436248 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 143520 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1136349
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 3194909 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 748680
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3216190 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3019200
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 488124
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240300
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3373440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 647000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 488310 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1603008
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 1377600 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 889200 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 116 | 2447040
| Cumilla Area Total |  |  |  | 2885 | 2045 | 43447072
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2330880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 498960
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3122400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 1552800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 195550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 554640
| Mymensingh Area Total |  |  |  | 614 | 422 | 8261330
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1032000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 994456 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2675945 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 33 | 804000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 824976 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 247000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1361856
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1892160
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2821560 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 24 | 552300 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 562584 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7072500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9496000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243180
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 9362700
| Sylhet Area Total |  |  |  | 2477 | 1690 | 39943217
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 851 | 20621818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 547200 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 391680 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 222 | 4767360
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 4070880 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 379875
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 540480 | Low demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1725120 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 147312 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 446400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1514 | 33638125
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 17 | 439680 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 544444 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2073435 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 13337000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 225 | 5169355
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 254400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 973 | 21818314
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 201808 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 23 | 343379 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 3104 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 345329 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 207 | 4230691
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 159 | 4012764 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 8530072 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 387800 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 484560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 184840
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 794568 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 159 | 1473421 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2196192 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2548128
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29220
| Rajshahi Area Total |  |  |  | 2129 | 1358 | 25765876
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4289400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1925308 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 14729
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1202112 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 370 | 7431549
| Total |  |  |  | 21396 | 13485 | 289478940
| Eastern Grid Total |  |  |  | 14205 | 9270 | 200825076
| Western Grid Total |  |  |  | 7191 | 4215 | 88653864
| National Grid Total |  |  |  | 21396 | 13485 | 289478940
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-29
(a) ENTIRE EASTERN GRID : |  | 8745.7 | MW | (b) ENTIRE WESTERN GRID : |  | 4111.56 | MW
i) Dhaka area |  | 4840 | MW | i) Khulna area |  | 1573.4 | MW
ii) Chittagong area |  | 1310.7 | MW | ii) Rajshahi area |  | 1351.2 | MW
iii) Comilla area |  | 1137 | MW | iii) Barisal area |  | 390.96 | MW
iv) Mymensingh area |  | 1027 | MW | iv) Rangpur area |  | 796 | MW
v) Sylhet area |  | 431 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12857.26 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 33 | 19:00 | Hasnabad | 102 | 00:00 | Palashbari | 118 | 01:00
Agargaon | 96 | 13:00 | Hathazari | 95 | 21:00 | Panchagarh | 52 | 19:30
Agrabad | 78 | 16:00 | Ishurdi | 78 | 20:00 | Patuakhali | 118 | 00:00
AKS | 12 | 13:00 | Jaldhaka | 55 | 20:00 | Payra | 1 | 16:00
AKSML | 117 | 00:00 | Jamalpur | 140 | 20:00 | PHP | 8 | 10:00
Amnura | 54 | 22:00 | Jashore | 121 | 21:00 | Purbachal | 19 | 00:00
Ashuganj | 33 | 23:00 | Jhenaidah | 120 | 22:00 | Purbasadipur | 114 | 19:30
Bagerhat | 107 | 23:00 | Joydebpur | 202 | 22:00 | Rahim | 10 | 18:00
Bakulia | 130 | 13:00 | Joypurhat | 66 | 00:00 | Rajbari | 62 | 19:30
Banani | 60 | 13:00 | Juldah | 30 | 09:00 | Rajendrapur | 104 | 18:00
Bangabhaban | 20 | 10:00 | Kabirpur | 275 | 12:00 | Rajshahi | 154 | 22:00
Barapukuria | 51 | 00:00 | Kachua | 70 | 22:00 | Rajshahi | 41 | 00:00
Barguna | 20 | 00:00 | Kallyanpur | 102 | 00:00 | Ramganj | 100 | 19:30
Barishal | 105 | 21:00 | Kalurghat | 7 | 15:00 | Rampur | 22 | 16:00
Barishal | 66 | 19:30 | Kamrangirchar | 72 | 19:30 | Rangamati | 12 | 18:00
Baroaulia | 78 | 09:00 | Kaptai | 4 | 19:00 | Rangpur | 137 | 19:00
Baroirhat | 66 | 00:00 | Kazla | 89 | 00:00 | Ruppur | 5.2 | 15:00
Bashundhara | 167 | 12:00 | Keranigonj | 64 | 22:00 | Saidpur | 98 | 20:00
BashundharaCement | 7 | 16:00 | Khagrachori | 24 | 00:00 | Satkhira | 121 | 21:00
Beanibazar | 58 | 22:00 | Khulna | 113 | 13:00 | Satmasjid | 104 | 13:00
Benapole | 58 | 23:00 | Khulshi | 181 | 15:00 | Savar | 193 | 12:00
Bhaluka | 160 | 20:00 | Kishoreganj | 134 | 22:00 | Shahjadpur | 100 | 22:00
Bhandaria | 60 | 22:00 | Kodda | 315 | 15:00 | Shahjibazar | 110 | 22:00
Bhangura | 34 | 21:00 | KSRM | 21.5 | 11:00 | Shahmirpur | 47 | 21:00
Bheramara(GK) | 63 | 21:00 | Kulaura | 42 | 00:00 | Shariatpur | 80 | 22:00
Bhulta | 259 | 23:00 | Kurigram | 62 | 20:00 | Sherpur | 124 | 23:00
Bog-Sherpur | 64 | 22:00 | Kushtia | 142 | 19:30 | Shikalbaha | 32 | 00:00
Bogura | 168 | 22:00 | Lalbag | 98 | 13:00 | Shitalakhya | 122 | 12:00
Borhanuddin | 41 | 00:00 | Lalmonirhat | 47 | 20:00 | Sholosohor | N/A | N/A
Brahmanbaria | 170 | 00:00 | Madanganj | 98 | 21:00 | Shyampur | 176 | 10:00
BSRM | 157 | 17:00 | Madaripur | 104 | 21:00 | Siddhirganj | 116 | 12:00
Cantonment | 157 | 13:00 | Madartek | 86 | 00:00 | Sirajganj | 106 | 19:30
Chandpur | 65 | 00:00 | Madunaghat | 59 | 19:00 | Sonargaon | 88 | 23:00
Chandraghona | 30 | 00:00 | Magura | 54 | 19:00 | Sreemongol | 53 | 00:00
Chapai | 70 | 21:00 | Mahasthangarh | 66 | 00:00 | Srinagar | 45.27 | 21:00
Charsaidpur | 47 | 23:00 | Manikganj | 84 | 21:00 | SSM | 4 | 09:00
Chauddagram | 50 | 01:00 | Maniknagar | 74 | 13:00 | Sunamganj | 38 | 22:00
Chhatak | 23 | 21:00 | Matarbari | 40 | 19:30 | Sylhet | 128 | 19:00
Chowmuhani | 204 | 00:00 | Matuail | 66 | 10:00 | Tangail | 200 | 19:00
Chuadanga | 106 | 20:00 | Millgate | 60 | 11:00 | Thakurgaon | 79 | 19:30
Coxsbazar | 112 | 19:00 | Mirpur | 133 | 20:00 | TK | 29.1 | 21:00
Cumilla(N) | 145 | 21:00 | Mirsorai | N/A | N/A | Tongi | 138 | 11:00
Cumilla(S) | 160 | 00:00 | Mithapukur | 30 | 00:00 | Ullon | 46 | 00:00
Daudkandi | 146 | 21:00 | Modern | 0 | 00:00 | Uttara | 92 | 19:00
Dhaka | 40 | 12:00 | Mogbazar | 133 | 13:00 | UttaraNew | 21 | 12:00
Dhamrai | 132 | 11:00 | Mongla | 36 | 11:00 | Zigatola | 45 | 13:00
Dhanmondi | 157 | 13:00 | Motijheel | 38 | 10:00
Dohazari | 90 | 21:00 | Munshiganj | 112 | 00:00
Faridpur | 149 | 21:00 | Mymensingh | 211 | 20:00
Fatullah | 68 | 10:00 | Naogaon | 120 | 20:00
Fenchuganj | 39 | 00:00 | Narail | 49 | 23:00
Feni | 112 | 23:00 | Narinda | 72 | 16:00
Ghorashal | 69 | 00:00 | Narshingdi | 189 | 20:00
Goalpara | 29 | 21:00 | Natore | 139 | 21:00
Gollamari | 50 | 00:00 | Nawabganj | 55.6 | 21:00
Gopalganj | 100.6 | 21:00 | Netrakona | 115 | 22:00
GPH | 91 | 14:00 | New | 86 | 11:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 403 | 05:00 | 388 | 12:00 | Kaliakoir | 393 | 05:00 | 380 | 11:00
| Bibiana | 409 | 06:00 | 402 | 02:00 | Payra | 417 | 08:00 | 409 | 01:00
| BIPTC | 403 | 06:00 | 394 | 10:00
| Gopalganj_I | 413 | 06:00 | 396 | 02:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 04:00 | 216 | 10:00 | Hathazari | 237 | 20:00 | 231 | 09:00
| AKSML | 236 | 22:00 | 224 | 01:00 | Ishurdi | 233 | 06:00 | 226 | 01:00
| Aminbazar | 228 | 05:00 | 219 | 08:00 | Jhenaidah | 230 | 06:00 | 221 | 21:00
| Baghabari | 231 | 05:00 | 226 | 01:00 | Kaliakoir | 228 | 04:00 | 219 | 09:00
| Barapukuria | 230 | 06:00 | 218 | 19:30 | Keranigonj | 227 | 02:00 | 217 | 10:00
| Barishal | 233 | 07:00 | 225 | 01:00 | Khulna(S) | 238 | 18:30 | 229 | 03:00
| Bheramara | 266 | 15:00 | 228 | 08:00 | Maniknagar | 231 | 04:00 | 222 | 12:00
| Bhulta | 232 | 02:00 | 224 | 11:00 | Meghnaghat | 232 | 19:30 | 226 | 12:00
| Bibiana | 242 | 02:00 | 235 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 232 | 06:00 | 222 | 01:00 | Rajshahi | 230 | 18:00 | 220 | 10:00
| Bogura | 233 | 06:00 | 220 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 19:30 | 233 | 00:00 | Rampura | 228 | 04:00 | 222 | 11:00
| BSRM | 235 | 20:00 | 228 | 09:00 | Shikalbaha | 238 | 22:00 | 226 | 09:00
| Cumilla(N) | 231 | 06:00 | 227 | 09:00 | Shyampur | 228 | 02:00 | 219 | 10:00
| Fenchuganj | 243 | 06:00 | 238 | 11:00 | Siddhirganj | 232 | 04:00 | 225 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 08:00 | 226 | 01:00
| GPH | 235 | 20:00 | 227 | 09:00 | Tongi | 225 | 06:00 | 215 | 11:00
| Haripur | 228 | 02:00 | 223 | 11:00
| Hasnabad | 228 | 01:00 | 220 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 05:00 | 127 | 12:00 | Manikganj | 133 | 05:00 | 128 | 00:00
| Agargaon | 135 | 02:00 | 127 | 10:00 | Maniknagar | 136 | 05:00 | 129 | 12:00
| Agrabad | 137 | 00:00 | 131 | 08:00 | Matarbari | 135 | 11:00 | 118 | 03:00
| AKS | 137 | 14:00 | 132 | 08:00 | Matuail | 133 | 21:00 | 130 | 09:00
| Aminbazar | 133 | 05:00 | 126 | 08:00 | Millgate | 135 | 03:00 | 125 | 12:00
| Amnura | 133 | 18:30 | 123 | 03:00 | Mirpur | 134 | 04:00 | 125 | 09:00
| Ashuganj | 136 | 14:00 | 132 | 19:00 | Mithapukur | 139 | 06:00 | 124 | 00:00
| Bagerhat | 134 | 05:00 | 129 | 01:00 | Modern | 137 | 19:00 | 133 | 08:00
| Bakulia | 138 | 20:00 | 133 | 08:00 | Mogbazar | 135 | 01:00 | 128 | 12:00
| Banani | 133 | 06:00 | 124 | 12:00 | Mongla | 133 | 09:00 | 129 | 01:00
| Bangabhaban | 136 | 04:00 | 129 | 10:00 | Motijheel | 136 | 04:00 | 129 | 10:00
| Barapukuria | 138 | 06:00 | 130 | 00:00 | Munshiganj | 136 | 03:00 | 131 | 08:00
| Barguna | 138 | 07:00 | 133 | 00:00 | Mymensingh | 132 | 18:00 | 118 | 02:00
| Barishal | 139 | 07:00 | 133 | 01:00 | Naogaon | 130 | 06:00 | 121 | 00:00
| Barishal | 140 | 07:00 | 135 | 00:00 | Narail | 133 | 16:00 | 126 | 01:00
| Baroaulia | 140 | 20:00 | 135 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 131 | 07:00 | 127 | 00:00 | Narshingdi | 139 | 07:00 | 126 | 00:00
| Bashundhara | 135 | 04:00 | 124 | 12:00 | Natore | 135 | 07:00 | 126 | 01:00
| BashundharaCement | 134 | 00:00 | 131 | 09:00 | Nawabganj | 137 | 05:00 | 130 | 09:00
| Beanibazar | 134 | 06:00 | 129 | 19:00 | Netrakona | 132 | 06:00 | 115 | 19:00
| Benapole | 132 | 05:00 | 126 | 03:00 | New | 133 | 04:00 | 125 | 12:00
| Bhaluka | 131 | 18:00 | 112 | 19:00 | Niamatpur | 130 | 18:30 | 117 | 23:00
| Bhandaria | 136 | 08:00 | 127 | 00:00 | Noapara | 135 | 18:30 | 131 | 13:00
| Bhangura | 138 | 06:00 | 133 | 01:00 | Pabna | 135 | 06:00 | 129 | 01:00
| Bheramara | 136 | 06:00 | 132 | 01:00 | Palashbari | 132 | 05:00 | 120 | 01:00
| Bheramara(GK) | 138 | 06:00 | 132 | 19:00 | Panchagarh | 139 | 18:00 | 117 | 01:00
| Bhulta | 126 | 03:00 | 123 | 12:00 | Patuakhali | 137 | 07:00 | 133 | 00:00
| Bog-Sherpur | 135 | 07:00 | 127 | 01:00 | Payra | 138 | 06:00 | 135 | 00:00
| Bogura | 136 | 06:00 | 130 | 00:00 | PHP | 132 | 18:30 | 126 | 01:00
| Bogura | 137 | 06:00 | 128 | 01:00 | Purbachal | 135 | 05:00 | 126 | 08:00
| Brahmanbaria | 131 | 06:00 | 127 | 00:00 | Purbasadipur | 136 | 18:00 | 119 | 01:00
| Cantonment | 134 | 02:00 | 126 | 10:00 | Rahim | 135 | 05:00 | 132 | 09:00
| Chandpur | 138 | 20:00 | 134 | 03:00 | Rajbari | 134 | 06:00 | 125 | 01:00
| Chandraghona | 139 | 21:00 | 133 | 08:00 | Rajendrapur | 136 | 21:00 | 127 | 07:00
| Chapai | 133 | 18:00 | 125 | 09:00 | Rajshahi | 132 | 18:30 | 122 | 01:00
| Charsaidpur | 136 | 01:00 | 131 | 09:00 | Rajshahi | 132 | 18:00 | 124 | 10:00
| Chauddagram | 133 | 18:30 | 127 | 01:00 | Ramganj | 135 | 18:30 | 125 | 01:00
| Chhatak | 136 | 03:00 | 130 | 00:00 | Rampur | 138 | 21:00 | 132 | 08:00
| Chowmuhani | 131 | 08:00 | 123 | 01:00 | Rampura | 134 | 04:00 | 128 | 10:00
| Chuadanga | 129 | 16:00 | 121 | 01:00 | Rangamati | 138 | 18:00 | 133 | 09:00
| Coxsbazar | 130 | 06:00 | 118 | 19:00 | Rangpur | 137 | 07:00 | 121 | 01:00
| Cumilla(N) | 135 | 07:00 | 132 | 04:00 | Ruppur | 135 | 06:00 | 131 | 01:00
| Cumilla(S) | 136 | 07:00 | 127 | 00:00 | Saidpur | 136 | 18:00 | 122 | 01:00
| Daudkandi | 136 | 20:00 | 130 | 09:00 | Satkhira | 132 | 08:00 | 126 | 01:00
| Dhaka | 135 | 03:00 | 128 | 10:00 | Satmasjid | 135 | 05:00 | 126 | 10:00
| Dhamrai | 132 | 05:00 | 123 | 10:00 | Savar | 133 | 03:00 | 125 | 10:00
| Dhanmondi | 135 | 04:00 | 130 | 11:00 | Shahjadpur | 140 | 04:00 | 134 | 12:00
| Dohazari | 135 | 18:30 | 132 | 01:00 | Shahjibazar | 135 | 14:00 | 130 | 00:00
| Faridpur | 133 | 07:00 | 126 | 01:00 | Shahmirpur | 139 | 21:00 | 131 | 09:00
| Fatullah | 136 | 02:00 | 130 | 09:00 | Shariatpur | 136 | 07:00 | 128 | 01:00
| Fenchuganj | 138 | 06:00 | 134 | 19:00 | Sherpur | 137 | 18:00 | 119 | 03:00
| Feni | 133 | 18:00 | 127 | 02:00 | Shikalbaha | 140 | 20:00 | 134 | 08:00
| Ghorashal | 138 | 13:00 | 135 | 01:00 | Shikalbaha | 139 | 05:00 | 133 | 09:00
| Goalpara | 137 | 18:30 | 133 | 01:00 | Shitalakhya | 137 | 05:00 | 131 | 12:00
| Gollamari | 133 | 16:00 | 124 | 01:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gopalganj | 134 | 06:00 | 126 | 02:00 | Shyampur | 134 | 22:00 | 129 | 09:00
| Gopalganj_I | 137 | 20:00 | 130 | 02:00 | Shyampur | 135 | 01:00 | 129 | 09:00
| Gulshan | 135 | 05:00 | 127 | 12:00 | Siddhirganj | 134 | 01:00 | 131 | 09:00
| Halishahar | 138 | 05:00 | 132 | 08:00 | Sirajganj | 135 | 06:00 | 129 | 01:00
| Haripur | 135 | 22:00 | 132 | 09:00 | Sonargaon | 135 | 00:00 | 131 | 11:00
| HaripurSBU | 135 | 22:00 | 131 | 12:00 | Sreemongol | 137 | 07:00 | 134 | 00:00
| Hasnabad | 137 | 02:00 | 132 | 08:00 | Srinagar | 136 | 04:00 | 130 | 10:00
| Hathazari | 140 | 22:00 | 135 | 02:00 | SSM | 141 | 22:00 | 136 | 10:00
| Ish-D | 136 | 18:00 | 131 | 01:00 | Sunamganj | 135 | 06:00 | 129 | 19:30
| Ishurdi | 135 | 05:00 | 121 | 01:00 | Sylhet | 135 | 07:00 | 132 | 00:00
| Jaldhaka | 140 | 18:30 | 121 | 03:00 | Tangail | 136 | 18:00 | 128 | 00:00
| Jamalpur | 132 | 06:00 | 128 | 01:00 | Thakurgaon | 137 | 18:00 | 117 | 01:00
| Jashore | 135 | 06:00 | 129 | 01:00 | TK | 139 | 20:00 | 132 | 08:00
| Jhenaidah | 135 | 06:00 | 129 | 00:00 | Tongi | 134 | 06:00 | 127 | 11:00
| Jhenaidah | 140 | 03:00 | 134 | 07:00 | Ullon | 135 | 05:00 | 127 | 11:00
| Joydebpur | 131 | 18:30 | 120 | 00:00 | Uttara | 133 | 04:00 | 125 | 09:00
| Joypurhat | 139 | 22:00 | 134 | 15:00 | UttaraNew | 133 | 03:00 | 125 | 09:00
| Juldah | 137 | 06:00 | 122 | 12:00 | Zigatola | 138 | 04:00 | 130 | 10:00
| Kabirpur | 135 | 17:00 | 130 | 03:00
| Kachua | 140 | 20:00 | 126 | 11:00
| Kaliakoir | 133 | 04:00 | 126 | 09:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-06-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 50 | 8807 | 4280 | 13087 |  |  |  | QF-LDC-11
0:30 | 199 | 8934 | 4080.5 | 13014.5 | Date: | 2022-06-29
1:00 | 348 | 9061 | 3881 | 12942
1:30 | 366 | 8940 | 3801 | 12741
2:00 | 384 | 8819 | 3721 | 12540
2:30 | 419 | 8757.5 | 3554.5 | 12312 | [5 empty] | Gen. at Eve. Peak | 13485 | 13485 MW (20:00 )
3:00 | 454 | 8696 | 3388 | 12084 | [6 empty] | 20:00
3:30 | 374 | 8578 | 3370 | 11948 | [5 empty] | Gen. at Day Peak | 11705 | 11705 MW (12:00 )
4:00 | 294 | 8460 | 3352 | 11812 | [6 empty] | 12:00
4:30 | 246 | 8315.5 | 3351.5 | 11667 | [5 empty] | Highest Generation | 13485
5:00 | 198 | 8171 | 3351 | 11522 | [6 empty] | 20:00
5:30 | 104 | 7822.5 | 3281.5 | 11104
6:00 | 10 | 7474 | 3212 | 10686
6:30 | 95 | 7328 | 3208.5 | 10536.5
7:00 | 180 | 7182 | 3205 | 10387
7:30 | 214 | 7201 | 3184.5 | 10385.5
8:00 | 248 | 7220 | 3164 | 10384
8:30 | 324 | 7277 | 3215.5 | 10492.5
9:00 | 400 | 7334 | 3267 | 10601
9:30 | 320 | 7566.5 | 3259.5 | 10826
10:00 | 240 | 7799 | 3252 | 11051
10:30 | 280 | 7851.5 | 3347 | 11198.5
11:00 | 320 | 7904 | 3442 | 11346
11:30 | 273 | 8051.5 | 3474 | 11525.5
12:00 | 226 | 8199 | 3506 | 11705
12:30 | 203 | 8204.5 | 3545.5 | 11750
13:00 | 180 | 8210 | 3585 | 11795
13:30 | 139 | 8130.5 | 3540.5 | 11671
14:00 | 98 | 8051 | 3496 | 11547
14:30 | 150 | 8118 | 3487 | 11605
15:00 | 202 | 8185 | 3478 | 11663
15:30 | 216 | 8145.5 | 3493.5 | 11639
16:00 | 230 | 8106 | 3509 | 11615
16:30 | 190 | 8057.5 | 3383.5 | 11441
17:00 | 150 | 8009 | 3258 | 11267
17:30 | 148 | 8024 | 3228.5 | 11252.5
18:00 | 146 | 8039 | 3199 | 11238
18:30 | 88 | 8497.5 | 3437 | 11934.5
19:00 | 30 | 8956 | 3675 | 12631
19:30 | 106 | 9346 | 4127 | 13473
20:00 | 108 | 9270 | 4215 | 13485 |  |  |  | Executive Engineer
20:30 | 113 | 9237 | 4232 | 13469 |  |  |  | Network Operation Division
21:00 | 118 | 9204 | 4249 | 13453
21:30 | 82 | 9104.5 | 4290 | 13394.5
22:00 | 46 | 9005 | 4331 | 13336 |  |  |  |  | Page 6 of 7
22:30 | 31 | 8977 | 4326.5 | 13303.5
23:00 | 16 | 8949 | 4322 | 13271
23:30 | 33 | 8878 | 4301 | 13179
24:00 | 50 | 8807 | 4280 | 13087
13485 MW (20:00 )
11705 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-29 |  | Energy |  | 289478940
[13 empty] | 2022-06-29 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3802 | 855 | 1972 | 926 | 3501 | 797 | 125 | 437 | 745 | 142 | 0 | 0
0:30 | 3963 | 826.5 | 2062.5 | 938 | 3345 | 796.5 | 124 | 330 | 589.5 | 147 | 0 | 0 | Date: | 2022-06-29
1:00 | 4124 | 798 | 2153 | 950 | 3189 | 796 | 123 | 223 | 434 | 152 | 0 | 0
1:30 | 4128.5 | 798 | 2106.5 | 906 | 3123.5 | 796.5 | 123 | 223.5 | 385.5 | 150 | 0 | 0 | [7 empty] | Total Energy | 289.4789 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 4133 | 798 | 2060 | 862 | 3058 | 797 | 123 | 224 | 337 | 148 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4127.5 | 798 | 2076.5 | 674 | 3040.5 | 786 | 123 | 223 | 315.5 | 148 | 0 | 0 | [7 empty] | Energy Requirement | 289.4789
3:00 | 4122 | 798 | 2093 | 486 | 3023 | 775 | 123 | 222 | 294 | 148 | 0 | 0
3:30 | 4144 | 798 | 2081 | 352 | 3024 | 765 | 123 | 221 | 294 | 146 | 0 | 0 | [5 empty] | Shortage
4:00 | 4166 | 798 | 2069 | 218 | 3025 | 755 | 123 | 220 | 294 | 144 | 0 | 0
4:30 | 4116.5 | 806.5 | 2074 | 109 | 3037.5 | 745 | 123 | 285.5 | 295 | 139 | 0 | 0
5:00 | 4067 | 815 | 2079 | 0 | 3050 | 735 | 123 | 351 | 296 | 134 | 0 | 0
5:30 | 3994.5 | 815.5 | 2069 | 0 | 2796 | 705 | 123 | 352 | 245 | 130 | 3 | 0
6:00 | 3922 | 816 | 2059 | 0 | 2542 | 675 | 123 | 353 | 194 | 126 | 6 | 0
6:30 | 3934.5 | 863 | 2045.5 | 0 | 2385 | 655 | 123 | 336.5 | 178 | 122 | 24 | 0 |  |  |  | Coal
7:00 | 3947 | 910 | 2032 | 0 | 2228 | 635 | 123 | 320 | 162 | 118 | 42 | 0
7:30 | 3965 | 910.5 | 2053.5 | 0 | 2234.5 | 610 | 124 | 285 | 154 | 121 | 58 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3983 | 911 | 2075 | 0 | 2241 | 585 | 125 | 250 | 146 | 124 | 74 | 0
8:30 | 3937 | 910.5 | 2164 | 0 | 2286 | 585 | 124 | 250 | 162 | 127 | 77 | 0
9:00 | 3891 | 910 | 2253 | 0 | 2331 | 585 | 123 | 250 | 178 | 130 | 80 | 0
9:30 | 3875.5 | 892 | 2233 | 0 | 2582 | 580 | 123 | 250 | 211.5 | 127 | 82 | 0
10:00 | 3860 | 874 | 2213 | 0 | 2833 | 575 | 123 | 250 | 245 | 124 | 84 | 0
10:30 | 3853 | 874 | 2210.5 | 60.5 | 2839.5 | 575 | 124.5 | 324 | 282.5 | 128 | 86 | 0
11:00 | 3846 | 874 | 2208 | 121 | 2846 | 575 | 126 | 398 | 320 | 132 | 88 | 0
11:30 | 3849 | 874 | 2222 | 206.5 | 2880 | 585 | 125.5 | 412.5 | 343.5 | 133 | 95 | 0
12:00 | 3852 | 874 | 2236 | 292 | 2914 | 595 | 125 | 427 | 367 | 134 | 102 | 0
12:30 | 3826.5 | 873.5 | 2224 | 344.5 | 2898 | 610 | 125 | 426 | 387.5 | 136 | 111 | 0
13:00 | 3801 | 873 | 2212 | 397 | 2882 | 625 | 125 | 425 | 408 | 138 | 120 | 0
13:30 | 3801 | 873 | 2212 | 397 | 2882 | 625 | 125 | 425 | 408 | 138 | 120 | 0
14:00 | 3801 | 873 | 2212 | 397 | 2882 | 625 | 125 | 425 | 408 | 138 | 120 | 0
14:30 | 3838 | 873 | 2210.5 | 292 | 2904 | 620 | 123.5 | 428 | 419.5 | 138 | 94 | 0
15:00 | 3875 | 873 | 2209 | 187 | 2926 | 615 | 122 | 431 | 431 | 138 | 68 | 0
15:30 | 3914.5 | 872 | 2190 | 116 | 2930 | 620 | 121.5 | 433 | 456 | 137 | 62 | 0
16:00 | 3954 | 871 | 2171 | 45 | 2934 | 625 | 121 | 435 | 481 | 136 | 56 | 0
16:30 | 3985 | 870 | 2104.5 | 22.5 | 2914 | 620 | 121 | 377.5 | 451.5 | 137 | 45.5 | 0
17:00 | 3985 | 869 | 2038 | 0 | 2894 | 615 | 121 | 320 | 422 | 138 | 35 | 0
17:30 | 3920 | 869 | 1971 | 0 | 3043.5 | 630 | 121.5 | 285 | 408.5 | 133 | 21 | 0
18:00 | 3855 | 869 | 1904 | 0 | 3193 | 645 | 122 | 250 | 395 | 128 | 7 | 0
18:30 | 3992 | 868.5 | 1973.5 | 136 | 3364 | 665 | 122.5 | 266.5 | 539 | 138 | 3.5 | 0
19:00 | 4129 | 868 | 2043 | 272 | 3535 | 685 | 123 | 283 | 683 | 148 | 0 | 0
19:30 | 4058 | 851 | 2071 | 742 | 3775 | 765 | 123 | 376 | 762 | 146 | 0 | 0
20:00 | 4023 | 851 | 2051 | 774 | 3769 | 775 | 124 | 429 | 750 | 146 | 0 | 0
20:30 | 3952 | 851 | 2048 | 808.5 | 3774 | 786.5 | 124 | 434 | 758 | 146 | 0 | 0
21:00 | 3881 | 851 | 2045 | 843 | 3779 | 798 | 124 | 439 | 766 | 146 | 0 | 0
21:30 | 3884.5 | 853 | 2002 | 818.5 | 3783 | 798 | 124.5 | 440.5 | 766 | 144 | 0 | 0
22:00 | 3888 | 855 | 1959 | 794 | 3787 | 798 | 125 | 442 | 766 | 142 | 0 | 0
22:30 | 3889.5 | 854.5 | 1947.5 | 770 | 3793 | 797.5 | 124.5 | 441 | 761.5 | 144 | 0 | 0
23:00 | 3891 | 854 | 1936 | 746 | 3799 | 797 | 124 | 440 | 757 | 146 | 0 | 0
23:30 | 3846.5 | 854.5 | 1954 | 836 | 3650 | 797 | 124.5 | 438.5 | 751 | 144 | 0 | 0 | Max Temp. in Dhaka |  | 32.7° C
24:00 | 3802 | 855 | 1972 | 926 | 3501 | 797 | 125 | 437 | 745 | 142 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 90 | 88 | 88 | 91 | 90 | 90 | 88 | 87 | 86 | 86 | 87 |  | 88 | 88 | 89 | 89 | 90 | 89 | 90 | 2134865
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 |  |  |  | 1 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 519885
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 12 | 19 | 12 | 12 | 8 | 14 | 17 | 6 | 3 | 0 | [8 empty] | 115560
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 319086
12 | Hathazari 100 MW peaking PP | 51 | [18 empty] | 53 | 53 | 60 | 60 | 60 | 51 | 51 | 365296
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 68 |  | 80 | 105 | 97 | 88 | 102 | 105 | 105 | 2443854
| Daudkandi 200 MW PP (B.Trac) | 200 | 200 | 110 | [8 empty] | 0 | 40 | 0 | [5 empty] | 32 | 200 | 200 | 200 | 200 | 160 | 200 | 1603008
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 41 | [7 empty] | 7 | 33 | 42 | 42 | 42 | 50 | 50 |  | 50 | 50 | 50 | 50 | 49 | 50 | 50 | 748680
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [15 empty] | 35 | 62 | 0 | [7 empty] | 0 | 83000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 250 | 250 | 250 | 335 | 335 | 331 | 333 | 335 | 335 | 335 | 336 | 280 | 280 |  | 336 | 335 | 337 | 250 | 250 | 230 | 150 | 7370458
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 263 | 275 | 273 | 273 | 145 | 45 | 55 | 95 | 230 | 240 | 228 | 228 | 235 | 255 | 260 | 258 | 253 |  | 243 | 243 | 248 | 260 | 260 | 257 | 260 | 5607816
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4334400
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 40 | 0 | 20 | 35 | 35 | 70 | 65 | 124 | 175 | 240 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 3952709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 30 | 35 | 35 | 436248
33 | Ashuganj 225 MW CCPP | 197 | 196 | 202 | 207 | 211 | 211 | 213 | 210 | 201 | 199 | 188 | 187 | 187 | 187 | 189 | 189 | 192 | 190 |  | 202 | 205 | 211 | 208 | 211 | 206 | 207 | 4856000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 305 | 320 | 340 | 320 | 335 | 305 | 305 | 320 | 305 | 305 | 310 |  | 325 | 300 | 270 | 270 | 270 | 270 | 270 | 7393000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 355 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 7531500
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143520
36 | Chandpur 150 MW CCPP | 135 | 136 | 135 | 134 | 135 | 136 | 145 | 136 | 135 | 135 | 137 | 135 | 135 | 136 | 136 | 136 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 122 | 3216190
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 412 | 411 | 411 | 411 | 410 | 400 | 403 | 411 | 410 | 411 | 411 | 410 | 411 | 413 | 414 | 405 | 412 | 402 |  | 392 | 336 | 337 | 292 | 270 | 288 | 294 | 9363460
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5088550
41 | Haripur 360MW CCPP(HPL) | 329 | 337 | 337 | 331 | 339 | 342 | 337 | 303 | 348 | 312 | 312 | 326 | 332 | 332 | 348 | 351 | 341 | 303 |  | 300 | 300 | 300 | 303 | 235 | 200 | 201 | 7496000
42 | RPCL 210MW CCPP | 151 | 144 | 130 | 134 | 132 | 121 | 108 | 108 | 72 | 72 | 72 | 72 | 71 | 72 | 71 | 70 | 71 | 71 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2330880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 16 | 21 | 22 | 17 | 21 | 18 | 30 | 13 | 18 | 12 | 3 |  | 0 | [6 empty] | 195550
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 44 | 44 | 43 | 44 | 44 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1032000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 994456
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 51 | 52 | 51 | 52 | 51 | 50 | 51 | 50 | 60 | 58 | 58 | 61 | 62 | 63 | 63 | 40 |  | 62 | 56 | 57 | 59 | 60 | 56 | 51 | 1361856
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 84 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 84 | 50 |  | 84 | 84 | 84 | 86 | 86 | 86 | 86 | 1892160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 90 | 90 | 90 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2821560
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 23 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 25 | 25 | 24 | 24 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 552300
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243180
54 | Hobiganj 11MW PP Cofidence-E |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247000
55 | Fenchugonj 51 MW PP (Barakatullah) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 16 | 16 | 23 | 23 | 562584
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 260 | 280 | 275 | 265 | 270 | 280 | 280 | 310 | 300 | 300 | 300 | 305 | 290 | 290 | 280 | 270 | 300 |  | 290 | 310 | 300 | 290 | 260 | 280 | 320 | 7072500
| Bibiyana South 400 MW | 400 | 401 | 400 | 400 | 390 | 361 | 370 | 370 | 400 | 400 | 400 | 394 | 400 | 400 | 400 | 400 | 400 | 350 |  | 394 | 400 | 401 | 400 | 400 | 400 | 400 | 9362700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 5 | 35 | 35 | 35 | 35 | 10 | 35 | 35 |  | 35 | 35 | 35 | 0 |  | 5 | 17 | 854013
59 | Tangail Palli Power Gen 22 MW | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 554640
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 493296
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 0 | 15 | 22 | 22 | 22 | 0 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 390492
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498960
63 | Impoprt (Tripura) | 152 | 148 | 148 | 144 | 134 | 126 | 118 | 124 | 130 | 124 | 132 | 134 | 138 | 140 | 138 | 136 | 138 | 128 |  | 148 | 146 | 146 | 146 | 142 | 146 | 142 | 3373440
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 40 | 40 | 40 | 38 | 6 | 4 | 2 | 2 | 4 | 7 | 6 | 6 | 4 | 8 | 12 |  | 11 | 19 | 24 | 25 | 34 | 38 | 39 | 513600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488124
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240300
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 18 | 18 | 8 | 6 | 16 | 25 | 27 | 31 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 647000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488310
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 20 | 24 | 27 | 27 | 27 | 27 | 27 | 611820
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 824500
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 585600
73 | Ghorashal 108MW PP (Regent) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 62 | 62 | 56 | 59 | 59 | 61 | 65 | 65 | 65 | 62 | 62 |  | 62 | 66 | 67 | 67 | 67 | 67 | 67 | 1451091
Feni Lanka Power
| Chowmuhani 113 MW | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 55 | 85 | 85 |  | 92 | 95 | 94 | 97 | 98 | 97 | 91 | 1377600
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 72 | 90 | 90 | 108 | 108 | 108 | 152 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 54 | 2351520
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 73 | 20 | 20 | 23 | 55 | 86 | 91 | 91 | 92 | 99 | 99 | 80 | 60 |  | 72 | 100 | 100 | 100 | 100 | 100 | 100 | 1980480
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 44 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176480
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 64 | 32 | 16 | 48 | 115 | 132 | 132 | 132 | 132 | 132 | 150 | 115 | 98 |  | 150 | 150 | 132 | 132 | 132 | 132 | 132 | 2621280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 90 | 70 | 70 |  | 90 | 105 | 105 | 105 | 105 | 105 | 105 | 2442000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | [8 empty] | 22441
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 46 | 54 | 35 | 35 |  | 43 | 54 | 54 | 54 | 54 | 54 | 54 | 1323001
| Karnaphuli Power Ltd. | 110 | 102 | 103 | 110 | 110 | 95 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 85 | 68 |  | 81 | 110 | 110 | 110 | 110 | 110 | 110 | 2381125
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 261 | 260 | 285 | 270 | 237 | 268 | 240 | 265 | 281 | 300 | 285 | 295 | 265 | 265 | 280 | 250 | 140 | 140 |  | 148 | 145 | 125 | 125 | 120 | 115 | 110 | 5420305
87 | Meghnaghat 100 MW(IEL) | 79 | 79 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 79 | 79 | 79 | 79 | 73 | 72 | 79 | 79 | 79 |  | 79 | 80 | 79 | 80 | 79 | 80 | 81 | 1890240
| Meghnaghat 104 MW PP (OPCL) | 94 | 79 | 94 | 94 | 94 | 94 | 75 | 89 | 94 | 94 | 75 | 75 | 75 | 93 | 75 | 75 | 72 | 72 |  | 80 | 93 | 93 | 93 | 94 | 95 | 94 | 2094720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 397440
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 824976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1136349
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 50 | 50 | 50 | 65 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2085984
95 | Patenga 50MW PP (Baraka) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 30 | 30 | 24 | 24 | 25 | 35 | 36 |  | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 843800
96 | Chattogram 108 MW PP (ECPV) | 88 | 88 | 87 | 87 | 87 |  |  |  | 0 | 54 | 78 | 79 | 80 | 80 | 79 | 79 | 76 | 76 |  | 85 | 85 | 83 | 84 | 86 | 87 | 87 | 1656000
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1333332
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1212314
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2675945
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 6100
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1027080
104 | Keranigonj 300 MW PP (APR) | 300 | 220 | 162 | 55 | [5 empty] | 0 | 21 | 125 | 154 | 22 | 87 | 15 |  |  |  | 92 | 202 | 205 | 306 | 201 | 190 | 300 | 2568200
105 | Bramhangoan 100 MW PP (Aggreko) | 83 | 82 | 82 | 81 | [5 empty] | 0 | 50 | 85 | 85 | 30 | 70 | 30 |  |  |  | 85 | 80 | 80 | 80 | 80 | 80 | 80 | 1157988
106 | Mymensingh 200 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 114 | 114 | 114 | 114 | 114 | 115 | 116 | 116 | 181 |  | 180 | 180 | 180 | 179 | 179 | 178 | 116 | 3122400
112 | Aurahati 100MW PP (Aggreko) | 82 | 82 | 82 | 82 | [5 empty] | 0 | 50 | 82 | 82 | 30 | 30 | 0 |  |  |  | 60 | 80 | 80 | 81 | 81 | 81 | 80 | 1105239
114 | Kodda 149 MW PP Unit-1 (Summit) | 60 | 60 | 60 | 69 | 78 | 79 | 76 | 78 | 78 | 79 | 76 | 78 | 78 | 79 | 78 | 77 | 89 | 133 |  | 133 | 133 | 132 | 133 | 132 | 133 | 99 | 2191968
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 76 | 90 | 90 | 76 | 76 | 76 | 76 | 64 | 64 | 76 | 76 | 50 | 50 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1847040
116 | Chandpur 200MW (Desh energy) | 163 | 100 | 100 | 100 | 100 | 85 | 100 | 100 | 100 | 100 | 68 | 68 | 68 | 68 | 68 | 68 | 105 | 186 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3019200
117 | Ashuganj 150MW PP (Midland) | 133 | 131 | 113 | 117 | 128 | 128 | 100 | 108 | 122 | 127 | 135 | 137 | 138 | 138 | 138 | 138 | 140 | 145 |  | 143 | 144 | 143 | 142 | 138 | 140 | 138 | 3194909
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 400 | 399 | 369 | 370 | 370 | 401 | 402 | 401 | 403 | 402 | 402 | 401 | 400 | 401 | 362 |  | 400 | 402 | 400 | 401 | 400 | 402 | 401 | 9496000
| Jamalpur 115 MW PP (United) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 56 | 1552800
| Anwara 300 MW PP (United) | 176 | 176 | 176 | 176 | 176 | 80 | 45 | 45 | 50 | 201 | 207 | 200 | 212 | 212 | 212 | 212 | 213 | 287 |  | 300 | 295 | 295 | 300 | 300 | 300 | 300 | 4865127
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1204800
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 68 |  | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 2234345
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 889200
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 7 | 13 | 13 | 11 | 10 | 17 | 20 | 18 | 7 | 1 | 1 | [8 empty] | 151337
| Chandpur 115(Doreen) | 113 | 115 | 106 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 96 | 95 | 95 | 95 | 94 | 95 | 96 | 94 |  | 107 | 115 | 116 | 116 | 112 | 115 | 116 | 2447040
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 34 | 34 | 34 | 34 | 34 | 34 | 0 |  |  | 9 | 36 | 46 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1028520
120 | Eastern Zone Total | 9061 | 8819 | 8696 | 8460 | 8171 | 7474 | 7182 | 7220 | 7334 | 7799 | 7904 | 8199 | 8210 | 8051 | 8185 | 8106 | 8009 | 8039 |  | 8956 | 9346 | 9270 | 9204 | 9005 | 8949 | 8807 | 200825076
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 49 | 49 | 49 | 49 | 49 | 49 | 16 | 547200
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 32 | 32 | 32 | 32 | 7 | [10 empty] | 17 | 23 | 22 |  | 26 | 45 | 34 | 38 | 38 | 38 | 38 | 391680
| Khulna 225 MW CCPP | 223 | 224 | 222 | 220 | 223 | 223 | 190 | 120 | 120 | 120 | 210 | 214 | 214 | 216 | 219 | 221 | 150 | 120 |  | 145 | 180 | 222 | 220 | 222 | 221 | 222 | 4767360
129 | Rupsha 105 MW PP (Orion rupsha) | 75 | 75 | 75 | 75 | 75 | 35 | 17 | 17 | 17 | 55 | 73 | 75 | 75 | 90 | 93 | 92 | 53 | 53 |  | 55 | 93 | 93 | 93 | 93 | 93 | 93 | 1725120
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 24 | 38 | 29 | 24 | 38 | 51 | 70 | 14 | 13 | 22 | 17 | 3 | [8 empty] | 446400
131
132 | United Payra Power Ltd. | 35 | 35 | [17 empty] | 11 | 17 | 17 | 35 | 35 | 35 | 35 | 254400
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 225 | 223 | 223 | 221 | 165 | 165 | 201 | 226 | 224 | 225 | 224 | 226 | 226 | 224 | 224 | 222 | 167 |  | 221 | 221 | 225 | 224 | 227 | 222 | 220 | 5169355
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 16 | 16 | 17 | 32 | 32 | 32 | 32 | 439680
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 87 | 88 | 87 | 87 | 87 | 87 | 86 | 85 | 86 | 83 | 85 | 86 | 85 | 85 | 84 | 84 |  | 84 | 84 | 86 | 85 | 86 | 84 | 87 | 2073435
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 29 | 29 | 27 | 24 | 21 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 17 | 20 | 19 | 20 |  | 29 | 28 | 28 | 27 | 27 | 30 | 30 | 544444
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 99 | [18 empty] | 50 | 50 | 40 | 50 | 50 | 79 | 540480
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 379875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 26 | [18 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 147312
146 | Bheramara HVDC | 798 | 798 | 798 | 798 | 815 | 816 | 910 | 911 | 910 | 874 | 874 | 874 | 873 | 874 | 873 | 871 | 869 | 869 |  | 868 | 851 | 851 | 851 | 855 | 854 | 855 | 20621818
147 | Bheramara 410 MW CCPP | 130 | 135 | 140 | 170 | 175 | 190 | 200 | 205 | 200 | 190 | 180 | 175 | 170 | 165 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 165 | 165 | 165 | 4070880
148 | Payra 1320 MW | 622 | 622 | 600 | 580 | 560 | 500 | 460 | 410 | 410 | 400 | 400 | 420 | 450 | 430 | 440 | 450 | 440 | 470 |  | 510 | 590 | 600 | 622 | 622 | 622 | 622 | 13337000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 174 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 176 | 176 | 175 | 175 | 4289400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 201808
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 0 | 4 | 5 | 5 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 29220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 114 | 114 | 114 | 116 | [22 empty] | 500928
| Sirajgonj 225 MW CCPP Unit-2 (Oil) |  |  |  | 0 | 128 | 130 | 130 | 130 | 130 | 130 | 188 | 213 | 211 | 212 | 212 | 214 | 170 | 130 |  | 138 | 196 | 207 | 219 | 220 | 219 | 215 | 3729763
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 124 | 124 | 119 | 121 | 144 | 178 | 183 | 160 | 171 | 181 | 177 | 171 | 164 | 162 | 156 | 152 | 150 | 150 |  | 156 | 158 | 159 | 159 | 161 | 162 | 162 | 4012764
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 321 | 250 | 250 | 251 | 300 | 300 | 300 | 350 | 414 | 414 | 414 | 414 | 404 | 404 | 386 | 385 | 376 | 334 |  | 380 | 380 | 380 | 380 | 385 | 380 | 381 | 8530072
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 28 | 29 | 29 | 29 | [8 empty] | 4 | 6 | 6 | 20 | 26 | 27 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 343379
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 20 | 18 | 18 | 19 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 184840
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 8 | 3104
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 12 | 0 | [6 empty] | 5 | 16 | 16 | 16 | 16 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 345329
168 | Santahar 50 MW Peaking PP | 36 | 36 | 36 | 36 | 17 | 0 | [11 empty] | 22 |  | 36 | 38 | 37 | 37 | 37 | 37 | 37 | 387800
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | 90 | 43 | 0 | [8 empty] | 15 | 23 | 23 | 23 | 22 | 22 | 22 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 794568
171 | Baghabari 200 MW PP (Paramount) | 186 | 179 | 50 | 0 | [7 empty] | 0 | 36 | 0 | [5 empty] | 3 | 130 | 159 | 136 | 182 | 185 | 187 | 1473421
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 50 |  | 64 | 94 | 94 | 94 | 94 | 94 | 94 | 2196192
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 50 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2548128
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | [18 empty] | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 63 | 70 | 70 | 70 | 70 | 70 | 70 | 87 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 104 | 1925308
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | 1 | 0 | [8 empty] | 14729
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 34 | 1202112
178