## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-01 | Friday
|  |  | Date (day): | 2022-07-01 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12704.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14025 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-06-30 | 2022-07-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 280 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 64 | 71 | 71 | 73 |  | 35 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 392 | 312 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 236 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage due to dirty fuel
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 71 | 75 | 80 | 80 |  | 20 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 125 | 130 | 125 | 150 | 185 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | GT-2 U/M & Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 92 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 90 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 132 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 51 | 51 | 51 |  | 29 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 15 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 50 | 49 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 213 | 275 | 260 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 202 | 203 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 25 | 85 | 85 | 85 |  | 15 | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 81 | 81 | 25 | 81 |  | 19 | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 89 | 133 | 130 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 94 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 5 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3123 | 3399 | 3265 | 3457 | 1036 | 1358
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 44 | 40 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 124 | 125 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 52 | 0 | 60 |  | 38 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 20 | 20 | 20 | 20 |  | 80 | Engine problem
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 76 | 76 | 76 |  | 24 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 28 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 73 | 92 | 80 | 92 |  | 16 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 195 | 288 | 265 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 108 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 77 | 50 | 80 |  | 20 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1074 | 1356 | 1197 | 1379 | 311 | 690
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 160 | 209 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 300 | 300 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 300 | 300 | 330 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 290 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 33 | 30 | 33 | 12 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 50 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 147 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 122 | 123 | 120 | 125 |  | 38 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 21 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 146 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 200 | 150 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 96 | 94 | 96 |  | 17 | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 97 | 116 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1669 | 2069 | 1991 | 2214 | 499 | 74
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 69 | 105 | 120 | 120 | 82 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 177 | 175 | 177 |  | 23 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 98 | 95 | 98 |  | 17 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 4 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 14 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 258 | 424 | 485.6 | 439 | 82 | 48
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 22 | 22 | 22 |  | 29 | Engine problem
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 35 | 30 | 35 |  | 15 | Engine problem
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 60 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 84 | 84 | 84
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 24 | 6 | 25 | 25
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1682 | 1664 | 1692 | 1732 | 0 | 712
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 876 | 860 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 48 | 20 | 48 |  | 67 | Engine problem
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 0 | 34 |  | 20 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 223 | 222 | 120 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 165 | 160 | 200 | 200 | 210 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 19 | 50 | 0 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 11 | 105 | 70 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 36 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1447 | 1612 | 1573 | 1830 | 210 | 148
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 48 | 16 | 48 |  |  | Rampal Transformar S/D
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 29 | 20 | 29 |  | 11 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 84 | 85 | 85 | 109 |  | Gas shortage & GT-2 S/D
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 550 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 164 | 224 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 798 | 935 | 998 | 1039 | 109 | 11
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 27 | 0 | 35 |  | 36 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 8 | 25 |  | 25 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 6 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 214 | 217 | 150 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 149 | 200 | 220
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 377 | 373 | 414 | 414 |  |  | FGMO
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 48 | 80 | 100 | 200
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 87 | 94 | 94 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1057 | 1304 | 1134 | 1547 | 433 | 143
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 98 | 96 | 98 |  | 15 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 90 | 90 | 90 | 90 |  | 25 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 340 | 363 | 369 | 388 | 269 | 40
|  | Total |  |  |  |  | 22678 | 21396 | 11448 | 13126 | 12704.6 | 14025 | 2949 | 3224
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11010.7241 | 12624.63 | 12219.3261 | 13489.2912
| A. |  | 2022-06-30 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 13126 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10144 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13126 | MW
| 3 | Day peak Generation : |  |  | 11448 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12624.63 | MW
| 4 | Evening peak Generation : |  |  | 13126 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 372.9639 | MKWHr | By Solar | 0.63782 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.2875 | MKWHr |  | By Oil: | 192.2881 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.3771 | MKWHr |  | By Hydro: | 2.9495 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2949 | MW | Dhaka | 4656.23 | 4656.23 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3224 | MW | Chittagong | 1324 | 1324 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6173 | MW | Khulna | 1579 | 1579 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1021.03 | MMCFD |  |  | Rajshahi | 1321.4 | 1321.4 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151797055.194 | ii) Oil : | Taka | 2941074254.98 | Comilla | 1146 | 1146 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 140662067 | Total | Taka | 3233533377.174 | Mymensingh | 995 | 995 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.078 | MKWHr. | Sylhet | 400 | 400 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -46 | MW (E to W) at | 21:00 | hrs | Barisal | 374 | 374 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -182 | MW at | 24:00 | hrs | Rangpur | 829 | 829 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30° C |  |  | Total | 12624.63 | 12624.63 |  | 0
| B. |  | 2022-07-01 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 34.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14025 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1025 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 369.3837 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10047 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3345 | MKWHr. | ii) HVDC Flow at Peak Time |  | 860 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0893 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.07 |  | (b) Today: | 89.05 |  | (c) Rule Curve: |  | 84
.

## YesterdayGen
2022-06-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 325 | 231 |  | 0 | 225 | 115 | 78 | 0 | 40 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 20 | 87 | 37 | 19 | 39 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 122 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 32 | 20 | 138 | 107 | 0 | 22 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 51 | 86 | 0 | 120 | 0 | 24 | 10 | 300 | 23 | 11 | 200 | 260 | 300 | 80 | 115 | 81 | 78 | 0 | 76 | 147 | 130 | 371 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 54 | 50 | 400 | 79 | 0 | 54 | 90 | 0 | 35 | 0 | 105 | 55 | 0 |  | 877 | 0 | 165 | 0 | 16 | 223 | 0 | 0 | 38 | 0 | 8 | 86 | 29 | 32 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 25 | 24 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 99 | 159 | 0 | 388 | 93 | 183 | 94 | 32 | 71 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 8339 | 4273 | 12612 | 3656 | 877 | 1994 | 943 | 3166 | 797 | 125 | 437 | 693 | 138 | 0 | 0 | 89.09
2:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 372 | 263 |  | 0 | 225 | 130 | 77 | 0 | 50 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 87 | 32 | 21 | 39 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 122 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 32 | 20 | 136 | 103 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 52 | 86 | 0 | 120 | 0 | 24 | 10 | 280 | 23 | 0 | 150 | 260 | 184 | 77 | 115 | 82 | 78 | 0 | 76 | 100 | 138 | 401 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 48 | 50 | 400 | 88 | 0 | 54 | 90 | 0 | 35 | 0 | 97 | 55 | 0 |  | 889 | 0 | 165 | 0 | 16 | 223 | 0 | 0 | 35 | 0 | 8 | 85 | 29 | 16 | 0 | 0 | 0 | 34 | 22 | 90 | 0 | 25 | 24 | 0 | 35 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 50 | 157 | 0 | 386 | 93 | 120 | 94 | 15 | 70 | 0 | 0 | 113 | 610 | 223 | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 8166 | 4125 | 12291 | 3715 | 889 | 2021 | 663 | 3092 | 785 | 125 | 443 | 642 | 136 | 0 | 0 | 89.09
3:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 394 | 292 |  | 0 | 225 | 140 | 72 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 87 | 36 | 21 | 39 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 122 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 32 | 20 | 132 | 106 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 52 | 81 | 0 | 120 | 0 | 24 | 10 | 290 | 23 | 11 | 50 | 260 | 54 | 80 | 114 | 81 | 78 | 0 | 76 | 100 | 122 | 402 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 48 | 50 | 400 | 94 | 0 | 54 | 90 | 0 | 35 | 0 | 99 | 55 | 0 |  | 889 | 0 | 170 | 0 | 16 | 223 | 0 | 0 | 35 | 0 | 8 | 85 | 28 | 16 | 0 | 0 | 0 | 34 | 23 | 90 | 0 | 25 | 16 | 0 | 35 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 157 | 0 | 414 | 93 | 0 | 94 | 15 | 70 | 0 | 0 | 113 | 580 | 223 | 0 | 17 | 0 | 0 | 35 | 0 | 0 |  | 8005 | 3931 | 11936 | 3756 | 889 | 2092 | 265 | 3069 | 755 | 121 | 442 | 634 | 132 | 0 | 0 | 89.08
4:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 398 | 312 |  | 0 | 225 | 145 | 72 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 87 | 37 | 21 | 39 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 122 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 32 | 20 | 130 | 106 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 51 | 81 | 0 | 120 | 0 | 24 | 10 | 290 | 23 | 11 | 20 | 260 | 24 | 25 | 115 | 26 | 78 | 0 | 76 | 100 | 132 | 401 | 56 | 105 | 105 | 0 | 176 | 54 | 110 | 0 | 48 | 50 | 400 | 94 | 0 | 54 | 90 | 0 | 35 | 0 | 112 | 55 | 0 |  | 910 | 0 | 180 | 0 | 16 | 223 | 0 | 0 | 35 | 0 | 8 | 86 | 27 | 0 | 0 | 0 | 0 | 34 | 14 | 90 | 0 | 25 | 16 | 0 | 35 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 157 | 0 | 414 | 93 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 580 | 223 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 7869 | 3904 | 11773 | 3772 | 910 | 2116 | 95 | 3027 | 755 | 121 | 441 | 624 | 130 | 0 | 0 | 89.08
5:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 398 | 327 |  | 0 | 225 | 145 | 72 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 87 | 32 | 21 | 39 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 122 | 30 | 5 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 32 | 20 | 120 | 106 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 52 | 86 | 0 | 120 | 0 | 24 | 10 | 280 | 23 | 11 | 0 | 260 | 0 | 0 | 115 | 0 | 78 | 0 | 76 | 100 | 140 | 401 | 56 | 105 | 105 | 0 | 176 | 54 | 97 | 0 | 48 | 50 | 400 | 94 | 0 | 54 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 909 | 0 | 180 | 0 | 16 | 215 | 0 | 0 | 0 | 0 | 8 | 86 | 26 | 0 | 0 | 0 | 0 | 34 | 0 | 45 | 0 | 25 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 157 | 0 | 414 | 93 | 0 | 94 | 0 | 70 | 0 | 0 | 113 | 580 | 223 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 7767 | 3745 | 11512 | 3771 | 909 | 2125 | 0 | 3021 | 755 | 121 | 413 | 475 | 120 | 0 | 0 | 89.07
6:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 401 | 327 |  | 0 | 225 | 145 | 72 | 0 | 55 | 0 | 0 | 0 | 83 | 40 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 8 | 0 | 87 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 21 | 9 | 21 | 22 | 0 | 0 | 0 | 280 | 280 | 212 | 8 | 121 | 31 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 32 | 20 | 114 | 106 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 57 | 81 | 0 | 120 | 0 | 24 | 10 | 260 | 23 | 11 | 0 | 130 | 0 | 0 | 114 | 0 | 78 | 1 | 76 | 100 | 140 | 400 | 56 | 90 | 105 | 0 | 177 | 54 | 92 | 0 | 48 | 50 | 400 | 94 | 0 | 54 | 90 | 0 | 35 | 1 | 116 | 55 | 0 |  | 909 | 0 | 180 | 0 | 16 | 125 | 0 | 0 | 0 | 0 | 8 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 158 | 0 | 370 | 35 | 0 | 94 | 0 | 70 | 0 | 1 | 113 | 520 | 213 | 0 | 0 | 0 | 3 | 35 | 0 | 0 |  | 7190 | 3294 | 10484 | 3782 | 909 | 2023 | 0 | 2562 | 695 | 122 | 255 | 146 | 114 | 6 | 0 | 89.07
7:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 403 | 333 |  | 0 | 225 | 145 | 72 | 0 | 55 | 0 | 0 | 0 | 8 | 40 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 8 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 11 | 29 | 19 | 36 | 0 | 0 | 0 | 280 | 315 | 208 | 8 | 122 | 31 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 32 | 20 | 108 | 105 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 40 | 78 | 0 | 120 | 0 | 24 | 10 | 300 | 23 | 0 | 0 | 80 | 0 | 0 | 114 | 0 | 78 | 1 | 76 | 100 | 70 | 400 | 56 | 90 | 105 | 1 | 100 | 54 | 81 | 0 | 48 | 50 | 400 | 94 | 3 | 54 | 90 | 0 | 35 | 2 | 115 | 55 | 0 |  | 909 | 0 | 180 | 0 | 16 | 140 | 0 | 0 | 0 | 0 | 8 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 168 | 0 | 400 | 17 | 0 | 35 | 0 | 70 | 0 | 1 | 50 | 460 | 223 | 0 | 0 | 0 | 14 | 34 | 0 | 0 |  | 6976 | 3168 | 10144 | 3795 | 909 | 2119 | 0 | 2147 | 635 | 123 | 270 | 146 | 108 | 22 | 0 | 89.06
8:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 404 | 335 |  | 0 | 225 | 120 | 67 | 0 | 55 | 0 | 0 | 0 | 14 | 70 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 13 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 14 | 32 | 19 | 14 | 0 | 0 | 0 | 280 | 270 | 212 | 8 | 122 | 31 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 31 | 20 | 112 | 95 | 0 | 22 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 40 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 23 | 0 | 0 | 100 | 0 | 0 | 114 | 0 | 78 | 0 | 76 | 68 | 76 | 400 | 56 | 90 | 105 | 2 | 125 | 54 | 73 | 0 | 48 | 50 | 400 | 85 | 12 | 54 | 90 | 0 | 35 | 5 | 116 | 55 | 0 |  | 910 | 0 | 185 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 8 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 165 | 0 | 406 | 22 | 0 | 35 | 0 | 70 | 0 | 2 | 70 | 450 | 203 | 0 | 0 | 0 | 46 | 34 | 0 | 0 |  | 6987 | 3212 | 10199 | 3735 | 910 | 2047 | 0 | 2217 | 625 | 124 | 280 | 212 | 112 | 67 | 0 | 89.06
9:00 | 0 | 0 | 0 | 180 | 280 | 67 | 0 | 403 | 332 |  | 0 | 225 | 140 | 65 | 0 | 55 | 0 | 0 | 0 | 80 | 85 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 25 | 42 | 0 | 89 | 35 | 100 | 0 | 15 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 65 | 31 | 19 | 4 | 0 | 0 | 0 | 280 | 270 | 181 | 8 | 122 | 34 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 21 | 20 | 116 | 71 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 78 | 0 | 120 | 0 | 24 | 10 | 280 | 23 | 0 | 0 | 230 | 0 | 0 | 114 | 0 | 78 | 0 | 76 | 68 | 128 | 352 | 56 | 90 | 105 | 2 | 191 | 54 | 89 | 0 | 48 | 50 | 400 | 89 | 13 | 54 | 90 | 0 | 35 | 15 | 116 | 55 | 145 |  | 912 | 0 | 180 | 0 | 16 | 140 | 0 | 0 | 0 | 0 | 8 | 84 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 166 | 0 | 414 | 78 | 0 | 70 | 0 | 70 | 0 | 3 | 113 | 420 | 224 | 0 | 0 | 1 | 24 | 44 | 0 | 0 |  | 7513 | 3345 | 10858 | 3785 | 912 | 2072 | 0 | 2827 | 595 | 124 | 270 | 228 | 116 | 59 | 0 | 89.06
10:00 | 0 | 0 | 0 | 180 | 280 | 65 | 0 | 404 | 350 |  | 0 | 225 | 140 | 73 | 0 | 55 | 0 | 0 | 0 | 92 | 85 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 27 | 33 | 8 | 42 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 70 | 31 | 19 | 4 | 0 | 0 | 0 | 270 | 200 | 145 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 15 | 20 | 120 | 70 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 23 | 11 | 0 | 243 | 0 | 0 | 114 | 0 | 78 | 0 | 76 | 68 | 140 | 401 | 56 | 90 | 105 | 5 | 194 | 54 | 92 | 0 | 48 | 50 | 400 | 94 | 19 | 54 | 90 | 0 | 35 | 16 | 105 | 55 | 286 |  | 875 | 0 | 165 | 0 | 16 | 190 | 0 | 0 | 0 | 0 | 8 | 83 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 166 | 0 | 393 | 93 | 0 | 70 | 0 | 63 | 0 | 4 | 113 | 400 | 225 | 0 | 0 | 1 | 66 | 90 | 0 | 0 |  | 7606 | 3439 | 11045 | 3775 | 875 | 2065 | 0 | 2941 | 575 | 124 | 360 | 268 | 120 | 112 | 0 | 89.06
11:00 | 0 | 0 | 0 | 180 | 280 | 64 | 0 | 402 | 340 |  | 0 | 225 | 125 | 65 | 0 | 55 | 0 | 0 | 0 | 92 | 88 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 27 | 33 | 8 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 68 | 31 | 19 | 3 | 0 | 0 | 0 | 270 | 147 | 139 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 16 | 20 | 116 | 70 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 24 | 10 | 290 | 16 | 11 | 20 | 230 | 73 | 0 | 114 | 80 | 86 | 0 | 76 | 68 | 138 | 401 | 56 | 90 | 105 | 6 | 195 | 54 | 92 | 0 | 48 | 50 | 400 | 93 | 20 | 90 | 90 | 0 | 35 | 5 | 93 | 43 | 240 |  | 875 | 0 | 170 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 8 | 85 | 17 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 163 | 0 | 391 | 93 | 0 | 70 | 0 | 70 | 0 | 4 | 113 | 420 | 167 | 0 | 0 | 4 | 63 | 90 | 0 | 0 |  | 7649 | 3549 | 11198 | 3675 | 875 | 1978 | 173 | 3008 | 595 | 124 | 436 | 330 | 116 | 103 | 0 | 89.05
12:00 | 0 | 0 | 0 | 180 | 280 | 64 | 0 | 392 | 320 |  | 0 | 225 | 125 | 71 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 20 | 33 | 25 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 20 | 73 | 31 | 19 | 3 | 0 | 0 | 0 | 270 | 0 | 160 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 16 | 20 | 122 | 69 | 0 | 0 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 24 | 10 | 300 | 16 | 11 | 200 | 213 | 202 | 25 | 113 | 81 | 89 | 15 | 76 | 68 | 140 | 401 | 57 | 90 | 105 | 2 | 195 | 54 | 92 | 0 | 48 | 50 | 400 | 93 | 4 | 17 | 90 | 0 | 35 | 5 | 97 | 55 | 290 |  | 876 | 0 | 165 | 0 | 16 | 223 | 0 | 0 | 0 | 0 | 8 | 84 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 19 | 157 | 0 | 377 | 93 | 48 | 87 | 11 | 70 | 0 | 5 | 113 | 420 | 164 | 0 | 0 | 2 | 36 | 90 | 0 | 0 |  | 7806 | 3642 | 11448 | 3584 | 876 | 1954 | 575 | 3023 | 595 | 124 | 437 | 302 | 122 | 70 | 0 | 89.05
13:00 | 0 | 0 | 0 | 180 | 280 | 64 | 0 | 374 | 299 |  | 0 | 225 | 130 | 68 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 25 | 25 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 20 | 79 | 31 | 19 | 8 | 0 | 0 | 0 | 270 | 0 | 190 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 8 | 13 | 20 | 136 | 67 | 0 | 22 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 64 | 81 | 0 | 120 | 0 | 24 | 10 | 270 | 16 | 11 | 200 | 220 | 50 | 25 | 112 | 81 | 87 | 14 | 76 | 68 | 131 | 400 | 58 | 90 | 105 | 4 | 195 | 54 | 92 | 0 | 48 | 50 | 400 | 93 | 4 | 17 | 90 | 0 | 35 | 8 | 109 | 52 | 303 |  | 875 | 0 | 165 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 8 | 84 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 20 | 154 | 0 | 372 | 93 | 120 | 94 | 50 | 70 | 0 | 7 | 113 | 440 | 164 | 0 | 0 | 2 | 15 | 90 | 0 | 0 |  | 7779 | 3768 | 11547 | 3621 | 875 | 1911 | 496 | 3083 | 615 | 124 | 440 | 407 | 136 | 55 | 0 | 89.05
14:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 359 | 285 |  | 0 | 225 | 135 | 70 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 32 | 8 | 42 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 83 | 31 | 19 | 9 | 0 | 0 | 0 | 270 | 0 | 172 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 50 | 0 | 22 | 8 | 13 | 20 | 136 | 66 | 0 | 22 | 1 | 44 | 42 | 17 | 15 | 110 | 0 | 64 | 81 | 0 | 120 | 0 | 24 | 10 | 270 | 16 | 11 | 50 | 218 | 70 | 0 | 112 | 81 | 86 | 15 | 76 | 68 | 135 | 400 | 59 | 88 | 105 | 1 | 195 | 54 | 92 | 0 | 48 | 50 | 400 | 94 | 6 | 48 | 90 | 0 | 35 | 5 | 116 | 43 | 294 |  | 876 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 152 | 0 | 353 | 93 | 0 | 94 | 50 | 70 | 0 | 7 | 113 | 440 | 164 | 0 | 0 | 0 | 2 | 90 | 0 | 0 |  | 7616 | 3588 | 11204 | 3561 | 876 | 1854 | 201 | 3160 | 615 | 121 | 445 | 417 | 136 | 37 | 0 | 89.05
15:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 342 | 273 |  | 0 | 225 | 135 | 72 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 32 | 8 | 41 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 85 | 32 | 0 | 4 | 0 | 0 | 0 | 270 | 0 | 173 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 50 | 0 | 22 | 8 | 25 | 20 | 138 | 66 | 0 | 22 | 1 | 44 | 42 | 17 | 35 | 110 | 0 | 64 | 78 | 0 | 120 | 0 | 5 | 10 | 300 | 16 | 11 | 100 | 240 | 300 | 0 | 114 | 82 | 86 | 16 | 76 | 68 | 143 | 401 | 59 | 88 | 105 | 1 | 195 | 54 | 89 | 0 | 48 | 50 | 400 | 86 | 11 | 54 | 90 | 0 | 35 | 4 | 116 | 55 | 240 |  | 876 | 0 | 155 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 8 | 85 | 18 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 149 | 0 | 358 | 93 | 2 | 94 | 50 | 66 | 0 | 6 | 113 | 470 | 164 | 0 | 0 | 0 | 3 | 90 | 0 | 0 |  | 7909 | 3607 | 11516 | 3476 | 876 | 1869 | 484 | 3207 | 645 | 121 | 442 | 434 | 138 | 42 | 0 | 89.05
16:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 331 | 258 |  | 0 | 225 | 130 | 70 | 0 | 45 | 0 | 0 | 0 | 94 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 8 | 41 | 0 | 44 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 84 | 32 | 16 | 6 | 0 | 0 | 0 | 270 | 15 | 175 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 46 | 0 | 22 | 8 | 25 | 18 | 134 | 66 | 0 | 22 | 1 | 44 | 42 | 17 | 35 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 6 | 10 | 300 | 16 | 11 | 200 | 245 | 157 | 0 | 114 | 82 | 86 | 7 | 76 | 68 | 140 | 402 | 58 | 88 | 105 | 1 | 195 | 54 | 92 | 0 | 60 | 50 | 400 | 75 | 18 | 54 | 90 | 0 | 35 | 6 | 108 | 55 | 0 |  | 877 | 0 | 150 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 8 | 84 | 20 | 110 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 145 | 0 | 360 | 93 | 68 | 94 | 50 | 70 | 0 | 4 | 113 | 460 | 164 | 0 | 0 | 1 | 1 | 90 | 0 | 0 |  | 7558 | 3694 | 11252 | 3247 | 877 | 1857 | 507 | 3189 | 635 | 79 | 442 | 464 | 134 | 39 | 0 | 89.05
17:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 323 | 249 |  | 0 | 225 | 130 | 72 | 0 | 50 | 0 | 0 | 0 | 92 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 8 | 41 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 83 | 35 | 16 | 6 | 0 | 0 | 0 | 270 | 100 | 178 | 8 | 122 | 10 | 2 | 0 | 51 | 0 | 49 | 0 | 22 | 8 | 25 | 18 | 126 | 69 | 0 | 22 | 0 | 44 | 42 | 19 | 35 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 6 | 10 | 280 | 16 | 11 | 0 | 243 | 0 | 0 | 113 | 0 | 90 | 2 | 76 | 115 | 145 | 401 | 58 | 94 | 105 | 1 | 195 | 54 | 92 | 0 | 95 | 50 | 400 | 74 | 3 | 54 | 90 | 0 | 35 | 5 | 101 | 55 | 0 |  | 876 | 0 | 150 | 0 | 16 | 228 | 0 | 0 | 33 | 0 | 8 | 84 | 20 | 110 | 0 | 0 | 0 | 34 | 4 | 10 | 0 | 25 | 16 | 0 | 28 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 145 | 0 | 359 | 93 | 0 | 94 | 50 | 85 | 0 | 3 | 113 | 450 | 164 | 0 | 0 | 0 | 2 | 90 | 0 | 0 |  | 7250 | 3707 | 10957 | 3339 | 876 | 1845 | 0 | 3259 | 625 | 119 | 446 | 524 | 126 | 16 | 0 | 89.05
18:00 | 0 | 0 | 0 | 180 | 280 | 68 | 0 | 317 | 242 |  | 0 | 225 | 140 | 73 | 0 | 55 | 0 | 0 | 0 | 70 | 64 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 27 | 33 | 15 | 41 | 0 | 85 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 48 | 37 | 16 | 16 | 0 | 0 | 0 | 270 | 105 | 186 | 8 | 122 | 10 | 5 | 0 | 51 | 0 | 49 | 0 | 22 | 8 | 23 | 20 | 124 | 70 | 0 | 22 | 0 | 44 | 42 | 19 | 35 | 110 | 0 | 62 | 50 | 0 | 120 | 0 | 6 | 10 | 290 | 24 | 11 | 0 | 243 | 0 | 0 | 110 | 0 | 132 | 0 | 76 | 170 | 145 | 352 | 32 | 105 | 105 | 0 | 284 | 54 | 93 | 0 | 95 | 60 | 365 | 46 | 2 | 60 | 90 | 0 | 35 | 2 | 116 | 55 | 0 |  | 877 | 0 | 150 | 0 | 19 | 223 | 0 | 0 | 34 | 0 | 8 | 82 | 20 | 110 | 0 | 0 | 0 | 34 | 10 | 60 | 0 | 8 | 16 | 0 | 37 | 19 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 324 | 93 | 0 | 70 | 50 | 90 | 0 | 2 | 70 | 420 | 164 | 0 | 0 | 0 | 1 | 90 | 0 | 0 |  | 7265 | 3536 | 10801 | 3275 | 877 | 1802 | 0 | 3276 | 595 | 120 | 353 | 502 | 124 | 7 | 0 | 89.05
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 280 | 69 | 0 | 312 | 238 |  | 0 | 225 | 130 | 73 | 0 | 55 | 0 | 0 | 0 | 60 | 80 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 20 | 33 | 15 | 0 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 30 | 46 | 20 | 62 | 39 | 21 | 23 | 0 | 0 | 0 | 270 | 150 | 209 | 8 | 122 | 10 | 5 | 0 | 51 | 0 | 49 | 0 | 22 | 8 | 23 | 20 | 142 | 82 | 0 | 22 | 0 | 44 | 42 | 19 | 35 | 110 | 0 | 62 | 84 | 0 | 120 | 0 | 6 | 10 | 300 | 24 | 11 | 190 | 243 | 157 | 85 | 125 | 80 | 133 | 0 | 76 | 200 | 145 | 401 | 54 | 105 | 105 | 0 | 284 | 54 | 94 | 0 | 97 | 78 | 394 | 48 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 861 | 0 | 155 | 0 | 48 | 222 | 0 | 0 | 34 | 10 | 40 | 85 | 26 | 110 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 6 | 145 | 0 | 365 | 93 | 19 | 80 | 50 | 98 | 0 | 0 | 100 | 420 | 164 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8233 | 3824 | 12057 | 3440 | 861 | 1890 | 537 | 3576 | 595 | 123 | 382 | 671 | 142 | 0 | 0 | 89.05
19:30 | 0 | 0 | 0 | 180 | 280 | 70 | 0 | 313 | 238 |  | 0 | 225 | 130 | 73 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 20 | 33 | 15 | 26 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 48 | 51 | 20 | 89 | 40 | 21 | 23 | 0 | 0 | 0 | 270 | 225 | 212 | 8 | 122 | 10 | 10 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 25 | 20 | 148 | 100 | 0 | 22 | 0 | 44 | 42 | 19 | 35 | 110 | 0 | 64 | 84 | 0 | 120 | 0 | 6 | 10 | 275 | 24 | 11 | 200 | 243 | 301 | 85 | 177 | 81 | 133 | 0 | 76 | 200 | 146 | 401 | 96 | 105 | 105 | 0 | 280 | 54 | 92 | 0 | 97 | 78 | 400 | 93 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 861 | 0 | 155 | 0 | 48 | 223 | 0 | 0 | 45 | 10 | 40 | 85 | 27 | 110 | 0 | 0 | 0 | 34 | 22 | 92 | 0 | 25 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 100 | 146 | 0 | 357 | 93 | 181 | 94 | 72 | 98 | 0 | 0 | 113 | 530 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8751 | 4358 | 13109 | 3551 | 861 | 1920 | 948 | 3867 | 705 | 124 | 432 | 762 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 280 | 70 | 0 | 312 | 238 |  | 0 | 225 | 130 | 72 | 0 | 55 | 0 | 0 | 0 | 88 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 20 | 33 | 15 | 34 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 42 | 51 | 20 | 91 | 42 | 21 | 29 | 0 | 0 | 0 | 270 | 300 | 212 | 8 | 122 | 28 | 20 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 29 | 20 | 150 | 103 | 0 | 22 | 0 | 44 | 42 | 22 | 35 | 110 | 0 | 64 | 84 | 0 | 120 | 0 | 6 | 10 | 275 | 24 | 11 | 160 | 260 | 107 | 85 | 177 | 81 | 134 | 0 | 76 | 200 | 147 | 360 | 98 | 105 | 105 | 0 | 287 | 54 | 96 | 0 | 98 | 78 | 400 | 90 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 861 | 0 | 160 | 0 | 48 | 224 | 0 | 0 | 35 | 0 | 40 | 86 | 25 | 110 | 0 | 0 | 0 | 34 | 27 | 92 | 0 | 25 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 97 | 146 | 0 | 302 | 93 | 175 | 94 | 105 | 98 | 0 | 0 | 113 | 530 | 225 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8619 | 4328 | 12947 | 3615 | 861 | 1887 | 705 | 3929 | 705 | 124 | 439 | 747 | 150 | 0 | 0 | 89.05
21:00 | 0 | 0 | 0 | 180 | 280 | 71 | 0 | 312 | 236 |  | 0 | 225 | 130 | 75 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 15 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 52 | 51 | 20 | 92 | 44 | 21 | 28 | 0 | 0 | 0 | 270 | 300 | 209 | 8 | 123 | 33 | 50 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 22 | 35 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 6 | 10 | 290 | 24 | 11 | 150 | 275 | 203 | 85 | 177 | 81 | 133 | 0 | 76 | 200 | 147 | 403 | 98 | 105 | 105 | 0 | 288 | 54 | 108 | 0 | 96 | 77 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 160 | 0 | 48 | 222 | 0 | 0 | 34 | 0 | 40 | 84 | 29 | 48 | 0 | 0 | 0 | 34 | 27 | 90 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 50 | 149 | 0 | 373 | 93 | 80 | 94 | 105 | 98 | 0 | 0 | 113 | 550 | 224 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8912 | 4214 | 13126 | 3673 | 860 | 2004 | 649 | 3967 | 725 | 125 | 439 | 755 | 146 | 0 | 0 | 89.05
22:00 | 0 | 0 | 0 | 180 | 280 | 71 | 0 | 314 | 237 |  | 0 | 225 | 130 | 73 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 16 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 52 | 51 | 20 | 93 | 44 | 21 | 35 | 0 | 0 | 0 | 270 | 300 | 210 | 8 | 123 | 36 | 53 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 150 | 105 | 0 | 22 | 0 | 44 | 42 | 22 | 35 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 6 | 10 | 290 | 24 | 11 | 100 | 276 | 185 | 85 | 177 | 81 | 133 | 0 | 76 | 200 | 147 | 402 | 98 | 105 | 105 | 0 | 284 | 54 | 110 | 0 | 99 | 77 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 160 | 0 | 48 | 223 | 0 | 0 | 34 | 0 | 40 | 85 | 28 | 32 | 0 | 0 | 0 | 34 | 27 | 90 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 150 | 0 | 371 | 93 | 20 | 94 | 105 | 98 | 0 | 0 | 113 | 600 | 222 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8849 | 4136 | 12985 | 3681 | 860 | 2010 | 471 | 3952 | 775 | 125 | 440 | 738 | 150 | 0 | 0 | 89.05
23:00 | 0 | 0 | 0 | 180 | 280 | 71 | 0 | 336 | 274 |  | 0 | 225 | 130 | 81 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 26 | 33 | 16 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 20 | 93 | 44 | 21 | 38 | 0 | 0 | 0 | 270 | 300 | 212 | 8 | 123 | 36 | 46 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 150 | 106 | 0 | 22 | 0 | 43 | 42 | 22 | 34 | 110 | 0 | 62 | 84 | 0 | 120 | 0 | 6 | 10 | 280 | 24 | 11 | 30 | 275 | 153 | 84 | 177 | 80 | 133 | 0 | 76 | 200 | 140 | 401 | 98 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 96 | 77 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 160 | 0 | 48 | 224 | 0 | 0 | 29 | 0 | 40 | 86 | 31 | 32 | 0 | 0 | 0 | 16 | 28 | 90 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 150 | 0 | 364 | 93 | 0 | 94 | 105 | 98 | 0 | 0 | 113 | 600 | 202 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8762 | 4074 | 12836 | 3704 | 860 | 2008 | 347 | 3925 | 775 | 126 | 443 | 717 | 150 | 0 | 0 | 89.05
24:00 | 0 | 0 | 0 | 180 | 200 | 71 | 0 | 358 | 288 |  | 0 | 225 | 140 | 79 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 18 | 33 | 23 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 20 | 87 | 44 | 21 | 40 | 0 | 0 | 0 | 290 | 300 | 208 | 8 | 123 | 36 | 49 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 148 | 106 | 0 | 22 | 0 | 43 | 42 | 22 | 35 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 6 | 10 | 290 | 24 | 11 | 100 | 276 | 301 | 83 | 114 | 81 | 89 | 0 | 76 | 200 | 137 | 401 | 58 | 105 | 105 | 0 | 212 | 54 | 110 | 0 | 49 | 50 | 400 | 95 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 165 | 0 | 16 | 221 | 0 | 0 | 25 | 0 | 40 | 86 | 31 | 32 | 0 | 0 | 0 | 16 | 28 | 90 | 0 | 25 | 32 | 0 | 30 | 22 | 0 | 5 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 150 | 0 | 364 | 93 | 10 | 94 | 105 | 70 | 0 | 0 | 113 | 600 | 223 | 0 | 0 | 0 | 0 | 72 | 0 | 0 |  | 8659 | 4010 | 12669 | 3661 | 860 | 2069 | 575 | 3529 | 775 | 127 | 438 | 704 | 148 | 0 | 0 | 89.05
KWH | 0 | 0 | 0 | 4359600 | 6606318 | 1598500 | 0 | 8824830 | 6832000 |  | 0 | 5095850 | 3181527 | 1743360 | 0 | 1311347 | 35545 | 0 | 0 | 2011104 | 2058480 | 2623200 | 0 | 0 | 0 | 0 | 929520 | 1291130 | 573274 | 440424 | 600000 | 585180 | 801300 | 414000 | 981120 | 0 | 2109502 | 840000 | 2400000 | 0 | 534254 | 0 | 0 | 0 | 0 |  | 520800 | 304272 | 282028 | 510960 | 1744320 | 832320 | 448560 | 552480 | 0 | 0 | 0 | 7009800 | 4777000 | 4669000 | 150545 | 2831270 | 478872 | 296640 | 0 | 1132374 | 0 | 825880 | 0 | 500940 | 227520 | 640600 | 502240 | 3089280 | 2064000 | 0 | 490392 | 8900 | 1033000 | 970728 | 661800 | 816408 | 2664654 | 0 | 1385184 | 1901760 | 0 | 2892500 | 0 | 423520 | 244080 | 7076500 | 527520 | 219920 | 1946304 | 5655489 | 2716427 | 758261 | 3024000 | 1233720 | 2313940 | 66015 | 1810560 | 2902560 | 3245090 | 9395000 | 1519200 | 2345076 | 2542534 | 24961 | 5000618 | 1368550 | 2361054 | 0 | 1535520 | 1349760 | 9515700 | 2093760 | 109250 | 1935360 | 2169109 | 0 | 889920 | 84014 | 2664000 | 1314000 | 1722700 |  | 21334545 | 0 | 4233312 | 0 | 534720 | 95029440 | 0 | 0 | 375360 | 9088 | 357750 | 2039617 | 540543 | 1345056 | 0 | 0 | 0 | 444944 | 250343 | 997912 | 0 | 494912 | 343994 | 0 | 400299 | 481680 | 0 | 184122 | 0 | 0 | 4275700 | 0 | 0 | 0 | 0 | 0 | 4960264 | 0 | 491520 | 3968518 | 0 | 9040254 | 2040960 | 1137141 | 2109696 | 961920 | 1866480 | 0 | 51040 | 2593248 | 13101400 | 4801145 | 0 | 117600 | 17160 | 276480 | 1653312 | 0 | 0 |  | 190102384 | 182861475 | 372963859 | 87795212 | 21334545 | 47492260 | 8283373 | 77157743 | 17377100 | 2949502 | 99989704 | 6857320 | 3089280 | 637820 | 0
Fuel Cost | 0 | 0 | 0 | 6495804 | 7399076.16 | 2126005 | 0 | 9266071.5 | 7378560 |  | 0 | 5554476.5 | 3531494.97 | 19490764.8 | 0 | 17375347.75 | 39810.4 | 0 | 0 | 29402340.48 | 28962813.6 | 42522072 | 0 | 0 | 0 | 0 | 11823494.4 | 17430255 | 7687604.34 | 330318 | 450000 | 0 | 0 | 0 | 16688851.2 | 0 | 569565.54 | 226800 | 4536000 | 0 | 8735052.9 | 0 | 0 | 0 | 0 |  | 6796440 | 5075256.96 | 4800116.56 | 6903069.6 | 22117977.6 | 9629942.4 | 569671.2 | 1839758.4 | 0 | 0 | 0 | 7780878 | 5206930 | 5416040 | 194203.05 | 3454149.4 | 541125.36 | 441993.6 | 0 | 1891064.58 | 0 | 14262947.6 | 0 | 686287.8 | 170640 | 1121050 | 376680 | 22181030.4 | 2249760 | 0 | 666933.12 | 141866 | 1415210 | 1281360.96 | 1151532 | 1412385.84 | 3064352.1 | 0 | 2687256.96 | 4336012.8 | 0 | 2921425 | 0 | 631044.8 | 483278.4 | 7076500 | 395640 | 167139.2 | 40794531.84 | 77197424.85 | 56936309.92 | 15673254.87 | 40763520 | 25500992.4 | 32048069 | 771715.35 | 18684979.2 | 39648969.6 | 43062344.3 | 8643400 | 18473472 | 33909798.96 | 32163055.1 | 0 | 58707255.32 | 14903509.5 | 25098004.02 | 0 | 19792852.8 | 15900172.8 | 8754444 | 27114192 | 1578662.5 | 24559718.4 | 24684460.42 | 0 | 11622355.2 | 1003967.3 | 39880080 | 17305380 | 0 |  | 64003635 | 0 | 4741309.44 | 0 | 5566435.2 | 1567985760 | 0 | 0 | 6760233.6 | 163584 | 5140867.5 | 2284371.04 | 1048653.42 | 14661110.4 | 0 | 0 | 0 | 7461710.88 | 4378499.07 | 15607343.68 | 0 | 8195742.72 | 5816938.54 | 0 | 6753044.13 | 997077.6 | 0 | 139380.354 | 0 | 0 | 22618453 | 0 | 0 | 0 | 0 | 0 | 86606209.44 | 0 | 10312089.6 | 4603480.88 | 0 | 8949851.46 | 27430502.4 | 23845846.77 | 24957703.68 | 13899744 | 23704296 | 0 | 563992 | 31482030.72 | 118043614 | 4897167.9 | 0 | 870240 | 194079.6 | 3243110.4 | 25345272.96 | 0 | 0 |  | 1174738419.88 | 2153273381.384 | 3328011801.264 | 94791642.774 | 64003635 | 57005412.42 | 173063025.4 | 999817513.12 | 140662067 | 796365.54 | 1654591969.44 | 113601747.02 | 22181030.4 | 7497393.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 280 | 64 | 0 | 392 | 320 |  | 0 | 225 | 125 | 71 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 20 | 33 | 25 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 20 | 73 | 31 | 19 | 3 | 0 | 0 | 0 | 270 | 0 | 160 | 0 | 122 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 16 | 20 | 122 | 69 | 0 | 0 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 63 | 78 | 0 | 120 | 0 | 24 | 10 | 300 | 16 | 11 | 200 | 213 | 202 | 25 | 113 | 81 | 89 | 15 | 76 | 68 | 140 | 401 | 57 | 90 | 105 | 2 | 195 | 54 | 92 | 0 | 48 | 50 | 400 | 93 | 4 | 17 | 90 | 0 | 35 | 5 | 97 | 55 | 290 |  | 876 | 0 | 165 | 0 | 16 | 223 | 0 | 0 | 0 | 0 | 8 | 84 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 19 | 157 | 0 | 377 | 93 | 48 | 87 | 11 | 70 | 0 | 5 | 113 | 420 | 164 | 0 | 0 | 2 | 36 | 90 | 0 | 0 |  | 11448 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 71 | 0 | 312 | 236 | 0 | 0 | 225 | 130 | 75 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 15 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 51 | 20 | 92 | 44 | 21 | 28 | 0 | 0 | 0 | 270 | 300 | 209 | 8 | 123 | 33 | 50 | 0 | 51 | 0 | 49 | 0 | 22 | 11 | 33 | 20 | 146 | 105 | 0 | 22 | 0 | 44 | 42 | 22 | 35 | 110 | 0 | 63 | 84 | 0 | 120 | 0 | 6 | 10 | 290 | 24 | 11 | 150 | 275 | 203 | 85 | 177 | 81 | 133 | 0 | 76 | 200 | 147 | 403 | 98 | 105 | 105 | 0 | 288 | 54 | 108 | 0 | 96 | 77 | 400 | 94 | 0 | 162 | 90 | 0 | 35 | 0 | 116 | 55 | 0 |  | 860 | 0 | 160 | 0 | 48 | 222 | 0 | 0 | 34 | 0 | 40 | 84 | 29 | 48 | 0 | 0 | 0 | 34 | 27 | 90 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 50 | 149 | 0 | 373 | 93 | 80 | 94 | 105 | 98 | 0 | 0 | 113 | 550 | 224 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 13126 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 412 | 330 | 0 | 0 | 225 | 150 | 80 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 60 | 51 | 20 | 92 | 44 | 22 | 25 | 0 | 0 | 0 | 300 | 330 | 215 | 8 | 125 | 33 | 55 | 0 | 51 | 0 | 50 | 0 | 22 | 11 | 33 | 20 | 165 | 120 | 0 | 22 | 0 | 44 | 42 | 22 | 35 | 110 | 0 | 64 | 84 | 0 | 120 | 0 | 25 | 10 | 341 | 24 | 11 | 200 | 275 | 300 | 85 | 177 | 81 | 133 | 0 | 76 | 200 | 150 | 400 | 98 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 96 | 80 | 400 | 104 | 0 | 162 | 90 | 0 | 35 |  | 115 | 55 |  |  | 930 | 0 | 200 | 0 | 48 | 220 | 0 | 0 | 34 | 60 | 40 | 85 | 29 | 48 | 0 | 0 | 0 | 34 | 35 | 90 | 0 | 25 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 0 | 220 | 0 | 100 | 220 | 0 | 414 | 93 | 200 | 94 | 105 | 98 | 0 | 0 | 113 | 622 | 220 |  | 35 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 412 | 330 | 0 | 0 | 225 | 125 | 80 | 0 | 55 | 0 | 0 | 0 | 100 | 90 | 130 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 80 | 40 | 22 | 10 | 0 | 0 | 0 | 300 | 300 | 215 | 8 | 120 | 30 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 143 | 120 | 0 | 22 | 1.6 | 44 | 42 | 22 | 30 | 110 | 0 | 60 | 84 | 0 | 120 | 0 | 25 | 10 | 310 | 24 | 11 | 100 | 260 | 200 | 85 | 175 | 25 | 130 | 20 | 76 | 200 | 140 | 400 | 95 | 105 | 105 | 5 | 265 | 54 | 110 | 0 | 94 | 50 | 400 | 90 | 50 | 162 | 90 | 0 | 35 | 30 | 115 | 55 |  |  | 930 | 0 | 200 | 0 | 20 | 120 | 0 | 0 | 0 | 0 | 40 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 414 | 93 | 100 | 94 | 70 | 96 | 0 | 8 | 113 | 622 | 220 |  | 35 | 6 | 100 | 90
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 400 | 322 | 0 | 0 | 225 | 145 | 81 | 0 | 55 | 0 | 0 | 0 | 50 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 22 | 25 | 20 | 33 | 25 | 24 | 0 | 86 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 0 | 27 | 21 | 17 | 0 | 0 | 0 | 290 | 285 | 179 | 8 | 123 | 36 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 32 | 20 | 80 | 105 | 0 | 22 | 1 | 43 | 42 | 22 | 35 | 110 | 0 | 64 | 84 | 0 | 120 | 0 | 6 | 10 | 270 | 24 | 11 | 0 | 145 | 0 | 0 | 114 | 0 | 60 | 1 | 76 | 200 | 133 | 352 | 24 | 105 | 105 | 0 | 65 | 54 | 110 | 0 | 48 | 50 | 360 | 104 | 18 | 35 | 90 | 0 | 35 | 3 | 116 | 55 | 0 | 0 | 909 | 0 | 180 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 153 | 0 | 353 | 35 | 0 | 94 | 91 | 70 | 0 | 0 | 113 | 420 | 225 | 0 | 0 | 3 | 17 | 34 | 0 | 0 | 0 |  |  |  |  | 192288140 |  | 0
192288140
| Minimum Generation |  | 10144 | 7:00
| Highest Generation |  | 13126 | 21:00
| Day Peak Generation |  | 11448 | 12:00
| Evening Peak Generation |  | 13126 | 21:00
| HVDC Max Flow |  | 912 | 9:00
| HVDC EvPeak Flow |  | 860 | 21:00
| Load factor L.F |  | 118.4%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-01
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-06-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11448 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10047 | MW
Evening Peak Generation : |  | 13126 | MW Hour : | 21:00 | Available Max Generation : |  | 14025 | MW
E.P. Demand (at gen end) : |  | 13126 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 13126 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1025 | MW
Total Gen. (MKWH) : |  | 372.9639 | System Load Factor : | 118.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -182 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-01
Actual : | 89.05 | Ft.(MSL) , | Rule curve : | 84 | Ft.( MSL )
Gas Consumed : | Total = | 1021.03 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151797055.194
: |  | Coal : | 140662067 | Oil : | 2941074254.98 | Total : | 3233533377.174
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4514.6771 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1207.6142 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1595.137 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1427.9811 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1266.2992 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 932.9354 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 515.0457 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 342.0488 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 711.2535 |  |  | 0 | 0%
Total | 0 |  | 12512.992 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4,7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Feni-PHP 132 kV Ckt was under shut down from 09:32 to 17:10 for D/W.
b) PHP-Baroirhat 132 kV Ckt was under shut down from 08:51 to 17:08 for D/W.
c) Aminbazar-Manikganj P/S 132 kV Ckt-1 was under shut down from 10:03 to 13:25 for D/W.
d) Jhenidah-HVDC 230 kV Ckt-2 tripped at 10:02 showing gen.trip & air lock and was switched on at 10:43.
e) Sholoshahar 132/33 kV T-1 transformer was under shut down from 11:51 to 16:21 for D/W.
f) Ashuganj(S)-360 MW was shut down at 11:15 due to gas shortage.
g) Rajbari 132/33 kV T-1 transformer was shut down at 12:40 due to red hot maintenance at 33 kV PBS | [5 empty] | About 10 MW power interruption occurred under
Baliakandi bus DS and was switched on at 14:16. | [5 empty] | Rajbari S/S area from 12:40 to 14:16.
h) Ashuganj(S)-360 MW CCPP GT & ST were synchronized at 15:56 & 18:07 respectively.
i) Chapainawabganj-Amnura 132 kV Ckt tripped at 15:42 showing dist.Z1 and was switched on at 16:00.
j) Hasnabad 132/33 kv T-2 transformer tripped at 16:10 showing O/C relay due to 33 kV Dohar feeder fault | [5 empty] | About 15 MW power interruption occurred under
and was switched on at 16:23. | [5 empty] | Hasnabad S/S area from 16:10 to 16:23.
k) Niamatpur 33 kV bus-1 & 2 were shut down at 09:15 for C/M at 33 kV bus coupler and was switched | [5 empty] | About 55 MW power interruption occurred under
on at 21:50. | [5 empty] | Niamatpur S/S area from 21:15 to 21:50.
l) Barishal(N) 132/33 kV T-4 T-5 transformers 33 kV CB tripped at 00:07(1/7/22) showing under frequency | [5 empty] | About 57 MW power interruption occurred under
and was switched on at 00:20(1/7/22). | [5 empty] | Barishal(N) S/S area from 00:07 to 00:20(1/7/22).
m) Ashuganj (East) GT was synchronized at 08:28 and shut down at 15:22.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-06-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4359600
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6606318 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1598500 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 312 | 8824830 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 236 | 6832000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5095850 | Gas shortage due to dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 75 | 1743360 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3181527 | FGMO & GT-1 S/D due to gas shortage.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1311347
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 440424
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-2 U/M and gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 100 | 2011104
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 35545
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2058480 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 929520 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2623200 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1291130
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 573274 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1185180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 414000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 981120 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 5655489 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 203 | 2716427
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 85 | 758261 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 81 | 1233720 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2313940 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2345076
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 2093760 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1935360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 84014
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1314000
| Dhaka area Total |  |  |  | 5847 | 3399 | 73347656
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 534254
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 66015
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 832320 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 2949502 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2542534
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 304272 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 282028 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 20 | 510960 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1810560 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 448560
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 552480
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 1744320 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24961
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 288 | 5000618
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1368550
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 108 | 2361054
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 77 | 1349760 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2169109 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1356 | 27251857
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4669000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7009800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 4777000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 1722700 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 478872 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 296640 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 150545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1132374
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 3245090 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 825880
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 123 | 2831270 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2902560
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 500940
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227520
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3089280
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 640600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 502240 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 1946304 | low demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1535520 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 889920 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 116 | 2664000
| Cumilla Area Total |  |  |  | 2885 | 2069 | 42038055
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2064000 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 490392
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 177 | 3024000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1519200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 109250
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 520800
| Mymensingh Area Total |  |  |  | 614 | 424 | 7736542
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1033000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 970728 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2664654 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 661800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 35 | 816408 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 219920
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1385184
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1901760
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2892500 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 6 | 423520 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 527520
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7076500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9395000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244080
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9515700
| Sylhet Area Total |  |  |  | 2477 | 1664 | 39728274
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 860 | 21334545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 534720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 375360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 222 | 95029440
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9088 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 4233312 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 357750
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 491520
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 2040960 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 961920
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 276480
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1612 | 125645095
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 1345056 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 29 | 540543 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 84 | 2039617 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 13101400 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4801145
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 117600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 935 | 21945361
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 444944 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 27 | 250343 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 494912 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 343994 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 217 | 4960264
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 149 | 3968518 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 373 | 9040254 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 400299 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 481680
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184122
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 997912 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 80 | 1137141 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2109696 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2593248
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17160
| Rajshahi Area Total |  |  |  | 2129 | 1304 | 27424487
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4275700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1866480 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51040
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1653312 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 363 | 7846532
| Total |  |  |  | 21396 | 13126 | 372963859
| Eastern Grid Total |  |  |  | 14205 | 8912 | 190102384
| Western Grid Total |  |  |  | 7191 | 4214 | 182861475
| National Grid Total |  |  |  | 21396 | 13126 | 372963859
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-06-30
(a) ENTIRE EASTERN GRID : |  | 8521.23 | MW | (b) ENTIRE WESTERN GRID : |  | 4103.4 | MW
i) Dhaka area |  | 4656.23 | MW | i) Khulna area |  | 1579 | MW
ii) Chittagong area |  | 1324 | MW | ii) Rajshahi area |  | 1321.4 | MW
iii) Comilla area |  | 1146 | MW | iii) Barisal area |  | 374 | MW
iv) Mymensingh area |  | 995 | MW | iv) Rangpur area |  | 829 | MW
v) Sylhet area |  | 400 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12624.63 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Aftabnagar | 32 | 00:00 | Hasnabad | 86 | 21:00 | Palashbari | 110 | 00:00
Agargaon | 89 | 13:00 | Hathazari | 93 | 19:00 | Panchagarh | 62 | 20:00
Agrabad | 80 | 12:00 | Ishurdi | 77 | 19:30 | Patuakhali | 116 | 22:00
AKS | 10 | 20:00 | Jaldhaka | 65 | 21:00 | Payra | 1.15 | 18:30
AKSML | 139 | 07:00 | Jamalpur | 124 | 02:00 | PHP | 7 | 02:00
Amnura | 53 | 00:00 | Jashore | 120 | 21:00 | Purbachal | 18 | 00:00
Ashuganj | 33 | 00:00 | Jhenaidah | 120 | 20:00 | Purbasadipur | 119 | 21:00
Bagerhat | 103 | 19:30 | Joydebpur | 207 | 20:00 | Rahim | 14 | 18:00
Bakulia | 131 | 12:00 | Joypurhat | 63 | 00:00 | Rajbari | 56 | 01:00
Banani | 53 | 10:00 | Juldah | 28 | 00:00 | Rajendrapur | 103 | 22:00
Bangabhaban | 20 | 10:00 | Kabirpur | 272 | 15:00 | Rajshahi | 157 | 21:00
Barapukuria | 49 | 00:00 | Kachua | 70 | 00:00 | Rajshahi | 30 | 22:00
Barguna | 20 | 22:00 | Kallyanpur | 99 | 00:00 | Ramganj | 112 | 22:00
Barishal | 102 | 20:00 | Kalurghat | 25 | 20:00 | Rampur | 22 | 19:00
Barishal | 66 | 19:30 | Kamrangirchar | 72 | 19:00 | Rangamati | 14 | 20:00
Baroaulia | 69 | 00:00 | Kaptai | 4.2 | 19:00 | Rangpur | 134 | 20:00
Baroirhat | 64 | 19:30 | Kazla | 87 | 19:30 | Ruppur | 4.6 | 10:00
Bashundhara | 155 | 12:00 | Keranigonj | 64 | 19:30 | Saidpur | 108 | 21:00
BashundharaCement | 6 | 00:00 | Khagrachori | 24 | 19:00 | Satkhira | 125 | 01:00
Beanibazar | 62 | 22:00 | Khulna | 94 | 00:00 | Satmasjid | 98 | 19:30
Benapole | 58 | 23:00 | Khulshi | 180 | 19:30 | Savar | 187 | 11:00
Bhaluka | 154 | 19:30 | Kishoreganj | 130 | 21:00 | Shahjadpur | 92 | 21:00
Bhandaria | 58 | 00:00 | Kodda | 308 | 09:00 | Shahjibazar | 107 | 00:00
Bhangura | 34 | 20:00 | KSRM | 33.32 | 15:00 | Shahmirpur | 45 | 19:30
Bheramara(GK) | 57 | 00:00 | Kulaura | 42 | 19:30 | Shariatpur | 74 | 00:00
Bhulta | 267 | 00:00 | Kurigram | 62 | 19:30 | Sherpur | 124 | 19:30
Bog-Sherpur | 64 | 20:00 | Kushtia | 136 | 19:30 | Shikalbaha | 31 | 23:00
Bogura | 159 | 00:00 | Lalbag | 91 | 19:00 | Shitalakhya | 121 | 11:00
Borhanuddin | 41 | 23:00 | Lalmonirhat | 50 | 20:00 | Sholosohor | N/A | N/A
Brahmanbaria | 156 | 00:00 | Madanganj | 99 | 19:00 | Shyampur | 170 | 12:00
BSRM | 162 | 11:00 | Madaripur | 102 | 22:00 | Siddhirganj | 114 | 10:00
Cantonment | 144 | 11:00 | Madartek | 81 | 00:00 | Sirajganj | 98 | 21:00
Chandpur | 64 | 00:00 | Madunaghat | 57 | 19:30 | Sonargaon | 90 | 00:00
Chandraghona | 32 | 19:00 | Magura | 54 | 23:00 | Sreemongol | 53 | 19:30
Chapai | 66 | 11:00 | Mahasthangarh | 66 | 00:00 | Srinagar | 44.77 | 22:00
Charsaidpur | 48 | 00:00 | Manikganj | 83 | 22:00 | SSM | 3 | 12:00
Chauddagram | 61 | 22:00 | Maniknagar | 70 | 12:00 | Sunamganj | 39 | 22:00
Chhatak | 35 | 18:30 | Matarbari | 38 | 00:00 | Sylhet | 124 | 19:30
Chowmuhani | 190 | 19:30 | Matuail | 64 | 12:00 | Tangail | 209 | 21:00
Chuadanga | 105 | 21:00 | Millgate | 58 | 10:00 | Thakurgaon | 87 | 20:00
Coxsbazar | 102 | 00:00 | Mirpur | 128 | 19:00 | TK | 29.5 | 23:00
Cumilla(N) | 144 | 22:00 | Mirsorai | N/A | N/A | Tongi | 133 | 11:00
Cumilla(S) | 150 | 20:00 | Mithapukur | 36 | 19:00 | Ullon | 135 | 09:00
Daudkandi | 140 | 00:00 | Modern | 0 | 00:00 | Uttara | 86 | 11:00
Dhaka | 38 | 12:00 | Mogbazar | 123 | 13:00 | UttaraNew | 17 | 00:00
Dhamrai | 128 | 19:30 | Mongla | 38 | 10:00 | Zigatola | 42 | 20:00
Dhanmondi | 143 | 13:00 | Motijheel | 37 | 13:00
Dohazari | 92 | 19:00 | Munshiganj | 106 | 00:00
Faridpur | 145 | 00:00 | Mymensingh | 207 | 20:00
Fatullah | 67 | 10:00 | Naogaon | 116 | 00:00
Fenchuganj | 38 | 00:00 | Narail | 52 | 20:00
Feni | 103 | 21:00 | Narinda | 70 | 14:00
Ghorashal | 61 | 00:00 | Narshingdi | 180 | 00:00
Goalpara | 28 | 00:00 | Natore | 135 | 22:00
Gollamari | 45 | 00:00 | Nawabganj | 51.6 | 22:00
Gopalganj | 96 | 19:30 | Netrakona | 115 | 22:00
GPH | 95 | 16:00 | New | 84.4 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-06-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 401 | 06:00 | 383 | 16:00 | Kaliakoir | 480 | 18:30 | 281 | 10:00
| Bibiana | 412 | 05:00 | 401 | 12:00 | Payra | 421 | 08:00 | 408 | 22:00
| BIPTC | 399 | 04:00 | 394 | 15:00
| Gopalganj_I | 421 | 08:00 | 398 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 04:00 | 214 | 10:00 | Hathazari | 237 | 20:00 | 228 | 16:00
| AKSML | 233 | 04:00 | 227 | 13:00 | Ishurdi | 236 | 19:00 | 227 | 00:00
| Aminbazar | 226 | 01:00 | 217 | 10:00 | Jhenaidah | 231 | 19:00 | 222 | 00:00
| Baghabari | 233 | 16:00 | 228 | 20:00 | Kaliakoir | 228 | 05:00 | 219 | 09:00
| Barapukuria | 228 | 18:00 | 216 | 21:00 | Keranigonj | 225 | 02:00 | 217 | 22:00
| Barishal | 243 | 17:00 | 228 | 00:00 | Khulna(S) | 239 | 11:00 | 229 | 23:00
| Bheramara | 257 | 10:00 | 225 | 00:00 | Maniknagar | 228 | 02:00 | 220 | 10:00
| Bhulta | 231 | 01:00 | 222 | 10:00 | Meghnaghat | 230 | 00:00 | 224 | 15:00
| Bibiana | 242 | 06:00 | 235 | 13:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 19:00 | 224 | 23:00 | Rajshahi | 235 | 19:00 | 223 | 07:00
| Bogura | 231 | 06:00 | 222 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 14:00 | 235 | 00:00 | Rampura | 228 | 04:00 | 221 | 10:00
| BSRM | 235 | 23:00 | 228 | 15:00 | Shikalbaha | 238 | 22:00 | 229 | 16:00
| Cumilla(N) | 232 | 06:00 | 226 | 10:00 | Shyampur | 226 | 01:00 | 217 | 10:00
| Fenchuganj | 243 | 06:00 | 239 | 01:00 | Siddhirganj | 231 | 05:00 | 222 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 17:00 | 227 | 21:00
| GPH | 236 | 23:00 | 228 | 15:00 | Tongi | 226 | 04:00 | 218 | 10:00
| Haripur | 227 | 00:00 | 220 | 10:00
| Hasnabad | 227 | 21:00 | 217 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 05:00 | 127 | 17:00 | Manikganj | 133 | 05:00 | 130 | 09:00
| Agargaon | 134 | 02:00 | 126 | 10:00 | Maniknagar | 135 | 04:00 | 128 | 18:00
| Agrabad | 138 | 20:00 | 132 | 15:00 | Matarbari | 128 | 07:00 | 118 | 03:00
| AKS | 137 | 03:00 | 131 | 14:00 | Matuail | 134 | 03:00 | 129 | 10:00
| Aminbazar | 132 | 01:00 | 124 | 10:00 | Millgate | 134 | 06:00 | 126 | 09:00
| Amnura | 136 | 18:30 | 126 | 07:00 | Mirpur | 133 | 02:00 | 124 | 17:00
| Ashuganj | 136 | 06:00 | 133 | 00:00 | Mithapukur | 134 | 06:00 | 124 | 01:00
| Bagerhat | 135 | 11:00 | 130 | 00:00 | Modern | 138 | 21:00 | 133 | 15:00
| Bakulia | 139 | 20:00 | 133 | 15:00 | Mogbazar | 136 | 04:00 | 128 | 13:00
| Banani | 133 | 01:00 | 125 | 10:00 | Mongla | 134 | 11:00 | 128 | 00:00
| Bangabhaban | 135 | 01:00 | 128 | 10:00 | Motijheel | 135 | 01:00 | 128 | 10:00
| Barapukuria | 136 | 18:00 | 127 | 21:00 | Munshiganj | 136 | 02:00 | 130 | 09:00
| Barguna | 139 | 05:00 | 129 | 22:00 | Mymensingh | 132 | 07:00 | 118 | 00:00
| Barishal | 140 | 06:00 | 129 | 22:00 | Naogaon | 133 | 18:30 | 122 | 00:00
| Barishal | 142 | 06:00 | 130 | 22:00 | Narail | 134 | 11:00 | 129 | 00:00
| Baroaulia | 140 | 04:00 | 134 | 16:00 | Narinda | 0 | 00:00 | N/A | N/A
| Baroirhat | 133 | 07:00 | 129 | 00:00 | Narshingdi | 138 | 01:00 | 125 | 09:00
| Bashundhara | 134 | 02:00 | 126 | 10:00 | Natore | 135 | 18:30 | 128 | 00:00
| BashundharaCement | 135 | 22:00 | 129 | 10:00 | Nawabganj | 137 | 05:00 | 128 | 10:00
| Beanibazar | 135 | 06:00 | 128 | 19:00 | Netrakona | 132 | 13:00 | 117 | 00:00
| Benapole | 134 | 18:00 | 127 | 00:00 | New | 134 | 04:00 | 126 | 17:00
| Bhaluka | 131 | 06:00 | 116 | 00:00 | Niamatpur | 132 | 18:00 | 115 | 21:00
| Bhandaria | 141 | 07:00 | 125 | 21:00 | Noapara | 137 | 19:00 | 132 | 22:00
| Bhangura | 139 | 19:00 | 132 | 21:00 | Pabna | 136 | 19:00 | 130 | 22:00
| Bheramara | 137 | 19:00 | 133 | 00:00 | Palashbari | 133 | 06:00 | 123 | 00:00
| Bheramara(GK) | 138 | 17:00 | 132 | 00:00 | Panchagarh | 134 | 06:00 | 116 | 21:00
| Bhulta | 127 | 02:00 | 123 | 09:00 | Patuakhali | 138 | 05:00 | 131 | 23:00
| Bog-Sherpur | 136 | 17:00 | 128 | 21:00 | Payra | 140 | 08:00 | 133 | 22:00
| Bogura | 136 | 17:00 | 129 | 23:00 | PHP | 133 | 06:00 | 127 | 02:00
| Bogura | 136 | 06:00 | 130 | 01:00 | Purbachal | 134 | 04:00 | 127 | 09:00
| Brahmanbaria | 132 | 09:00 | 127 | 1:00 | Purbasadipur | 135 | 05:00 | 119 | 21:00
| Cantonment | 133 | 02:00 | 126 | 10:00 | Rahim | 135 | 22:00 | 130 | 09:00
| Chandpur | 140 | 18:00 | 134 | 01:00 | Rajbari | 138 | 09:00 | 128 | 00:00
| Chandraghona | 138 | 06:00 | 134 | 16:00 | Rajendrapur | 134 | 01:00 | 130 | 10:00
| Chapai | 135 | 19:30 | 127 | 07:00 | Rajshahi | 133 | 17:00 | 127 | 00:00
| Charsaidpur | 137 | 06:00 | 130 | 10:00 | Rajshahi | 134 | 16:00 | 124 | 02:00
| Chauddagram | 134 | 11:00 | 129 | 01:00 | Ramganj | 135 | 07:00 | 129 | 19:00
| Chhatak | 135 | 05:00 | 129 | 22:00 | Rampur | 139 | 20:00 | 133 | 00:00
| Chowmuhani | 132 | 23:00 | 124 | 02:00 | Rampura | 135 | 05:00 | 128 | 10:00
| Chuadanga | 132 | 17:00 | 121 | 00:00 | Rangamati | 138 | 08:00 | 134 | 15:00
| Coxsbazar | 132 | 07:00 | 118 | 19:00 | Rangpur | 132 | 05:00 | 121 | 21:00
| Cumilla(N) | 136 | 06:00 | 132 | 14:00 | Ruppur | 136 | 16:00 | 132 | 00:00
| Cumilla(S) | 135 | 07:00 | 129 | 15:00 | Saidpur | 133 | 17:00 | 121 | 00:00
| Daudkandi | 135 | 01:00 | 130 | 09:00 | Satkhira | 133 | 09:00 | 125 | 23:00
| Dhaka | 135 | 05:00 | 127 | 10:00 | Satmasjid | 134 | 04:00 | 126 | 10:00
| Dhamrai | 132 | 06:00 | 123 | 10:00 | Savar | 132 | 04:00 | 122 | 10:00
| Dhanmondi | 136 | 05:00 | 130 | 10:00 | Shahjadpur | 140 | 17:00 | 135 | 00:00
| Dohazari | 137 | 09:00 | 128 | 02:00 | Shahjibazar | 136 | 08:00 | 131 | 00:00
| Faridpur | 135 | 07:00 | 130 | 00:00 | Shahmirpur | 139 | 20:00 | 133 | 15:00
| Fatullah | 135 | 22:00 | 128 | 10:00 | Shariatpur | 139 | 08:00 | 126 | 22:00
| Fenchuganj | 139 | 06:00 | 135 | 02:00 | Sherpur | 138 | 20:00 | 120 | 00:00
| Feni | 134 | 07:00 | 127 | 02:00 | Shikalbaha | 140 | 20:00 | 130 | 11:00
| Ghorashal | 138 | 01:00 | 136 | 00:00 | Shikalbaha | 139 | 09:00 | 134 | 16:00
| Goalpara | 137 | 08:00 | 133 | 22:00 | Shitalakhya | 136 | 03:00 | 130 | 10:00
| Gollamari | 138 | 08:00 | 131 | 02:00 | Sholosohor | N/A | N/A | N/A | N/A
| Gopalganj | 137 | 06:00 | 132 | 00:00 | Shyampur | 133 | 02:00 | 128 | 12:00
| Gopalganj_I | 141 | 08:00 | 132 | 23:00 | Shyampur | 135 | 22:00 | 121 | 21:00
| Gulshan | 134 | 03:00 | 127 | 10:00 | Siddhirganj | 134 | 00:00 | 130 | 17:00
| Halishahar | 139 | 21:00 | 132 | 15:00 | Sirajganj | 136 | 18:30 | 129 | 21:00
| Haripur | 135 | 22:00 | 130 | 09:00 | Sonargaon | 135 | 06:00 | 131 | 15:00
| HaripurSBU | 135 | 00:00 | 131 | 13:00 | Sreemongol | 138 | 08:00 | 134 | 00:00
| Hasnabad | 136 | 23:00 | 131 | 09:00 | Srinagar | 136 | 22:00 | 128 | 10:00
| Hathazari | 140 | 08:00 | 134 | 14:00 | SSM | 142 | 22:00 | 137 | 14:00
| Ishurdi | 137 | 19:00 | 132 | 24:00 | Sunamganj | 134 | 06:00 | 128 | 22:00
| Jaldhaka | 131 | 17:00 | 118 | 21:00 | Sylhet | 135 | 05:00 | 132 | 00:00
| Jamalpur | 140 | 20:00 | 121 | 02:00 | Tangail | 137 | 13:00 | 129 | 00:00
| Jashore | 134 | 18:00 | 130 | 03:00 | Thakurgaon | 133 | 17:00 | 114 | 23:00
| Jhenaidah | 138 | 18:30 | 130 | 22:00 | TK | 138 | 00:00 | 135 | 12:00
| Jhenaidah | 137 | 19:00 | 131 | 00:00 | Tongi | 136 | 04:00 | 128 | 10:00
| Joydebpur | 141 | 18:00 | 136 | 10:00 | Ullon | 135 | 04:00 | 128 | 10:00
| Joypurhat | 135 | 06:00 | 120 | 00:00 | Uttara | 132 | 06:00 | 123 | 10:00
| Juldah | 139 | 20:00 | 133 | 15:00 | UttaraNew | 132 | 01:00 | 122 | 10:00
| Kabirpur | 137 | 01:00 | 124 | 10:00 | Zigatola | 136 | 02:00 | 130 | 10:00
| Kachua | 139 | 08:00 | 132 | 03:00
| Kaliakoir | 140 | 05:00 | 130 | 00:00
| Kallyanpur | 132 | 02:00 | 124 | 10:00
Page 7 of 7

## L-Curve
Date | 2022-06-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 182 | 8659 | 4010 | 12669 |  |  |  | QF-LDC-11
0:30 | 161 | 8499 | 4141.5 | 12640.5 | Date: | 2022-06-30
1:00 | 140 | 8339 | 4273 | 12612
1:30 | 108 | 8252.5 | 4199 | 12451.5
2:00 | 76 | 8166 | 4125 | 12291
2:30 | 74 | 8085.5 | 4028 | 12113.5 | [5 empty] | Gen. at Eve. Peak | 13126 | 13126 MW (21:00 )
3:00 | 72 | 8005 | 3931 | 11936 | [6 empty] | 21:00
3:30 | 80 | 7937 | 3917.5 | 11854.5 | [5 empty] | Gen. at Day Peak | 11448 | 11448 MW (12:00 )
4:00 | 88 | 7869 | 3904 | 11773 | [6 empty] | 12:00
4:30 | 95 | 7818 | 3824.5 | 11642.5 | [5 empty] | Highest Generation | 13126
5:00 | 102 | 7767 | 3745 | 11512 | [6 empty] | 21:00
5:30 | 109 | 7478.5 | 3519.5 | 10998
6:00 | 116 | 7190 | 3294 | 10484
6:30 | 62 | 7083 | 3231 | 10314
7:00 | 8 | 6976 | 3168 | 10144
7:30 | 59 | 6981.5 | 3190 | 10171.5
8:00 | 110 | 6987 | 3212 | 10199
8:30 | 172 | 7250 | 3278.5 | 10528.5
9:00 | 234 | 7513 | 3345 | 10858
9:30 | 279 | 7559.5 | 3392 | 10951.5
10:00 | 324 | 7606 | 3439 | 11045
10:30 | 294 | 7627.5 | 3494 | 11121.5
11:00 | 264 | 7649 | 3549 | 11198
11:30 | 293 | 7727.5 | 3595.5 | 11323
12:00 | 322 | 7806 | 3642 | 11448
12:30 | 343 | 7792.5 | 3705 | 11497.5
13:00 | 364 | 7779 | 3768 | 11547
13:30 | 378 | 7697.5 | 3678 | 11375.5
14:00 | 392 | 7616 | 3588 | 11204
14:30 | 401 | 7762.5 | 3597.5 | 11360
15:00 | 410 | 7909 | 3607 | 11516
15:30 | 490 | 7733.5 | 3650.5 | 11384
16:00 | 570 | 7558 | 3694 | 11252
16:30 | 609 | 7404 | 3700.5 | 11104.5
17:00 | 648 | 7250 | 3707 | 10957
17:30 | 613 | 7257.5 | 3621.5 | 10879
18:00 | 578 | 7265 | 3536 | 10801
18:30 | 534 | 7749 | 3680 | 11429
19:00 | 490 | 8233 | 3824 | 12057
19:30 | 208 | 8751 | 4358 | 13109
20:00 | 158 | 8619 | 4328 | 12947 |  |  |  | Executive Engineer
20:30 | 102 | 8765.5 | 4271 | 13036.5 |  |  |  | Network Operation Division
21:00 | 46 | 8912 | 4214 | 13126
21:30 | 68 | 8880.5 | 4175 | 13055.5
22:00 | 90 | 8849 | 4136 | 12985 |  |  |  |  | Page 6 of 7
22:30 | 82 | 8805.5 | 4105 | 12910.5
23:00 | 74 | 8762 | 4074 | 12836
23:30 | 128 | 8710.5 | 4042 | 12752.5
24:00 | 182 | 8659 | 4010 | 12669
13126 MW (21:00 )
11448 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-06-30 |  | Energy |  | 372963859
[13 empty] | 2022-06-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3661 | 860 | 2069 | 575 | 3529 | 775 | 127 | 438 | 704 | 148 | 0 | 0
0:30 | 3658.5 | 868.5 | 2031.5 | 759 | 3347.5 | 786 | 126 | 437.5 | 698.5 | 143 | 0 | 0 | Date: | 2022-06-30
1:00 | 3656 | 877 | 1994 | 943 | 3166 | 797 | 125 | 437 | 693 | 138 | 0 | 0
1:30 | 3685.5 | 883 | 2007.5 | 803 | 3129 | 791 | 125 | 440 | 667.5 | 137 | 0 | 0 | [8 empty] | Total Energy | 372.9639 | Total Energy Gen 372.964 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 372.964 MKWHr
2:00 | 3715 | 889 | 2021 | 663 | 3092 | 785 | 125 | 443 | 642 | 136 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3735.5 | 889 | 2056.5 | 464 | 3080.5 | 770 | 123 | 442.5 | 638 | 134 | 0 | 0 | [8 empty] | Energy Requirement | 372.9639
3:00 | 3756 | 889 | 2092 | 265 | 3069 | 755 | 121 | 442 | 634 | 132 | 0 | 0
3:30 | 3764 | 899.5 | 2104 | 180 | 3048 | 755 | 121 | 441.5 | 629 | 131 | 0 | 0 | [6 empty] | Shortage
4:00 | 3772 | 910 | 2116 | 95 | 3027 | 755 | 121 | 441 | 624 | 130 | 0 | 0
4:30 | 3771.5 | 909.5 | 2120.5 | 47.5 | 3024 | 755 | 121 | 427 | 549.5 | 125 | 0 | 0
5:00 | 3771 | 909 | 2125 | 0 | 3021 | 755 | 121 | 413 | 475 | 120 | 0 | 0
5:30 | 3776.5 | 909 | 2074 | 0 | 2791.5 | 725 | 121.5 | 334 | 310.5 | 117 | 3 | 0
6:00 | 3782 | 909 | 2023 | 0 | 2562 | 695 | 122 | 255 | 146 | 114 | 6 | 0
6:30 | 3788.5 | 909 | 2071 | 0 | 2354.5 | 665 | 122.5 | 262.5 | 146 | 111 | 14 | 0 |  |  |  |  | Coal
7:00 | 3795 | 909 | 2119 | 0 | 2147 | 635 | 123 | 270 | 146 | 108 | 22 | 0
7:30 | 3765 | 909.5 | 2083 | 0 | 2182 | 630 | 123.5 | 275 | 179 | 110 | 44.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3735 | 910 | 2047 | 0 | 2217 | 625 | 124 | 280 | 212 | 112 | 67 | 0
8:30 | 3760 | 911 | 2059.5 | 0 | 2522 | 610 | 124 | 275 | 220 | 114 | 63 | 0
9:00 | 3785 | 912 | 2072 | 0 | 2827 | 595 | 124 | 270 | 228 | 116 | 59 | 0
9:30 | 3780 | 893.5 | 2068.5 | 0 | 2884 | 585 | 124 | 315 | 248 | 118 | 85.5 | 0
10:00 | 3775 | 875 | 2065 | 0 | 2941 | 575 | 124 | 360 | 268 | 120 | 112 | 0
10:30 | 3725 | 875 | 2021.5 | 86.5 | 2974.5 | 585 | 124 | 398 | 299 | 118 | 107.5 | 0
11:00 | 3675 | 875 | 1978 | 173 | 3008 | 595 | 124 | 436 | 330 | 116 | 103 | 0
11:30 | 3629.5 | 875.5 | 1966 | 374 | 3015.5 | 595 | 124 | 436.5 | 316 | 119 | 86.5 | 0
12:00 | 3584 | 876 | 1954 | 575 | 3023 | 595 | 124 | 437 | 302 | 122 | 70 | 0
12:30 | 3602.5 | 875.5 | 1932.5 | 535.5 | 3053 | 605 | 124 | 438.5 | 354.5 | 129 | 62.5 | 0
13:00 | 3621 | 875 | 1911 | 496 | 3083 | 615 | 124 | 440 | 407 | 136 | 55 | 0
13:30 | 3621 | 875 | 1911 | 496 | 3083 | 615 | 124 | 440 | 407 | 136 | 55 | 0
14:00 | 3621 | 875 | 1911 | 496 | 3083 | 615 | 124 | 440 | 407 | 136 | 55 | 0
14:30 | 3548.5 | 875.5 | 1890 | 490 | 3145 | 630 | 122.5 | 441 | 420.5 | 137 | 48.5 | 0
15:00 | 3476 | 876 | 1869 | 484 | 3207 | 645 | 121 | 442 | 434 | 138 | 42 | 0
15:30 | 3361.5 | 876.5 | 1863 | 495.5 | 3198 | 640 | 100 | 442 | 449 | 136 | 40.5 | 0
16:00 | 3247 | 877 | 1857 | 507 | 3189 | 635 | 79 | 442 | 464 | 134 | 39 | 0
16:30 | 3339 | 876.5 | 1851 | 253.5 | 3224 | 630 | 99 | 444 | 494 | 130 | 27.5 | 0
17:00 | 3339 | 876 | 1845 | 0 | 3259 | 625 | 119 | 446 | 524 | 126 | 16 | 0
17:30 | 3307 | 876.5 | 1823.5 | 0 | 3267.5 | 610 | 119.5 | 399.5 | 513 | 125 | 11.5 | 0
18:00 | 3275 | 877 | 1802 | 0 | 3276 | 595 | 120 | 353 | 502 | 124 | 7 | 0
18:30 | 3357.5 | 869 | 1846 | 268.5 | 3426 | 595 | 121.5 | 367.5 | 586.5 | 133 | 3.5 | 0
19:00 | 3440 | 861 | 1890 | 537 | 3576 | 595 | 123 | 382 | 671 | 142 | 0 | 0
19:30 | 3551 | 861 | 1920 | 948 | 3867 | 705 | 124 | 432 | 762 | 148 | 0 | 0
20:00 | 3615 | 861 | 1887 | 705 | 3929 | 705 | 124 | 439 | 747 | 150 | 0 | 0
20:30 | 3644 | 860.5 | 1945.5 | 677 | 3948 | 715 | 124.5 | 439 | 751 | 148 | 0 | 0
21:00 | 3673 | 860 | 2004 | 649 | 3967 | 725 | 125 | 439 | 755 | 146 | 0 | 0
21:30 | 3677 | 860 | 2007 | 560 | 3959.5 | 750 | 125 | 439.5 | 746.5 | 148 | 0 | 0
22:00 | 3681 | 860 | 2010 | 471 | 3952 | 775 | 125 | 440 | 738 | 150 | 0 | 0
22:30 | 3692.5 | 860 | 2009 | 409 | 3938.5 | 775 | 125.5 | 441.5 | 727.5 | 150 | 0 | 0
23:00 | 3704 | 860 | 2008 | 347 | 3925 | 775 | 126 | 443 | 717 | 150 | 0 | 0
23:30 | 3682.5 | 860 | 2038.5 | 461 | 3727 | 775 | 126.5 | 440.5 | 710.5 | 149 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30° C
24:00 | 3661 | 860 | 2069 | 575 | 3529 | 775 | 127 | 438 | 704 | 148 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 372.964 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 372.964 MKWHr
Note on W13: Author:

## Generation
g | 2022-06-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 86 | 86 | 86 | 87 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 44 | 84 | 85 |  | 88 | 89 | 89 | 90 | 90 | 91 | 92 | 2109502
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 0 |  |  | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 534254
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 1 |  |  |  |  | 15 | 14 | 15 | 16 | 7 | 2 | 0 | [8 empty] | 66015
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 46 | 51 | 51 | 51 | 51 | 51 | 51 | 282028
12 | Hathazari 100 MW peaking PP | 51 | 0 | [17 empty] | 30 | 48 | 42 | 52 | 52 | 51 | 51 | 304272
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2542534
| Daudkandi 200 MW PP (B.Trac) | 200 | 150 | 50 | 20 | 0 | [5 empty] | 20 | 200 | 200 | 50 | 100 | 200 | 0 |  |  | 190 | 200 | 160 | 150 | 100 | 30 | 100 | 1946304
14 | Titas 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 0 | [6 empty] | 41 | 50 | 50 | 46 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 825880
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [26 empty] | 35545
18 | Kodda 300 MW PP Unit-2 (Summit) | 260 | 260 | 260 | 260 | 260 | 130 | 80 | 100 | 230 | 243 | 230 | 213 | 220 | 218 | 240 | 245 | 243 | 243 |  | 243 | 243 | 260 | 275 | 276 | 275 | 276 | 5655489
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 150545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4359600
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 200 | 6606318
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 34 | 0 | 0 | 0 |  |  |  |  | 10 | 10 |  | 10 | 10 | 28 | 33 | 36 | 36 | 36 | 478872
33 | Ashuganj 225 MW CCPP | 211 | 209 | 208 | 211 | 209 | 212 | 208 | 212 | 181 | 145 | 139 | 160 | 190 | 172 | 173 | 175 | 178 | 186 |  | 209 | 212 | 212 | 209 | 210 | 212 | 208 | 4669000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 280 | 315 | 270 | 270 | 200 | 147 |  |  |  |  | 15 | 100 | 105 |  | 150 | 225 | 300 | 300 | 300 | 300 | 300 | 4777000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 7009800
| Ashuganj 420 MW CCPP(East) | [8 empty] | 145 | 286 | 240 | 290 | 303 | 294 | 240 | 0 | [10 empty] | 1722700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0 | 0 | 0 |  |  |  | 2 | 5 |  | 5 | 10 | 20 | 50 | 53 | 46 | 49 | 296640
36 | Chandpur 150 MW CCPP | 122 | 122 | 122 | 122 | 122 | 121 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 |  | 122 | 122 | 122 | 123 | 123 | 123 | 123 | 2831270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 325 | 372 | 394 | 398 | 398 | 401 | 403 | 404 | 403 | 404 | 402 | 392 | 374 | 359 | 342 | 331 | 323 | 317 |  | 312 | 313 | 312 | 312 | 314 | 336 | 358 | 8824830
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5095850
41 | Haripur 360MW CCPP(HPL) | 231 | 263 | 292 | 312 | 327 | 327 | 333 | 335 | 332 | 350 | 340 | 320 | 299 | 285 | 273 | 258 | 249 | 242 |  | 238 | 238 | 238 | 236 | 237 | 274 | 288 | 6832000
42 | RPCL 210MW CCPP | 107 | 103 | 106 | 106 | 106 | 106 | 105 | 95 | 71 | 70 | 70 | 69 | 67 | 66 | 66 | 66 | 69 | 70 |  | 82 | 100 | 103 | 105 | 105 | 106 | 106 | 2064000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 12 | 13 | 19 | 20 | 4 | 4 | 6 | 11 | 18 | 3 | 2 |  | 0 | [6 empty] | 109250
44 | Fenchugonj CCPP Phase-1 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 1033000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 970728
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 52 | 52 | 51 | 52 | 57 | 40 | 40 | 62 | 62 | 63 | 63 | 64 | 64 | 64 | 63 | 63 | 62 |  | 62 | 64 | 64 | 63 | 63 | 62 | 63 | 1385184
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 81 | 81 | 86 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 81 | 81 | 78 | 78 | 84 | 50 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1901760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2892500
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 5 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 423520
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244080
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 | 11 | 11 | 11 | 11 | 0 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219920
55 | Fenchugonj 51 MW PP (Barakatullah) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 661800
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 527520
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 280 | 290 | 290 | 280 | 260 | 300 | 290 | 280 | 290 | 290 | 300 | 270 | 270 | 300 | 300 | 280 | 290 |  | 300 | 275 | 275 | 290 | 290 | 280 | 290 | 7076500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 365 |  | 394 | 400 | 400 | 400 | 400 | 400 | 400 | 9515700
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 17 | 17 |  | 17 | 17 | 17 | 55 | 55 | 35 | 35 | 573274
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 14 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520800
60 | Barabkunda 22 MW PP (Regent) | 19 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 16 | 16 | 16 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 448560
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 440424
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 490392
63 | Impoprt (Tripura) | 138 | 136 | 132 | 130 | 120 | 114 | 108 | 112 | 116 | 120 | 116 | 122 | 136 | 136 | 138 | 134 | 126 | 124 |  | 142 | 148 | 150 | 146 | 150 | 150 | 148 | 3089280
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 39 | 39 | 22 | 36 | 14 | 4 | 4 | 3 | 3 | 8 | 9 | 4 | 6 | 6 | 16 |  | 23 | 23 | 29 | 28 | 35 | 38 | 40 | 552480
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500940
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 227520
67 | Jangalia 33MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 21 | 15 | 16 | 16 | 13 | 13 | 25 | 25 | 25 | 23 |  | 23 | 25 | 29 | 33 | 33 | 33 | 33 | 640600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 502240
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 20 | 27 | 26 | 27 | 27 | 27 | 27 |  | 20 | 20 | 20 | 26 | 26 | 26 | 18 | 585180
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 32 | 32 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | 8 | 8 | 15 |  | 15 | 15 | 15 | 15 | 16 | 16 | 23 | 414000
73 | Ghorashal 108MW PP (Regent) | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 64 | 64 | 64 | 68 | 68 | 68 | 68 | 68 |  | 69 | 70 | 70 | 71 | 71 | 71 | 71 | 1598500
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 54 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 60 | 95 | 95 |  | 97 | 97 | 98 | 96 | 99 | 96 | 49 | 1535520
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 | 17 | 17 | 48 | 54 | 54 | 54 | 60 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 1935360
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 83 | 8 | 14 | 80 | 92 | 92 | 92 | 92 | 92 | 100 | 94 | 92 | 70 |  | 60 | 100 | 88 | 100 | 100 | 100 | 100 | 2011104
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 8 | 8 | 13 | 42 | 42 | 41 | 41 | 41 | 42 | 41 | 41 | 41 | 41 |  | 0 | 26 | 34 | 50 | 50 | 50 | 50 | 981120
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 16 | 16 | 82 | 98 | 98 | 115 | 82 | 132 | 132 | 150 | 150 | 132 | 132 |  | 132 | 132 | 132 | 132 | 115 | 115 | 115 | 2623200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 88 | 94 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2345076
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 5 | 6 | 2 | 4 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 24961
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1368550
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 97 | 92 | 81 | 73 | 89 | 92 | 92 | 92 | 92 | 92 | 89 | 92 | 92 | 93 |  | 94 | 92 | 96 | 108 | 110 | 110 | 110 | 2361054
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 115 | 130 | 140 | 145 | 145 | 145 | 145 | 120 | 140 | 140 | 125 | 125 | 130 | 135 | 135 | 130 | 130 | 140 |  | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 3181527
87 | Meghnaghat 100 MW(IEL) | 78 | 77 | 72 | 72 | 72 | 72 | 72 | 67 | 65 | 73 | 65 | 71 | 68 | 70 | 72 | 70 | 72 | 73 |  | 73 | 73 | 72 | 75 | 73 | 81 | 79 | 1743360
| Meghnaghat 104 MW PP (OPCL) | 79 | 88 | 94 | 94 | 94 | 94 | 94 | 85 | 89 | 94 | 93 | 93 | 93 | 94 | 86 | 75 | 74 | 46 |  | 48 | 93 | 90 | 94 | 94 | 94 | 95 | 2093760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 510960
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 816408
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1132374
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 40 | 40 | 70 | 85 | 85 | 88 | 94 | 94 | 94 | 94 | 94 | 94 | 64 |  | 80 | 94 | 94 | 94 | 94 | 94 | 94 | 2058480
95 | Patenga 50MW PP (Baraka) | 37 | 32 | 36 | 37 | 32 | 9 | 29 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 35 | 37 |  | 39 | 40 | 42 | 44 | 44 | 44 | 44 | 832320
96 | Chattogram 108 MW PP (ECPV) | 87 | 87 | 87 | 87 | 87 | 21 | 11 | 14 | 65 | 70 | 68 | 73 | 79 | 83 | 85 | 84 | 83 | 48 |  | 62 | 89 | 91 | 92 | 93 | 93 | 87 | 1744320
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1311347
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 1291130
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2664654
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 8900
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 929520
104 | Keranigonj 300 MW PP (APR) | 300 | 184 | 54 | 24 | 0 | [5 empty] | 73 | 202 | 50 | 70 | 300 | 157 | 0 |  |  | 157 | 301 | 107 | 203 | 185 | 153 | 301 | 2716427
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 77 | 80 | 25 | 0 | [6 empty] | 25 | 25 | 0 | [5 empty] | 85 | 85 | 85 | 85 | 85 | 84 | 83 | 758261
106 | Mymensingh 200 MW PP (United) | 115 | 115 | 114 | 115 | 115 | 114 | 114 | 114 | 114 | 114 | 114 | 113 | 112 | 112 | 114 | 114 | 113 | 110 |  | 125 | 177 | 177 | 177 | 177 | 177 | 114 | 3024000
112 | Aurahati 100MW PP (Aggreko) | 81 | 82 | 81 | 26 | 0 | [5 empty] | 80 | 81 | 81 | 81 | 82 | 82 | 0 |  |  | 80 | 81 | 81 | 81 | 81 | 80 | 81 | 1233720
114 | Kodda 149 MW PP Unit-1 (Summit) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 86 | 89 | 87 | 86 | 86 | 86 | 90 | 132 |  | 133 | 133 | 134 | 133 | 133 | 133 | 89 | 2313940
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1810560
116 | Chandpur 200MW (Desh energy) | 147 | 100 | 100 | 100 | 100 | 100 | 100 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 115 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2902560
117 | Ashuganj 150MW PP (Midland) | 130 | 138 | 122 | 132 | 140 | 140 | 70 | 76 | 128 | 140 | 138 | 140 | 131 | 135 | 143 | 140 | 145 | 145 |  | 145 | 146 | 147 | 147 | 147 | 140 | 137 | 3245090
118 | Bibiyana-III 400 MW CCPP | 371 | 401 | 402 | 401 | 401 | 400 | 400 | 400 | 352 | 401 | 401 | 401 | 400 | 400 | 401 | 402 | 401 | 352 |  | 401 | 401 | 360 | 403 | 402 | 401 | 401 | 9395000
| Jamalpur 115 MW PP (United) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 58 | 59 | 59 | 58 | 58 | 32 |  | 54 | 96 | 98 | 98 | 98 | 98 | 58 | 1519200
| Anwara 300 MW PP (United) | 176 | 176 | 176 | 176 | 176 | 177 | 100 | 125 | 191 | 194 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 284 |  | 284 | 280 | 287 | 288 | 284 | 300 | 212 | 5000618
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 |  | 78 | 78 | 78 | 77 | 77 | 77 | 50 | 1349760
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2169109
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 889920
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 2 | 5 | 15 | 16 | 5 | 5 | 8 | 5 | 4 | 6 | 5 | 2 |  | 0 | [6 empty] | 84014
| Chandpur 115(Doreen) | 105 | 97 | 99 | 112 | 116 | 116 | 115 | 116 | 116 | 105 | 93 | 97 | 109 | 116 | 116 | 108 | 101 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2664000
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 43 | 55 | 52 | 43 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1314000
120 | Eastern Zone Total | 8339 | 8166 | 8005 | 7869 | 7767 | 7190 | 6976 | 6987 | 7513 | 7606 | 7649 | 7806 | 7779 | 7616 | 7909 | 7558 | 7250 | 7265 |  | 8233 | 8751 | 8619 | 8912 | 8849 | 8762 | 8659 | 190102384
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 |  | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 534720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 38 | 35 | 35 | 35 | 0 | [11 empty] | 33 | 34 |  | 34 | 45 | 35 | 34 | 34 | 29 | 25 | 375360
| Khulna 225 MW CCPP | 223 | 223 | 223 | 223 | 215 | 125 | 140 | 150 | 140 | 190 | 221 | 223 | 224 | 226 | 224 | 224 | 228 | 223 |  | 222 | 223 | 224 | 222 | 223 | 224 | 221 | 95029440
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 93 | 93 | 35 | 17 | 22 | 78 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2040960
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 14 | 46 | 24 | 66 | 63 | 36 | 15 | 2 | 3 | 1 | 2 | 1 |  | 0 | [6 empty] | 276480
131
132 | United Payra Power Ltd. | 35 | 35 | 17 | 0 | [22 empty] | 117600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 223 | 223 | 223 | 223 | 213 | 223 | 203 | 224 | 225 | 167 | 164 | 164 | 164 | 164 | 164 | 164 | 164 |  | 164 | 220 | 225 | 224 | 222 | 202 | 223 | 4801145
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 16 | 16 | 0 | [6 empty] | 63 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 48 | 32 | 32 | 32 | 1345056
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 84 | 83 | 85 | 84 | 84 | 84 | 85 | 84 | 84 | 82 |  | 85 | 85 | 86 | 84 | 85 | 86 | 86 | 2039617
140 | Bhola 33 MW PP (Venture) | 29 | 29 | 28 | 27 | 26 | 20 | 19 | 16 | 17 | 17 | 17 | 20 | 20 | 19 | 18 | 20 | 20 | 20 |  | 26 | 27 | 25 | 29 | 28 | 31 | 31 | 540543
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 50 | 0 | [8 empty] | 19 | 20 | [6 empty] | 6 | 100 | 97 | 50 | 0 |  |  | 491520
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 357750
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 10 | 10 | [5 empty] | 9088
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 32 | 15 | 15 | 0 | [7 empty] | 11 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 72 | 105 | 105 | 105 | 105 | 105 | 961920
146 | Bheramara HVDC | 877 | 889 | 889 | 910 | 909 | 909 | 909 | 910 | 912 | 875 | 875 | 876 | 875 | 876 | 876 | 877 | 876 | 877 |  | 861 | 861 | 861 | 860 | 860 | 860 | 860 | 21334545
147 | Bheramara 410 MW CCPP | 165 | 165 | 170 | 180 | 180 | 180 | 180 | 185 | 180 | 165 | 170 | 165 | 165 | 160 | 155 | 150 | 150 | 150 |  | 155 | 155 | 160 | 160 | 160 | 160 | 165 | 4233312
148 | Payra 1320 MW | 622 | 610 | 580 | 580 | 580 | 520 | 460 | 450 | 420 | 400 | 420 | 420 | 440 | 440 | 470 | 460 | 450 | 420 |  | 420 | 530 | 530 | 550 | 600 | 600 | 600 | 13101400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4275700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 0 | [8 empty] | 0 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 16 | 16 | 444944
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 1 | 1 | 4 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | [8 empty] | 17160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 214 | 220 | 219 | 218 | 198 | 130 | 130 | 130 | 130 | 170 | 215 | 214 | 216 | 219 | 218 | 218 | 218 | 130 |  | 160 | 209 | 215 | 217 | 217 | 219 | 217 | 4960264
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 159 | 157 | 157 | 157 | 157 | 158 | 168 | 165 | 166 | 166 | 163 | 157 | 154 | 152 | 149 | 145 | 145 | 145 |  | 145 | 146 | 146 | 149 | 150 | 150 | 150 | 3968518
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 388 | 386 | 414 | 414 | 414 | 370 | 400 | 406 | 414 | 393 | 391 | 377 | 372 | 353 | 358 | 360 | 359 | 324 |  | 365 | 357 | 302 | 373 | 371 | 364 | 364 | 9040254
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 23 | 22 | 23 | 14 | 0 | [11 empty] | 4 | 10 |  | 15 | 22 | 27 | 27 | 27 | 28 | 28 | 250343
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 19 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 184122
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | 25 | 25 | 25 |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 494912
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 16 | 16 | 16 | 0 | [5 empty] | 6 | 18 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 343994
168 | Santahar 50 MW Peaking PP | 37 | 35 | 35 | 35 | 0 | [11 empty] | 28 | 37 |  | 37 | 38 | 38 | 37 | 37 | 37 | 30 | 400299
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 90 | 90 | 45 | [11 empty] | 10 | 60 |  | 92 | 92 | 92 | 90 | 90 | 90 | 90 | 997912
171 | Baghabari 200 MW PP (Paramount) | 183 | 120 | 0 | [8 empty] | 48 | 120 |  | 2 | 68 | 0 |  |  | 19 | 181 | 175 | 80 | 20 | 0 | 10 | 1137141
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 35 | 35 | 70 | 70 | 70 | 87 | 94 | 94 | 94 | 94 | 94 | 70 |  | 80 | 94 | 94 | 94 | 94 | 94 | 94 | 2109696
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 50 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2593248
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 71 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 63 | 70 | 70 | 70 | 70 | 66 | 70 | 85 | 90 |  | 98 | 98 | 98 | 98 | 98 | 98 | 70 | 1866480
177 | Sympa Solar Power 8MW | [5 empty] | 1 | 1 | 2 | 3 | 4 | 4 | 5 | 7 | 7 | 6 | 4 | 3 | 2 |  | 0 | [6 empty] | 51040
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 44 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 72 | 1653312
178