## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-05 | Tuesday
|  |  | Date (day): | 2022-07-05 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11819.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13070 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-04 | 2022-07-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 80 | 80 | 80 |  | 28 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 254 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 171 | 152 | 185 | 185 | 175 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 200 | 180 | 210 | 210 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 39 | 32 | 40 | 40 |  | 60 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 45 | 40 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 40 | 40 | 40 |  | 60 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 177 | 180 | 180 | 155 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 17 | 17 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 53 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 275 | 260 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 229 | 300 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 80 | 0 | 80 |  | 20 | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel Shortage
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 72 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2797 | 2911 | 2822 | 3084 | 1613 | 1139
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 37 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 88 | 122 | 87 | 122 |  | 108 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 36 |  | 62 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 85 | 60 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 20 | 20 | 20 | 20 | 80 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 76 | 65 | 76 |  | 24 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 18 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 94 | 91 | 90 | 91 |  | 17 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 168 | 280 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 39 | 35 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 104 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 80 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1090 | 1277 | 1168 | 1401 | 350 | 615
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 205 | 180 | 205
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 270 | 270 | 270 | 90 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 220 | 200 | 260 | 100 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 8 | 20 | 8 | 20 | 25 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 50 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 137 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 85 | 85 |  | 78 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 158 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 9 | 8 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 160 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 8 | 8 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 53 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1447 | 1754 | 1774 | 1904 | 857 | 108
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 99 | 103 | 100 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 186 | 175 | 190 |  | 10 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 60 | 115 |  | 0 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 11 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 329 | 448 | 428.6 | 457 | 92 | 18
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 33 | 33 | 33 | 33 |  | 37 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 90 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 0 | 5 | 5 |  | 46 | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 0 | 5 | 35 |  | 15 | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 86 | 86
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 120 | 120 |  | 111 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 6 | 6
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 279 | 280 | 280 | 280 |  | 120 | ST under maint.
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 401 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1456 | 1432 | 1494 | 1555 | 0 | 869
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 893 | 855 | 868 | 868
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 49 | 16 | 49 |  | 66 | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 22 | 28 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 204 | 205 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 75 | 50 | 75 |  | 34 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 160 | 170 | 165 | 180 | 230 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 8 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 95 | 98 | 90 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 92 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 51 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1646 | 1718 | 1750 | 1765 | 230 | 131
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 11 | 36 | 20 | 36
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 63 | 0 | 0 | 0 | 194 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 622 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 90 | 17 | 90 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 828 | 1078 | 895 | 1078 | 194 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 24 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 16 | 16 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 43 | 34 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 24 | 16 | 30 |  | 20 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 213 | 220 | 220 |  |  | Running by HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 161 | 163 | 160 | 170 | 50 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 353 | 380 | 360 | 380 | 34 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 0 | 52 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 89 | 80 | 90 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 20 | 150 | 50 |  | Fuel shortage
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 94 | 95 |  | 18 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 944 | 1227 | 1186 | 1425 | 567 | 131
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 175 | 175 | 175 | 99 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 91 | 70 | 91 |  | 22 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 110 | 34 | 110
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 294 | 391 | 302 | 401 | 269 | 22
|  | Total |  |  |  |  | 22678 | 21396 | 10831 | 12236 | 11819.6 | 13070 | 4172 | 3033
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11460.8816 | 12947.59 | 12506.9741 | 13830.0916
| A. |  | 2022-07-04 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12242 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10741 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13636 | MW
| 3 | Day peak Generation : |  |  | 10831 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12947.59 | MW
| 4 | Evening peak Generation : |  |  | 12236 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1400 | MW
| 5 | Total Energy Generation : |  | 271.0487 | MKWHr | By Solar | 1.4022 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 112.2041 | MKWHr |  | By Oil: | 110.5313 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.321 | MKWHr |  | By Hydro: | 2.7759 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4172 | MW | Dhaka | 4825.08 | 4525.08 |  | 300
|  |  |  | For Plants S/D or M/C prob = |  |  | 3033 | MW | Chittagong | 1250.55 | 1125.55 |  | 125 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7205 | MW | Khulna | 1609.2 | 1369.2 |  | 240 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 882.52 | MMCFD |  |  | Rajshahi | 1326.4 | 1106.4 |  | 220 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 127441994.97 | ii) Oil : | Taka | 1613159305.13 | Comilla | 1262.5 | 1082.5 |  | 180 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 158083234 | Total | Taka | 1898684534.1 | Mymensingh | 1028 | 903 |  | 125 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.033 | MKWHr. | Sylhet | 472 | 427 |  | 45 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 608 | MW (E to W) at | 21:00 | hrs | Barisal | 380.86 | 380.86 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 360 | MW at | 8:00 | hrs | Rangpur | 793 | 628 |  | 165 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.7° C |  |  | Total | 12947.59 | 11547.59 |  | 1400
| B. |  | 2022-07-05 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 983.6373 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13070 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 309.9723 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10737 | MW at | 8:00 | 218.8694 | 147.7119 | 133.2543 | 130.6587 | 94.9637 | 97.5739 | 49.0848 | -0.35834 | 111.879
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1171 | MKWHr. | ii) HVDC Flow at Peak Time |  | 855 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.697 | MKWHr. | iii) Maximum HVDC Flow : |  | 894 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.95 |  | (b) Today: | 88.95 |  | (c) Rule Curve: |  | 84.48
.

## YesterdayGen
2022-07-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 279 | 154 |  | 0 | 185 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 26 | 81 | 20 | 93 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 270 | 146 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 35 | 0 | 22 | 11 | 27 | 21 | 160 | 104 | 0 | 20 | 0 | 33 | 42 | 8 | 5 | 110 | 0 | 54 | 86 | 0 | 120 | 0 | 0 | 9 | 310 | 24 | 11 | 0 | 260 | 303 | 0 | 114 | 0 | 149 | 0 | 76 | 200 | 135 | 280 | 60 | 105 | 105 | 0 | 177 | 35 | 110 | 0 | 36 | 50 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 112 | 55 | 0 |  | 887 | 0 | 165 | 0 | 16 | 206 | 0 | 0 | 38 | 61 | 8 | 65 | 30 | 96 | 0 | 0 | 0 | 34 | 25 | 90 | 0 | 34 | 32 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 213 | 0 | 98 | 160 | 0 | 373 | 92 | 0 | 94 | 105 | 104 | 0 | 0 | 113 | 622 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7535 | 4377 | 11912 | 3365 | 887 | 1678 | 401 | 3462 | 797 | 124 | 434 | 817 | 160 | 0 | 0 | 89
2:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 279 | 152 |  | 0 | 190 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 26 | 81 | 20 | 92 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 270 | 153 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 32 | 21 | 160 | 103 | 0 | 20 | 0 | 33 | 42 | 8 | 5 | 110 | 0 | 55 | 86 | 0 | 120 | 0 | 0 | 9 | 320 | 24 | 11 | 0 | 273 | 304 | 0 | 114 | 0 | 121 | 0 | 76 | 200 | 130 | 280 | 60 | 105 | 105 | 0 | 175 | 54 | 110 | 0 | 34 | 50 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 887 | 0 | 165 | 0 | 16 | 206 | 0 | 0 | 38 | 61 | 8 | 63 | 30 | 80 | 0 | 0 | 0 | 34 | 27 | 83 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 97 | 160 | 0 | 373 | 92 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 224 | 0 | 17 | 0 | 0 | 52 | 0 | 0 |  | 7565 | 4257 | 11822 | 3375 | 887 | 1692 | 401 | 3345 | 797 | 125 | 435 | 819 | 160 | 0 | 0 | 88.99
3:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 280 | 154 |  | 0 | 200 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 26 | 81 | 20 | 92 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 270 | 152 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 32 | 21 | 158 | 103 | 0 | 20 | 0 | 33 | 42 | 8 | 5 | 110 | 0 | 55 | 86 | 0 | 120 | 0 | 0 | 9 | 315 | 16 | 11 | 0 | 263 | 306 | 0 | 115 | 0 | 115 | 0 | 76 | 100 | 130 | 280 | 60 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 29 | 50 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 887 | 0 | 165 | 0 | 16 | 207 | 0 | 0 | 36 | 61 | 8 | 65 | 29 | 48 | 0 | 0 | 0 | 34 | 27 | 90 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 97 | 160 | 0 | 384 | 92 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 223 | 0 | 17 | 0 | 0 | 34 | 0 | 0 |  | 7448 | 4225 | 11673 | 3369 | 887 | 1708 | 403 | 3179 | 797 | 125 | 437 | 825 | 158 | 0 | 0 | 88.98
4:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 287 | 153 |  | 0 | 210 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 50 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 81 | 20 | 92 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 270 | 152 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 32 | 21 | 156 | 105 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 55 | 86 | 0 | 120 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 275 | 302 | 0 | 115 | 0 | 114 | 0 | 76 | 68 | 132 | 280 | 59 | 105 | 105 | 0 | 178 | 35 | 110 | 0 | 29 | 50 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 888 | 0 | 165 | 0 | 16 | 206 | 0 | 0 | 36 | 61 | 8 | 64 | 26 | 32 | 0 | 0 | 0 | 34 | 27 | 90 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 96 | 160 | 0 | 384 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 622 | 223 | 0 | 17 | 0 | 0 | 34 | 0 | 0 |  | 7389 | 4202 | 11591 | 3377 | 888 | 1706 | 398 | 3126 | 797 | 124 | 435 | 798 | 156 | 0 | 0 | 88.97
5:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 285 | 190 |  | 0 | 210 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 81 | 20 | 92 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 270 | 153 | 8 | 85 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 32 | 21 | 150 | 105 | 0 | 20 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 55 | 86 | 0 | 120 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 275 | 304 | 0 | 115 | 0 | 112 | 0 | 76 | 68 | 132 | 280 | 59 | 105 | 105 | 0 | 178 | 35 | 110 | 0 | 28 | 50 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 893 | 0 | 170 | 0 | 16 | 207 | 0 | 0 | 36 | 61 | 8 | 64 | 25 | 32 | 0 | 0 | 0 | 34 | 27 | 89 | 0 | 34 | 16 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 216 | 0 | 96 | 160 | 0 | 394 | 92 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 223 | 0 | 17 | 0 | 0 | 34 | 0 | 0 |  | 7400 | 4208 | 11608 | 3375 | 893 | 1742 | 400 | 3123 | 797 | 123 | 438 | 783 | 150 | 0 | 0 | 88.96
6:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 280 | 181 |  | 0 | 210 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 50 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 93 | 38 | 16 | 30 | 0 | 0 | 0 | 280 | 270 | 155 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 32 | 21 | 138 | 105 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 60 | 86 | 0 | 120 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 275 | 117 | 0 | 115 | 0 | 116 | 1 | 76 | 68 | 130 | 280 | 60 | 105 | 105 | 0 | 165 | 35 | 110 | 0 | 29 | 50 | 398 | 104 | 1 | 35 | 108 | 0 | 35 | 1 | 116 | 55 | 0 |  | 894 | 0 | 170 | 0 | 16 | 205 | 0 | 0 | 36 | 0 | 8 | 63 | 1 | 16 | 0 | 0 | 0 | 34 | 27 | 89 | 0 | 34 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 185 | 0 | 10 | 160 | 0 | 396 | 92 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 580 | 123 | 0 | 17 | 0 | 4 | 34 | 0 | 0 |  | 7122 | 3815 | 10937 | 3349 | 894 | 1601 | 127 | 3099 | 755 | 123 | 405 | 624 | 138 | 7 | 0 | 88.95
7:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 270 | 183 |  | 0 | 210 | 0 | 34 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 0 | 33 | 50 | 0 | 86 | 0 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 92 | 38 | 16 | 30 | 0 | 0 | 0 | 280 | 200 | 122 | 8 | 84 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 22 | 21 | 136 | 105 | 0 | 20 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 60 | 84 | 0 | 120 | 0 | 0 | 9 | 310 | 16 | 0 | 0 | 275 | 200 | 0 | 116 | 0 | 115 | 5 | 76 | 68 | 128 | 280 | 59 | 105 | 105 | 1 | 165 | 35 | 110 | 0 | 29 | 50 | 400 | 95 | 3 | 35 | 108 | 0 | 35 | 3 | 112 | 55 | 0 |  | 894 | 0 | 170 | 0 | 16 | 206 | 0 | 0 | 36 | 0 | 8 | 62 | 23 | 16 | 0 | 0 | 0 | 34 | 16 | 89 | 0 | 34 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 30 | 160 | 0 | 385 | 92 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 530 | 224 | 0 | 17 | 1 | 25 | 34 | 0 | 0 |  | 7007 | 3853 | 10860 | 3182 | 894 | 1733 | 230 | 3077 | 705 | 86 | 351 | 558 | 136 | 38 | 0 | 88.94
8:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 262 | 183 |  | 0 | 210 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 88 | 0 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 92 | 38 | 16 | 8 | 0 | 0 | 0 | 280 | 0 | 145 | 8 | 89 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 20 | 19 | 136 | 101 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 59 | 84 | 0 | 120 | 0 | 0 | 9 | 320 | 16 | 11 | 0 | 275 | 307 | 0 | 116 | 0 | 149 | 11 | 65 | 68 | 120 | 263 | 59 | 105 | 105 | 3 | 166 | 35 | 110 | 0 | 29 | 50 | 390 | 104 | 5 | 35 | 108 | 0 | 35 | 10 | 115 | 55 | 0 |  | 893 | 0 | 165 | 0 | 16 | 204 | 0 | 0 | 36 | 0 | 8 | 65 | 11 | 16 | 0 | 0 | 0 | 34 | 16 | 89 | 0 | 34 | 16 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 160 | 0 | 361 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 530 | 220 | 0 | 17 | 2 | 57 | 34 | 0 | 0 |  | 6990 | 3751 | 10741 | 3031 | 893 | 1680 | 379 | 3089 | 705 | 88 | 219 | 433 | 136 | 88 | 0 | 88.93
9:00 | 0 | 0 | 0 | 180 | 300 | 70 | 0 | 254 | 171 |  | 0 | 200 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 88 | 0 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 94 | 38 | 16 | 2 | 0 | 0 | 0 | 320 | 0 | 204 | 8 | 85 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 9 | 20 | 140 | 99 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 61 | 84 | 0 | 120 | 0 | 0 | 9 | 280 | 16 | 11 | 160 | 275 | 229 | 0 | 116 | 0 | 149 | 16 | 76 | 68 | 122 | 279 | 59 | 105 | 105 | 4 | 168 | 35 | 104 | 0 | 28 | 50 | 401 | 104 | 11 | 35 | 108 | 0 | 35 | 25 | 115 | 55 | 0 |  | 893 | 0 | 160 | 0 | 16 | 204 | 0 | 0 | 22 | 0 | 8 | 63 | 11 | 16 | 0 | 0 | 0 | 34 | 16 | 89 | 0 | 34 | 16 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 161 | 0 | 353 | 92 | 0 | 94 | 105 | 69 | 0 | 1 | 113 | 500 | 221 | 0 | 17 | 3 | 51 | 34 | 0 | 0 |  | 7119 | 3712 | 10831 | 3121 | 893 | 1600 | 484 | 3099 | 675 | 88 | 219 | 401 | 140 | 111 | 0 | 88.92
10:00 | 0 | 0 | 0 | 180 | 300 | 70 | 0 | 236 | 139 |  | 0 | 180 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 20 | 33 | 28 | 42 | 0 | 88 | 0 | 90 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 89 | 38 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 201 | 8 | 85 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 0 | 20 | 144 | 82 | 0 | 20 | 1 | 33 | 42 | 5 | 5 | 110 | 0 | 55 | 84 | 0 | 120 | 0 | 0 | 9 | 320 | 16 | 11 | 200 | 275 | 302 | 0 | 116 | 0 | 149 | 19 | 76 | 68 | 127 | 275 | 59 | 88 | 105 | 5 | 168 | 35 | 92 | 0 | 32 | 50 | 386 | 104 | 3 | 35 | 108 | 0 | 35 | 22 | 115 | 55 | 0 |  | 859 | 0 | 155 | 0 | 16 | 203 | 0 | 0 | 15 | 0 | 8 | 64 | 11 | 16 | 0 | 0 | 0 | 34 | 9 | 87 | 0 | 34 | 20 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 152 | 0 | 340 | 90 | 0 | 94 | 105 | 63 | 0 | 3 | 113 | 500 | 222 | 0 | 17 | 5 | 90 | 34 | 0 | 0 |  | 7120 | 3674 | 10794 | 3053 | 859 | 1575 | 597 | 3030 | 675 | 88 | 218 | 407 | 144 | 148 | 0 | 88.91
11:00 | 0 | 0 | 0 | 180 | 300 | 72 | 0 | 230 | 111 |  | 0 | 160 | 0 | 34 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 20 | 33 | 25 | 41 | 0 | 89 | 0 | 90 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 87 | 38 | 19 | 2 | 0 | 0 | 0 | 340 | 0 | 198 | 8 | 71 | 8 | 0 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 0 | 20 | 142 | 82 | 0 | 20 | 1 | 33 | 42 | 5 | 5 | 100 | 0 | 55 | 84 | 0 | 120 | 0 | 0 | 10 | 320 | 16 | 11 | 200 | 262 | 301 | 0 | 115 | 0 | 149 | 13 | 63 | 68 | 120 | 261 | 59 | 88 | 105 | 5 | 166 | 35 | 93 | 0 | 8 | 50 | 378 | 93 | 9 | 37 | 108 | 0 | 35 | 36 | 115 | 55 | 0 |  | 859 | 0 | 150 | 0 | 16 | 199 | 0 | 0 | 15 | 0 | 8 | 62 | 15 | 16 | 0 | 0 | 0 | 26 | 0 | 86 | 0 | 43 | 24 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 151 | 0 | 334 | 73 | 0 | 94 | 105 | 69 | 0 | 6 | 113 | 520 | 215 | 0 | 17 | 3 | 84 | 34 | 0 | 0 |  | 6943 | 3651 | 10594 | 3003 | 859 | 1510 | 596 | 2955 | 695 | 89 | 214 | 374 | 142 | 157 | 0 | 88.9
12:00 | 0 | 0 | 0 | 180 | 300 | 72 | 0 | 211 | 65 |  | 0 | 160 | 0 | 31 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 20 | 35 | 35 | 22 | 25 | 20 | 33 | 28 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 78 | 20 | 91 | 38 | 19 | 2 | 0 | 0 | 0 | 350 | 180 | 190 | 8 | 62 | 30 | 0 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 20 | 154 | 70 | 0 | 20 | 2 | 33 | 42 | 0 | 0 | 100 | 0 | 55 | 84 | 0 | 120 | 0 | 0 | 9 | 320 | 16 | 11 | 200 | 262 | 300 | 0 | 115 | 0 | 135 | 20 | 63 | 68 | 117 | 280 | 59 | 96 | 105 | 5 | 168 | 35 | 86 | 0 | 9 | 50 | 398 | 91 | 19 | 54 | 100 | 0 | 35 | 34 | 115 | 55 | 0 |  | 858 | 0 | 150 | 0 | 16 | 201 | 0 | 0 | 15 | 0 | 8 | 62 | 14 | 16 | 0 | 0 | 0 | 26 | 0 | 86 | 0 | 43 | 24 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 151 | 0 | 347 | 80 | 0 | 94 | 89 | 70 | 0 | 7 | 113 | 540 | 219 | 0 | 17 | 3 | 45 | 34 | 0 | 0 |  | 7148 | 3642 | 10790 | 3190 | 858 | 1469 | 595 | 2932 | 715 | 125 | 216 | 401 | 154 | 135 | 0 | 88.9
13:00 | 0 | 0 | 0 | 180 | 300 | 73 | 0 | 0 | 140 |  | 0 | 150 | 0 | 31 | 0 | 40 | 0 | 0 | 0 | 35 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 24 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 89 | 38 | 19 | 7 | 0 | 0 | 0 | 350 | 140 | 200 | 123 | 64 | 28 | 1 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 20 | 156 | 69 | 0 | 20 | 1 | 33 | 42 | 0 | 0 | 90 | 0 | 59 | 84 | 0 | 120 | 0 | 0 | 9 | 290 | 16 | 11 | 200 | 263 | 301 | 0 | 122 | 0 | 132 | 19 | 76 | 68 | 120 | 279 | 59 | 105 | 87 | 2 | 178 | 35 | 97 | 0 | 8 | 50 | 394 | 91 | 25 | 54 | 108 | 0 | 35 | 35 | 115 | 55 | 0 |  | 870 | 0 | 155 | 0 | 16 | 202 | 0 | 0 | 4 | 0 | 8 | 63 | 20 | 16 | 0 | 0 | 0 | 16 | 0 | 86 | 0 | 43 | 24 | 0 | 18 | 18 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 151 | 0 | 342 | 92 | 0 | 94 | 89 | 70 | 0 | 6 | 113 | 540 | 219 | 0 | 35 | 4 | 93 | 34 | 0 | 0 |  | 7090 | 3738 | 10828 | 2949 | 870 | 1617 | 597 | 2992 | 715 | 125 | 217 | 405 | 156 | 185 | 0 | 88.89
14:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 0 | 127 |  | 0 | 150 | 0 | 31 | 0 | 40 | 7 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 24 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 3 | 89 | 20 | 89 | 37 | 19 | 2 | 0 | 0 | 0 | 340 | 50 | 121 | 90 | 58 | 30 | 10 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 20 | 162 | 69 | 0 | 20 | 1 | 33 | 42 | 0 | 0 | 90 | 0 | 60 | 84 | 0 | 120 | 0 | 0 | 10 | 305 | 16 | 11 | 200 | 275 | 301 | 0 | 122 | 0 | 132 | 17 | 76 | 68 | 125 | 280 | 69 | 105 | 105 | 1 | 178 | 35 | 110 | 0 | 8 | 50 | 373 | 104 | 26 | 35 | 108 | 0 | 35 | 32 | 115 | 55 | 0 |  | 869 | 0 | 155 | 0 | 16 | 200 | 0 | 0 | 0 | 0 | 8 | 61 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 43 | 6 | 0 | 38 | 17 | 0 | 8 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 151 | 0 | 348 | 80 | 0 | 94 | 90 | 70 | 0 | 7 | 113 | 560 | 214 | 0 | 35 | 4 | 96 | 34 | 0 | 0 |  | 6934 | 3748 | 10682 | 2749 | 869 | 1592 | 597 | 3037 | 735 | 125 | 215 | 417 | 162 | 184 | 0 | 88.89
15:00 | 0 | 0 | 0 | 180 | 300 | 74 | 0 | 0 | 62 |  | 0 | 150 | 0 | 31 | 0 | 40 | 12 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 19 | 33 | 24 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 3 | 89 | 20 | 89 | 37 | 19 | 2 | 0 | 0 | 0 | 335 | 80 | 117 | 73 | 55 | 30 | 5 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 20 | 154 | 69 | 0 | 20 | 1 | 33 | 42 | 0 | 0 | 90 | 0 | 59 | 84 | 0 | 120 | 0 | 0 | 10 | 315 | 16 | 8 | 200 | 275 | 307 | 0 | 121 | 0 | 126 | 14 | 76 | 68 | 125 | 264 | 69 | 90 | 105 | 4 | 177 | 35 | 110 | 0 | 8 | 50 | 384 | 97 | 35 | 35 | 108 | 0 | 35 | 20 | 115 | 55 | 0 |  | 869 | 0 | 150 | 0 | 15 | 198 | 0 | 0 | 0 | 0 | 8 | 61 | 22 | 7 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 43 | 0 | 0 | 38 | 17 | 0 | 8 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 10 | 0 | 98 | 143 | 0 | 333 | 73 | 0 | 94 | 105 | 68 | 0 | 7 | 113 | 590 | 214 | 0 | 35 | 2 | 85 | 34 | 0 | 0 |  | 6835 | 3739 | 10574 | 2749 | 869 | 1502 | 605 | 3003 | 765 | 125 | 223 | 421 | 154 | 168 | 0 | 88.88
16:00 | 0 | 0 | 0 | 180 | 300 | 76 | 0 | 0 | 62 |  | 0 | 150 | 0 | 31 | 0 | 40 | 12 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 17 | 33 | 24 | 41 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 5 | 74 | 20 | 89 | 33 | 21 | 2 | 0 | 0 | 0 | 340 | 105 | 117 | 73 | 56 | 20 | 5 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 18 | 158 | 69 | 0 | 20 | 1 | 33 | 42 | 0 | 0 | 90 | 0 | 59 | 86 | 0 | 120 | 0 | 0 | 10 | 320 | 16 | 8 | 200 | 275 | 253 | 0 | 122 | 0 | 118 | 9 | 76 | 68 | 127 | 280 | 69 | 90 | 100 | 3 | 177 | 35 | 110 | 0 | 8 | 50 | 383 | 92 | 29 | 35 | 108 | 0 | 35 | 21 | 72 | 55 | 0 |  | 870 | 0 | 150 | 0 | 19 | 202 | 0 | 0 | 0 | 0 | 8 | 62 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 43 | 0 | 0 | 38 | 18 | 0 | 8 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 98 | 139 | 0 | 348 | 73 | 0 | 77 | 105 | 64 | 0 | 5 | 113 | 610 | 217 | 0 | 35 | 2 | 40 | 34 | 0 | 0 |  | 6740 | 3729 | 10469 | 2780 | 870 | 1529 | 551 | 2933 | 785 | 123 | 232 | 413 | 158 | 110 | 0 | 88.88
17:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 0 | 84 |  | 0 | 150 | 0 | 31 | 0 | 40 | 16 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 25 | 41 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 6 | 89 | 20 | 90 | 31 | 21 | 6 | 0 | 0 | 0 | 300 | 140 | 114 | 45 | 56 | 20 | 5 | 0 | 51 | 0 | 40 | 0 | 0 | 11 | 0 | 20 | 160 | 69 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 60 | 84 | 0 | 120 | 0 | 0 | 10 | 300 | 17 | 11 | 200 | 275 | 194 | 80 | 122 | 0 | 146 | 3 | 76 | 117 | 130 | 280 | 69 | 100 | 105 | 2 | 177 | 35 | 110 | 0 | 8 | 50 | 392 | 104 | 13 | 35 | 108 | 0 | 35 | 12 | 53 | 55 | 0 |  | 869 | 0 | 150 | 0 | 23 | 185 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 48 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 43 | 18 | 0 | 37 | 19 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 42 | 0 | 98 | 155 | 0 | 352 | 93 | 0 | 94 | 105 | 64 | 0 | 1 | 113 | 590 | 218 | 0 | 35 | 1 | 18 | 34 | 0 | 0 |  | 6826 | 3744 | 10570 | 2753 | 869 | 1512 | 572 | 3093 | 765 | 123 | 242 | 473 | 160 | 50 | 0 | 88.87
18:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 0 | 140 |  | 0 | 150 | 0 | 31 | 0 | 40 | 155 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 5 | 33 | 25 | 45 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 6 | 89 | 20 | 90 | 34 | 21 | 2 | 0 | 0 | 0 | 270 | 160 | 115 | 8 | 57 | 20 | 5 | 0 | 51 | 0 | 39 | 0 | 0 | 11 | 0 | 20 | 154 | 69 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 60 | 84 | 0 | 120 | 0 | 0 | 10 | 280 | 17 | 11 | 100 | 275 | 106 | 40 | 186 | 0 | 118 | 1 | 76 | 200 | 130 | 280 | 115 | 105 | 105 | 0 | 285 | 35 | 110 | 0 | 8 | 50 | 360 | 104 | 4 | 35 | 108 | 0 | 35 | 3 | 52 | 0 | 0 |  | 870 | 0 | 150 | 0 | 20 | 150 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 48 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 43 | 27 | 0 | 37 | 20 | 0 | 5 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 75 | 0 | 20 | 157 | 0 | 320 | 93 | 0 | 94 | 105 | 85 | 0 | 2 | 113 | 560 | 221 | 0 | 35 | 0 | 8 | 95 | 0 | 0 |  | 6877 | 3685 | 10562 | 2833 | 870 | 1483 | 266 | 3401 | 735 | 123 | 240 | 514 | 154 | 18 | 0 | 88.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 0 | 147 |  | 0 | 160 | 0 | 31 | 0 | 40 | 170 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 46 | 89 | 20 | 90 | 37 | 21 | 8 | 0 | 0 | 0 | 270 | 160 | 146 | 8 | 70 | 20 | 5 | 0 | 51 | 0 | 40 | 0 | 8 | 11 | 8 | 20 | 180 | 102 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 59 | 84 | 0 | 120 | 0 | 0 | 10 | 300 | 17 | 11 | 200 | 275 | 300 | 80 | 186 | 0 | 113 | 0 | 76 | 200 | 130 | 267 | 115 | 105 | 105 | 0 | 265 | 35 | 110 | 0 | 8 | 50 | 200 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 52 | 20 | 0 |  | 870 | 0 | 165 | 0 | 49 | 200 | 0 | 0 | 0 | 21 | 40 | 0 | 34 | 48 | 0 | 0 | 0 | 24 | 4 | 0 | 0 | 43 | 32 | 8 | 38 | 21 | 0 | 5 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 188 | 0 | 24 | 157 | 0 | 371 | 93 | 0 | 94 | 105 | 90 | 0 | 0 | 113 | 570 | 215 | 0 | 35 | 0 | 0 | 110 | 0 | 0 |  | 7393 | 3957 | 11350 | 2797 | 870 | 1583 | 604 | 3619 | 745 | 123 | 403 | 614 | 180 | 0 | 0 | 88.85
19:30 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 0 | 152 |  | 0 | 180 | 0 | 31 | 0 | 40 | 170 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 46 | 74 | 20 | 91 | 37 | 21 | 10 | 0 | 0 | 0 | 270 | 160 | 167 | 8 | 70 | 20 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 8 | 20 | 176 | 102 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 60 | 84 | 0 | 120 | 0 | 0 | 10 | 300 | 17 | 11 | 200 | 275 | 301 | 80 | 186 | 0 | 120 | 0 | 76 | 200 | 130 | 280 | 115 | 105 | 105 | 0 | 270 | 35 | 110 | 0 | 8 | 50 | 158 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 53 | 44 | 0 |  | 870 | 0 | 170 | 0 | 49 | 204 | 0 | 0 | 0 | 45 | 32 | 0 | 34 | 64 | 0 | 0 | 0 | 24 | 4 | 0 | 0 | 43 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 208 | 0 | 97 | 160 | 0 | 390 | 73 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 620 | 221 | 0 | 54 | 0 | 0 | 110 | 0 | 0 |  | 7444 | 4175 | 11619 | 2815 | 870 | 1635 | 678 | 3665 | 795 | 123 | 427 | 643 | 176 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 152 |  | 0 | 180 | 0 | 31 | 0 | 40 | 170 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 25 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 46 | 89 | 20 | 90 | 37 | 21 | 14 | 0 | 0 | 0 | 270 | 160 | 194 | 8 | 71 | 20 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 8 | 20 | 164 | 103 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 61 | 84 | 0 | 120 | 0 | 0 | 10 | 300 | 16 | 11 | 200 | 275 | 200 | 80 | 186 | 0 | 118 | 0 | 76 | 200 | 132 | 280 | 115 | 105 | 105 | 0 | 280 | 35 | 110 | 0 | 8 | 50 | 325 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 52 | 47 | 0 |  | 856 | 0 | 175 | 0 | 49 | 204 | 0 | 0 | 0 | 78 | 40 | 0 | 37 | 110 | 0 | 0 | 0 | 24 | 12 | 0 | 0 | 43 | 32 | 8 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 212 | 0 | 97 | 161 | 0 | 380 | 80 | 0 | 94 | 105 | 90 | 0 | 0 | 113 | 620 | 224 | 0 | 54 | 0 | 0 | 110 | 0 | 0 |  | 7565 | 4267 | 11832 | 3024 | 856 | 1636 | 577 | 3736 | 795 | 123 | 431 | 702 | 164 | 0 | 0 | 88.86
21:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 152 |  | 0 | 180 | 0 | 32 | 0 | 45 | 177 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 25 | 49 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 37 | 21 | 18 | 0 | 0 | 0 | 270 | 220 | 205 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 8 | 20 | 158 | 103 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 56 | 84 | 0 | 120 | 0 | 0 | 10 | 290 | 16 | 11 | 200 | 275 | 300 | 80 | 186 | 0 | 149 | 0 | 76 | 200 | 137 | 280 | 115 | 105 | 105 | 0 | 280 | 39 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 855 | 0 | 170 | 0 | 49 | 205 | 0 | 0 | 28 | 75 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 24 | 16 | 80 | 0 | 43 | 24 | 8 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 213 | 0 | 98 | 163 | 0 | 380 | 93 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 622 | 220 | 0 | 90 | 0 | 0 | 110 | 0 | 0 |  | 7822 | 4414 | 12236 | 3184 | 855 | 1625 | 678 | 3842 | 797 | 122 | 433 | 755 | 158 | 0 | 0 | 88.85
22:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 152 |  | 0 | 180 | 0 | 34 | 0 | 55 | 179 | 0 | 0 | 42 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 25 | 27 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 37 | 21 | 23 | 0 | 0 | 0 | 330 | 220 | 195 | 8 | 84 | 21 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 8 | 20 | 160 | 102 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 30 | 84 | 0 | 120 | 0 | 0 | 10 | 290 | 16 | 11 | 200 | 275 | 301 | 80 | 187 | 0 | 149 | 0 | 76 | 200 | 143 | 280 | 115 | 105 | 105 | 0 | 280 | 54 | 110 | 0 | 8 | 50 | 388 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 52 | 55 | 0 |  | 855 | 0 | 175 | 0 | 49 | 204 | 0 | 0 | 38 | 70 | 8 | 0 | 38 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 24 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 40 | 164 | 0 | 385 | 93 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 622 | 223 | 0 | 90 | 0 | 0 | 110 | 0 | 0 |  | 7873 | 4369 | 12242 | 3197 | 855 | 1641 | 621 | 3845 | 797 | 123 | 434 | 784 | 160 | 0 | 0 | 88.85
23:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 164 |  | 0 | 185 | 0 | 40 | 0 | 55 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 28 | 25 | 30 | 49 | 0 | 88 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 38 | 21 | 29 | 0 | 0 | 0 | 300 | 210 | 183 | 8 | 84 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 14 | 20 | 160 | 104 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 30 | 84 | 0 | 120 | 0 | 0 | 10 | 310 | 16 | 11 | 200 | 248 | 305 | 80 | 187 | 0 | 149 | 0 | 76 | 200 | 145 | 220 | 115 | 105 | 105 | 0 | 280 | 54 | 110 | 0 | 8 | 50 | 387 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 52 | 55 | 0 |  | 855 | 0 | 175 | 0 | 49 | 205 | 0 | 0 | 38 | 70 | 8 | 0 | 37 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 24 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 212 | 0 | 88 | 166 | 0 | 393 | 93 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 622 | 223 | 0 | 90 | 0 | 0 | 115 | 0 | 0 |  | 7607 | 4421 | 12028 | 3069 | 855 | 1691 | 673 | 3659 | 797 | 123 | 432 | 781 | 160 | 0 | 0 | 88.84
24:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 173 |  | 0 | 190 | 0 | 32 | 0 | 55 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 28 | 33 | 30 | 49 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 38 | 21 | 25 | 0 | 0 | 0 | 285 | 210 | 191 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 15 | 20 | 164 | 103 | 0 | 20 | 0 | 33 | 42 | 53 | 38 | 110 | 0 | 30 | 84 | 0 | 120 | 0 | 0 | 10 | 310 | 16 | 11 | 150 | 245 | 208 | 80 | 115 | 0 | 149 | 0 | 76 | 200 | 143 | 80 | 58 | 105 | 105 | 0 | 280 | 54 | 110 | 0 | 16 | 50 | 390 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 856 | 0 | 175 | 0 | 16 | 205 | 0 | 0 | 33 | 70 | 8 | 0 | 36 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 27 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 98 | 166 | 0 | 380 | 92 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 622 | 223 | 0 | 90 | 0 | 0 | 108 | 0 | 0 |  | 7336 | 4374 | 11710 | 2934 | 856 | 1798 | 536 | 3503 | 797 | 124 | 431 | 778 | 164 | 0 | 0 | 88.84
KWH | 0 | 0 | 0 | 4347000 | 7190891 | 1768909 | 0 | 3299330 | 3378000 |  | 0 | 3691150 | 0 | 850560 | 0 | 1024201 | 1169237 | 0 | 0 | 969130 | 2219616 | 3255360 | 0 | 0 | 0 | 0 | 639720 | 1070411 | 953479 | 379620 | 522460 | 499680 | 713000 | 661400 | 1104000 | 0 | 2135927 | 640000 | 2100000 | 0 | 599994 | 0 | 0 | 0 | 0 |  | 593040 | 177696 | 1897097 | 496920 | 2191680 | 901440 | 419712 | 416160 | 0 | 0 | 0 | 7560700 | 3993000 | 3885000 | 552000 | 1788140 | 384768 | 74880 | 0 | 1183093 | 0 | 962528 | 0 | 337464 | 246960 | 302900 | 480430 | 3696960 | 2130240 | 0 | 421164 | 7750 | 778000 | 962912 | 127800 | 102090 | 2352273 | 0 | 1315776 | 2030400 | 0 | 2886040 | 0 | 0 | 220140 | 7530000 | 41522 | 240000 | 3056448 | 6493525 | 6536658 | 608526 | 3192000 | 0 | 3211776 | 145530 | 1783680 | 2915520 | 3119636 | 6380000 | 1792800 | 2463600 | 2529999 | 39000 | 4860109 | 997296 | 2593552 | 0 | 437640 | 1217280 | 9023700 | 2542080 | 181950 | 1368000 | 2595655 | 0 | 887400 | 245408 | 2232000 | 1287000 | 900 |  | 21117090 | 0 | 4033152 | 0 | 546240 | 4855680 | 0 | 0 | 468960 | 663808 | 266625 | 1007000 | 569117 | 1154784 | 0 | 0 | 0 | 675664 | 342505 | 1783288 | 0 | 872651 | 456160 | 42946 | 601317 | 467760 | 0 | 240390 | 0 | 0 | 4300800 | 363000 | 0 | 0 | 0 | 4230 | 3010815 | 0 | 2001600 | 4031791 | 0 | 8746691 | 2079840 | 0 | 2252928 | 2513520 | 1843478 | 0 | 43265 | 2730336 | 15020200 | 5215145 | 0 | 901200 | 35160 | 704160 | 1474944 | 0 | 0 |  | 173610418 | 97438240 | 271048658 | 73778509 | 21117090 | 38425608 | 12203232 | 78814231 | 19321000 | 2775927 | 8229495 | 11284383 | 3696960 | 1402223 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 8053797.92 | 2352648.97 | 0 | 3464296.5 | 3648240 |  | 0 | 4023353.5 | 0 | 9509260.8 | 0 | 13570663.25 | 1309545.44 | 0 | 0 | 14168680.6 | 31229997.12 | 52769385.6 | 0 | 0 | 0 | 0 | 8137238.4 | 14450548.5 | 12786153.39 | 284715 | 391845 | 0 | 0 | 0 | 18779040 | 0 | 576700.29 | 172800 | 3969000 | 0 | 9809901.9 | 0 | 0 | 0 | 0 |  | 7739172 | 2963969.28 | 32288590.94 | 6713389.2 | 27790502.4 | 10429660.8 | 533034.24 | 1385812.8 | 0 | 0 | 0 | 8392377 | 4352370 | 4506600 | 712080 | 2181530.8 | 434787.84 | 111571.2 | 0 | 1975765.31 | 0 | 16622858.56 | 0 | 462325.68 | 185220 | 530075 | 360322.5 | 26544172.8 | 2321961.6 | 0 | 572783.04 | 123535 | 1065860 | 1271043.84 | 222372 | 176615.7 | 2705113.95 | 0 | 2552605.44 | 4629312 | 0 | 2914900.4 | 0 | 0 | 435877.2 | 7530000 | 31141.5 | 182400 | 64063150.08 | 88636616.25 | 137008351.68 | 12578232.42 | 43028160 | 0 | 44483097.6 | 1701245.7 | 18407577.6 | 39826003.2 | 41397569.72 | 5869600 | 21800448 | 35623656 | 32004487.35 | 0 | 57057679.66 | 10860553.44 | 27569457.76 | 0 | 5641179.6 | 14339558.4 | 8301804 | 32919936 | 2629177.5 | 17359920 | 29538553.9 | 0 | 11589444 | 2932625.6 | 33413040 | 16949790 | 0 |  | 63351270 | 0 | 4517130.24 | 0 | 5686358.4 | 80118720 | 0 | 0 | 8445969.6 | 11948544 | 3831401.25 | 1127840 | 1104086.98 | 12587145.6 | 0 | 0 | 0 | 11330885.28 | 5990412.45 | 27890624.32 | 0 | 14451100.56 | 7713665.6 | 585353.98 | 10144217.79 | 968263.2 | 0 | 181975.23 | 0 | 0 | 22751232 | 15253260 | 0 | 0 | 0 | 5414.4 | 52568829.9 | 0 | 41993568 | 4676877.56 | 0 | 8659224.09 | 27953049.6 | 0 | 26652138.24 | 36320364 | 23412170.6 | 0 | 478078.25 | 33146279.04 | 135332002 | 5319447.9 | 0 | 6668880 | 397659.6 | 8259796.8 | 22610891.52 | 0 | 0 |  | 1261417467.66 | 744434127.98 | 2005851595.64 | 81482210.17 | 63351270 | 45959784.8 | 255643302.18 | 1021466069.63 | 158083234 | 749500.29 | 147940809.9 | 188109123.42 | 26544172.8 | 16522118.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 70 | 0 | 254 | 171 |  | 0 | 200 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 20 | 33 | 25 | 50 | 0 | 88 | 0 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 94 | 38 | 16 | 2 | 0 | 0 | 0 | 320 | 0 | 204 | 8 | 85 | 8 | 0 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 9 | 20 | 140 | 99 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 61 | 84 | 0 | 120 | 0 | 0 | 9 | 280 | 16 | 11 | 160 | 275 | 229 | 0 | 116 | 0 | 149 | 16 | 76 | 68 | 122 | 279 | 59 | 105 | 105 | 4 | 168 | 35 | 104 | 0 | 28 | 50 | 401 | 104 | 11 | 35 | 108 | 0 | 35 | 25 | 115 | 55 | 0 |  | 893 | 0 | 160 | 0 | 16 | 204 | 0 | 0 | 22 | 0 | 8 | 63 | 11 | 16 | 0 | 0 | 0 | 34 | 16 | 89 | 0 | 34 | 16 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 161 | 0 | 353 | 92 | 0 | 94 | 105 | 69 | 0 | 1 | 113 | 500 | 221 | 0 | 17 | 3 | 51 | 34 | 0 | 0 |  | 10831 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 152 | 0 | 0 | 180 | 0 | 32 | 0 | 45 | 177 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 25 | 49 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 20 | 91 | 37 | 21 | 18 | 0 | 0 | 0 | 270 | 220 | 205 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 8 | 20 | 158 | 103 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 90 | 0 | 56 | 84 | 0 | 120 | 0 | 0 | 10 | 290 | 16 | 11 | 200 | 275 | 300 | 80 | 186 | 0 | 149 | 0 | 76 | 200 | 137 | 280 | 115 | 105 | 105 | 0 | 280 | 39 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 855 | 0 | 170 | 0 | 49 | 205 | 0 | 0 | 28 | 75 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 24 | 16 | 80 | 0 | 43 | 24 | 8 | 37 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 213 | 0 | 98 | 163 | 0 | 380 | 93 | 0 | 94 | 105 | 91 | 0 | 0 | 113 | 622 | 220 | 0 | 90 | 0 | 0 | 110 | 0 | 0 |  | 12236 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 185 | 0 | 0 | 210 | 0 | 40 | 0 | 55 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 28 | 33 | 25 | 50 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 36 | 85 | 20 | 91 | 38 | 21 | 20 | 0 | 0 | 0 | 270 | 260 | 205 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 165 | 110 | 0 | 20 | 0 | 33 | 42 | 5 | 35 | 110 | 0 | 60 | 86 | 0 | 120 | 0 | 6 | 10 | 341 | 16 | 11 | 200 | 275 | 300 | 80 | 190 | 50 | 149 | 0 | 76 | 200 | 150 | 280 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 8 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 115 | 55 |  |  | 868 | 0 | 180 | 0 | 49 | 220 | 0 | 0 | 35 | 75 | 40 | 0 | 36 | 110 | 0 | 0 | 0 | 34 | 30 | 90 | 0 | 43 | 30 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 10 | 0 | 0 | 0 | 220 | 0 | 100 | 170 | 0 | 380 | 93 | 150 | 95 | 105 | 91 | 0 | 0 | 113 | 622 | 220 |  | 90 |  |  | 110
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 185 | 0 | 0 | 210 | 0 | 40 | 0 | 40 | 180 | 0 | 0 | 40 | 94 | 130 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 25 | 50 | 0 | 87 | 0 | 90 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 60 | 20 | 90 | 38 | 20 | 10 | 0 | 0 | 0 | 270 | 200 | 180 | 8 | 85 | 8 | 5 | 0 | 50 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 143 | 100 | 0 | 20 | 1.6 | 33 | 42 | 5 | 5 | 110 | 0 | 60 | 86 | 0 | 120 | 0 | 6 | 10 | 310 | 16 | 11 | 200 | 260 | 300 | 0 | 175 | 0 | 149 | 20 | 65 | 200 | 140 | 280 | 60 | 105 | 105 | 5 | 200 | 35 | 110 | 0 | 8 | 80 | 400 | 104 | 50 | 72 | 108 | 0 | 35 | 30 | 115 | 55 |  |  | 868 | 0 | 165 | 0 | 16 | 220 | 0 | 0 | 35 | 50 | 8 | 0 | 20 | 16 | 0 | 0 | 0 | 24 | 16 | 90 | 0 | 34 | 16 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 220 | 0 | 90 | 160 | 0 | 360 | 93 | 20 | 94 | 105 | 70 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 34
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 265 | 0 | 0 | 225 | 0 | 32 | 0 | 55 | 306 | 0 | 0 | 40 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 0 | 33 | 33 | 41 | 0 | 75 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 85 | 20 | 91 | 38 | 21 | 8 | 0 | 0 | 0 | 270 | 210 | 179 | 8 | 85 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 33 | 18 | 122 | 71 | 0 | 20 | 1 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 0 | 0 | 18 | 10 | 270 | 16 | 11 | 0 | 243 | 12 | 25 | 117 | 0 | 149 | 9 | 76 | 100 | 123 | 80 | 59 | 88 | 105 | 3 | 176 | 54 | 110 | 0 | 8 | 77 | 400 | 102 | 10 | 17 | 108 | 0 | 35 | 8 | 75 | 55 | 0 | 0 | 893 | 0 | 185 | 0 | 16 | 206 | 0 | 0 | 30 | 10 | 8 | 0 | 19 | 32 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 95 | 175 | 0 | 414 | 92 | 10 | 94 | 105 | 70 | 0 | 3 | 113 | 550 | 196 | 0 | 17 | 1 | 27 | 34 | 0 | 0 | 0 |  |  |  |  | 110531341 |  | 0
110531341
| Minimum Generation |  | 10741 | 8:00
| Highest Generation |  | 12242 | 22:00
| Day Peak Generation |  | 10831 | 9:00
| Evening Peak Generation |  | 12236 | 21:00
| HVDC Max Flow |  | 894 | 6:00
| HVDC EvPeak Flow |  | 855 | 21:00
| Load factor L.F |  | 92.25%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-05
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10831 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10737 | MW
Evening Peak Generation : |  | 12236 | MW Hour : | 21:00 | Available Max Generation : |  | 13070 | MW
E.P. Demand (at gen end) : |  | 13636 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12242 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 271.0487 | System Load Factor : | 92.25% | Load Shed : |  | 983.6373 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 360 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-05
Actual : | 88.95 | Ft.(MSL) , | Rule curve : | 84.48 | Ft.( MSL )
Gas Consumed : | Total = | 882.52 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 127441994.97
: |  | Coal : | 158083234 | Oil : | 1613159305.13 | Total : | 1898684534.1
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 300 | 7200:00 | 5337.8694 |  |  | 218.8694 | 4.276%
Chittagong Area | 125 | 3000:00 | 1447.7119 |  |  | 147.7119 | 11.36%
Khulna Area | 240 | 5760:00 | 1883.2543 |  |  | 133.2543 | 7.615%
Rajshahi Area | 220 | 5280:00 | 1688.6587 |  |  | 130.6587 | 8.386%
Cumilla Area | 180 | 4320:00 | 1494.9637 |  |  | 94.9637 | 6.783%
Mymensingh Area | 125 | 3000:00 | 1097.5739 |  |  | 97.5739 | 9.757%
Sylhet Area | 45 | 1080:00 | 611.0848 |  |  | 49.0848 | 8.734%
Barisal Area | 0 | 0:00 | 394.6417 |  |  | -0.35834 | -0.09072%
Rangpur Area | 165 | 3960:00 | 843.879 |  |  | 111.879 | 15.28%
Total | 1400 |  | 14799.6373 |  |  | 983.6373
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Shajibazar 330 MW
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Sirajganj Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kishorganj 132/33 kV T-3 transformer was under shut down from 08:12 to 17:45 for D/W.
b) Sikalbaha-Intermediate 132 kv Ckt-1 was under shut down from 08:54 to 18:24 for D/W.
c) Mirpur 132/33 kV T-1 transformer was under shut down from 08:54 for C/M.
d) Patuakhali 132/33 kV T-2 transformer was under shut down from 08:42 to 09:58 for C/M.
e) Gallamari 132/33 kV T-1 transformer was under shut at 09:25 for D/W.
f) Haripur EGCB-335 MW CCPP GT was synchronized at 13:40.
g) Megnaghat-Haripur 230 kV Ckt-1 was under shut down at 11:29 for C/M.
h) Ashuganj(S)-360 MW CCPP GT & ST were synchronized at 11:28 & 15:47 respectively.
i) Haripur EGCB-412 MW CCPP was shut down at 12:37 due to gas shortage.
j) Barishal(S)-Bhandaria 132 kV Ckt tripped at 11:09 showing dist.A-phase and was switched on at 11:14. | [5 empty] | About 32 MW power interruption occurred under
Bhandaria S/S area from 11:09 to 11:14.
k) Rajbari 132/33 kV T-1 transformer was under shut down from 10:55 to 12:34 due to red hot maintenance. | [5 empty] | About 18 MW power interruption occurred under
Rajbari S/S area from 10:55 to 12:34
l) Kishorganj 132/33 kV T-1 & T-2 transformers tripped at 13:42 due to 33 kV Pakundia feeder fault and | [5 empty] | About 90 MW power interruption occurred under
were switched on at 14:44. | [5 empty] | Kishorganj S/S area from 13:42 to 14:44.
m) Mirpur-Uttara 132 kV Ckt was under shut down at 16:30 due to red hot maintenance at Mirpur end and
switched on at 18:07.
n) HVDC 10CF25 400 kV filter tripped at 21:01.
o) Shahjibazar GT-8 was shut down at 21:35 due to cooling problem and was synchronized at 01:43(5/7/22).
p) Bhola-225 MW GT-2 tripped 16:06.
q) Sirajganj #2 CCPP GT & ST were synchronized at 14:52 & 17:27 respectively.
r) Chapainawabganj-100 MW tripped at 18:25 showing E/F relay and was synchronized at 20:06.
s) sylhet-225 MW tripped at 00:07(5/7/22) showing E/F relay and was synchronized at 02:32(5/7/22) and
again tripped at 06:05(5/7/22) showing E/F relay.
t) Ashuganj 230/132 kV OAT12 transformer tripped at 00:16(5/7/22) showing O/C relay and was switched
on at 00:43(5/7/22).
u) Kishorganj 132/33 kV T-1 & T-2 transformers tripped at 06:18(5/7/22) showing O/C relay due to 33 kV | [5 empty] | About 55 MW power interruption occurred under
Pakundia & Bajidpur feeder fault and were switched on at 06:38 & 06:40(5/7/22). | [5 empty] | Kishorganj S/S area from 06:18 to 06:38(5/7/22).
v) Rangpur 33 kV bus-1 was under shut down at 07:25(5/7/22) due to red maintenance and was switched | [5 empty] | About 20 MW power interruption occurred under
on at 08:35(5/7/22). | [5 empty] | Rangpur S/S area from 07:25 to 08:35(5/7/22).
w) Mymensing 132/33 kV T-1 & T-2 transformer tripped at 07:15(5/7/22) due to 33 kV Akua feeder fault | [5 empty] | About 116 MW power interruption occurred under
and was switched on at 07:25(5/7/22). | [5 empty] | Mymensing S/S area from 07:15 to 07:25(5/7/22).
x) Mymensing RPCL tripped at 07:13(5/7/22) showing E/F relay and was synchronized at 07:30(5/7/22).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7190891 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 80 | 1768909 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 3299330 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 152 | 3378000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 3691150 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 32 | 850560 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 1024201 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 379620
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 969130 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 177 | 1169237 | Gas shoratge
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2219616 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 639720 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 3255360 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 1070411 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 953479 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1022140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 713000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 661400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1104000 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 6493525 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 6536658
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 608526 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3211776
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2463600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2542080
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1368000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 245408
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1287000
| Dhaka area Total |  |  |  | 5847 | 2911 | 64463727
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 599994
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 145530
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 901440 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 122 | 2775927 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2529999
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 177696 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1897097
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 20 | 496920 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1783680 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 419712
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 416160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 2191680 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 39000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 280 | 4860109 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 39 | 997296 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2593552
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1217280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2595655 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1277 | 28738727
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 3885000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7560700 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 3993000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 384768 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 74880 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 552000 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1183093
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3119636 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 962528 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 1788140 | Gas shortage
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2915520
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 337464
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3696960
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 8 | 302900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 480430 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 3056448
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 437640 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887400 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 53 | 2232000
| Cumilla Area Total |  |  |  | 2885 | 1754 | 38098367
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2130240 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 421164
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 186 | 3192000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1792800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 181950
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 593040
| Mymensingh Area Total |  |  |  | 614 | 448 | 8318944
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 33 | 778000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 962912 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 90 | 2352273 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 127800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 102090 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 240000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1315776
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2030400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2886040 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 41522
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7530000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 280 | 6380000 | ST under S/D
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 220140
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9023700
| Sylhet Area Total |  |  |  | 2477 | 1432 | 33990653
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 855 | 21117090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 546240 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 468960 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 205 | 4855680 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 75 | 663808 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 170 | 4033152 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 266625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 2001600
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 2079840 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2513520
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 704160
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1718 | 39250675
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1154784
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 36 | 569117 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 1007000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15020200 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5215145
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 901200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1078 | 23867446
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 675664 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 342505 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 872651 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 456160 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 3015045
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 163 | 4031791 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 8746691 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 601317 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 467760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240390
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 42946 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1783288 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2252928 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2730336
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35160
| Rajshahi Area Total |  |  |  | 2129 | 1227 | 26294632
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4300800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 363000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1843478 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43265
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 110 | 1474944
| Rangpur Area Total |  |  |  | 720 | 391 | 8025487
| Total |  |  |  | 21396 | 12236 | 271048658
| Eastern Grid Total |  |  |  | 14205 | 7822 | 173610418
| Western Grid Total |  |  |  | 7191 | 4414 | 97438240
| National Grid Total |  |  |  | 21396 | 12236 | 271048658
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-04
(a) ENTIRE EASTERN GRID : |  | 8063.13 | MW | (b) ENTIRE WESTERN GRID : |  | 3484.46 | MW
i) Dhaka area |  | 4525.08 | MW | i) Khulna area |  | 1369.2 | MW
ii) Chittagong area |  | 1125.55 | MW | ii) Rajshahi area |  | 1106.4 | MW
iii) Comilla area |  | 1082.5 | MW | iii) Barisal area |  | 380.86 | MW
iv) Mymensingh area |  | 903 | MW | iv) Rangpur area |  | 628 | MW
v) Sylhet area |  | 427 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11547.59 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
AKS | 13 | 12:00 | Hasnabad | 111 | 21:00 | Pabna | 89 | 00:00
AKSML | 136 | 04:00 | Hathazari | 90 | 19:00 | Palashbari | 108 | 23:00
Aftabnagar | 37 | 21:00 | Ishurdi | 69 | 03:00 | Panchagarh | 46 | 08:00
Agargaon | 87 | 12:00 | Jaldhaka | 48 | 03:00 | Patuakhali | 133 | 22:00
Agrabad | 84 | 13:00 | Jamalpur | 122 | 22:00 | Payra | 1.02 | 16:00
Amnura | 52 | 05:00 | Jashore | 103 | 06:00 | Purbachal | 20 | 21:00
Ashuganj | 39 | 19:30 | Jhenaidah | 100 | 04:00 | Purbasadipur | 96 | 05:00
BSRM | 155 | 02:00 | Joydebpur | 188 | 16:00 | Rahim | 26 | 08:00
Bagerhat | 79 | 01:00 | Joypurhat | 52 | 03:00 | Rajbari | 60 | 19:30
Bakulia | 112 | 18:30 | Juldah | 26 | 09:00 | Rajendrapur | 92 | 05:00
Banani | 54 | 15:00 | KSRM | 32 | 11:00 | Rajshahi | 132 | 22:00
Bangabhaban | 22 | 11:00 | Kabirpur | 249 | 09:00 | Rajshahi-230 | 26 | 02:00
Barapukuria | 50 | 22:00 | Kachua | 62 | 22:00 | Ramganj | 88 | 19:00
Barguna | 20 | 22:00 | Kallyanpur | 105 | 23:00 | Rampur | 16 | 00:00
Barishal | 116 | 19:00 | Kalurghat | 33 | 16:00 | Rangamati | 14 | 19:00
Barishal-230 | 58 | 23:00 | Kamrangirchar | 55 | 10:00 | Rangpur | 105 | 08:00
Baroaulia | 75 | 01:00 | Kaptai | 4.2 | 19:00 | Ruppur | 5 | 09:00
Baroirhat | 55 | 19:00 | Kazla | 86 | 23:00 | SSM | 3 | 05:00
Bashundhara | 157 | 21:00 | Keranigonj | 48 | 03:00 | Saidpur | 93 | 08:00
BashundharaCement | 6 | 00:00 | Khagrachori | 26 | 23:00 | Satkhira | 95 | 06:00
Beanibazar | 48 | 03:00 | Khulna | 96 | 14:00 | Satmasjid | 101 | 19:00
Benapole | 46 | 21:00 | Khulshi | 202 | 19:00 | Savar | 156 | 09:00
Bhaluka | 130 | 08:00 | Kishoreganj | 116 | 02:00 | Shahjadpur | 85 | 22:00
Bhandaria | 62 | 23:00 | Kodda | 285 | 11:00 | Shahjibazar | 95 | 00:00
Bhangura | 28 | 03:00 | Kulaura | 38 | 01:00 | Shahmirpur | 46.5 | 18:30
Bheramara(GK) | 56 | 22:00 | Kurigram | 52 | 23:00 | Shariatpur | 78 | 22:00
Bhulta | 473 | 02:00 | Kushtia | 120 | 05:00 | Sherpur | 100 | 19:00
Bog-Sherpur | 58 | 03:00 | Lalbag | 95 | 13:00 | Shikalbaha | 28 | 19:00
Bogura | 148 | 22:00 | Lalmonirhat | 39 | 22:00 | Shikalbaha-230 | N/A | N/A
Borhanuddin | 42 | 00:00 | Madanganj | 88 | 22:00 | Shitalakhya | 114 | 12:00
Brahmanbaria | 140 | 00:00 | Madaripur | 116 | 21:00 | Sholosohor | N/A | N/A
Cantonment | 144 | 21:00 | Madartek | 83 | 21:00 | Shyampur | 144 | 01:00
Chandpur | 54.5 | 21:00 | Madunaghat | 53 | 01:00 | Siddhirganj | 108 | 22:00
Chandraghona | 26 | 02:00 | Magura | 46 | 04:00 | Sirajganj | 88 | 07:00
Chapai | 62 | 23:00 | Mahasthangarh | 62 | 23:00 | Sonargaon | 80 | 12:00
Charsaidpur | 31 | 00:00 | Manikganj | 88 | 22:00 | Sreemongol | 44 | 12:00
Chauddagram | 43 | 22:00 | Maniknagar | 80 | 12:00 | Srinagar | 46.28 | 21:00
Chhatak | 27 | 00:00 | Matarbari | 42 | 21:00 | Sunamganj | 38 | 22:00
Chowmuhani | 180 | 22:00 | Matuail | 56 | 23:00 | Sylhet | 136 | 00:00
Chuadanga | 78 | 00:00 | Millgate | 59 | 09:00 | TK | 28.5 | 19:00
Coxsbazar | 89 | 09:00 | Mirpur | 123 | 23:00 | Tangail | 195 | 22:00
Cumilla(N) | 152 | 22:00 | Mirsorai | N/A | N/A | Thakurgaon | 66 | 22:00
Cumilla(S) | 180 | 19:00 | Mithapukur | 28 | 09:00 | Tongi | 116 | 19:30
Daudkandi | 114 | 05:00 | Modern | 0 | 00:00 | Ullon | 40 | 21:00
Dhaka | 44 | 11:00 | Mogbazar | 131 | 15:00 | Uttara | 93 | 21:00
Dhamrai | 106 | 02:00 | Mongla | 34 | 01:00 | UttaraNew | 18 | 00:00
Dhanmondi | 148 | 12:00 | Motijheel | 39 | 14:00 | Zigatola | 57 | 19:00
Dohazari | 82 | 23:00 | Munshiganj | 109 | 23:00
Faridpur | 123 | 02:00 | Mymensingh | 219 | 23:00
Fatullah | 68 | 23:00 | Naogaon | 105 | 01:00
Fenchuganj | 44 | 19:00 | Narail | 40 | 22:00
Feni | 105 | 03:00 | Narinda | 70 | 13:00
GPH | 91 | 12:00 | Narshingdi | 147 | 19:00
Ghorashal | 73 | 20:00 | Natore | 118 | 03:00
Goalpara | 30 | 13:00 | Nawabganj | 36.9 | 19:00
Gollamari | 57 | 21:00 | Netrakona | 96 | 19:00
Gopalganj | 105.2 | 22:00 | New | 81 | 09:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Bhulta | 392 | 20:00 | 374 | 15:00 | Kaliakoir | 391 | 19:00 | 383 | 14:00
| Bibiana | 407 | 19:00 | 400 | 02:00 | Payra | 416 | 10:00 | 410 | 01:00
| BIPTC | 398 | 05:00 | 393 | 21:00
| Gopalganj_I | 411 | 20:00 | 401 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 19:30 | 214 | 15:00 | Hasnabad | 223 | 19:30 | 216 | 10:00
| AKSML | 236 | 20:00 | 221 | 09:00 | Hathazari | 236 | 00:00 | 228 | 10:00
| Aminbazar | 222 | 21:00 | 215 | 09:00 | Ishurdi | 235 | 19:30 | 230 | 01:00
| Ashuganj | 235 | 05:00 | 231 | 09:00 | Jhenaidah | 233 | 20:00 | 226 | 01:00
| Baghabari | 238 | 06:00 | 230 | 01:00 | Kaliakoir | 225 | 00:00 | 219 | 09:00
| Barapukuria | 230 | 17:00 | 220 | 04:00 | Keranigonj | 221 | 07:00 | 213 | 15:00
| Barishal | 241 | 07:00 | 238 | 00:00 | Khulna(S) | 242 | 19:30 | 235 | 01:00
| Bheramara | 233 | 20:00 | 226 | 07:00 | Maniknagar | 222 | 20:00 | 214 | 15:00
| Bhulta | 226 | 20:00 | 216 | 14:00 | Meghnaghat | 228 | 04:00 | 221 | 13:00
| Bibiana | 238 | 17:00 | 233 | 01:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 19:30 | 228 | 01:00 | Rajshahi | 235 | 15:00 | 228 | 05:00
| Bogura | 232 | 15:00 | 225 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 18:00 | 242 | 00:00 | Rampura | 224 | 05:00 | 214 | 15:00
| BSRM | 233 | 19:30 | 224 | 09:00 | Shikalbaha | 238 | 19:30 | 229 | 10:00
| Cumilla(N) | 229 | 19:30 | 223 | 10:00 | Shyampur | 222 | 05:00 | 215 | 15:00
| Fenchuganj | 241 | 20:00 | 235 | 02:00 | Siddhirganj | 229 | 01:00 | 216 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 20:00 | 227 | 08:00
| GPH | 235 | 03:00 | 228 | 11:00 | Tongi | 222 | 19:30 | 214 | 15:00
| Haripur | 222 | 20:00 | 216 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 131 | 05:00 | 125 | 10:00 | Lalbag | 133 | 03:00 | 128 | 15:00
| Agargaon | 132 | 04:00 | 126 | 15:00 | Lalmonirhat | 133 | 17:00 | 123 | 07:00
| Agrabad | 138 | 16:00 | 132 | 09:00 | Madanganj | 130 | 04:00 | 124 | 15:00
| AKS | 140 | 19:30 | 131 | 10:00 | Madaripur | 136 | 06:00 | 132 | 00:00
| Aminbazar | 131 | 19:00 | 123 | 09:00 | Madartek | 131 | 05:00 | 123 | 15:00
| Amnura | 137 | 10:00 | 125 | 18:30 | Madunaghat | 140 | 23:00 | 134 | 09:00
| Ashuganj | 135 | 13:00 | 132 | 00:00 | Magura | 137 | 19:30 | 132 | 06:00
| Bagerhat | 136 | 15:00 | 132 | 01:00 | Mahasthangarh | 136 | 17:00 | 129 | 05:00
| Bakulia | 140 | 19:30 | 135 | 06:00 | Manikganj | 136 | 12:00 | 132 | 01:00
| Banani | 132 | 05:00 | 126 | 09:00 | Maniknagar | 132 | 06:00 | 124 | 15:00
| Bangabhaban | 131 | 05:00 | 124 | 15:00 | Matarbari | 133 | 16:00 | 121 | 19:00
| Barapukuria | 138 | 18:00 | 130 | 04:00 | Matuail | 131 | 05:00 | 125 | 14:00
| Barguna | 137 | 21:00 | 133 | 00:00 | Millgate | 132 | 06:00 | 126 | 09:00
| Barishal | 136 | 21:00 | 131 | 15:00 | Mirpur | 131 | 19:30 | 123 | 09:00
| Barishal-230 | 137 | 07:00 | 133 | 15:00 | Mithapukur | 136 | 18:00 | 126 | 05:00
| Baroaulia | 143 | 19:00 | 136 | 04:00 | Modern | 140 | 23:00 | 134 | 07:00
| Baroirhat | 132 | 12:00 | 126 | 05:00 | Mogbazar | 132 | 04:00 | 125 | 14:00
| Bashundhara | 132 | 05:00 | 126 | 09:00 | Mongla | 136 | 09:00 | 129 | 19:00
| BashundharaCement | 136 | 19:00 | 124 | 15:00 | Motijheel | 131 | 07:00 | 124 | 15:00
| Beanibazar | 131 | 04:00 | 128 | 02:00 | Munshiganj | 132 | 11:00 | 123 | 15:00
| Benapole | 136 | 19:30 | 131 | 01:00 | Mymensingh | 132 | 12:00 | 120 | 01:00
| Bhaluka | 131 | 12:00 | 118 | 01:00 | Naogaon | 134 | 16:00 | 124 | 17:00
| Bhandaria | 134 | 07:00 | 127 | 00:00 | Narail | 136 | 20:00 | 132 | 00:00
| Bhangura | 139 | 12:00 | 135 | 03:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 12:00 | 134 | 01:00 | Narshingdi | 126 | 00:00 | 121 | 15:00
| Bheramara(GK) | 137 | 21:00 | 134 | 02:00 | Natore | 135 | 12:00 | 130 | 05:00
| Bhulta | 123 | 01:00 | 117 | 15:00 | Nawabganj | 134 | 20:00 | 127 | 15:00
| Bog-Sherpur | 136 | 15:00 | 131 | 06:00 | Netrakona | 132 | 12:00 | 122 | 02:00
| Bogura | 138 | 19:30 | 131 | 07:00 | New | 138 | 03:00 | 126 | 15:00
| Bogura-230 | 138 | 19:30 | 132 | 06:00 | Niamatpur | 133 | 15:00 | 120 | 07:00
| Brahmanbaria | 130 | 07:00 | 126 | 00:00 | Noapara | 139 | 19:30 | 134 | 05:00
| Cantonment | 131 | 05:00 | 125 | 10:00 | Pabna | 136 | 19:30 | 132 | 01:00
| Chandpur | 139 | 18:00 | 133 | 06:00 | Palashbari | 134 | 17:00 | 126 | 03:00
| Chandraghona | 141 | 19:00 | 133 | 09:00 | Panchagarh | 135 | 19:30 | 121 | 07:00
| Chapai | 136 | 16:00 | 132 | 01:00 | Patuakhali | 137 | 21:00 | 132 | 01:00
| Charsaidpur | 131 | 04:00 | 125 | 14:00 | Payra | 137 | 07:00 | 135 | 00:00
| Chauddagram | 133 | 20:00 | 128 | 03:00 | PHP | 132 | 17:00 | 126 | 04:00
| Chhatak | 132 | 06:00 | 128 | 01:00 | Purbachal | 132 | 04:00 | 126 | 15:00
| Chowmuhani | 132 | 12:00 | 125 | 18:30 | Purbasadipur | 136 | 18:00 | 124 | 05:00
| Chuadanga | 133 | 17:00 | 129 | 00:00 | Rahim | 131 | 00:00 | 126 | 14:00
| Coxsbazar | 134 | 19:30 | 123 | 01:00 | Rajbari | 133 | 09:00 | 128 | 01:00
| Cumilla(N) | 135 | 19:30 | 131 | 02:00 | Rajendrapur | 138 | 18:00 | 132 | 00:00
| Cumilla(S) | 135 | 19:30 | 124 | 14:00 | Rajshahi | 135 | 12:00 | 129 | 06:00
| Daudkandi | 134 | 12:00 | 129 | 00:00 | Rajshahi-230 | 135 | 15:00 | 130 | 05:00
| Dhaka | 132 | 05:00 | 125 | 10:00 | Ramganj | 132 | 09:00 | 127 | 19:00
| Dhamrai | 130 | 19:00 | 126 | 02:00 | Rampur | 140 | 19:30 | 133 | 09:00
| Dhanmondi | 132 | 04:00 | 125 | 14:00 | Rampura | 132 | 05:00 | 123 | 15:00
| Dohazari | 140 | 15:00 | 132 | 09:00 | Rangamati | 138 | 17:00 | 133 | 10:00
| Faridpur | 134 | 12:00 | 130 | 00:00 | Rangpur | 134 | 17:00 | 124 | 05:00
| Fatullah | 136 | 15:00 | 126 | 16:00 | Ruppur | 137 | 12:00 | 133 | 06:00
| Fenchuganj | 135 | 00:00 | 133 | 02:00 | Saidpur | 137 | 18:00 | 123 | 07:00
| Feni | 134 | 17:00 | 127 | 04:00 | Satkhira | 135 | 20:00 | 128 | 13:00
| Ghorashal | 137 | 07:00 | 135 | 00:00 | Satmasjid | 131 | 03:00 | 126 | 11:00
| Goalpara | 139 | 19:30 | 135 | 02:00 | Savar | 133 | 20:00 | 124 | 09:00
| Gollamari | 137 | 19:30 | 133 | 01:00 | Shahjadpur | 140 | 01:00 | 136 | 07:00
| Gopalganj | 138 | 20:00 | 135 | 01:00 | Shahjibazar | 134 | 14:00 | 131 | 00:00
| Gopalganj_I | 138 | 20:00 | 133 | 01:00 | Shahmirpur | 140 | 00:00 | 134 | 10:00
| Gulshan | 131 | 05:00 | 125 | 10:00 | Shariatpur | 134 | 09:00 | 129 | 22:00
| Halishahar | 140 | 19:30 | 133 | 09:00 | Sherpur | 137 | 19:30 | 125 | 01:00
| Haripur | 131 | 00:00 | 126 | 14:00 | Shikalbaha | 141 | 17:00 | 135 | 09:00
| HaripurSBU | 130 | 00:00 | 127 | 13:00 | Shikalbaha-230 | 140 | 19:30 | 135 | 10:00
| Hasnabad | 135 | 19:30 | 128 | 15:00 | Shitalakhya | 135 | 05:00 | 129 | 15:00
| Hathazari | 139 | 19:30 | 134 | 10:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 137 | 19:30 | 134 | 01:00 | Shyampur | 131 | 05:00 | 127 | 11:00
| Jaldhaka | 133 | 18:00 | 122 | 07:00 | Shyampur-230 | 137 | 16:00 | 126 | 15:00
| Jamalpur | 139 | 18:00 | 126 | 01:00 | Siddhirganj | 130 | 03:00 | 127 | 10:00
| Jashore | 137 | 20:00 | 132 | 01:00 | Sirajganj | 136 | 00:00 | 131 | 05:00
| Jhenaidah | 138 | 19:30 | 133 | 06:00 | Sonargaon | 132 | 07:00 | 129 | 11:00
| Jhenaidah-230 | 138 | 19:30 | 134 | 00:00 | Sreemongol | 135 | 09:00 | 132 | 01:00
| Joydebpur | 142 | 10:00 | 137 | 15:00 | Srinagar | 133 | 03:00 | 128 | 15:00
| Joypurhat | 135 | 16:00 | 124 | 06:00 | SSM | 145 | 19:00 | 137 | 09:00
| Juldah | 140 | 17:00 | 135 | 10:00 | Sunamganj | 131 | 07:00 | 127 | 01:00
| Kabirpur | 139 | 12:00 | 125 | 15:00 | Sylhet | 132 | 00:00 | 130 | 02:00
| Kachua | 137 | 17:00 | 131 | 03:00 | Tangail | 137 | 12:00 | 131 | 00:00
| Kaliakoir | 140 | 12:00 | 128 | 15:00 | Thakurgaon | 135 | 19:30 | 121 | 05:00
| Kallyanpur | 132 | 20:00 | 125 | 23:00 | TK | 141 | 19:30 | 134 | 04:00
Page 7 of 7

## L-Curve
Date | 2022-07-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 676 | 7336 | 4374 | 11710 |  |  |  | QF-LDC-11
0:30 | 666 | 7435.5 | 4375.5 | 11811 | Date: | 2022-07-04
1:00 | 656 | 7535 | 4377 | 11912
1:30 | 578 | 7550 | 4317 | 11867
2:00 | 500 | 7565 | 4257 | 11822
2:30 | 493 | 7506.5 | 4241 | 11747.5 | [5 empty] | Gen. at Eve. Peak | 12236 | 12236 MW (21:00 )
3:00 | 486 | 7448 | 4225 | 11673 | [6 empty] | 21:00
3:30 | 456 | 7418.5 | 4213.5 | 11632 | [5 empty] | Gen. at Day Peak | 10831 | 10831 MW (09:00 )
4:00 | 426 | 7389 | 4202 | 11591 | [6 empty] | 9:00
4:30 | 440 | 7394.5 | 4205 | 11599.5 | [5 empty] | Highest Generation | 12242
5:00 | 454 | 7400 | 4208 | 11608 | [6 empty] | 22:00
5:30 | 490 | 7261 | 4011.5 | 11272.5
6:00 | 526 | 7122 | 3815 | 10937
6:30 | 471 | 7064.5 | 3834 | 10898.5
7:00 | 416 | 7007 | 3853 | 10860
7:30 | 388 | 6998.5 | 3802 | 10800.5
8:00 | 360 | 6990 | 3751 | 10741
8:30 | 474 | 7054.5 | 3731.5 | 10786
9:00 | 588 | 7119 | 3712 | 10831
9:30 | 658 | 7119.5 | 3693 | 10812.5
10:00 | 728 | 7120 | 3674 | 10794
10:30 | 744 | 7031.5 | 3662.5 | 10694
11:00 | 760 | 6943 | 3651 | 10594
11:30 | 780 | 7045.5 | 3646.5 | 10692
12:00 | 800 | 7148 | 3642 | 10790
12:30 | 790 | 7119 | 3690 | 10809
13:00 | 780 | 7090 | 3738 | 10828
13:30 | 771 | 7012 | 3743 | 10755
14:00 | 762 | 6934 | 3748 | 10682
14:30 | 818 | 6884.5 | 3743.5 | 10628
15:00 | 874 | 6835 | 3739 | 10574
15:30 | 954 | 6787.5 | 3734 | 10521.5
16:00 | 1034 | 6740 | 3729 | 10469
16:30 | 962 | 6783 | 3736.5 | 10519.5
17:00 | 890 | 6826 | 3744 | 10570
17:30 | 919 | 6851.5 | 3714.5 | 10566
18:00 | 948 | 6877 | 3685 | 10562
18:30 | 944 | 7135 | 3821 | 10956
19:00 | 940 | 7393 | 3957 | 11350
19:30 | 890 | 7444 | 4175 | 11619
20:00 | 640 | 7565 | 4267 | 11832 |  |  |  | Executive Engineer
20:30 | 624 | 7693.5 | 4340.5 | 12034 |  |  |  | Network Operation Division
21:00 | 608 | 7822 | 4414 | 12236
21:30 | 621 | 7847.5 | 4391.5 | 12239
22:00 | 634 | 7873 | 4369 | 12242 |  |  |  |  | Page 6 of 7
22:30 | 657 | 7740 | 4395 | 12135
23:00 | 680 | 7607 | 4421 | 12028
23:30 | 678 | 7471.5 | 4397.5 | 11869
24:00 | 676 | 7336 | 4374 | 11710
12236 MW (21:00 )
10831 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-04 |  | Energy |  | 271048658
[13 empty] | 2022-07-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2934 | 856 | 1798 | 536 | 3503 | 797 | 124 | 431 | 778 | 164 | 0
0:30 | 3149.5 | 871.5 | 1738 | 468.5 | 3482.5 | 797 | 124 | 432.5 | 797.5 | 162 | 0 |  | Date: | 2022-07-04
1:00 | 3365 | 887 | 1678 | 401 | 3462 | 797 | 124 | 434 | 817 | 160 | 0
1:30 | 3370 | 887 | 1685 | 401 | 3403.5 | 797 | 124.5 | 434.5 | 818 | 160 | 0 | [9 empty] | Total Energy | 271.0487 | Total Energy Gen 271.049 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 271.049 MKWHr
2:00 | 3375 | 887 | 1692 | 401 | 3345 | 797 | 125 | 435 | 819 | 160 | 0 | [9 empty] | Energy not Served | 0
2:30 | 3372 | 887 | 1700 | 402 | 3262 | 797 | 125 | 436 | 822 | 159 | 0 | [9 empty] | Energy Requirement | 271.0487
3:00 | 3369 | 887 | 1708 | 403 | 3179 | 797 | 125 | 437 | 825 | 158 | 0
3:30 | 3373 | 887.5 | 1707 | 400.5 | 3152.5 | 797 | 124.5 | 436 | 811.5 | 157 | 0 | [7 empty] | Shortage
4:00 | 3377 | 888 | 1706 | 398 | 3126 | 797 | 124 | 435 | 798 | 156 | 0
4:30 | 3376 | 890.5 | 1724 | 399 | 3124.5 | 797 | 123.5 | 436.5 | 790.5 | 153 | 0
5:00 | 3375 | 893 | 1742 | 400 | 3123 | 797 | 123 | 438 | 783 | 150 | 0
5:30 | 3362 | 893.5 | 1671.5 | 263.5 | 3111 | 776 | 123 | 421.5 | 703.5 | 144 | 3.5
6:00 | 3349 | 894 | 1601 | 127 | 3099 | 755 | 123 | 405 | 624 | 138 | 7
6:30 | 3265.5 | 894 | 1667 | 178.5 | 3088 | 730 | 104.5 | 378 | 591 | 137 | 22.5 | [5 empty] | Coal
7:00 | 3182 | 894 | 1733 | 230 | 3077 | 705 | 86 | 351 | 558 | 136 | 38
7:30 | 3106.5 | 893.5 | 1706.5 | 304.5 | 3083 | 705 | 87 | 285 | 495.5 | 136 | 63 |  |  |  |  | Oil |  |  |  | ,
8:00 | 3031 | 893 | 1680 | 379 | 3089 | 705 | 88 | 219 | 433 | 136 | 88
8:30 | 3076 | 893 | 1640 | 431.5 | 3094 | 690 | 88 | 219 | 417 | 138 | 99.5
9:00 | 3121 | 893 | 1600 | 484 | 3099 | 675 | 88 | 219 | 401 | 140 | 111
9:30 | 3087 | 876 | 1587.5 | 540.5 | 3064.5 | 675 | 88 | 218.5 | 404 | 142 | 129.5
10:00 | 3053 | 859 | 1575 | 597 | 3030 | 675 | 88 | 218 | 407 | 144 | 148
10:30 | 3028 | 859 | 1542.5 | 596.5 | 2992.5 | 685 | 88.5 | 216 | 390.5 | 143 | 152.5
11:00 | 3003 | 859 | 1510 | 596 | 2955 | 695 | 89 | 214 | 374 | 142 | 157
11:30 | 3096.5 | 858.5 | 1489.5 | 595.5 | 2943.5 | 705 | 107 | 215 | 387.5 | 148 | 146
12:00 | 3190 | 858 | 1469 | 595 | 2932 | 715 | 125 | 216 | 401 | 154 | 135
12:30 | 3069.5 | 864 | 1543 | 596 | 2962 | 715 | 125 | 216.5 | 403 | 155 | 160
13:00 | 2949 | 870 | 1617 | 597 | 2992 | 715 | 125 | 217 | 405 | 156 | 185
13:30 | 2949 | 870 | 1617 | 597 | 2992 | 715 | 125 | 217 | 405 | 156 | 185
14:00 | 2949 | 870 | 1617 | 597 | 2992 | 715 | 125 | 217 | 405 | 156 | 185
14:30 | 2849 | 869.5 | 1559.5 | 601 | 2997.5 | 740 | 125 | 220 | 413 | 155 | 176.5
15:00 | 2749 | 869 | 1502 | 605 | 3003 | 765 | 125 | 223 | 421 | 154 | 168
15:30 | 2764.5 | 869.5 | 1515.5 | 578 | 2968 | 775 | 124 | 227.5 | 417 | 156 | 139
16:00 | 2780 | 870 | 1529 | 551 | 2933 | 785 | 123 | 232 | 413 | 158 | 110
16:30 | 2753 | 869.5 | 1520.5 | 561.5 | 3013 | 775 | 123 | 237 | 443 | 159 | 80
17:00 | 2753 | 869 | 1512 | 572 | 3093 | 765 | 123 | 242 | 473 | 160 | 50
17:30 | 2793 | 869.5 | 1497.5 | 419 | 3247 | 750 | 123 | 241 | 493.5 | 157 | 34
18:00 | 2833 | 870 | 1483 | 266 | 3401 | 735 | 123 | 240 | 514 | 154 | 18
18:30 | 2815 | 870 | 1533 | 435 | 3510 | 740 | 123 | 321.5 | 564 | 167 | 9
19:00 | 2797 | 870 | 1583 | 604 | 3619 | 745 | 123 | 403 | 614 | 180 | 0
19:30 | 2815 | 870 | 1635 | 678 | 3665 | 795 | 123 | 427 | 643 | 176 | 0
20:00 | 3024 | 856 | 1636 | 577 | 3736 | 795 | 123 | 431 | 702 | 164 | 0 | 700
20:30 | 3104 | 855.5 | 1630.5 | 627.5 | 3789 | 796 | 122.5 | 432 | 728.5 | 161 | 0 | 1400
21:00 | 3184 | 855 | 1625 | 678 | 3842 | 797 | 122 | 433 | 755 | 158 | 0 | 700
21:30 | 3190.5 | 855 | 1633 | 649.5 | 3843.5 | 797 | 122.5 | 433.5 | 769.5 | 159 | 0
22:00 | 3197 | 855 | 1641 | 621 | 3845 | 797 | 123 | 434 | 784 | 160 | 0
22:30 | 3133 | 855 | 1666 | 647 | 3752 | 797 | 123 | 433 | 782.5 | 160 | 0
23:00 | 3069 | 855 | 1691 | 673 | 3659 | 797 | 123 | 432 | 781 | 160 | 0
23:30 | 3001.5 | 855.5 | 1744.5 | 604.5 | 3581 | 797 | 123.5 | 431.5 | 779.5 | 162 | 0 |  | Max Temp. in Dhaka |  | 24.7° C | 34.7° C
24:00 | 2934 | 856 | 1798 | 536 | 3503 | 797 | 124 | 431 | 778 | 164 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 271.049 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 271.049 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-07-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 89 | 90 | 90 | 89 | 88 | 88 | 86 | 88 | 88 | 88 | 89 | 90 | 90 | 90 | 90 | 88 | 88 | 88 |  | 88 | 88 | 88 | 87 | 88 | 88 | 89 | 2135927
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 640000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 599994
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 11 | 16 | 19 | 13 | 20 | 19 | 17 | 14 | 9 | 3 | 1 | [8 empty] | 145530
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 81 | 81 | 81 | 81 | 81 | 51 | 51 | 51 | 51 | 51 | 51 | 78 | 85 | 89 | 89 | 74 | 89 | 89 |  | 89 | 74 | 89 | 85 | 85 | 85 | 85 | 1897097
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | [10 empty] | 3 | 3 | 5 | 6 | 6 |  | 46 | 46 | 46 |  |  |  |  | 177696
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 87 | 105 | 105 | 100 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2529999
| Daudkandi 200 MW PP (B.Trac) | [8 empty] | 160 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 100 |  | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 3056448
14 | Titas 50 MW Peaking PP | 35 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 |  | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 962528
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [13 empty] | 7 | 12 | 12 | 16 | 155 |  | 170 | 170 | 170 | 177 | 179 | 180 | 180 | 1169237
18 | Kodda 300 MW PP Unit-2 (Summit) | 260 | 273 | 263 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 262 | 262 | 263 | 275 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 248 | 245 | 6493525
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 123 | 90 | 73 | 73 | 45 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 552000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7190891
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 30 | 28 | 30 | 30 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 21 | 20 | 20 | 384768
33 | Ashuganj 225 MW CCPP | 146 | 153 | 152 | 152 | 153 | 155 | 122 | 145 | 204 | 201 | 198 | 190 | 200 | 121 | 117 | 117 | 114 | 115 |  | 146 | 167 | 194 | 205 | 195 | 183 | 191 | 3885000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 200 | 0 |  |  | 0 | 180 | 140 | 50 | 80 | 105 | 140 | 160 |  | 160 | 160 | 160 | 220 | 220 | 210 | 210 | 3993000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 320 | 350 | 340 | 350 | 350 | 340 | 335 | 340 | 300 | 270 |  | 270 | 270 | 270 | 270 | 330 | 300 | 285 | 7560700
| Ashuganj 420 MW CCPP(East) | [26 empty] | 900
35 | Ashuganj 55 MW PP (Precision) | [12 empty] | 1 | 10 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 74880
36 | Chandpur 150 MW CCPP | 84 | 84 | 84 | 84 | 85 | 84 | 84 | 89 | 85 | 85 | 71 | 62 | 64 | 58 | 55 | 56 | 56 | 57 |  | 70 | 70 | 71 | 85 | 84 | 84 | 85 | 1788140
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 279 | 279 | 280 | 287 | 285 | 280 | 270 | 262 | 254 | 236 | 230 | 211 | [14 empty] | 3299330
40 | Meghnaghat 450 MW CCPP(MPL) | 185 | 190 | 200 | 210 | 210 | 210 | 210 | 210 | 200 | 180 | 160 | 160 | 150 | 150 | 150 | 150 | 150 | 150 |  | 160 | 180 | 180 | 180 | 180 | 185 | 190 | 3691150
41 | Haripur 360MW CCPP(HPL) | 154 | 152 | 154 | 153 | 190 | 181 | 183 | 183 | 171 | 139 | 111 | 65 | 140 | 127 | 62 | 62 | 84 | 140 |  | 147 | 152 | 152 | 152 | 152 | 164 | 173 | 3378000
42 | RPCL 210MW CCPP | 104 | 103 | 103 | 105 | 105 | 105 | 105 | 101 | 99 | 82 | 82 | 70 | 69 | 69 | 69 | 69 | 69 | 69 |  | 102 | 102 | 103 | 103 | 102 | 104 | 103 | 2130240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 3 | 5 | 11 | 3 | 9 | 19 | 25 | 26 | 35 | 29 | 13 | 4 |  | 0 | [6 empty] | 181950
44 | Fenchugonj CCPP Phase-1 | 33 | 33 | 33 | 33 | 32 | 33 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 778000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 962912
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 54 | 55 | 55 | 55 | 55 | 60 | 60 | 59 | 61 | 55 | 55 | 55 | 59 | 60 | 59 | 59 | 60 | 60 |  | 59 | 60 | 61 | 56 | 30 | 30 | 30 | 1315776
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 86 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 2030400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2886040
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 0 | 0 | 0 |  | 0
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 220140
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | [13 empty] | 53 | 127800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 41522
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 320 | 315 | 310 | 300 | 290 | 310 | 320 | 280 | 320 | 320 | 320 | 290 | 305 | 315 | 320 | 300 | 280 |  | 300 | 300 | 300 | 290 | 290 | 310 | 310 | 7530000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 398 | 400 | 390 | 401 | 386 | 378 | 398 | 394 | 373 | 384 | 383 | 392 | 360 |  | 200 | 158 | 325 | 400 | 388 | 387 | 390 | 9023700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 953479
59 | Tangail Palli Power Gen 22 MW | 23 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 593040
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 419712
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 379620
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 421164
63 | Impoprt (Tripura) | 160 | 160 | 158 | 156 | 150 | 138 | 136 | 136 | 140 | 144 | 142 | 154 | 156 | 162 | 154 | 158 | 160 | 154 |  | 180 | 176 | 164 | 158 | 160 | 160 | 164 | 3696960
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 8 | 2 | 2 | 2 | 2 | 7 | 2 | 2 | 2 | 6 | 2 |  | 8 | 10 | 14 | 18 | 23 | 29 | 25 | 416160
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 0 | [7 empty] | 8 | 19 | 19 | 19 | 19 | 19 | 19 | 337464
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246960
67 | Jangalia 33MW PP (Summit) | 27 | 32 | 32 | 32 | 32 | 32 | 22 | 20 | 9 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 14 | 15 | 302900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480430
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 19 | 19 | 522460
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 17 | 20 | 5 |  | 20 | 20 | 27 | 28 | 28 | 28 | 28 | 499680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 713000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 28 | 25 | 28 | 24 | 24 | 24 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 27 | 30 | 30 | 661400
73 | Ghorashal 108MW PP (Regent) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 70 | 70 | 72 | 72 | 73 | 74 | 74 | 76 | 77 | 77 |  | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 1768909
Feni Lanka Power
| Chowmuhani 113 MW | 36 | 34 | 29 | 29 | 28 | 29 | 29 | 29 | 28 | 32 | 8 | 9 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 437640
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 54 | 54 | 35 | 35 | 35 | 35 | 35 |  | 162 | 162 | 162 | 162 | 162 | 17 | 17 | 1368000
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 42 | 40 | 40 | 969130
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 45 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1104000
79 | Kodda 150MW PP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 150 | 132 | 150 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3255360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 96 | 105 | 105 | 90 | 90 | 100 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2463600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 2 | 1 | 4 | 3 | 2 | 0 | [8 empty] | 39000
| Jodiac Power | 35 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 39 | 54 | 54 | 54 | 997296
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 104 | 92 | 93 | 86 | 97 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2593552
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 39 | 39 | 39 | 40 | 39 | 39 | 34 | 39 | 39 | 39 | 34 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 32 | 34 | 40 | 32 | 850560
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 95 | 104 | 104 | 104 | 93 | 91 | 91 | 104 | 97 | 92 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2542080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 496920
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [14 empty] | 38 | 102090
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1183093
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2219616
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 33 | 31 | 34 |  | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 901440
96 | Chattogram 108 MW PP (ECPV) | 93 | 92 | 92 | 92 | 92 | 93 | 92 | 92 | 94 | 89 | 87 | 91 | 89 | 89 | 89 | 89 | 90 | 90 |  | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 2191680
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 45 | 55 | 55 | 55 | 1024201
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1070411
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 2352273
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 7750
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 639720
104 | Keranigonj 300 MW PP (APR) | 303 | 304 | 306 | 302 | 304 | 117 | 200 | 307 | 229 | 302 | 301 | 300 | 301 | 301 | 307 | 253 | 194 | 106 |  | 300 | 301 | 200 | 300 | 301 | 305 | 208 | 6536658
105 | Bramhangoan 100 MW PP (Aggreko) | [16 empty] | 80 | 40 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 608526
106 | Mymensingh 200 MW PP (United) | 114 | 114 | 115 | 115 | 115 | 115 | 116 | 116 | 116 | 116 | 115 | 115 | 122 | 122 | 121 | 122 | 122 | 186 |  | 186 | 186 | 186 | 186 | 187 | 187 | 115 | 3192000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 121 | 115 | 114 | 112 | 116 | 115 | 149 | 149 | 149 | 149 | 135 | 132 | 132 | 126 | 118 | 146 | 118 |  | 113 | 120 | 118 | 149 | 149 | 149 | 149 | 3211776
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 65 | 76 | 76 | 63 | 63 | 76 | 76 | 76 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1783680
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 100 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 117 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2915520
117 | Ashuganj 150MW PP (Midland) | 135 | 130 | 130 | 132 | 132 | 130 | 128 | 120 | 122 | 127 | 120 | 117 | 120 | 125 | 125 | 127 | 130 | 130 |  | 130 | 130 | 132 | 137 | 143 | 145 | 143 | 3119636
118 | Bibiyana-III 400 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 263 | 279 | 275 | 261 | 280 | 279 | 280 | 264 | 280 | 280 | 280 |  | 267 | 280 | 280 | 280 | 280 | 220 | 80 | 6380000
| Jamalpur 115 MW PP (United) | 60 | 60 | 60 | 59 | 59 | 60 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 69 | 69 | 69 | 69 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 58 | 1792800
| Anwara 300 MW PP (United) | 177 | 175 | 177 | 178 | 178 | 165 | 165 | 166 | 168 | 168 | 166 | 168 | 178 | 178 | 177 | 177 | 177 | 285 |  | 265 | 270 | 280 | 280 | 280 | 280 | 280 | 4860109
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1217280
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 100 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2595655
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887400
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 10 | 25 | 22 | 36 | 34 | 35 | 32 | 20 | 21 | 12 | 3 | [8 empty] | 245408
| Chandpur 115(Doreen) | 112 | 116 | 116 | 116 | 116 | 116 | 112 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 72 | 53 | 52 |  | 52 | 53 | 52 | 53 | 52 | 52 | 53 | 2232000
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  |  | 20 | 44 | 47 | 55 | 55 | 55 | 55 | 1287000
120 | Eastern Zone Total | 7535 | 7565 | 7448 | 7389 | 7400 | 7122 | 7007 | 6990 | 7119 | 7120 | 6943 | 7148 | 7090 | 6934 | 6835 | 6740 | 6826 | 6877 |  | 7393 | 7444 | 7565 | 7822 | 7873 | 7607 | 7336 | 173610418
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 19 | 23 | 20 |  | 49 | 49 | 49 | 49 | 49 | 49 | 16 | 546240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 38 | 38 | 36 | 36 | 36 | 36 | 36 | 36 | 22 | 15 | 15 | 15 | 4 | [9 empty] | 28 | 38 | 38 | 33 | 468960
| Khulna 225 MW CCPP | 206 | 206 | 207 | 206 | 207 | 205 | 206 | 204 | 204 | 203 | 199 | 201 | 202 | 200 | 198 | 202 | 185 | 150 |  | 200 | 204 | 204 | 205 | 204 | 205 | 205 | 4855680
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 73 | 80 | 92 | 80 | 73 | 73 | 93 | 93 |  | 93 | 73 | 80 | 93 | 93 | 93 | 92 | 2079840
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 25 | 57 | 51 | 90 | 84 | 45 | 93 | 96 | 85 | 40 | 18 | 8 | [8 empty] | 704160
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 54 | 54 | 90 | 90 | 90 | 90 | 901200
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 224 | 223 | 223 | 223 | 123 | 224 | 220 | 221 | 222 | 215 | 219 | 219 | 214 | 214 | 217 | 218 | 221 |  | 215 | 221 | 224 | 220 | 223 | 223 | 223 | 5215145
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 96 | 80 | 48 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 16 | 48 | 48 |  | 48 | 64 | 110 | 110 | 110 | 110 | 110 | 1154784
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 63 | 65 | 64 | 64 | 63 | 62 | 65 | 63 | 64 | 62 | 62 | 63 | 61 | 61 | 62 | [10 empty] | 1007000
140 | Bhola 33 MW PP (Venture) | 30 | 30 | 29 | 26 | 25 | 1 | 23 | 11 | 11 | 11 | 15 | 14 | 20 | 20 | 22 | 21 | 21 | 25 |  | 34 | 34 | 37 | 36 | 38 | 37 | 36 | 569117
141 | Noapara 100 MW PP (Bangla Trac) | 98 | 97 | 97 | 96 | 96 | 10 | 30 | 72 | 95 | 95 | 95 | 95 | 96 | 96 | 98 | 98 | 98 | 20 |  | 24 | 97 | 97 | 98 | 40 | 88 | 98 | 2001600
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 32 | 40 | 40 | 8 | 8 | 8 | 266625
143 | Gopalganj 100 MW Peaking PP | 61 | 61 | 61 | 61 | 61 | [14 empty] | 21 | 45 | 78 | 75 | 70 | 70 | 70 | 663808
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 90 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2513520
146 | Bheramara HVDC | 887 | 887 | 887 | 888 | 893 | 894 | 894 | 893 | 893 | 859 | 859 | 858 | 870 | 869 | 869 | 870 | 869 | 870 |  | 870 | 870 | 856 | 855 | 855 | 855 | 856 | 21117090
147 | Bheramara 410 MW CCPP | 165 | 165 | 165 | 165 | 170 | 170 | 170 | 165 | 160 | 155 | 150 | 150 | 155 | 155 | 150 | 150 | 150 | 150 |  | 165 | 170 | 175 | 170 | 175 | 175 | 175 | 4033152
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 580 | 530 | 530 | 500 | 500 | 520 | 540 | 540 | 560 | 590 | 610 | 590 | 560 |  | 570 | 620 | 620 | 622 | 622 | 622 | 622 | 15020200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4300800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 26 | 26 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 675664
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 5 | 3 | 3 | 4 | 4 | 2 | 2 | 1 | 0 | [8 empty] | 35160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [26 empty] | 4230
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 213 | 214 | 215 | 214 | 216 | 185 | 130 | [7 empty] | 10 | 15 | 42 | 75 |  | 188 | 208 | 212 | 213 | 215 | 212 | 211 | 3010815
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 161 | 152 | 151 | 151 | 151 | 151 | 143 | 139 | 155 | 157 |  | 157 | 160 | 161 | 163 | 164 | 166 | 166 | 4031791
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 373 | 373 | 384 | 384 | 394 | 396 | 385 | 361 | 353 | 340 | 334 | 347 | 342 | 348 | 333 | 348 | 352 | 320 |  | 371 | 390 | 380 | 380 | 385 | 393 | 380 | 8746691
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 25 | 27 | 27 | 27 | 27 | 27 | 16 | 16 | 16 | 9 | [9 empty] | 4 | 4 | 12 | 16 | 30 | 30 | 30 | 342505
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 18 | 18 | 17 | 17 | 18 | 19 | 20 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 467760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 240390
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 872651
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 20 | 24 | 24 | 24 | 6 |  |  | 18 | 27 |  | 32 | 32 | 32 | 24 | 24 | 24 | 27 | 456160
168 | Santahar 50 MW Peaking PP | 37 | 37 | 37 | 37 | 37 | [7 empty] | 18 | 38 | 38 | 38 | 37 | 37 |  | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 601317
169 | Natore 52 MW PP (Rajlanka) | 8 | [18 empty] | 8 | 8 | 8 | 8 | 8 | 0 |  | 42946
170 | Chapainawabganj 100 MW Peaking PP | 90 | 83 | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 87 | 86 | 86 | 86 | 85 | 85 | 85 | 85 | 85 |  |  |  |  | 80 | 88 | 88 | 88 | 1783288
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 77 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2252928
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2730336
173 | Rangpur 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 363000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 104 | 70 | 70 | 69 | 70 | 70 | 70 | 69 | 69 | 63 | 69 | 70 | 70 | 70 | 68 | 64 | 64 | 85 |  | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 1843478
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 3 | 6 | 7 | 6 | 7 | 7 | 5 | 1 | 2 | [8 empty] | 43265
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 95 |  | 110 | 110 | 110 | 110 | 110 | 115 | 108 | 1474944
178