## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-06 | Wednesday
|  |  | Date (day): | 2022-07-06 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12822.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13878 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-05 | 2022-07-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 77 | 85 | 82 | 82 |  | 26 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 191 | 146 | 200 | 200 | 160 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 180 | 210 | 210 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 24 | 32 | 32 | 32 |  | 68 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 40 | 40 | 40 |  | 60 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 258 | 187 | 250 | 250 | 85 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 132 | 133 | 133 |  | 16 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 52 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 30 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 48 | 40 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 243 | 260 | 260 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 301 | 300 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 82 | 80 | 0 | 0 | 100 |  | Fuel Shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 81 | 50 | 80 | 20 |  | Fuel Shortage
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 147 | 132 | 114 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 92 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 15 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2875 | 3047 | 3071 | 3133 | 1598 | 1105
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 44 | 44 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 121 | 122 | 122 |  | 108 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 34 | 0 | 36 |  | 62 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 85 | 62 | 60 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 30 | 40 | 55 | 55 | 45 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 76 | 76 |  | 24 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 20 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 27 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 86 | 92 | 85 | 91 |  | 17 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 177 | 263 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 108 | 92 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 93 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1247 | 1377 | 1299 | 1452 | 305 | 617
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 191 | 204 | 180 | 170 | 51 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 310 | 320 | 310 | 50 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 210 | 340 | 330 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 34 | 36 | 36 | 9 |  | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 117 | 143 | 145 | 147
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 47 | 41 | 41 |  | 11 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 84 | 76 | 85 | 85 |  | 78 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 200 | 68 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 152 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 7 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 155 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 9 | 9 | 9 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 74 | 93 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1435 | 1971 | 1807 | 2033 | 742 | 108
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 55 | 103 | 70 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 14 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 200 | 115 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 59 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 15 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 15 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 288 | 447 | 337.6 | 457 | 102 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 33 | 33 | 33 | 33 |  | 37 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 5 | 5 |  | 46 | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 45 | 47 | 5 | 5 |  | 45 | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 61 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 66 | 86 | 86 | 86
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 140 | 140 |  | 91 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 18 | 22 | 6 | 6
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 80 | 405 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1235 | 1596 | 1634 | 1665 | 0 | 759
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 876 | 857 | 881 | 886
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 48 | 16 | 49 |  | 66 | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 17 | 32 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 202 | 203 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 10 | 65 | 0 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 170 | 265 | 240 | 200 | 210 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 8 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 95 | 75 | 90 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 92 | 75 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 52 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1643 | 1765 | 1788 | 1798 | 210 | 136
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 32 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 31 | 20 | 36
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 20 | 85 | 109 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 622 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 222 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 72 | 17 | 90 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 804 | 1057 | 931 | 1163 | 109 | 0
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 24 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 34 | 34 | 43 |  | 7 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 16 | 30 |  | 20 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 140 | 140 | 70 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 211 | 214 | 220 | 220 |  |  | Running by HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 210 | 200 | 200 | 20 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 395 | 414 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 88 | 85 | 90 | 90 |  | 14 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 10 | 180 | 170 | 170 | 30 |  | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 94 | 95 |  | 18 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1175 | 1470 | 1578 | 1701 | 291 | 131
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 175 | 275 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 96 | 70 | 91 |  | 22 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 112 | 34 | 110
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 299 | 498 | 377 | 476 | 194 | 22
|  | Total |  |  |  |  | 22678 | 21396 | 11001 | 13228 | 12822.6 | 13878 | 3551 | 2886
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10792.806 | 12977.66 | 12579.9322 | 13615.3587
| A. |  | 2022-07-05 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13228 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10737 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13678 | MW
| 3 | Day peak Generation : |  |  | 11001 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12977.66 | MW
| 4 | Evening peak Generation : |  |  | 13228 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 450 | MW
| 5 | Total Energy Generation : |  | 281.812 | MKWHr | By Solar | 1.3107 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 118.8259 | MKWHr |  | By Oil: | 113.2835 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.7441 | MKWHr |  | By Hydro: | 2.8401 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3551 | MW | Dhaka | 4891.34 | 4791.34 |  | 100
|  |  |  | For Plants S/D or M/C prob = |  |  | 2886 | MW | Chittagong | 1448 | 1388 |  | 60 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6437 | MW | Khulna | 1508.8 | 1448.8 |  | 60 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 971.2 | MMCFD |  |  | Rajshahi | 1177.6 | 1117.6 |  | 60 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 136649230.663 | ii) Oil : | Taka | 1649782658.1 | Comilla | 1230 | 1180 |  | 50 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 167187969 | Total | Taka | 1953619857.763 | Mymensingh | 1059 | 1009 |  | 50 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 469 | 439 |  | 30 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 770 | MW (E to W) at | 21:00 | hrs | Barisal | 401.92 | 401.92 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 437 | MW at | 7:00 | hrs | Rangpur | 792 | 752 |  | 40 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 12977.66 | 12527.66 |  | 450
| B. |  | 2022-07-06 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13878 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12400 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 298.2588 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10793 | MW at | 8:00 | -162.6788 | 36.427 | -0.28758 | 9.8351 | -11.0219 | 21.2642 | 4.5708 | -24.735 | 50.4073
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1942 | MKWHr. | ii) HVDC Flow at Peak Time |  | 857 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6134 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.83 |  | (b) Today: | 89.12 |  | (c) Rule Curve: |  | 84.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 183 |  | 0 | 190 | 0 | 32 | 0 | 41 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 27 | 49 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 20 | 91 | 33 | 21 | 28 | 0 | 0 | 0 | 290 | 210 | 198 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 21 | 18 | 164 | 103 | 0 | 20 | 0 | 33 | 42 | 53 | 35 | 110 | 0 | 30 | 84 | 0 | 0 | 0 | 11 | 10 | 310 | 16 | 11 | 0 | 243 | 303 | 80 | 116 | 0 | 134 | 0 | 76 | 68 | 138 | 80 | 58 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 10 | 50 | 390 | 92 | 0 | 17 | 108 | 0 | 35 | 0 | 69 | 55 | 0 |  | 855 | 0 | 165 | 0 | 16 | 206 | 0 | 0 | 33 | 64 | 8 | 0 | 34 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 32 | 0 | 38 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 97 | 166 | 0 | 374 | 93 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 224 | 0 | 90 | 0 | 0 | 108 | 0 | 0 |  | 6945 | 4336 | 11281 | 2845 | 855 | 1812 | 480 | 3205 | 797 | 124 | 432 | 778 | 164 | 0 | 0 | 88.84
2:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 187 |  | 0 | 205 | 0 | 32 | 0 | 55 | 222 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 28 | 33 | 27 | 49 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 20 | 82 | 38 | 21 | 29 | 0 | 0 | 0 | 310 | 210 | 200 | 8 | 86 | 26 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 25 | 18 | 162 | 102 | 0 | 20 | 0 | 33 | 42 | 50 | 38 | 110 | 0 | 35 | 84 | 0 | 0 | 0 | 19 | 10 | 300 | 16 | 8 | 0 | 245 | 302 | 80 | 116 | 0 | 130 | 0 | 76 | 68 | 123 | 15 | 58 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 8 | 50 | 392 | 100 | 0 | 17 | 108 | 0 | 35 | 0 | 97 | 55 | 0 |  | 887 | 0 | 165 | 0 | 16 | 205 | 0 | 0 | 32 | 64 | 8 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 96 | 166 | 0 | 400 | 93 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 224 | 0 | 72 | 0 | 0 | 108 | 0 | 0 |  | 6978 | 4372 | 11350 | 2836 | 887 | 1853 | 478 | 3214 | 797 | 124 | 434 | 779 | 162 | 0 | 0 | 88.83
3:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 193 |  | 0 | 210 | 0 | 32 | 0 | 55 | 245 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 17 | 21 | 29 | 0 | 0 | 0 | 270 | 210 | 196 | 8 | 84 | 36 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 33 | 18 | 166 | 105 | 0 | 20 | 0 | 33 | 42 | 50 | 42 | 110 | 0 | 50 | 84 | 0 | 120 | 0 | 19 | 10 | 300 | 16 | 5 | 0 | 243 | 306 | 80 | 116 | 0 | 130 | 0 | 76 | 68 | 125 | 80 | 58 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 85 | 55 | 0 |  | 875 | 0 | 165 | 0 | 16 | 206 | 0 | 0 | 32 | 64 | 8 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 30 | 88 | 0 | 43 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 96 | 165 | 0 | 414 | 93 | 1 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 222 | 0 | 72 | 0 | 0 | 34 | 0 | 0 |  | 7212 | 4293 | 11505 | 3066 | 875 | 1880 | 483 | 3121 | 797 | 124 | 436 | 772 | 166 | 0 | 0 | 88.83
4:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 213 |  | 0 | 210 | 0 | 31 | 0 | 55 | 260 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 45 | 0 | 46 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 23 | 21 | 27 | 0 | 0 | 0 | 270 | 210 | 200 | 8 | 85 | 35 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 33 | 18 | 148 | 105 | 0 | 20 | 0 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 120 | 0 | 19 | 10 | 290 | 16 | 11 | 0 | 244 | 302 | 80 | 116 | 0 | 131 | 0 | 76 | 68 | 132 | 80 | 58 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 80 | 55 | 0 |  | 893 | 0 | 175 | 0 | 16 | 206 | 0 | 0 | 31 | 64 | 8 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 28 | 88 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 216 | 0 | 96 | 168 | 0 | 414 | 93 | 50 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 223 | 0 | 35 | 0 | 0 | 34 | 0 | 0 |  | 7186 | 4273 | 11459 | 3104 | 893 | 1890 | 528 | 3089 | 797 | 81 | 437 | 708 | 148 | 0 | 0 | 88.83
5:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 223 |  | 0 | 210 | 0 | 30 | 0 | 55 | 262 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 46 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 84 | 38 | 21 | 11 | 0 | 0 | 0 | 305 | 210 | 188 | 8 | 85 | 31 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 33 | 18 | 148 | 105 | 0 | 20 | 0 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 120 | 0 | 19 | 10 | 310 | 16 | 11 | 0 | 244 | 309 | 80 | 116 | 0 | 133 | 0 | 90 | 68 | 132 | 80 | 59 | 105 | 105 | 0 | 177 | 54 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 69 | 55 | 0 |  | 893 | 0 | 180 | 0 | 16 | 206 | 0 | 0 | 31 | 64 | 8 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 27 | 88 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 213 | 0 | 95 | 169 | 0 | 414 | 93 | 48 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 223 | 0 | 17 | 0 | 0 | 34 | 0 | 0 |  | 7245 | 4254 | 11499 | 3131 | 893 | 1904 | 532 | 3088 | 797 | 81 | 434 | 704 | 148 | 0 | 0 | 88.83
6:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 241 |  | 0 | 210 | 0 | 30 | 0 | 55 | 275 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 86 | 38 | 21 | 25 | 0 | 0 | 0 | 270 | 210 | 174 | 8 | 84 | 31 | 5 | 0 | 51 | 0 | 40 | 0 | 19 | 11 | 33 | 18 | 126 | 105 | 0 | 20 | 0 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 120 | 0 | 18 | 10 | 280 | 16 | 11 | 0 | 244 | 152 | 80 | 116 | 0 | 130 | 1 | 90 | 68 | 138 | 80 | 59 | 90 | 105 | 0 | 177 | 54 | 110 | 0 | 8 | 64 | 400 | 104 | 3 | 17 | 108 | 0 | 35 | 1 | 79 | 45 | 0 |  | 893 | 0 | 180 | 0 | 16 | 207 | 0 | 0 | 31 | 10 | 8 | 0 | 27 | 84 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 216 | 0 | 95 | 170 | 0 | 414 | 92 | 50 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 225 | 0 | 17 | 0 | 4 | 34 | 0 | 0 |  | 7080 | 4155 | 11235 | 3095 | 893 | 1903 | 377 | 3065 | 797 | 122 | 438 | 626 | 126 | 9 | 0 | 88.83
7:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 242 |  | 0 | 225 | 0 | 31 | 0 | 40 | 300 | 0 | 0 | 40 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 89 | 38 | 21 | 25 | 0 | 0 | 0 | 270 | 210 | 168 | 8 | 85 | 32 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 33 | 18 | 124 | 103 | 0 | 20 | 0 | 33 | 42 | 50 | 43 | 110 | 0 | 51 | 84 | 0 | 0 | 0 | 19 | 10 | 295 | 16 | 11 | 0 | 243 | 220 | 80 | 116 | 0 | 144 | 3 | 76 | 82 | 137 | 80 | 59 | 90 | 105 | 1 | 177 | 54 | 102 | 0 | 8 | 77 | 400 | 96 | 8 | 17 | 108 | 0 | 35 | 8 | 73 | 55 | 0 |  | 893 | 0 | 180 | 0 | 16 | 207 | 0 | 0 | 30 | 10 | 8 | 0 | 27 | 48 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 95 | 172 | 0 | 414 | 92 | 50 | 94 | 105 | 70 | 0 | 1 | 113 | 580 | 225 | 0 | 17 | 1 | 18 | 34 | 0 | 0 |  | 7079 | 4092 | 11171 | 2997 | 893 | 1935 | 445 | 3031 | 755 | 122 | 436 | 607 | 124 | 40 | 0 | 88.83
8:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 265 |  | 0 | 225 | 0 | 32 | 0 | 55 | 306 | 0 | 0 | 40 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 0 | 33 | 33 | 41 | 0 | 75 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 85 | 20 | 91 | 38 | 21 | 8 | 0 | 0 | 0 | 270 | 210 | 179 | 8 | 85 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 33 | 18 | 122 | 71 | 0 | 20 | 1 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 0 | 0 | 18 | 10 | 270 | 16 | 11 | 0 | 243 | 12 | 25 | 117 | 0 | 149 | 9 | 76 | 100 | 123 | 80 | 59 | 88 | 105 | 3 | 176 | 54 | 110 | 0 | 8 | 77 | 400 | 102 | 10 | 17 | 108 | 0 | 35 | 8 | 75 | 55 | 0 |  | 893 | 0 | 185 | 0 | 16 | 206 | 0 | 0 | 30 | 10 | 8 | 0 | 19 | 32 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 95 | 175 | 0 | 414 | 92 | 10 | 94 | 105 | 70 | 0 | 3 | 113 | 550 | 196 | 0 | 17 | 1 | 27 | 34 | 0 | 0 |  | 6750 | 3987 | 10737 | 2939 | 893 | 1877 | 142 | 3038 | 725 | 110 | 436 | 608 | 122 | 62 | 0 | 88.84
9:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 242 |  | 0 | 225 | 0 | 28 | 0 | 55 | 295 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 26 | 33 | 33 | 41 | 0 | 82 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 20 | 91 | 38 | 21 | 3 | 0 | 0 | 0 | 270 | 210 | 190 | 8 | 84 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 25 | 18 | 132 | 55 | 0 | 20 | 1 | 33 | 42 | 50 | 43 | 110 | 0 | 50 | 84 | 0 | 0 | 0 | 18 | 10 | 300 | 16 | 11 | 0 | 245 | 155 | 82 | 116 | 0 | 149 | 10 | 76 | 100 | 113 | 80 | 59 | 88 | 105 | 3 | 178 | 54 | 110 | 0 | 8 | 77 | 401 | 104 | 6 | 17 | 108 | 0 | 35 | 13 | 74 | 55 | 0 |  | 893 | 0 | 175 | 0 | 16 | 206 | 0 | 0 | 30 | 10 | 8 | 0 | 17 | 32 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 199 | 0 | 95 | 176 | 0 | 400 | 92 | 10 | 94 | 105 | 68 | 0 | 3 | 113 | 550 | 223 | 0 | 17 | 3 | 40 | 34 | 0 | 0 |  | 6972 | 3985 | 10957 | 2932 | 893 | 1889 | 342 | 3018 | 725 | 117 | 420 | 609 | 132 | 79 | 0 | 88.84
10:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 0 | 191 |  | 0 | 225 | 0 | 24 | 0 | 55 | 258 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 16 | 41 | 0 | 83 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 30 | 86 | 38 | 21 | 2 | 0 | 0 | 0 | 305 | 210 | 191 | 8 | 84 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 8 | 20 | 138 | 55 | 0 | 20 | 2 | 33 | 42 | 50 | 45 | 110 | 0 | 50 | 66 | 0 | 0 | 0 | 18 | 10 | 310 | 16 | 11 | 0 | 243 | 301 | 82 | 113 | 0 | 147 | 12 | 90 | 100 | 117 | 80 | 59 | 88 | 105 | 5 | 177 | 54 | 108 | 0 | 8 | 93 | 394 | 104 | 15 | 17 | 108 | 0 | 35 | 15 | 74 | 55 | 0 |  | 876 | 0 | 170 | 0 | 16 | 202 | 0 | 0 | 17 | 10 | 8 | 0 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 95 | 170 | 0 | 395 | 92 | 10 | 94 | 105 | 69 | 0 | 6 | 113 | 550 | 221 | 0 | 0 | 3 | 52 | 34 | 0 | 0 |  | 7080 | 3921 | 11001 | 2872 | 876 | 1820 | 488 | 3029 | 725 | 118 | 428 | 608 | 138 | 110 | 0 | 88.85
11:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 0 | 159 |  | 0 | 200 | 0 | 24 | 0 | 40 | 232 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 16 | 33 | 0 | 82 | 35 | 80 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 30 | 89 | 38 | 17 | 2 | 0 | 0 | 0 | 305 | 210 | 192 | 8 | 85 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 7 | 20 | 148 | 68 | 0 | 20 | 2 | 33 | 42 | 50 | 47 | 110 | 0 | 50 | 84 | 0 | 0 | 0 | 20 | 10 | 325 | 16 | 11 | 0 | 238 | 305 | 82 | 114 | 0 | 130 | 20 | 90 | 100 | 135 | 80 | 59 | 88 | 105 | 4 | 178 | 54 | 92 | 0 | 0 | 100 | 388 | 92 | 27 | 17 | 108 | 0 | 35 | 24 | 98 | 55 | 0 |  | 876 | 0 | 165 | 0 | 16 | 202 | 0 | 0 | 17 | 10 | 8 | 0 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 176 | 15 | 0 | 0 | 0 | 0 | 208 | 0 | 80 | 164 | 0 | 330 | 92 | 36 | 94 | 105 | 69 | 0 | 7 | 113 | 580 | 175 | 0 | 0 | 4 | 91 | 34 | 0 | 0 |  | 7042 | 3882 | 10924 | 2829 | 876 | 1692 | 503 | 3002 | 756 | 117 | 425 | 605 | 148 | 179 | 0 | 88.85
12:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 0 | 141 |  | 0 | 190 | 0 | 30 | 0 | 40 | 221 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 26 | 33 | 25 | 41 | 0 | 84 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 76 | 30 | 89 | 38 | 17 | 8 | 0 | 0 | 0 | 300 | 210 | 184 | 8 | 71 | 10 | 5 | 0 | 51 | 0 | 48 | 0 | 19 | 8 | 0 | 20 | 144 | 52 | 0 | 20 | 1 | 33 | 42 | 53 | 47 | 110 | 0 | 35 | 81 | 0 | 0 | 0 | 20 | 10 | 310 | 16 | 11 | 0 | 225 | 302 | 85 | 111 | 0 | 123 | 15 | 90 | 100 | 138 | 103 | 59 | 88 | 105 | 6 | 178 | 54 | 92 | 0 | 0 | 100 | 385 | 91 | 35 | 17 | 108 | 0 | 35 | 27 | 93 | 50 | 0 |  | 876 | 0 | 165 | 0 | 16 | 200 | 0 | 0 | 17 | 10 | 8 | 0 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 87 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 176 | 15 | 0 | 0 | 0 | 0 | 208 | 0 | 97 | 157 | 0 | 370 | 92 | 81 | 94 | 105 | 69 | 0 | 7 | 113 | 590 | 220 | 0 | 0 | 3 | 36 | 34 | 0 | 0 |  | 6940 | 3973 | 10913 | 2782 | 876 | 1746 | 565 | 2968 | 766 | 119 | 423 | 602 | 144 | 130 | 0 | 88.86
13:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 0 | 121 |  | 0 | 160 | 0 | 33 | 0 | 40 | 211 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 29 | 35 | 35 | 19 | 25 | 18 | 33 | 26 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 75 | 30 | 90 | 38 | 17 | 4 | 0 | 0 | 0 | 270 | 210 | 195 | 8 | 70 | 10 | 5 | 0 | 51 | 0 | 48 | 0 | 19 | 8 | 0 | 20 | 140 | 80 | 0 | 20 | 1 | 33 | 42 | 50 | 46 | 110 | 0 | 35 | 86 | 0 | 0 | 0 | 20 | 10 | 300 | 8 | 11 | 0 | 230 | 303 | 25 | 111 | 0 | 114 | 8 | 90 | 100 | 138 | 305 | 59 | 88 | 105 | 3 | 178 | 54 | 93 | 0 | 0 | 100 | 393 | 78 | 33 | 115 | 108 | 0 | 35 | 35 | 97 | 47 | 0 |  | 876 | 0 | 165 | 0 | 16 | 201 | 0 | 0 | 14 | 10 | 8 | 0 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 86 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 200 | 15 | 0 | 0 | 0 | 0 | 212 | 0 | 97 | 160 | 0 | 375 | 79 | 40 | 94 | 105 | 69 | 0 | 7 | 113 | 610 | 218 | 0 | 0 | 5 | 53 | 34 | 0 | 0 |  | 7124 | 3990 | 11114 | 2978 | 876 | 1687 | 465 | 3071 | 810 | 125 | 428 | 601 | 140 | 145 | 0 | 88.86
14:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 115 |  | 0 | 160 | 0 | 32 | 0 | 40 | 188 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 53 | 55 | 22 | 25 | 24 | 33 | 26 | 41 | 0 | 90 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 75 | 30 | 90 | 38 | 17 | 4 | 0 | 0 | 0 | 270 | 240 | 204 | 8 | 65 | 10 | 5 | 0 | 51 | 0 | 48 | 0 | 19 | 8 | 0 | 20 | 156 | 80 | 0 | 20 | 2 | 33 | 42 | 53 | 46 | 110 | 0 | 35 | 84 | 0 | 0 | 0 | 23 | 10 | 290 | 16 | 11 | 0 | 230 | 302 | 25 | 110 | 0 | 114 | 18 | 90 | 100 | 135 | 317 | 58 | 105 | 105 | 2 | 178 | 54 | 93 | 0 | 0 | 100 | 398 | 84 | 16 | 162 | 108 | 0 | 35 | 31 | 94 | 55 | 0 |  | 875 | 0 | 165 | 0 | 16 | 204 | 0 | 0 | 17 | 10 | 8 | 0 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 43 | 0 | 0 | 36 | 18 | 0 | 8 | 0 | 0 | 223 | 15 | 0 | 0 | 0 | 0 | 180 | 0 | 86 | 160 | 0 | 370 | 92 | 10 | 94 | 105 | 68 | 0 | 7 | 113 | 622 | 215 | 0 | 0 | 2 | 95 | 34 | 0 | 0 |  | 7290 | 4032 | 11322 | 3026 | 875 | 1665 | 423 | 3231 | 845 | 125 | 399 | 584 | 156 | 173 | 0 | 88.87
15:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 0 | 110 |  | 0 | 160 | 0 | 31 | 0 | 55 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 26 | 40 | 0 | 91 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 75 | 30 | 89 | 37 | 17 | 9 | 0 | 0 | 0 | 280 | 240 | 204 | 8 | 66 | 10 | 10 | 0 | 51 | 0 | 48 | 0 | 19 | 11 | 0 | 20 | 162 | 80 | 0 | 20 | 1 | 33 | 42 | 51 | 46 | 110 | 0 | 61 | 84 | 0 | 0 | 0 | 23 | 10 | 300 | 16 | 11 | 0 | 235 | 303 | 25 | 111 | 0 | 116 | 5 | 90 | 100 | 127 | 362 | 58 | 105 | 97 | 4 | 184 | 54 | 92 | 0 | 0 | 100 | 390 | 75 | 18 | 162 | 108 | 0 | 35 | 16 | 96 | 55 | 0 |  | 876 | 0 | 165 | 0 | 16 | 200 | 0 | 0 | 16 | 10 | 8 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 20 | 0 | 37 | 18 | 0 | 8 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 196 | 0 | 99 | 160 | 0 | 368 | 92 | 10 | 94 | 105 | 68 | 0 | 2 | 113 | 622 | 215 | 0 | 0 | 2 | 88 | 34 | 0 | 0 |  | 7360 | 4108 | 11468 | 3097 | 876 | 1677 | 437 | 3225 | 897 | 126 | 411 | 620 | 162 | 136 | 0 | 88.87
16:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 0 | 112 |  | 0 | 160 | 0 | 33 | 0 | 55 | 180 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 26 | 40 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 75 | 30 | 78 | 37 | 17 | 8 | 0 | 0 | 0 | 280 | 240 | 207 | 8 | 66 | 21 | 30 | 0 | 51 | 0 | 48 | 0 | 19 | 11 | 0 | 20 | 170 | 80 | 0 | 20 | 1 | 33 | 42 | 53 | 45 | 110 | 0 | 61 | 86 | 0 | 0 | 0 | 23 | 10 | 310 | 16 | 11 | 0 | 235 | 300 | 25 | 111 | 0 | 121 | 5 | 90 | 100 | 137 | 403 | 58 | 90 | 105 | 1 | 187 | 54 | 92 | 0 | 0 | 100 | 396 | 73 | 15 | 162 | 108 | 0 | 35 | 15 | 94 | 55 | 0 |  | 876 | 0 | 165 | 0 | 16 | 200 | 0 | 0 | 16 | 10 | 8 | 0 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 24 | 0 | 37 | 19 | 0 | 8 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 210 | 0 | 98 | 163 | 0 | 383 | 77 | 32 | 77 | 105 | 68 | 0 | 2 | 113 | 622 | 211 | 0 | 9 | 2 | 48 | 34 | 0 | 0 |  | 7452 | 4098 | 11550 | 3161 | 876 | 1725 | 455 | 3200 | 897 | 124 | 425 | 638 | 170 | 89 | 0 | 88.88
17:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 0 | 111 |  | 0 | 160 | 0 | 34 | 0 | 55 | 188 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 26 | 40 | 0 | 87 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 75 | 40 | 79 | 37 | 20 | 5 | 0 | 0 | 0 | 280 | 240 | 207 | 8 | 64 | 21 | 40 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 0 | 20 | 156 | 94 | 0 | 20 | 0 | 33 | 42 | 52 | 46 | 110 | 0 | 62 | 86 | 0 | 0 | 0 | 23 | 10 | 270 | 16 | 11 | 0 | 225 | 112 | 25 | 129 | 0 | 130 | 4 | 90 | 125 | 140 | 403 | 58 | 88 | 105 | 0 | 187 | 54 | 92 | 0 | 0 | 100 | 400 | 73 | 9 | 162 | 108 | 0 | 35 | 12 | 94 | 55 | 0 |  | 875 | 0 | 175 | 0 | 16 | 202 | 0 | 0 | 16 | 15 | 8 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 34 | 24 | 0 | 37 | 19 | 0 | 8 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 165 | 0 | 60 | 172 | 0 | 414 | 73 | 10 | 94 | 105 | 72 | 0 | 2 | 113 | 610 | 188 | 0 | 16 | 1 | 33 | 34 | 0 | 0 |  | 7288 | 4016 | 11304 | 3210 | 875 | 1695 | 207 | 3279 | 885 | 122 | 382 | 597 | 156 | 61 | 0 | 88.89
18:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 111 |  | 0 | 170 | 0 | 32 | 0 | 55 | 188 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 28 | 48 | 0 | 86 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 75 | 40 | 87 | 38 | 20 | 16 | 0 | 0 | 0 | 280 | 240 | 208 | 8 | 72 | 21 | 54 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 5 | 20 | 144 | 92 | 0 | 20 | 0 | 33 | 42 | 53 | 46 | 110 | 0 | 63 | 86 | 0 | 0 | 0 | 21 | 10 | 260 | 16 | 11 | 0 | 238 | 0 | 25 | 176 | 0 | 133 | 1 | 90 | 200 | 138 | 378 | 115 | 105 | 105 | 0 | 251 | 54 | 92 | 0 | 9 | 100 | 360 | 91 | 3 | 162 | 108 | 0 | 35 | 2 | 94 | 55 | 0 |  | 876 | 0 | 195 | 0 | 16 | 203 | 0 | 0 | 16 | 15 | 8 | 0 | 19 | 32 | 0 | 0 | 0 | 19 | 0 | 85 | 0 | 34 | 24 | 0 | 37 | 21 | 0 | 8 | 0 | 0 | 274 | 15 | 0 | 0 | 0 | 0 | 130 | 0 | 10 | 179 | 0 | 350 | 73 | 0 | 94 | 105 | 91 | 0 | 1 | 113 | 550 | 203 | 0 | 17 | 0 | 12 | 34 | 0 | 0 |  | 7471 | 3859 | 11330 | 3188 | 876 | 1675 | 35 | 3615 | 824 | 121 | 348 | 615 | 144 | 19 | 0 | 88.9
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 122 |  | 0 | 180 | 0 | 32 | 0 | 55 | 186 | 0 | 0 | 40 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 22 | 33 | 28 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 75 | 40 | 89 | 37 | 20 | 18 | 0 | 0 | 0 | 285 | 240 | 205 | 8 | 86 | 34 | 55 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 6 | 20 | 178 | 102 | 0 | 14 | 0 | 33 | 42 | 53 | 46 | 110 | 0 | 62 | 86 | 0 | 0 | 0 | 22 | 10 | 290 | 16 | 11 | 100 | 248 | 300 | 80 | 186 | 78 | 132 | 0 | 90 | 200 | 143 | 396 | 115 | 105 | 105 | 0 | 263 | 54 | 92 | 0 | 9 | 100 | 394 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 105 | 55 | 0 |  | 876 | 0 | 225 | 0 | 49 | 202 | 0 | 0 | 31 | 35 | 40 | 0 | 26 | 32 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 0 | 37 | 21 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 193 | 0 | 414 | 75 | 32 | 94 | 105 | 96 | 0 | 0 | 113 | 550 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8186 | 4224 | 12410 | 3323 | 876 | 1818 | 605 | 3790 | 825 | 121 | 367 | 657 | 178 | 0 | 0 | 88.93
19:30 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 128 |  | 0 | 180 | 0 | 32 | 0 | 55 | 186 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 28 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 35 | 75 | 40 | 91 | 38 | 0 | 20 | 0 | 0 | 0 | 295 | 240 | 207 | 8 | 77 | 34 | 55 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 6 | 20 | 158 | 103 | 0 | 14 | 0 | 33 | 42 | 53 | 47 | 110 | 0 | 63 | 86 | 0 | 0 | 0 | 22 | 10 | 290 | 16 | 11 | 150 | 255 | 301 | 84 | 186 | 81 | 132 | 0 | 90 | 200 | 145 | 404 | 115 | 105 | 105 | 0 | 263 | 54 | 92 | 0 | 9 | 100 | 399 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 115 | 55 | 0 |  | 858 | 0 | 240 | 0 | 49 | 203 | 0 | 0 | 38 | 50 | 40 | 0 | 29 | 32 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 0 | 38 | 21 | 0 | 11 | 0 | 0 | 274 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 96 | 206 | 0 | 414 | 75 | 146 | 94 | 105 | 96 | 0 | 0 | 113 | 590 | 220 | 0 | 17 | 0 | 0 | 112 | 0 | 0 |  | 8296 | 4560 | 12856 | 3354 | 858 | 1830 | 858 | 3836 | 864 | 121 | 429 | 759 | 158 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 132 |  | 0 | 180 | 0 | 31 | 0 | 55 | 186 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 35 | 75 | 40 | 89 | 39 | 0 | 24 | 0 | 0 | 0 | 300 | 300 | 207 | 8 | 77 | 34 | 55 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 0 | 20 | 162 | 104 | 0 | 14 | 0 | 33 | 42 | 53 | 47 | 110 | 0 | 63 | 86 | 0 | 0 | 0 | 22 | 10 | 280 | 16 | 11 | 150 | 260 | 100 | 85 | 200 | 81 | 132 | 0 | 90 | 200 | 143 | 404 | 115 | 105 | 105 | 0 | 263 | 54 | 92 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 109 | 55 | 0 |  | 857 | 0 | 250 | 0 | 48 | 204 | 0 | 0 | 32 | 71 | 40 | 0 | 30 | 66 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 0 | 38 | 21 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 213 | 0 | 65 | 210 | 0 | 380 | 75 | 161 | 94 | 105 | 96 | 0 | 0 | 113 | 610 | 211 | 0 | 29 | 0 | 0 | 112 | 0 | 0 |  | 8169 | 4599 | 12768 | 3431 | 857 | 1785 | 642 | 3890 | 885 | 121 | 432 | 776 | 162 | 0 | 0 | 88.92
21:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 146 |  | 0 | 180 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 15 | 34 | 62 | 40 | 92 | 44 | 20 | 27 | 0 | 0 | 0 | 310 | 340 | 204 | 8 | 76 | 34 | 55 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 7 | 20 | 152 | 103 | 0 | 14 | 0 | 33 | 42 | 53 | 47 | 110 | 0 | 61 | 86 | 0 | 0 | 0 | 22 | 10 | 300 | 16 | 11 | 155 | 260 | 300 | 80 | 200 | 81 | 132 | 0 | 90 | 200 | 143 | 405 | 115 | 105 | 105 | 0 | 263 | 54 | 92 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 857 | 0 | 265 | 0 | 48 | 203 | 0 | 0 | 32 | 65 | 40 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 75 | 210 | 0 | 414 | 75 | 180 | 94 | 105 | 96 | 0 | 0 | 113 | 622 | 222 | 0 | 72 | 0 | 0 | 112 | 0 | 0 |  | 8438 | 4790 | 13228 | 3518 | 857 | 1869 | 871 | 3969 | 897 | 121 | 432 | 756 | 152 | 0 | 0 | 88.93
22:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 148 |  | 0 | 180 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 48 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 34 | 75 | 40 | 91 | 44 | 21 | 28 | 0 | 0 | 0 | 330 | 345 | 207 | 10 | 77 | 33 | 55 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 8 | 20 | 164 | 102 | 0 | 17 | 0 | 33 | 42 | 53 | 47 | 110 | 0 | 63 | 86 | 0 | 0 | 0 | 22 | 10 | 290 | 16 | 11 | 195 | 260 | 202 | 30 | 200 | 80 | 132 | 0 | 90 | 200 | 143 | 404 | 115 | 105 | 105 | 0 | 262 | 54 | 91 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 858 | 0 | 280 | 0 | 48 | 205 | 0 | 0 | 32 | 61 | 8 | 0 | 33 | 110 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 215 | 0 | 97 | 211 | 0 | 414 | 82 | 170 | 94 | 105 | 89 | 0 | 0 | 113 | 622 | 220 | 0 | 81 | 0 | 0 | 112 | 0 | 0 |  | 8389 | 4795 | 13184 | 3567 | 858 | 1861 | 774 | 3954 | 897 | 122 | 435 | 767 | 164 | 0 | 0 | 88.94
23:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 163 |  | 0 | 190 | 0 | 31 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 30 | 48 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 75 | 40 | 91 | 44 | 21 | 30 | 0 | 0 | 0 | 330 | 345 | 207 | 44 | 80 | 33 | 54 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 8 | 20 | 168 | 110 | 0 | 17 | 0 | 33 | 42 | 53 | 48 | 110 | 0 | 62 | 86 | 0 | 35 | 0 | 22 | 10 | 290 | 8 | 11 | 150 | 260 | 160 | 0 | 200 | 81 | 132 | 0 | 90 | 200 | 140 | 405 | 115 | 105 | 105 | 0 | 262 | 37 | 89 | 0 | 9 | 100 | 393 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 113 | 55 | 0 |  | 857 | 0 | 285 | 0 | 48 | 205 | 0 | 0 | 26 | 61 | 8 | 15 | 32 | 110 | 0 | 0 | 0 | 24 | 3 | 85 | 0 | 34 | 24 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 25 | 0 | 0 | 216 | 0 | 98 | 212 | 0 | 414 | 92 | 167 | 94 | 105 | 95 | 0 | 0 | 113 | 622 | 222 | 0 | 81 | 0 | 0 | 111 | 0 | 0 |  | 8369 | 4852 | 13221 | 3645 | 857 | 1926 | 656 | 3964 | 897 | 124 | 436 | 764 | 168 | 0 | 0 | 88.94
24:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 166 |  | 0 | 190 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 32 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 60 | 44 | 91 | 44 | 21 | 30 | 0 | 0 | 0 | 320 | 350 | 209 | 73 | 80 | 33 | 50 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 8 | 20 | 156 | 153 | 0 | 17 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 63 | 86 | 0 | 75 | 0 | 22 | 9 | 300 | 16 | 11 | 110 | 260 | 206 | 0 | 115 | 80 | 132 | 0 | 90 | 200 | 135 | 405 | 59 | 105 | 105 | 0 | 262 | 37 | 85 | 0 | 9 | 90 | 393 | 92 | 0 | 162 | 108 | 0 | 17 | 0 | 116 | 55 | 0 |  | 857 | 0 | 285 | 0 | 16 | 205 | 0 | 0 | 26 | 41 | 8 | 65 | 32 | 64 | 0 | 0 | 0 | 24 | 4 | 85 | 0 | 34 | 24 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 137 | 0 | 0 | 216 | 0 | 98 | 211 | 0 | 414 | 92 | 168 | 94 | 105 | 96 | 0 | 0 | 113 | 622 | 223 | 0 | 42 | 0 | 0 | 34 | 0 | 0 |  | 8215 | 4795 | 13010 | 3897 | 857 | 1873 | 662 | 3594 | 897 | 124 | 436 | 730 | 156 | 0 | 0 | 88.96
KWH | 0 | 0 | 0 | 4347000 | 7165055 | 1907954 | 0 | 0 | 4046000 |  | 0 | 4008450 | 0 | 754560 | 0 | 1269634 | 5350221 | 0 | 0 | 976320 | 2192544 | 3056640 | 0 | 0 | 0 | 0 | 783360 | 1069968 | 1002053 | 414612 | 600000 | 598320 | 808000 | 706500 | 1070400 | 0 | 1996129 | 844000 | 2200000 | 0 | 611928 | 0 | 0 | 0 | 0 |  | 570480 | 213744 | 1883022 | 738840 | 2125440 | 901440 | 459216 | 411840 | 0 | 0 | 0 | 7450800 | 5894000 | 4744000 | 284363 | 1865740 | 545760 | 547680 | 0 | 1211424 | 0 | 1065560 | 0 | 458640 | 244080 | 339900 | 478020 | 3613440 | 2056320 | 0 | 408280 | 10600 | 777000 | 983520 | 1214400 | 1040184 | 2578091 | 0 | 1246464 | 1998720 | 0 | 470260 | 0 | 448160 | 236340 | 7282500 | 353904 | 252000 | 885888 | 5803525 | 5473125 | 1336611 | 3170400 | 412866 | 3182256 | 120285 | 2005440 | 3006240 | 3228363 | 5364000 | 1736400 | 2358000 | 2523309 | 30961 | 4885200 | 1332331 | 2405371 | 0 | 158760 | 2003520 | 9437800 | 2266560 | 203410 | 2142720 | 2606945 | 0 | 874440 | 217697 | 2179200 | 1315800 | 0 |  | 21194181 | 0 | 4808448 | 0 | 530880 | 4935360 | 0 | 0 | 554880 | 786176 | 267375 | 46000 | 621998 | 1546656 | 0 | 0 | 0 | 474192 | 159021 | 2052960 | 0 | 876976 | 291037 | 30874 | 497723 | 473040 | 0 | 235669 | 0 | 0 | 5300100 | 358000 | 0 | 175300 | 0 | 0 | 5119627 | 0 | 2105280 | 4494055 | 0 | 9484363 | 2051040 | 1431855 | 2259936 | 2549232 | 1851542 | 0 | 46549 | 2739168 | 15444000 | 5251527 | 0 | 831600 | 31740 | 649440 | 1402944 | 0 | 0 |  | 177851243 | 103960744 | 281811987 | 75778884 | 21194181 | 43047034 | 11645625 | 80189970 | 20744100 | 2840129 | 10412987 | 11034955 | 3613440 | 1310682 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 8024861.6 | 2537578.82 | 0 | 0 | 4369680 |  | 0 | 4369210.5 | 0 | 8435980.8 | 0 | 16822650.5 | 5992247.52 | 0 | 0 | 14273798.4 | 30849094.08 | 49548134.4 | 0 | 0 | 0 | 0 | 9964339.2 | 14444568 | 13437530.73 | 310959 | 450000 | 0 | 0 | 0 | 18207504 | 0 | 538954.83 | 227880 | 4158000 | 0 | 10005022.8 | 0 | 0 | 0 | 0 |  | 7444764 | 3565249.92 | 32049034.44 | 9981728.4 | 26950579.2 | 10429660.8 | 583204.32 | 1371427.2 | 0 | 0 | 0 | 8270388 | 6424460 | 5503040 | 366828.27 | 2276202.8 | 616708.8 | 816043.2 | 0 | 2023078.08 | 0 | 18402221.2 | 0 | 628336.8 | 183060 | 594825 | 358515 | 25944499.2 | 2241388.8 | 0 | 555260.8 | 168964 | 1064490 | 1298246.4 | 2113056 | 1799518.32 | 2964804.65 | 0 | 2418140.16 | 4557081.6 | 0 | 474962.6 | 0 | 667758.4 | 467953.2 | 7282500 | 265428 | 191520 | 18568212.48 | 79218116.25 | 114716700 | 27627749.37 | 42736992 | 8533940.22 | 44074245.6 | 1406131.65 | 20696140.8 | 41065238.4 | 42840377.01 | 4934880 | 21114624 | 34096680 | 31919858.85 | 0 | 57352248 | 14509084.59 | 25569093.73 | 0 | 2046416.4 | 23601465.6 | 8682776 | 29351952 | 2939274.5 | 27191116.8 | 29667034.1 | 0 | 11420186.4 | 2601479.15 | 32622624 | 17329086 | 0 |  | 63582543 | 0 | 5385461.76 | 0 | 5526460.8 | 81433440 | 0 | 0 | 9993388.8 | 14151168 | 3842178.75 | 51520 | 1206676.12 | 16858550.4 | 0 | 0 | 0 | 7952199.84 | 2781277.29 | 32108294.4 | 0 | 14522722.56 | 4921435.67 | 420812.62 | 8396587.01 | 979192.8 | 0 | 178401.433 | 0 | 0 | 28037529 | 15043160 | 0 | 203348 | 0 | 0 | 89388687.42 | 0 | 44168774.4 | 5213103.8 | 0 | 9389519.37 | 27565977.6 | 30025999.35 | 26735042.88 | 36836402.4 | 23514583.4 | 0 | 514366.45 | 33253499.52 | 139150440 | 5356557.54 | 0 | 6153840 | 358979.4 | 7617931.2 | 21507131.52 | 0 | 0 |  | 1235193676.64 | 824327184.503 | 2059520861.143 | 84010766.593 | 63582543 | 52638464.07 | 243641375.82 | 1036407003.89 | 167187969 | 766834.83 | 185865287.42 | 183868990.97 | 25944499.2 | 15607126.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 0 | 191 |  | 0 | 225 | 0 | 24 | 0 | 55 | 258 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 16 | 41 | 0 | 83 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 30 | 86 | 38 | 21 | 2 | 0 | 0 | 0 | 305 | 210 | 191 | 8 | 84 | 10 | 5 | 0 | 51 | 0 | 41 | 0 | 19 | 11 | 8 | 20 | 138 | 55 | 0 | 20 | 2 | 33 | 42 | 50 | 45 | 110 | 0 | 50 | 66 | 0 | 0 | 0 | 18 | 10 | 310 | 16 | 11 | 0 | 243 | 301 | 82 | 113 | 0 | 147 | 12 | 90 | 100 | 117 | 80 | 59 | 88 | 105 | 5 | 177 | 54 | 108 | 0 | 8 | 93 | 394 | 104 | 15 | 17 | 108 | 0 | 35 | 15 | 74 | 55 | 0 |  | 876 | 0 | 170 | 0 | 16 | 202 | 0 | 0 | 17 | 10 | 8 | 0 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 175 | 15 | 0 | 0 | 0 | 0 | 211 | 0 | 95 | 170 | 0 | 395 | 92 | 10 | 94 | 105 | 69 | 0 | 6 | 113 | 550 | 221 | 0 | 0 | 3 | 52 | 34 | 0 | 0 |  | 11001 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 146 | 0 | 0 | 180 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 48 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 62 | 40 | 92 | 44 | 20 | 27 | 0 | 0 | 0 | 310 | 340 | 204 | 8 | 76 | 34 | 55 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 7 | 20 | 152 | 103 | 0 | 14 | 0 | 33 | 42 | 53 | 47 | 110 | 0 | 61 | 86 | 0 | 0 | 0 | 22 | 10 | 300 | 16 | 11 | 155 | 260 | 300 | 80 | 200 | 81 | 132 | 0 | 90 | 200 | 143 | 405 | 115 | 105 | 105 | 0 | 263 | 54 | 92 | 0 | 9 | 100 | 400 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 857 | 0 | 265 | 0 | 48 | 203 | 0 | 0 | 32 | 65 | 40 | 0 | 31 | 110 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 34 | 24 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 0 | 0 | 0 | 214 | 0 | 75 | 210 | 0 | 414 | 75 | 180 | 94 | 105 | 96 | 0 | 0 | 113 | 622 | 222 | 0 | 72 | 0 | 0 | 112 | 0 | 0 |  | 13228 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 32 | 0 | 55 | 250 | 0 | 0 | 40 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 50 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 36 | 85 | 55 | 91 | 44 | 21 | 20 | 0 | 0 | 0 | 310 | 320 | 170 | 8 | 85 | 36 | 55 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 165 | 100 | 0 | 20 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 60 | 86 | 0 | 140 | 0 | 6 | 10 | 341 | 16 | 11 | 200 | 275 | 300 | 0 | 200 | 80 | 149 | 0 | 76 | 200 | 147 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 115 | 55 |  |  | 886 | 0 | 200 | 0 | 49 | 220 | 0 | 0 | 35 | 70 | 40 | 85 | 36 | 110 | 0 | 0 | 0 | 34 | 30 | 90 | 0 | 43 | 30 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 10 | 140 | 0 | 0 | 220 | 0 | 100 | 200 | 0 | 414 | 93 | 170 | 95 | 105 | 91 | 0 | 0 | 113 | 622 | 220 |  | 90 |  |  | 110
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 32 | 0 | 55 | 250 | 0 | 0 | 40 | 94 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 25 | 40 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 60 | 55 | 85 | 44 | 20 | 10 | 0 | 0 | 0 | 320 | 330 | 180 | 8 | 85 | 36 | 55 | 0 | 51 | 0 | 41 | 0 | 22 | 11 | 33 | 20 | 143 | 70 | 0 | 20 | 1.6 | 33 | 42 | 5 | 5 | 110 | 0 | 60 | 86 | 0 | 140 | 0 | 6 | 10 | 310 | 16 | 11 | 100 | 260 | 300 | 0 | 115 | 50 | 114 | 20 | 76 | 68 | 145 | 400 | 59 | 105 | 105 | 5 | 200 | 54 | 110 | 0 | 9 | 100 | 400 | 104 | 50 | 162 | 108 | 0 | 35 | 30 | 115 | 55 |  |  | 881 | 0 | 240 | 0 | 16 | 220 | 0 | 0 | 35 | 0 | 8 | 20 | 20 | 32 | 0 | 0 | 0 | 24 | 16 | 90 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 140 | 0 | 0 | 220 | 0 | 90 | 200 | 0 | 414 | 93 | 170 | 94 | 105 | 70 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 34
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 197 | 0 | 0 | 210 | 0 | 31 | 0 | 55 | 252 | 0 | 0 | 40 | 85 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 24 | 0 | 86 | 35 | 100 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 44 | 11 | 44 | 19 | 7 | 0 | 0 | 0 | 330 | 345 | 212 | 92 | 85 | 36 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 16 | 20 | 132 | 88 | 0 | 17 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 40 | 86 | 0 | 140 | 0 | 6 | 10 | 270 | 16 | 11 | 0 | 260 | 0 | 0 | 115 | 0 | 125 | 3 | 76 | 68 | 125 | 398 | 59 | 105 | 17 | 2 | 15 | 54 | 110 | 0 | 9 | 100 | 360 | 104 | 4 | 72 | 108 | 0 | 17 | 5 | 115 | 55 | 130 | 0 | 910 | 0 | 260 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 222 | 0 | 0 | 148 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 370 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 460 | 223 | 0 | 17 | 1 | 10 | 52 | 0 | 0 | 0 |  |  |  |  | 113283537 |  | 0
113283537
| Minimum Generation |  | 10737 | 8:00
| Highest Generation |  | 13228 | 21:00
| Day Peak Generation |  | 11001 | 10:00
| Evening Peak Generation |  | 13228 | 21:00
| HVDC Max Flow |  | 893 | 4:00
| HVDC EvPeak Flow |  | 857 | 21:00
| Load factor L.F |  | 88.77%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-06
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11001 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 10793 | MW
Evening Peak Generation : |  | 13228 | MW Hour : | 21:00 | Available Max Generation : |  | 13878 | MW
E.P. Demand (at gen end) : |  | 13678 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13228 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 281.812 | System Load Factor : | 88.77% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 437 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-06
Actual : | 89.12 | Ft.(MSL) , | Rule curve : | 84.8 | Ft.( MSL )
Gas Consumed : | Total = | 971.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 136649230.663
: |  | Coal : | 167187969 | Oil : | 1649782658.1 | Total : | 1953619857.763
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 100 | 2400:00 | 4956.3212 |  |  | -162.6788 | -3.178%
Chittagong Area | 60 | 1440:00 | 1336.427 |  |  | 36.427 | 2.802%
Khulna Area | 60 | 1440:00 | 1749.7124 |  |  | -0.28758 | -0.01643%
Rajshahi Area | 60 | 1440:00 | 1567.8351 |  |  | 9.8351 | 0.6313%
Cumilla Area | 50 | 1200:00 | 1388.9781 |  |  | -11.0219 | -0.7873%
Mymensingh Area | 50 | 1200:00 | 1021.2642 |  |  | 21.2642 | 2.126%
Sylhet Area | 30 | 720:00 | 566.5708 |  |  | 4.5708 | 0.8133%
Barisal Area | 0 | 0:00 | 370.265 |  |  | -24.735 | -6.262%
Rangpur Area | 40 | 960:00 | 782.4073 |  |  | 50.4073 | 6.886%
Total | 450 |  | 13739.7811 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) SirShajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kishorganj 132/33 kV T-3 (A+B) transformers were under shut down from 08:30 to 17:36 for C/M.
b) Tongi-Kabirpur 132 kV Ckt-2 tripped at 08:58 showing Dist.Z2,Y,B at Tongi end and Dist.Z1,B,C at
Kabirpur end and was switched on at 09:18.
c) Rampura-Bashundhara 132 kV Ckt-2 was under shut down from 10:15 to 12:45 for testing purpose.
d) Chowmuhoni-HPPL 132 kV Ckt was under shut down from 10:30 to 15:46 for right of way.
e) Ishurdi-Ghorashal 230 kV Ckt-1 tripped at 10:55 showing Dist.Z1 at Ishurdi end and Dist.Z1,B at
Ghorashal end and was switched on at 11:05.
f) Munshiganj-Madanganj 132 kV Ckt-2 was under shut down from 11:37 to 14:38 for C/M.
g) Bibiyana-3 ST was synchronized at 11:54.
h) Sylhet 225 MW GT synchronized at 12:26 and was tripped at 12:40 and again GT was synchronized at 22:30.
i) Jamalpur 132/33 kV T-3 transformer was under shut down from 14:15 to 14:50 for C/M.
j) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 14;58 to 16:06 for C/M.
k) Matuail 132/33 kV Bus-2 was under shut down from 10:35 to 15:17 for C/M.
l) Cox'sbazar 132/33 kV T-2 & T-3 transformers tripped at 15:46 from 33 kV sides showing O/C relay due to | [5 empty] | About 40 MW power interruption occurred under
Kolatoli PDB feeder fault and was switched on at 15:59. | [5 empty] | Cox'sbazar S/S area from 15:46 to 15:59.
m) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 16:37 showing Dist.Z1,3-φ at Dohazari end.
n) Amnura 132/33 kV T-1 transformer was switched on at 20:40 from 132 kV side.
o) Sirajganj unit-1 GT was synchronized at 22:22.
p) Bhola 225 GT-1 was synchronized at 22:19.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7165055 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 85 | 1907954 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 146 | 4046000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4008450 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 32 | 754560 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1269634
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 414612
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 976320 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 187 | 5350221 | Gas shoratge
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2192544 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 783360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 3056640 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1069968
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1002053
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1198320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 808000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 706500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1070400 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 5803525 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 5473125
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 1336611 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 81 | 412866 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3182256
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2358000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2266560 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2142720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 217697
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1315800
| Dhaka area Total |  |  |  | 5847 | 3047 | 66636751
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2200000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 611928
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 120285
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 901440 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 121 | 2840129 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2523309
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 213744 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 62 | 1883022
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 40 | 738840 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2005440 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 459216
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 411840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 2125440 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30961
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 263 | 4885200 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1332331
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2405371 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2003520
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2606945 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1377 | 30298961
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4744000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7450800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 340 | 5894000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 545760 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 547680
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 284363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1211424
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 3228363 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 1065560 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 76 | 1865740 | Gas shortage
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3006240
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 458640
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3613440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 7 | 339900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 478020 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 155 | 885888
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 158760 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 874440 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 2179200
| Cumilla Area Total |  |  |  | 2885 | 1971 | 39076298
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2056320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 408280
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 3170400
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1736400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 203410
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 15 | 570480
| Mymensingh Area Total |  |  |  | 614 | 447 | 8155890
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 33 | 777000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 983520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2578091 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1214400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1040184 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 252000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1246464
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1998720
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 470260 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 22 | 448160 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 353904
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7282500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 405 | 5364000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 236340
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9437800
| Sylhet Area Total |  |  |  | 2477 | 1596 | 33683343
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 857 | 21194181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 530880 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 554880 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 203 | 4935360 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 786176 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 4808448 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 267375
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 75 | 2105280 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 2051040 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2549232
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 649440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1765 | 40432292
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1546656
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 621998 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 46000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15444000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5251527
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 831600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1057 | 23741781
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 474192 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 159021 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 876976 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 291037 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 175300 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 214 | 5119627
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4494055 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9484363
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 497723 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 473040
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235669
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 30874 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 2052960 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 180 | 1431855 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2259936 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2739168
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31740
| Rajshahi Area Total |  |  |  | 2129 | 1470 | 30827536
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 275 | 5300100
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 358000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 96 | 1851542 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46549
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 112 | 1402944
| Rangpur Area Total |  |  |  | 720 | 498 | 8959135
| Total |  |  |  | 21396 | 13228 | 281811987
| Eastern Grid Total |  |  |  | 14205 | 8438 | 177851243
| Western Grid Total |  |  |  | 7191 | 4790 | 103960744
| National Grid Total |  |  |  | 21396 | 13228 | 281811987
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-05
(a) ENTIRE EASTERN GRID : |  | 8807.34 | MW | (b) ENTIRE WESTERN GRID : |  | 3720.32 | MW
i) Dhaka area |  | 4791.34 | MW | i) Khulna area |  | 1448.8 | MW
ii) Chittagong area |  | 1388 | MW | ii) Rajshahi area |  | 1117.6 | MW
iii) Comilla area |  | 1180 | MW | iii) Barisal area |  | 401.92 | MW
iv) Mymensingh area |  | 1009 | MW | iv) Rangpur area |  | 752 | MW
v) Sylhet area |  | 439 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12527.66 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 10 | 12:00 | Chowmuhani | 182 | 22:00 | Kaptai | 4 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 68 | 07:00 | Chuadanga | 92 | 07:00 | Kazla | 94 | 11:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 35 | 22:00 | Coxsbazar | 107 | 21:00 | Keranigonj | 44 | 19:30 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 96 | 13:00 | Cumilla(N) | 160 | 22:00 | Khagrachori | 24 | 00:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 88 | 19:00 | Cumilla(S) | 178 | 19:00 | Khulna | 103 | 17:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 50 | 22:00 | Daudkandi | 140 | 19:30 | Khulshi | 190 | 19:30 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 44 | 23:00 | Dhaka | 44 | 11:00 | Kishoreganj | 124 | 18:30 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 117 | 08:00 | Dhamrai | 110 | 08:00 | Kodda | 277 | 08:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 87 | 06:00 | Dhanmondi | 143 | 11:00 | Kulaura | 40 | 22:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 133 | 19:00 | Dohazari | 104 | 22:00 | Kurigram | 59 | 23:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 54 | 10:00 | Faridpur | 118 | 23:00 | Kushtia | 120 | 07:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 11:00 | Fatullah | 70 | 00:00 | Lalbag | 86 | 10:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 54 | 19:30 | Fenchuganj | 37 | 01:00 | Lalmonirhat | 43 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 22:00 | Feni | 114 | 19:00 | Madanganj | 94 | 23:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 116 | 00:00 | GPH | 89 | 21:00 | Madaripur | 107 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 68 | 19:30 | Ghorashal | 71 | 19:30 | Madartek | 85 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 152 | 16:00 | Goalpara | 29 | 21:00 | Madunaghat | 59 | 21:00 | Rajshahi | 132 | 22:00
Baroirhat | 58 | 21:00 | Gollamari | 66 | 18:00 | Magura | 46 | 03:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 155 | 21:00 | Gopalganj | 106.8 | 21:00 | Mahasthangarh | 72 | 19:30 | Ramganj | 88 | 19:00
BashundharaCement | 6 | 00:00 | Gulshan | 124 | 14:00 | Manikganj | 100 | 20:00 | Rampur | 16 | 00:00
Beanibazar | 46 | 09:00 | Halishahar | 87.5 | 18:00 | Maniknagar | 78 | 11:00 | Rangamati | 14 | 19:00
Benapole | 48 | 21:00 | HaripurSBU | 149 | 11:00 | Matarbari | 39 | 22:00 | Rangpur | 105 | 08:00
Bhaluka | 130 | 03:00 | Hasnabad | 116 | 19:00 | Matuail | 58 | 11:00 | Ruppur | 5 | 09:00
Bhandaria | 62 | 23:00 | Hathazari | 93 | 19:30 | Millgate | 54 | 09:00 | SSM | 3 | 05:00
Bhangura | 28 | 04:00 | Ishurdi | 71 | 03:00 | Mirpur | 130 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 58 | 00:00 | Jaldhaka | 49 | 21:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 246 | 21:00 | Jamalpur | 164 | 21:00 | Mithapukur | 28 | 05:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 52 | 04:00 | Jashore | 116 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 153 | 19:30 | Jhenaidah | 106 | 22:00 | Mogbazar | 125 | 10:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 01:00 | Joydebpur | 199 | 19:30 | Mongla | 32 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 144 | 19:30 | Joypurhat | 54 | 22:00 | Motijheel | 38 | 12:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 143 | 21:00 | Juldah | 25 | 18:00 | Munshiganj | 107 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 72 | 19:30 | KSRM | 35.25 | 06:00 | Mymensingh | 222 | 20:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 19:30 | Kabirpur | 260 | 08:00 | Naogaon | 116 | 23:00 | Shikalbaha | 28 | 19:00
Chapai | 68 | 07:00 | Kachua | 68 | 23:00 | Narail | 43 | 23:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 22 | 00:00 | Kallyanpur | 108 | 21:00 | Narinda | 64 | 19:30 | Shitalakhya | 114 | 12:00
Chauddagram | 49 | 19:00 | Kalurghat | 23 | 00:00 | Narshingdi | 155 | 07:00 | Sholosohor | N/A | N/A
Chhatak | 24 | 22:00 | Kamrangirchar | 61 | 11:00 | Natore | 142 | 03:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 392 | 19:30 | 379 | 10:00 | Kaliakoir | 390 | 03:00 | 338 | 20:00
| Bibiana | 408 | 17:00 | 401 | 09:00 | Payra | 417 | 08:00 | 412 | 13:00
| BIPTC | 399 | 06:00 | 392 | 21:00
| Gopalganj_I | 412 | 18:00 | 403 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 223 | 19:30 | 213 | 10:00 | Hasnabad | 224 | 19:30 | 214 | 09:00
| AKSML | 237 | 00:00 | 222 | 21:00 | Hathazari | 240 | 00:00 | 230 | 23:00
| Aminbazar | 224 | 19:00 | 215 | 10:00 | Ishurdi | 235 | 20:00 | 227 | 11:00
| Ashuganj | 235 | 00:00 | 230 | 09:00 | Jhenaidah | 232 | 20:00 | 225 | 05:00
| Baghabari | 233 | 20:00 | 227 | 09:00 | Kaliakoir | 225 | 03:00 | 217 | 09:00
| Barapukuria | 227 | 00:00 | 216 | 04:00 | Keranigonj | 222 | 07:00 | 213 | 10:00
| Barishal | 243 | 08:00 | 238 | 14:00 | Khulna(S) | 242 | 19:30 | 233 | 06:00
| Bheramara | 232 | 20:00 | 27 | 12:00 | Maniknagar | 223 | 19:30 | 216 | 10:00
| Bhulta | 226 | 19:30 | 218 | 10:00 | Meghnaghat | 226 | 19:30 | 221 | 13:00
| Bibiana | 238 | 13:00 | 233 | 09:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 20:00 | 226 | 04:00 | Rajshahi | 232 | 00:00 | 226 | 05:00
| Bogura | 231 | 20:00 | 223 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 18:00 | 241 | 01:00 | Rampura | 224 | 20:00 | 215 | 10:00
| BSRM | 235 | 00:00 | 226 | 21:00 | Shikalbaha | 237 | 01:00 | 231 | 22:00
| Cumilla(N) | 227 | 00:00 | 222 | 10:00 | Shyampur | 222 | 03:00 | 214 | 10:00
| Fenchuganj | 242 | 07:00 | 237 | 00:00 | Siddhirganj | 225 | 04:00 | 218 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 239 | 18:30 | 227 | 04:00
| GPH | 238 | 00:00 | 228 | 21:00 | Tongi | 224 | 04:00 | 216 | 09:00
| Haripur | 223 | 20:00 | 216 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 20:00 | 125 | 09:00 | Lalbag | 135 | 20:00 | 128 | 10:00
| Agargaon | 132 | 03:00 | 126 | 10:00 | Lalmonirhat | 130 | 00:00 | 121 | 04:00
| Agrabad | 139 | 00:00 | 132 | 19:00 | Madanganj | 131 | 19:00 | 125 | 09:00
| AKS | 138 | 00:00 | 132 | 18:30 | Madaripur | 136 | 08:00 | 131 | 21:00
| Aminbazar | 130 | 06:00 | 124 | 10:00 | Madartek | 133 | 20:00 | 124 | 10:00
| Amnura | 136 | 01:00 | 131 | 05:00 | Madunaghat | 140 | 00:00 | 134 | 21:00
| Ashuganj | 136 | 17:00 | 133 | 01:00 | Magura | 136 | 08:00 | 131 | 06:00
| Bagerhat | 136 | 00:00 | 133 | 13:00 | Mahasthangarh | 134 | 00:00 | 127 | 04:00
| Bakulia | 140 | 00:00 | 14 | 00:00 | Manikganj | 135 | 03:00 | 131 | 10:00
| Banani | 132 | 03:00 | 125 | 10:00 | Maniknagar | 131 | 04:00 | 125 | 10:00
| Bangabhaban | 131 | 04:00 | 125 | 11:00 | Matarbari | 136 | 09:00 | 105 | 21:00
| Barapukuria | 136 | 00:00 | 127 | 04:00 | Matuail | 131 | 20:00 | 125 | 09:00
| Barguna | 137 | 07:00 | 132 | 14:00 | Millgate | 132 | 03:00 | 126 | 10:00
| Barishal | 136 | 02:00 | 132 | 19:00 | Mirpur | 130 | 19:00 | 122 | 10:00
| Barishal-230 | 138 | 08:00 | 133 | 23:00 | Mithapukur | 133 | 00:00 | 123 | 05:00
| Baroaulia | 142 | 00:00 | 134 | 19:00 | Modern | 141 | 00:00 | 135 | 16:00
| Baroirhat | 132 | 00:00 | 125 | 19:00 | Mogbazar | 133 | 20:00 | 127 | 09:00
| Bashundhara | 132 | 03:00 | 125 | 08:00 | Mongla | 136 | 08:00 | 131 | 06:00
| BashundharaCement | 131 | 19:00 | 125 | 09:00 | Motijheel | 131 | 04:00 | 125 | 11:00
| Beanibazar | 131 | 03:00 | 128 | 01:00 | Munshiganj | 132 | 19:30 | 126 | 10:00
| Benapole | 135 | 08:00 | 130 | 23:00 | Mymensingh | 133 | 03:00 | 123 | 10:00
| Bhaluka | 131 | 04:00 | 120 | 21:00 | Naogaon | 132 | 00:00 | 120 | 06:00
| Bhandaria | 136 | 09:00 | 126 | 19:30 | Narail | 134 | 00:00 | 130 | 23:00
| Bhangura | 138 | 20:00 | 134 | 04:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 00:00 | 133 | 04:00 | Narshingdi | 128 | 18:00 | 120 | 08:00
| Bheramara(GK) | 137 | 00:00 | 134 | 05:00 | Natore | 134 | 00:00 | 128 | 04:00
| Bhulta | 124 | 12:00 | 119 | 08:00 | Nawabganj | 136 | 19:30 | 127 | 10:00
| Bog-Sherpur | 135 | 00:00 | 129 | 04:00 | Netrakona | 132 | 04:00 | 121 | 09:00
| Bogura | 137 | 00:00 | 130 | 04:00 | New | 133 | 20:00 | 125 | 08:00
| Bogura-230 | 136 | 00:00 | 130 | 05:00 | Niamatpur | 132 | 20:00 | 116 | 06:00
| Brahmanbaria | 132 | 14:00 | 128 | 00:00 | Noapara | 139 | 19:30 | 134 | 06:00
| Cantonment | 131 | 03:00 | 124 | 10:00 | Pabna | 135 | 19:00 | 131 | 06:00
| Chandpur | 139 | 17:00 | 133 | 21:00 | Palashbari | 131 | 01:00 | 123 | 00:00
| Chandraghona | 139 | 00:00 | 134 | 19:00 | Panchagarh | 133 | 19:00 | 113 | 04:00
| Chapai | 134 | 00:00 | 129 | 05:00 | Patuakhali | 137 | 00:00 | 132 | 22:00
| Charsaidpur | 132 | 19:30 | 127 | 09:00 | Payra | 138 | 08:00 | 134 | 00:00
| Chauddagram | 132 | 08:00 | 126 | 19:00 | PHP | 132 | 00:00 | 125 | 19:00
| Chhatak | 131 | 00:00 | 124 | 01:00 | Purbachal | 133 | 05:00 | 125 | 09:00
| Chowmuhani | 129 | 17:00 | 122 | 19:00 | Purbasadipur | 134 | 19:00 | 116 | 04:00
| Chuadanga | 131 | 01:00 | 125 | 07:00 | Rahim | 131 | 20:00 | 126 | 09:00
| Coxsbazar | 134 | 00:00 | 95 | 21:00 | Rajbari | 135 | 08:00 | 130 | 02:00
| Cumilla(N) | 134 | 00:00 | 129 | 23:00 | Rajendrapur | 137 | 03:00 | 131 | 09:00
| Cumilla(S) | 134 | 17:00 | 124 | 16:00 | Rajshahi | 133 | 00:00 | 128 | 04:00
| Daudkandi | 133 | 00:00 | 127 | 10:00 | Rajshahi-230 | 134 | 20:00 | 129 | 05:00
| Dhaka | 133 | 20:00 | 125 | 09:00 | Ramganj | 134 | 17:00 | 125 | 19:00
| Dhamrai | 131 | 04:00 | 124 | 10:00 | Rampur | 141 | 00:00 | 132 | 19:00
| Dhanmondi | 136 | 11:00 | 124 | 10:00 | Rampura | 132 | 20:00 | 124 | 10:00
| Dohazari | 140 | 00:00 | 127 | 21:00 | Rangamati | 140 | 00:00 | 134 | 19:00
| Faridpur | 135 | 08:00 | 130 | 02:00 | Rangpur | 132 | 00:00 | 123 | 23:00
| Fatullah | 133 | 04:00 | 127 | 08:00 | Ruppur | 136 | 08:00 | 132 | 04:00
| Fenchuganj | 136 | 06:00 | 133 | 01:00 | Saidpur | 135 | 09:00 | 122 | 04:00
| Feni | 133 | 00:00 | 126 | 23:00 | Satkhira | 134 | 01:00 | 127 | 07:00
| Ghorashal | 137 | 01:00 | 135 | 15:00 | Satmasjid | 132 | 03:00 | 125 | 10:00
| Goalpara | 138 | 01:00 | 132 | 13:00 | Savar | 132 | 04:00 | 123 | 09:00
| Gollamari | 137 | 19:30 | 133 | 04:00 | Shahjadpur | 139 | 05:00 | 135 | 10:00
| Gopalganj | 138 | 18:00 | 135 | 06:00 | Shahjibazar | 136 | 18:00 | 131 | 01:00
| Gopalganj_I | 138 | 18:00 | 134 | 01:00 | Shahmirpur | 141 | 00:00 | 135 | 16:00
| Gulshan | 132 | 19:30 | 124 | 09:00 | Shariatpur | 134 | 08:00 | 129 | 23:00
| Halishahar | 138 | 05:00 | -140 | 00:00 | Sherpur | 136 | 19:30 | 123 | 21:00
| Haripur | 131 | 20:00 | 126 | 09:00 | Shikalbaha | 142 | 00:00 | 129 | 11:00
| HaripurSBU | 131 | 19:30 | 126 | 10:00 | Shikalbaha-230 | 140 | 01:00 | 134 | 21:00
| Hasnabad | 135 | 03:00 | 128 | 09:00 | Shitalakhya | 135 | 04:00 | 127 | 10:00
| Hathazari | 141 | 00:00 | 135 | 23:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 137 | 20:00 | 133 | 04:00 | Shyampur | 132 | 19:30 | 125 | 10:00
| Jaldhaka | 131 | 00:00 | 118 | 04:00 | Shyampur-230 | 132 | 03:00 | 127 | 10:00
| Jamalpur | 139 | 19:30 | 126 | 21:00 | Siddhirganj | 131 | 19:30 | 125 | 10:00
| Jashore | 135 | 01:00 | 131 | 23:00 | Sirajganj | 136 | 00:00 | 129 | 06:00
| Jhenaidah | 137 | 20:00 | 131 | 06:00 | Sonargaon | 131 | 07:00 | 31 | 19:00
| Jhenaidah-230 | 137 | 01:00 | 133 | 06:00 | Sreemongol | 136 | 12:00 | 134 | 00:00
| Joydebpur | 141 | 20:00 | 135 | 12:00 | Srinagar | 137 | 06:00 | 128 | 10:00
| Joypurhat | 132 | 00:00 | 120 | 06:00 | SSM | 143 | 00:00 | 138 | 16:00
| Juldah | 140 | 04:00 | 135 | 18:30 | Sunamganj | 129 | 00:00 | 125 | 01:00
| Kabirpur | 139 | 06:00 | 124 | 08:00 | Sylhet | 133 | 03:00 | 128 | 01:00
| Kachua | 136 | 18:00 | 130 | 04:00 | Tangail | 137 | 02:00 | 130 | 10:00
| Kaliakoir | 166 | 16:00 | 37 | 16:00 | Thakurgaon | 133 | 00:00 | 113 | 04:00
| Kallyanpur | 131 | 20:00 | 12 | 06:00 | TK | 140 | 00:00 | 132 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 738 | 8215 | 4795 | 13010 |  |  |  | QF-LDC-11
0:30 | 677 | 7580 | 4565.5 | 12145.5 | Date: | 2022-07-05
1:00 | 616 | 6945 | 4336 | 11281
1:30 | 593.5 | 6961.5 | 4354 | 11315.5
2:00 | 571 | 6978 | 4372 | 11350
2:30 | 552.5 | 7095 | 4332.5 | 11427.5 | [5 empty] | Gen. at Eve. Peak | 13228 | 13228 MW (21:00 )
3:00 | 534 | 7212 | 4293 | 11505 | [6 empty] | 21:00
3:30 | 509 | 7199 | 4283 | 11482 | [5 empty] | Gen. at Day Peak | 11001 | 11001 MW (10:00 )
4:00 | 484 | 7186 | 4273 | 11459 | [6 empty] | 10:00
4:30 | 464 | 7215.5 | 4263.5 | 11479 | [5 empty] | Highest Generation | 13228
5:00 | 444 | 7245 | 4254 | 11499 | [6 empty] | 21:00
5:30 | 445 | 7162.5 | 4204.5 | 11367
6:00 | 446 | 7080 | 4155 | 11235
6:30 | 441.5 | 7079.5 | 4123.5 | 11203
7:00 | 437 | 7079 | 4092 | 11171
7:30 | 545.5 | 6914.5 | 4039.5 | 10954
8:00 | 654 | 6750 | 3987 | 10737
8:30 | 674 | 6861 | 3986 | 10847
9:00 | 694 | 6972 | 3985 | 10957
9:30 | 657.5 | 7026 | 3953 | 10979
10:00 | 621 | 7080 | 3921 | 11001
10:30 | 705 | 7061 | 3901.5 | 10962.5
11:00 | 789 | 7042 | 3882 | 10924
11:30 | 673 | 6991 | 3927.5 | 10918.5
12:00 | 557 | 6940 | 3973 | 10913
12:30 | 634.5 | 7032 | 3981.5 | 11013.5
13:00 | 712 | 7124 | 3990 | 11114
13:30 | 740 | 7207 | 4011 | 11218
14:00 | 768 | 7290 | 4032 | 11322
14:30 | 725 | 7325 | 4070 | 11395
15:00 | 682 | 7360 | 4108 | 11468
15:30 | 719 | 7406 | 4103 | 11509
16:00 | 756 | 7452 | 4098 | 11550
16:30 | 717 | 7370 | 4057 | 11427
17:00 | 678 | 7288 | 4016 | 11304
17:30 | 632 | 7379.5 | 3937.5 | 11317
18:00 | 586 | 7471 | 3859 | 11330
18:30 | 630 | 7828.5 | 4041.5 | 11870
19:00 | 674 | 8186 | 4224 | 12410
19:30 | 636 | 8296 | 4560 | 12856
20:00 | 676 | 8169 | 4599 | 12768 |  |  |  | Executive Engineer
20:30 | 723 | 8303.5 | 4694.5 | 12998 |  |  |  | Network Operation Division
21:00 | 770 | 8438 | 4790 | 13228
21:30 | 727 | 8413.5 | 4792.5 | 13206
22:00 | 684 | 8389 | 4795 | 13184 |  |  |  |  | Page 6 of 7
22:30 | 724 | 8379 | 4823.5 | 13202.5
23:00 | 764 | 8369 | 4852 | 13221
23:30 | 751 | 8292 | 4823.5 | 13115.5
24:00 | 738 | 8215 | 4795 | 13010
13228 MW (21:00 )
11001 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-05 |  | Energy |  | 281811987
[13 empty] | 2022-07-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3897 | 857 | 1873 | 662 | 3594 | 897 | 124 | 436 | 730 | 156 | 0 | 0
0:30 | 3371 | 856 | 1842.5 | 571 | 3399.5 | 847 | 124 | 434 | 754 | 160 | 0 | 0 | Date: | 2022-07-05
1:00 | 2845 | 855 | 1812 | 480 | 3205 | 797 | 124 | 432 | 778 | 164 | 0 | 0
1:30 | 2840.5 | 871 | 1832.5 | 479 | 3209.5 | 797 | 124 | 433 | 778.5 | 163 | 0 | 0 | [8 empty] | Total Energy | 281.812 | Total Energy Gen 281.812 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 281.812 MKWHr
2:00 | 2836 | 887 | 1853 | 478 | 3214 | 797 | 124 | 434 | 779 | 162 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2951 | 881 | 1866.5 | 480.5 | 3167.5 | 797 | 124 | 435 | 775.5 | 164 | 0 | 0 | [8 empty] | Energy Requirement | 281.812
3:00 | 3066 | 875 | 1880 | 483 | 3121 | 797 | 124 | 436 | 772 | 166 | 0 | 0
3:30 | 3085 | 884 | 1885 | 505.5 | 3105 | 797 | 102.5 | 436.5 | 740 | 157 | 0 | 0 | [6 empty] | Shortage
4:00 | 3104 | 893 | 1890 | 528 | 3089 | 797 | 81 | 437 | 708 | 148 | 0 | 0
4:30 | 3117.5 | 893 | 1897 | 530 | 3088.5 | 797 | 81 | 435.5 | 706 | 148 | 0 | 0
5:00 | 3131 | 893 | 1904 | 532 | 3088 | 797 | 81 | 434 | 704 | 148 | 0 | 0
5:30 | 3113 | 893 | 1903.5 | 454.5 | 3076.5 | 797 | 101.5 | 436 | 665 | 137 | 4.5 | 0
6:00 | 3095 | 893 | 1903 | 377 | 3065 | 797 | 122 | 438 | 626 | 126 | 9 | 0
6:30 | 3046 | 893 | 1919 | 411 | 3048 | 776 | 122 | 437 | 616.5 | 125 | 24.5 | 0 |  |  |  |  | Coal
7:00 | 2997 | 893 | 1935 | 445 | 3031 | 755 | 122 | 436 | 607 | 124 | 40 | 0
7:30 | 2968 | 893 | 1906 | 293.5 | 3034.5 | 740 | 116 | 436 | 607.5 | 123 | 51 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2939 | 893 | 1877 | 142 | 3038 | 725 | 110 | 436 | 608 | 122 | 62 | 0
8:30 | 2935.5 | 893 | 1883 | 242 | 3028 | 725 | 113.5 | 428 | 608.5 | 127 | 70.5 | 0
9:00 | 2932 | 893 | 1889 | 342 | 3018 | 725 | 117 | 420 | 609 | 132 | 79 | 0
9:30 | 2902 | 884.5 | 1854.5 | 415 | 3023.5 | 725 | 117.5 | 424 | 608.5 | 135 | 94.5 | 0
10:00 | 2872 | 876 | 1820 | 488 | 3029 | 725 | 118 | 428 | 608 | 138 | 110 | 0
10:30 | 2850.5 | 876 | 1756 | 495.5 | 3015.5 | 740.5 | 117.5 | 426.5 | 606.5 | 143 | 144.5 | 0
11:00 | 2829 | 876 | 1692 | 503 | 3002 | 756 | 117 | 425 | 605 | 148 | 179 | 0
11:30 | 2805.5 | 876 | 1719 | 534 | 2985 | 761 | 118 | 424 | 603.5 | 146 | 154.5 | 0
12:00 | 2782 | 876 | 1746 | 565 | 2968 | 766 | 119 | 423 | 602 | 144 | 130 | 0
12:30 | 2880 | 876 | 1716.5 | 515 | 3019.5 | 788 | 122 | 425.5 | 601.5 | 142 | 137.5 | 0
13:00 | 2978 | 876 | 1687 | 465 | 3071 | 810 | 125 | 428 | 601 | 140 | 145 | 0
13:30 | 2978 | 876 | 1687 | 465 | 3071 | 810 | 125 | 428 | 601 | 140 | 145 | 0
14:00 | 2978 | 876 | 1687 | 465 | 3071 | 810 | 125 | 428 | 601 | 140 | 145 | 0
14:30 | 3037.5 | 876 | 1682 | 451 | 3148 | 853.5 | 125.5 | 419.5 | 610.5 | 151 | 140.5 | 0
15:00 | 3097 | 876 | 1677 | 437 | 3225 | 897 | 126 | 411 | 620 | 162 | 136 | 0
15:30 | 3129 | 876 | 1701 | 446 | 3212.5 | 897 | 125 | 418 | 629 | 166 | 112.5 | 0
16:00 | 3161 | 876 | 1725 | 455 | 3200 | 897 | 124 | 425 | 638 | 170 | 89 | 0
16:30 | 3210 | 875.5 | 1710 | 331 | 3239.5 | 891 | 123 | 403.5 | 617.5 | 163 | 75 | 0
17:00 | 3210 | 875 | 1695 | 207 | 3279 | 885 | 122 | 382 | 597 | 156 | 61 | 0
17:30 | 3199 | 875.5 | 1685 | 121 | 3447 | 854.5 | 121.5 | 365 | 606 | 150 | 40 | 0
18:00 | 3188 | 876 | 1675 | 35 | 3615 | 824 | 121 | 348 | 615 | 144 | 19 | 0
18:30 | 3255.5 | 876 | 1746.5 | 320 | 3702.5 | 824.5 | 121 | 357.5 | 636 | 161 | 9.5 | 0
19:00 | 3323 | 876 | 1818 | 605 | 3790 | 825 | 121 | 367 | 657 | 178 | 0 | 0
19:30 | 3354 | 858 | 1830 | 858 | 3836 | 864 | 121 | 429 | 759 | 158 | 0 | 0
20:00 | 3431 | 857 | 1785 | 642 | 3890 | 885 | 121 | 432 | 776 | 162 | 0 | 0
20:30 | 3474.5 | 857 | 1827 | 756.5 | 3929.5 | 891 | 121 | 432 | 766 | 157 | 0 | 0
21:00 | 3518 | 857 | 1869 | 871 | 3969 | 897 | 121 | 432 | 756 | 152 | 0 | 450
21:30 | 3542.5 | 857.5 | 1865 | 822.5 | 3961.5 | 897 | 121.5 | 433.5 | 761.5 | 158 | 0 | 0
22:00 | 3567 | 858 | 1861 | 774 | 3954 | 897 | 122 | 435 | 767 | 164 | 0 | 0
22:30 | 3606 | 857.5 | 1893.5 | 715 | 3959 | 897 | 123 | 435.5 | 765.5 | 166 | 0 | 0
23:00 | 3645 | 857 | 1926 | 656 | 3964 | 897 | 124 | 436 | 764 | 168 | 0 | 0
23:30 | 3771 | 857 | 1899.5 | 659 | 3779 | 897 | 124 | 436 | 747 | 162 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.6° C
24:00 | 3897 | 857 | 1873 | 662 | 3594 | 897 | 124 | 436 | 730 | 156 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 281.812 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 281.812 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 89 | 89 | 89 | 46 | 46 | 87 | 87 | 75 | 82 | 83 | 82 | 84 | 90 | 90 | 91 | 89 | 87 | 86 |  | 86 | 86 | 86 | 86 | 87 | 89 | 89 | 1996129
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 611928
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 9 | 10 | 12 | 20 | 15 | 8 | 18 | 5 | 5 | 4 | 1 | [8 empty] | 120285
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 76 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 62 | 75 | 75 | 60 | 1883022
12 | Hathazari 100 MW peaking PP | [17 empty] | 34 |  | 34 | 35 | 35 | 34 | 34 | 34 | 34 | 213744
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 97 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2523309
| Daudkandi 200 MW PP (B.Trac) | 0 | [18 empty] | 100 | 150 | 150 | 155 | 195 | 150 | 110 | 885888
14 | Titas 50 MW Peaking PP | 41 | 41 | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 47 | 47 | 47 | 47 | 48 | 47 | 47 | 1065560
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 180 | 222 | 245 | 260 | 262 | 275 | 300 | 306 | 295 | 258 | 232 | 221 | 211 | 188 | 180 | 180 | 188 | 188 |  | 186 | 186 | 186 | 187 | 187 | 187 | 187 | 5350221
18 | Kodda 300 MW PP Unit-2 (Summit) | 243 | 245 | 243 | 244 | 244 | 244 | 243 | 243 | 245 | 243 | 238 | 225 | 230 | 230 | 235 | 235 | 225 | 238 |  | 248 | 255 | 260 | 260 | 260 | 260 | 260 | 5803525
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 10 | 44 | 73 | 284363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7165055
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 26 | 36 | 35 | 31 | 31 | 32 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 21 | 21 | 21 |  | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 545760
33 | Ashuganj 225 MW CCPP | 198 | 200 | 196 | 200 | 188 | 174 | 168 | 179 | 190 | 191 | 192 | 184 | 195 | 204 | 204 | 207 | 207 | 208 |  | 205 | 207 | 207 | 204 | 207 | 207 | 209 | 4744000
34 | Ashuganj 450 MW CCPP(South) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 300 | 340 | 345 | 345 | 350 | 5894000
| Ashuganj 450 MW CCPP(North) | 290 | 310 | 270 | 270 | 305 | 270 | 270 | 270 | 270 | 305 | 305 | 300 | 270 | 270 | 280 | 280 | 280 | 280 |  | 285 | 295 | 300 | 310 | 330 | 330 | 320 | 7450800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 30 | 40 | 54 |  | 55 | 55 | 55 | 55 | 55 | 54 | 50 | 547680
36 | Chandpur 150 MW CCPP | 85 | 86 | 84 | 85 | 85 | 84 | 85 | 85 | 84 | 84 | 85 | 71 | 70 | 65 | 66 | 66 | 64 | 72 |  | 86 | 77 | 77 | 76 | 77 | 80 | 80 | 1865740
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 190 | 205 | 210 | 210 | 210 | 210 | 225 | 225 | 225 | 225 | 200 | 190 | 160 | 160 | 160 | 160 | 160 | 170 |  | 180 | 180 | 180 | 180 | 180 | 190 | 190 | 4008450
41 | Haripur 360MW CCPP(HPL) | 183 | 187 | 193 | 213 | 223 | 241 | 242 | 265 | 242 | 191 | 159 | 141 | 121 | 115 | 110 | 112 | 111 | 111 |  | 122 | 128 | 132 | 146 | 148 | 163 | 166 | 4046000
42 | RPCL 210MW CCPP | 103 | 102 | 105 | 105 | 105 | 105 | 103 | 71 | 55 | 55 | 68 | 52 | 80 | 80 | 80 | 80 | 94 | 92 |  | 102 | 103 | 104 | 103 | 102 | 110 | 153 | 2056320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 8 | 10 | 6 | 15 | 27 | 35 | 33 | 16 | 18 | 15 | 9 | 3 |  | 0 | [6 empty] | 203410
44 | Fenchugonj CCPP Phase-1 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 777000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 983520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 35 | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 35 | 35 | 35 | 61 | 61 | 62 | 63 |  | 62 | 63 | 63 | 61 | 63 | 62 | 63 | 1246464
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 66 | 84 | 81 | 86 | 84 | 84 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1998720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP |  |  | 120 | 120 | 120 | 120 | 0 | [17 empty] | 35 | 75 | 470260
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 11 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 18 | 18 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 448160
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 236340
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 50 | 53 | 51 | 53 | 52 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 5 | 1214400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 353904
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 290 | 310 | 280 | 295 | 270 | 300 | 310 | 325 | 310 | 300 | 290 | 300 | 310 | 270 | 260 |  | 290 | 290 | 280 | 300 | 290 | 290 | 300 | 7282500
| Bibiyana South 400 MW | 390 | 392 | 400 | 400 | 400 | 400 | 400 | 400 | 401 | 394 | 388 | 385 | 393 | 398 | 390 | 396 | 400 | 360 |  | 394 | 399 | 400 | 400 | 400 | 393 | 393 | 9437800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1002053
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 14 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 15 | 23 | 24 | 24 | 570480
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 |  | 20 |  |  | 20 | 21 | 21 | 21 | 459216
61 | Narshingdi 22 MW PP (Doreen) | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 414612
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 408280
63 | Impoprt (Tripura) | 164 | 162 | 166 | 148 | 148 | 126 | 124 | 122 | 132 | 138 | 148 | 144 | 140 | 156 | 162 | 170 | 156 | 144 |  | 178 | 158 | 162 | 152 | 164 | 168 | 156 | 3613440
64 | Malancha, Ctg. EPZ (United) | 28 | 29 | 29 | 27 | 11 | 25 | 25 | 8 | 3 | 2 | 2 | 8 | 4 | 4 | 9 | 8 | 5 | 16 |  | 18 | 20 | 24 | 27 | 28 | 30 | 30 | 411840
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 458640
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244080
67 | Jangalia 33MW PP (Summit) | 21 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 8 | 7 | 0 | [5 empty] | 5 |  | 6 | 6 |  | 7 | 8 | 8 | 8 | 339900
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 0 | 26 | 26 | 26 | 26 | 18 | 24 | 26 | 26 | 26 | 27 |  | 22 | 27 | 27 | 27 | 27 | 28 | 28 | 598320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 808000
72 | Rupganj 33 MW PP(Summit) | 27 | 27 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 25 | 26 | 26 | 26 | 26 | 26 | 28 |  | 28 | 28 | 30 | 30 | 30 | 30 | 32 | 706500
73 | Ghorashal 108MW PP (Regent) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 77 | 77 | 83 | 83 | 80 | 80 | 83 | 84 | 86 |  | 86 | 86 | 85 | 85 | 82 | 85 | 85 | 1907954
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [6 empty] | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 158760
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 115 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2142720
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976320
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 45 | 49 | 49 | 49 | 41 | 41 | 41 | 33 | 41 | 41 | 41 | 40 | 40 | 40 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 1070400
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 132 | 115 | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 3056640
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 105 | 105 | 90 | 88 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2358000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 3 | 5 | 4 | 6 | 3 | 2 | 4 | 1 | 0 | [9 empty] | 30961
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 37 | 37 | 1332331
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 110 | 110 | 108 | 92 | 92 | 93 | 93 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 91 | 89 | 85 | 2405371
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 32 | 32 | 32 | 31 | 30 | 30 | 31 | 32 | 28 | 24 | 24 | 30 | 33 | 32 | 31 | 33 | 34 | 32 |  | 32 | 32 | 31 | 32 | 32 | 31 | 32 | 754560
| Meghnaghat 104 MW PP (OPCL) | 92 | 100 | 104 | 104 | 104 | 104 | 96 | 102 | 104 | 104 | 92 | 91 | 78 | 84 | 75 | 73 | 73 | 91 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2266560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 44 | 738840
92 | Fenchuganj 44MW (Energyprima) | 35 | 38 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 45 | 47 | 47 | 46 | 46 | 46 | 45 | 46 | 46 |  | 46 | 47 | 47 | 47 | 47 | 48 | 5 | 1040184
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1211424
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2192544
95 | Patenga 50MW PP (Baraka) | 33 | 38 | 17 | 23 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 38 |  | 37 | 38 | 39 | 44 | 44 | 44 | 44 | 901440
96 | Chattogram 108 MW PP (ECPV) | 91 | 82 | 91 | 91 | 84 | 86 | 89 | 91 | 91 | 86 | 89 | 89 | 90 | 90 | 89 | 78 | 79 | 87 |  | 89 | 91 | 89 | 92 | 91 | 91 | 91 | 2125440
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 41 | 55 | 55 | 55 | 55 | 55 | 40 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1269634
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1069968
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2578091
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 10600
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 29 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 783360
104 | Keranigonj 300 MW PP (APR) | 303 | 302 | 306 | 302 | 309 | 152 | 220 | 12 | 155 | 301 | 305 | 302 | 303 | 302 | 303 | 300 | 112 |  |  | 300 | 301 | 100 | 300 | 202 | 160 | 206 | 5473125
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 25 | 82 | 82 | 82 | 85 | 25 | 25 | 25 | 25 | 25 | 25 |  | 80 | 84 | 85 | 80 | 30 |  | 0 | 1336611
106 | Mymensingh 200 MW PP (United) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 117 | 116 | 113 | 114 | 111 | 111 | 110 | 111 | 111 | 129 | 176 |  | 186 | 186 | 200 | 200 | 200 | 200 | 115 | 3170400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 78 | 81 | 81 | 81 | 80 | 81 | 80 | 412866
114 | Kodda 149 MW PP Unit-1 (Summit) | 134 | 130 | 130 | 131 | 133 | 130 | 144 | 149 | 149 | 147 | 130 | 123 | 114 | 114 | 116 | 121 | 130 | 133 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3182256
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 76 | 90 | 90 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2005440
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 68 | 82 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3006240
117 | Ashuganj 150MW PP (Midland) | 138 | 123 | 125 | 132 | 132 | 138 | 137 | 123 | 113 | 117 | 135 | 138 | 138 | 135 | 127 | 137 | 140 | 138 |  | 143 | 145 | 143 | 143 | 143 | 140 | 135 | 3228363
118 | Bibiyana-III 400 MW CCPP | 80 | 15 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 103 | 305 | 317 | 362 | 403 | 403 | 378 |  | 396 | 404 | 404 | 405 | 404 | 405 | 405 | 5364000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 59 | 1736400
| Anwara 300 MW PP (United) | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 176 | 178 | 177 | 178 | 178 | 178 | 178 | 184 | 187 | 187 | 251 |  | 263 | 263 | 263 | 263 | 262 | 262 | 262 | 4885200
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 64 | 77 | 77 | 77 | 93 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 2003520
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2606945
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 874440
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 8 | 8 | 13 | 15 | 24 | 27 | 35 | 31 | 16 | 15 | 12 | 2 | [8 empty] | 217697
| Chandpur 115(Doreen) | 69 | 97 | 85 | 80 | 69 | 79 | 73 | 75 | 74 | 74 | 98 | 93 | 97 | 94 | 96 | 94 | 94 | 94 |  | 105 | 115 | 109 | 93 | 96 | 113 | 116 | 2179200
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 50 | 47 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1315800
120 | Eastern Zone Total | 6945 | 6978 | 7212 | 7186 | 7245 | 7080 | 7079 | 6750 | 6972 | 7080 | 7042 | 6940 | 7124 | 7290 | 7360 | 7452 | 7288 | 7471 |  | 8186 | 8296 | 8169 | 8438 | 8389 | 8369 | 8215 | 177851243
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 49 | 49 | 48 | 48 | 48 | 48 | 16 | 530880
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 32 | 32 | 31 | 31 | 31 | 30 | 30 | 30 | 17 | 17 | 17 | 14 | 17 | 16 | 16 | 16 | 16 |  | 31 | 38 | 32 | 32 | 32 | 26 | 26 | 554880
| Khulna 225 MW CCPP | 206 | 205 | 206 | 206 | 206 | 207 | 207 | 206 | 206 | 202 | 202 | 200 | 201 | 204 | 200 | 200 | 202 | 203 |  | 202 | 203 | 204 | 203 | 205 | 205 | 205 | 4935360
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 93 | 93 | 93 | 93 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 79 | 92 | 92 | 77 | 73 | 73 |  | 75 | 75 | 75 | 75 | 82 | 92 | 92 | 2051040
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 18 | 27 | 40 | 52 | 91 | 36 | 53 | 95 | 88 | 48 | 33 | 12 | [8 empty] | 649440
131
132 | United Payra Power Ltd. | 90 | 72 | 72 | 35 | 17 | 17 | 17 | 17 | 17 | 0 | [5 empty] | 9 | 16 | 17 |  | 17 | 17 | 29 | 72 | 81 | 81 | 42 | 831600
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 222 | 223 | 223 | 225 | 225 | 196 | 223 | 221 | 175 | 220 | 218 | 215 | 215 | 211 | 188 | 203 |  | 220 | 220 | 211 | 222 | 220 | 222 | 223 | 5251527
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 84 | 48 | 32 | 32 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 66 | 110 | 110 | 110 | 64 | 1546656
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [24 empty] | 15 | 65 | 46000
140 | Bhola 33 MW PP (Venture) | 34 | 31 | 31 | 31 | 31 | 27 | 27 | 19 | 17 | 17 | 20 | 20 | 21 | 23 | 24 | 23 | 18 | 19 |  | 26 | 29 | 30 | 31 | 33 | 32 | 32 | 621998
141 | Noapara 100 MW PP (Bangla Trac) | 97 | 96 | 96 | 96 | 95 | 95 | 95 | 95 | 95 | 95 | 80 | 97 | 97 | 86 | 99 | 98 | 60 | 10 |  | 15 | 96 | 65 | 75 | 97 | 98 | 98 | 2105280
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 267375
143 | Gopalganj 100 MW Peaking PP | 64 | 64 | 64 | 64 | 64 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 |  | 35 | 50 | 71 | 65 | 61 | 61 | 41 | 786176
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2549232
146 | Bheramara HVDC | 855 | 887 | 875 | 893 | 893 | 893 | 893 | 893 | 893 | 876 | 876 | 876 | 876 | 875 | 876 | 876 | 875 | 876 |  | 876 | 858 | 857 | 857 | 858 | 857 | 857 | 21194181
147 | Bheramara 410 MW CCPP | 165 | 165 | 165 | 175 | 180 | 180 | 180 | 185 | 175 | 170 | 165 | 165 | 165 | 165 | 165 | 165 | 175 | 195 |  | 225 | 240 | 250 | 265 | 280 | 285 | 285 | 4808448
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 622 | 580 | 550 | 550 | 550 | 580 | 590 | 610 | 622 | 622 | 622 | 610 | 550 |  | 550 | 590 | 610 | 622 | 622 | 622 | 622 | 15444000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 176 | 176 | 200 | 223 | 275 | 275 | 275 | 274 |  | 275 | 274 | 275 | 275 | 275 | 275 | 275 | 5300100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  |  |  |  | 19 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 474192
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 3 | 3 | 4 | 3 | 5 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 31740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [24 empty] | 25 | 137 | 175300
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 211 | 214 | 215 | 216 | 213 | 216 | 214 | 215 | 199 | 211 | 208 | 208 | 212 | 180 | 196 | 210 | 165 | 130 |  | 150 | 211 | 213 | 214 | 215 | 216 | 216 | 5119627
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 166 | 165 | 168 | 169 | 170 | 172 | 175 | 176 | 170 | 164 | 157 | 160 | 160 | 160 | 163 | 172 | 179 |  | 193 | 206 | 210 | 210 | 211 | 212 | 211 | 4494055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 374 | 400 | 414 | 414 | 414 | 414 | 414 | 414 | 400 | 395 | 330 | 370 | 375 | 370 | 368 | 383 | 414 | 350 |  | 414 | 414 | 380 | 414 | 414 | 414 | 414 | 9484363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 30 | 30 | 30 | 28 | 27 | 0 | [18 empty] | 3 | 4 | 159021
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 19 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 473040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235669
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 876976
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 0 | [10 empty] | 20 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 291037
168 | Santahar 50 MW Peaking PP | 38 | 37 | 30 | 0 | [9 empty] | 36 | 37 | 37 | 37 | 37 |  | 37 | 38 | 38 | 37 | 37 | 37 | 37 | 497723
169 | Natore 52 MW PP (Rajlanka) | [22 empty] | 8 | 8 | 8 |  | 30874
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 86 | 86 | 86 | 86 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 2052960
171 | Baghabari 200 MW PP (Paramount) |  |  | 1 | 50 | 48 | 50 | 50 | 10 | 10 | 10 | 36 | 81 | 40 | 10 | 10 | 32 | 10 |  |  | 32 | 146 | 161 | 180 | 170 | 167 | 168 | 1431855
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 77 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2259936
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2739168
173 | Rangpur 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 358000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 69 | 69 | 69 | 69 | 68 | 68 | 68 | 72 | 91 |  | 96 | 96 | 96 | 96 | 89 | 95 | 96 | 1851542
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 3 | 6 | 7 | 7 | 7 | 7 | 2 | 2 | 2 | 1 | [8 empty] | 46549
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 108 | 112 | 112 | 112 | 112 | 111 | 34 | 1402944
178