## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-07 | Thursday
|  |  | Date (day): | 2022-07-07 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13047.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14175 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-06 | 2022-07-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 82 | 88 | 82 | 90 |  | 18 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 122 | 202 | 200 | 200 | 160 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 170 | 210 | 210 | 210 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 26 | 31 | 30 | 31 |  | 69 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 40 | 40 | 40 |  | 60 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 232 | 224 | 250 | 250 | 85 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 132 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 53 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 25 | 30
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 51 | 40 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 260 | 248 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 221 | 303 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel Shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 81 | 100 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 131 | 130 | 131 |  | 18 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2834 | 3115 | 3092 | 3141 | 1578 | 1134
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 42 | 42 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 123 | 124 | 122 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 0 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 50 | 51 |  | 51 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 55 | 55 | 55 | 55 | 45 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 22 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 80 | 86 | 85 | 86 |  | 22 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 189 | 290 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1123 | 1434 | 1301 | 1453 | 305 | 626
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 209 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 325 | 320 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 315 | 330 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 293 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 39 | 36 | 39 |  | 6 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 49 | 52 | 50 | 52
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 55 | 55 | 140 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 137 | 145 | 147
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 84 | 84 | 84 | 84 |  | 79 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 112 | 200 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 164 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 16 | 20 | 20
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 0 | 25 | 27 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 80 | 195 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 101 | 116 | 115 | 115
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1952 | 2186 | 1913 | 2264 | 476 | 121
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 69 | 104 | 90 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 14 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 200 | 115 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 59 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 19 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 301 | 457 | 357.6 | 457 | 102 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 32 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 0 | 5 | 5 |  | 46 | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 0 | 5 | 5 |  | 45 | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 60 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 86 | 86 | 86
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 140 | 140 |  | 91 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 6 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 19 | 16 | 16 | 16 |  | 9 | Engine problem
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 409 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1615 | 1610 | 1638 | 1673 | 0 | 749
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 864 | 840 | 881 | 886
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 49 | 16 | 49 |  | 66 | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 205 | 205 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 235 | 250 | 240 | 300 | 110 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 8 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 90 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 75 | 74 | 74 | 74 |  | 31 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 100 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 43 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1535 | 1751 | 1769 | 1869 | 110 | 165
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 32 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 32 | 20 | 32 |  | 8 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 87 | 80 | 87 | 107 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 622 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 229 | 225 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 17 | 90 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 817 | 1049 | 991 | 1161 | 107 | 8
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 101 | 140 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 220 | 220 | 220 |  |  | Running by HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 139 | 180 | 180 | 40 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 374 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 8 | 34
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 86 | 86 | 85 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 179 | 170 | 180 |  | 20 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 94 | 94 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1301 | 1536 | 1553 | 1671 | 271 | 163
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 98 | 70 | 98 |  | 15 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 113 | 90 | 113
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 360 | 476 | 433 | 486 | 194 | 15
|  | Total |  |  |  |  | 22678 | 21396 | 11838 | 13614 | 13047.6 | 14175 | 3143 | 2989
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11566.5973 | 13301.88 | 12748.4655 | 13850.0183
| A. |  | 2022-07-06 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13614 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10793 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13864 | MW
| 3 | Day peak Generation : |  |  | 11838 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13301.88 | MW
| 4 | Evening peak Generation : |  |  | 13614 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 250 | MW
| 5 | Total Energy Generation : |  | 296.4571 | MKWHr | By Solar | 0.89279 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.2555 | MKWHr |  | By Oil: | 112.7881 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.1115 | MKWHr |  | By Hydro: | 2.9179 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3143 | MW | Dhaka | 4801.79 | 4801.79 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2989 | MW | Chittagong | 1321.6 | 1321.6 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6132 | MW | Khulna | 1618.2 | 1576.2 |  | 42 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1020.3 | MMCFD |  |  | Rajshahi | 1425.4 | 1369.4 |  | 56 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151472806.382 | ii) Oil : | Taka | 1626409608.39 | Comilla | 1309 | 1291 |  | 18 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 158750695 | Total | Taka | 1936633109.772 | Mymensingh | 1008 | 922 |  | 86 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 527 | 527 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 370 | MW (E to W) at | 21:00 | hrs | Barisal | 399.89 | 399.89 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 248 | MW at | 7:00 | hrs | Rangpur | 891 | 843 |  | 48 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31° C |  |  | Total | 13301.88 | 13051.88 |  | 250
| B. |  | 2022-07-07 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14175 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12300 | MW
| 4 | Reserve(Generation end) |  |  |  | 175 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 304.8626 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11043 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.8836 | MKWHr. | ii) HVDC Flow at Peak Time |  | 840 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6077 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.12 |  | (b) Today: | 89.68 |  | (c) Rule Curve: |  | 84.96
.

## YesterdayGen
2022-07-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 172 |  | 0 | 200 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 32 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 25 | 60 | 44 | 88 | 45 | 21 | 29 | 0 | 0 | 0 | 310 | 355 | 210 | 92 | 85 | 34 | 48 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 16 | 20 | 158 | 117 | 0 | 17 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 6 | 10 | 300 | 16 | 11 | 195 | 250 | 302 | 0 | 114 | 80 | 100 | 0 | 90 | 116 | 125 | 403 | 59 | 105 | 105 | 0 | 174 | 54 | 89 | 0 | 9 | 90 | 400 | 87 | 0 | 162 | 108 | 0 | 17 | 0 | 109 | 55 | 0 |  | 872 | 0 | 280 | 0 | 16 | 207 | 0 | 0 | 24 | 41 | 8 | 65 | 31 | 64 | 0 | 0 | 0 | 24 | 10 | 85 | 0 | 34 | 24 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 275 | 15 | 0 | 144 | 0 | 0 | 216 | 0 | 98 | 211 | 0 | 414 | 92 | 168 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 221 | 0 | 35 | 0 | 0 | 52 | 0 | 0 |  | 8225 | 4793 | 13018 | 3936 | 872 | 1887 | 843 | 3360 | 897 | 125 | 438 | 718 | 158 | 0 | 0 | 88.98
2:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 182 |  | 0 | 200 | 0 | 31 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 28 | 33 | 32 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 26 | 60 | 44 | 90 | 44 | 21 | 27 | 0 | 0 | 0 | 310 | 355 | 209 | 92 | 85 | 34 | 52 | 0 | 51 | 0 | 47 | 0 | 21 | 11 | 21 | 18 | 156 | 108 | 0 | 17 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 6 | 0 | 260 | 16 | 11 | 195 | 250 | 254 | 0 | 115 | 81 | 96 | 0 | 76 | 68 | 133 | 402 | 59 | 105 | 105 | 0 | 177 | 54 | 92 | 0 | 9 | 90 | 400 | 75 | 0 | 162 | 108 | 0 | 17 | 0 | 116 | 55 | 0 |  | 889 | 0 | 280 | 0 | 16 | 207 | 0 | 0 | 24 | 41 | 8 | 65 | 29 | 64 | 0 | 0 | 0 | 24 | 21 | 85 | 0 | 34 | 24 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 148 | 0 | 0 | 218 | 0 | 95 | 211 | 0 | 414 | 92 | 162 | 94 | 105 | 68 | 0 | 0 | 113 | 622 | 208 | 0 | 35 | 0 | 0 | 0 | 0 | 0 |  | 8021 | 4724 | 12745 | 3932 | 889 | 1835 | 787 | 3195 | 872 | 125 | 440 | 732 | 156 | 0 | 0 | 89
3:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 187 |  | 0 | 210 | 0 | 32 | 0 | 55 | 187 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 32 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 26 | 60 | 44 | 91 | 45 | 21 | 29 | 0 | 0 | 0 | 310 | 350 | 209 | 92 | 86 | 34 | 52 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 25 | 18 | 152 | 108 | 0 | 17 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 5 | 10 | 270 | 16 | 11 | 100 | 260 | 154 | 0 | 115 | 80 | 96 | 0 | 90 | 68 | 125 | 403 | 59 | 105 | 105 | 0 | 177 | 54 | 106 | 0 | 9 | 90 | 400 | 91 | 0 | 162 | 108 | 0 | 17 | 0 | 114 | 55 | 0 |  | 890 | 0 | 270 | 0 | 16 | 207 | 0 | 0 | 24 | 41 | 8 | 65 | 29 | 32 | 0 | 0 | 0 | 24 | 25 | 85 | 0 | 34 | 24 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 147 | 0 | 0 | 217 | 0 | 10 | 212 | 0 | 415 | 92 | 100 | 94 | 105 | 69 | 0 | 0 | 113 | 600 | 222 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7958 | 4605 | 12563 | 3923 | 890 | 1882 | 444 | 3339 | 850 | 125 | 439 | 736 | 152 | 0 | 0 | 89.03
4:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 202 |  | 0 | 210 | 0 | 31 | 0 | 55 | 187 | 0 | 0 | 40 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 32 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 26 | 60 | 44 | 88 | 44 | 21 | 29 | 0 | 0 | 0 | 310 | 355 | 210 | 92 | 86 | 34 | 52 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 32 | 20 | 152 | 110 | 0 | 17 | 0 | 33 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 5 | 10 | 290 | 8 | 11 | 50 | 260 | 54 | 0 | 116 | 81 | 95 | 0 | 90 | 68 | 132 | 402 | 59 | 105 | 105 | 0 | 178 | 54 | 110 | 0 | 9 | 100 | 400 | 91 | 0 | 162 | 108 | 0 | 17 | 0 | 115 | 55 | 0 |  | 910 | 0 | 270 | 0 | 16 | 207 | 0 | 0 | 24 | 36 | 8 | 65 | 27 | 32 | 0 | 0 | 0 | 24 | 25 | 85 | 0 | 34 | 24 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 146 | 0 | 0 | 217 | 0 | 0 | 212 | 0 | 414 | 92 | 50 | 94 | 105 | 69 | 0 | 0 | 113 | 590 | 222 | 0 | 17 | 0 | 0 | 72 | 0 | 0 |  | 7841 | 4528 | 12369 | 3930 | 910 | 1914 | 235 | 3310 | 840 | 125 | 439 | 731 | 152 | 0 | 0 | 89.06
5:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 211 |  | 0 | 210 | 0 | 32 | 0 | 55 | 186 | 0 | 0 | 40 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 32 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 26 | 60 | 44 | 86 | 44 | 21 | 29 | 0 | 0 | 0 | 310 | 355 | 213 | 92 | 84 | 34 | 52 | 0 | 51 | 0 | 48 | 0 | 21 | 11 | 30 | 20 | 126 | 109 | 0 | 17 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 6 | 10 | 280 | 8 | 11 | 50 | 260 | 53 | 0 | 116 | 81 | 96 | 0 | 90 | 68 | 137 | 402 | 58 | 105 | 105 | 0 | 178 | 54 | 110 | 0 | 9 | 100 | 384 | 91 | 0 | 162 | 108 | 0 | 17 | 0 | 116 | 55 | 0 |  | 909 | 0 | 270 | 0 | 16 | 207 | 0 | 0 | 24 | 36 | 8 | 65 | 23 | 32 | 0 | 0 | 0 | 24 | 25 | 85 | 0 | 34 | 24 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 148 | 0 | 0 | 218 | 0 | 0 | 212 | 0 | 414 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 600 | 216 | 0 | 17 | 0 | 0 | 72 | 0 | 0 |  | 7792 | 4480 | 12272 | 3912 | 909 | 1904 | 184 | 3308 | 850 | 125 | 440 | 732 | 126 | 0 | 0 | 89.09
6:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 0 | 222 |  | 0 | 210 | 0 | 32 | 0 | 55 | 186 | 0 | 0 | 40 | 85 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 32 | 24 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 30 | 44 | 56 | 45 | 18 | 29 | 0 | 0 | 0 | 330 | 355 | 210 | 92 | 85 | 34 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 25 | 20 | 134 | 109 | 0 | 17 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 6 | 10 | 260 | 16 | 11 | 0 | 260 | 0 | 0 | 116 | 0 | 102 | 1 | 90 | 68 | 138 | 401 | 58 | 105 | 105 | 0 | 100 | 54 | 110 | 0 | 9 | 100 | 400 | 91 | 0 | 162 | 108 | 0 | 17 | 1 | 116 | 55 | 0 |  | 910 | 0 | 265 | 0 | 16 | 189 | 0 | 0 | 0 | 0 | 8 | 65 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 0 | 212 | 0 | 376 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 520 | 216 | 0 | 17 | 0 | 3 | 72 | 0 | 0 |  | 7328 | 4114 | 11442 | 3942 | 910 | 1851 | 0 | 3153 | 740 | 123 | 386 | 395 | 134 | 5 | 0 | 89.12
7:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 208 |  | 0 | 210 | 0 | 32 | 0 | 55 | 244 | 0 | 0 | 40 | 85 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 32 | 24 | 0 | 86 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 44 | 11 | 45 | 18 | 25 | 0 | 0 | 0 | 310 | 355 | 214 | 92 | 85 | 31 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 23 | 20 | 128 | 89 | 0 | 17 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 65 | 86 | 0 | 140 | 0 | 6 | 10 | 295 | 16 | 11 | 0 | 260 | 0 | 0 | 115 | 0 | 132 | 2 | 76 | 68 | 135 | 403 | 59 | 105 | 68 | 1 | 50 | 54 | 102 | 0 | 9 | 100 | 400 | 104 | 5 | 162 | 108 | 0 | 17 | 4 | 116 | 55 | 27 |  | 909 | 0 | 260 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 8 | 65 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 370 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 520 | 223 | 0 | 17 | 0 | 21 | 72 | 0 | 0 |  | 7181 | 4003 | 11184 | 3969 | 909 | 1873 | 0 | 2998 | 740 | 121 | 280 | 263 | 128 | 33 | 0 | 89.15
8:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 197 |  | 0 | 210 | 0 | 31 | 0 | 55 | 252 | 0 | 0 | 40 | 85 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 24 | 0 | 86 | 35 | 100 | 0 | 12 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 44 | 11 | 44 | 19 | 7 | 0 | 0 | 0 | 330 | 345 | 212 | 92 | 85 | 36 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 16 | 20 | 132 | 88 | 0 | 17 | 0 | 32 | 42 | 5 | 5 | 110 | 0 | 40 | 86 | 0 | 140 | 0 | 6 | 10 | 270 | 16 | 11 | 0 | 260 | 0 | 0 | 115 | 0 | 125 | 3 | 76 | 68 | 125 | 398 | 59 | 105 | 17 | 2 | 15 | 54 | 110 | 0 | 9 | 100 | 360 | 104 | 4 | 72 | 108 | 0 | 17 | 5 | 115 | 55 | 130 |  | 910 | 0 | 260 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 222 | 0 | 0 | 148 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 370 | 92 | 0 | 94 | 105 | 69 | 0 | 0 | 113 | 460 | 223 | 0 | 17 | 1 | 10 | 52 | 0 | 0 |  | 6997 | 3796 | 10793 | 3962 | 910 | 1817 | 0 | 2760 | 682 | 121 | 250 | 264 | 132 | 25 | 0 | 89.18
9:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 0 | 192 |  | 0 | 210 | 0 | 31 | 0 | 55 | 238 | 0 | 0 | 40 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 34 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 44 | 57 | 44 | 17 | 2 | 0 | 0 | 0 | 275 | 360 | 196 | 92 | 84 | 36 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 0 | 20 | 132 | 81 | 0 | 16 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 64 | 84 | 0 | 140 | 0 | 6 | 10 | 290 | 16 | 11 | 0 | 260 | 0 | 0 | 115 | 0 | 115 | 5 | 76 | 68 | 138 | 370 | 59 | 105 | 51 | 4 | 100 | 54 | 110 | 0 | 9 | 100 | 400 | 104 | 9 | 137 | 108 | 0 | 17 | 8 | 116 | 55 | 193 |  | 910 | 0 | 245 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 20 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 0 | 209 | 0 | 370 | 92 | 0 | 94 | 105 | 69 | 0 | 1 | 113 | 460 | 216 | 0 | 17 | 2 | 22 | 52 | 0 | 0 |  | 7376 | 3830 | 11206 | 3947 | 910 | 1815 | 0 | 3070 | 710 | 119 | 250 | 331 | 132 | 52 | 0 | 89.21
10:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 0 | 165 |  | 0 | 190 | 0 | 32 | 0 | 55 | 231 | 0 | 0 | 40 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 25 | 25 | 42 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 85 | 43 | 17 | 3 | 0 | 0 | 0 | 275 | 295 | 192 | 45 | 84 | 36 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 138 | 78 | 0 | 16 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 63 | 84 | 0 | 140 | 0 | 6 | 10 | 300 | 18 | 11 | 0 | 260 | 35 | 0 | 115 | 51 | 113 | 16 | 76 | 72 | 138 | 402 | 59 | 105 | 105 | 4 | 189 | 54 | 110 | 0 | 9 | 93 | 400 | 104 | 21 | 162 | 108 | 0 | 17 | 11 | 116 | 55 | 243 |  | 909 | 0 | 250 | 0 | 16 | 140 | 0 | 0 | 0 | 0 | 8 | 20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 146 | 0 | 0 | 130 | 0 | 0 | 211 | 0 | 414 | 92 | 0 | 94 | 105 | 69 | 0 | 4 | 113 | 440 | 220 | 0 | 17 | 1 | 36 | 35 | 0 | 0 |  | 7609 | 3898 | 11507 | 3928 | 909 | 1781 | 86 | 3289 | 690 | 121 | 270 | 331 | 138 | 94 | 0 | 89.24
11:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 153 |  | 0 | 190 | 0 | 26 | 0 | 55 | 232 | 0 | 0 | 40 | 94 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 42 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 83 | 37 | 17 | 2 | 0 | 0 | 0 | 280 | 275 | 177 | 45 | 84 | 36 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 142 | 78 | 0 | 16 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 64 | 84 | 0 | 140 | 0 | 6 | 10 | 280 | 19 | 11 | 30 | 260 | 131 | 0 | 114 | 81 | 113 | 18 | 90 | 81 | 138 | 402 | 59 | 105 | 105 | 4 | 195 | 54 | 106 | 0 | 9 | 90 | 400 | 104 | 34 | 162 | 108 | 0 | 17 | 27 | 116 | 55 | 287 |  | 865 | 0 | 240 | 0 | 16 | 208 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 146 | 0 | 0 | 152 | 0 | 0 | 207 | 0 | 370 | 73 | 0 | 94 | 89 | 69 | 0 | 6 | 113 | 440 | 222 | 0 | 17 | 3 | 34 | 35 | 0 | 0 |  | 7801 | 3922 | 11723 | 4014 | 865 | 1709 | 242 | 3252 | 690 | 121 | 360 | 353 | 142 | 127 | 0 | 89.27
12:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 122 |  | 0 | 170 | 0 | 26 | 0 | 55 | 232 | 0 | 0 | 40 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 42 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 80 | 37 | 17 | 2 | 0 | 0 | 0 | 280 | 280 | 198 | 45 | 84 | 36 | 49 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 148 | 69 | 0 | 15 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 63 | 81 | 0 | 140 | 0 | 6 | 9 | 290 | 19 | 11 | 80 | 260 | 221 | 0 | 114 | 81 | 114 | 10 | 76 | 112 | 140 | 402 | 59 | 105 | 87 | 4 | 189 | 54 | 92 | 0 | 9 | 90 | 400 | 104 | 19 | 162 | 90 | 0 | 17 | 24 | 101 | 55 | 293 |  | 864 | 0 | 235 | 0 | 16 | 205 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 144 | 0 | 0 | 190 | 0 | 0 | 202 | 0 | 414 | 75 | 0 | 94 | 89 | 69 | 0 | 6 | 113 | 450 | 229 | 0 | 17 | 3 | 43 | 35 | 0 | 0 |  | 7825 | 4013 | 11838 | 4021 | 864 | 1711 | 382 | 3183 | 700 | 123 | 395 | 391 | 148 | 110 | 0 | 89.3
13:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 0 | 121 |  | 0 | 170 | 0 | 27 | 0 | 55 | 245 | 0 | 0 | 40 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 23 | 0 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 84 | 37 | 17 | 4 | 0 | 0 | 0 | 280 | 280 | 143 | 8 | 70 | 36 | 10 | 0 | 51 | 0 | 27 | 0 | 21 | 11 | 0 | 10 | 152 | 69 | 0 | 14 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 62 | 86 | 0 | 140 | 0 | 6 | 9 | 310 | 19 | 5 | 190 | 260 | 300 | 0 | 114 | 81 | 114 | 4 | 90 | 120 | 133 | 391 | 59 | 105 | 87 | 5 | 190 | 54 | 89 | 0 | 9 | 100 | 398 | 104 | 11 | 162 | 72 | 0 | 17 | 35 | 116 | 55 | 240 |  | 865 | 0 | 235 | 0 | 16 | 206 | 0 | 0 | 0 | 0 | 8 | 86 | 23 | 16 | 0 | 0 | 0 | 0 | 4 | 86 | 0 | 33 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 143 | 0 | 0 | 213 | 0 | 1 | 196 | 0 | 414 | 75 | 10 | 94 | 89 | 69 | 0 | 6 | 113 | 470 | 220 | 0 | 17 | 2 | 32 | 35 | 0 | 0 |  | 7859 | 4048 | 11907 | 3896 | 865 | 1657 | 582 | 3165 | 720 | 123 | 419 | 445 | 152 | 96 | 0 | 89.33
14:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 138 |  | 0 | 180 | 0 | 32 | 0 | 55 | 245 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 23 | 42 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 2 | 0 | 55 | 78 | 37 | 17 | 3 | 0 | 0 | 0 | 280 | 280 | 119 | 8 | 70 | 36 | 10 | 0 | 51 | 0 | 40 | 0 | 21 | 11 | 0 | 10 | 166 | 70 | 0 | 14 | 1 | 44 | 42 | 5 | 5 | 110 | 0 | 62 | 86 | 0 | 140 | 0 | 6 | 9 | 290 | 20 | 5 | 191 | 260 | 255 | 0 | 114 | 83 | 126 | 18 | 90 | 112 | 130 | 403 | 59 | 105 | 87 | 4 | 190 | 54 | 92 | 0 | 9 | 90 | 400 | 104 | 27 | 162 | 90 | 0 | 17 | 17 | 116 | 55 | 124 |  | 865 | 0 | 245 | 0 | 16 | 206 | 0 | 0 | 0 | 0 | 8 | 86 | 24 | 16 | 0 | 0 | 0 | 0 | 4 | 86 | 0 | 34 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 129 | 0 | 0 | 215 | 0 | 38 | 181 | 0 | 414 | 75 | 125 | 94 | 105 | 69 | 0 | 6 | 113 | 490 | 221 | 0 | 17 | 2 | 22 | 35 | 0 | 0 |  | 7850 | 4224 | 12074 | 3776 | 865 | 1667 | 692 | 3262 | 741 | 123 | 421 | 479 | 166 | 97 | 0 | 89.36
15:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 150 |  | 0 | 180 | 0 | 32 | 0 | 55 | 244 | 0 | 0 | 40 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 23 | 42 | 0 | 92 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 9 | 0 | 55 | 78 | 37 | 19 | 3 | 0 | 0 | 0 | 280 | 220 | 133 | 8 | 70 | 36 | 10 | 0 | 51 | 0 | 40 | 0 | 21 | 11 | 0 | 10 | 164 | 69 | 0 | 14 | 1 | 43 | 42 | 5 | 5 | 85 | 0 | 61 | 86 | 0 | 140 | 0 | 6 | 10 | 300 | 22 | 5 | 191 | 260 | 300 | 0 | 115 | 83 | 131 | 0 | 90 | 120 | 137 | 404 | 59 | 90 | 87 | 4 | 191 | 54 | 92 | 0 | 9 | 90 | 380 | 104 | 15 | 162 | 90 | 0 | 17 | 33 | 116 | 55 | 0 |  | 864 | 0 | 225 | 0 | 16 | 203 | 0 | 0 | 17 | 0 | 8 | 85 | 24 | 16 | 0 | 0 | 0 | 0 | 4 | 85 | 0 | 34 | 24 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 114 | 0 | 0 | 209 | 0 | 79 | 173 | 0 | 414 | 75 | 159 | 94 | 105 | 68 | 0 | 5 | 113 | 540 | 209 | 0 | 17 | 2 | 23 | 34 | 0 | 0 |  | 7697 | 4319 | 12016 | 3543 | 864 | 1652 | 812 | 3258 | 790 | 127 | 412 | 520 | 164 | 83 | 0 | 89.38
16:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 0 | 172 |  | 0 | 200 | 0 | 29 | 0 | 55 | 244 | 0 | 0 | 40 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 23 | 42 | 0 | 91 | 35 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 24 | 26 | 0 | 55 | 78 | 37 | 19 | 2 | 0 | 0 | 0 | 295 | 250 | 207 | 8 | 70 | 35 | 10 | 0 | 51 | 0 | 40 | 0 | 21 | 11 | 0 | 12 | 162 | 71 | 0 | 14 | 1 | 44 | 42 | 5 | 5 | 85 | 0 | 62 | 86 | 0 | 140 | 0 | 6 | 9 | 290 | 23 | 5 | 192 | 248 | 300 | 0 | 115 | 82 | 121 | 0 | 90 | 120 | 132 | 403 | 59 | 105 | 87 | 0 | 195 | 54 | 92 | 0 | 9 | 90 | 400 | 104 | 14 | 162 | 90 | 0 | 17 | 10 | 116 | 55 | 0 |  | 556 | 0 | 175 | 0 | 16 | 205 | 0 | 0 | 23 | 0 | 8 | 85 | 24 | 16 | 0 | 0 | 0 | 0 | 18 | 85 | 0 | 34 | 24 | 0 | 34 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 103 | 0 | 0 | 213 | 0 | 95 | 162 | 0 | 390 | 64 | 178 | 94 | 105 | 63 | 0 | 3 | 113 | 570 | 219 | 0 | 17 | 1 | 29 | 35 | 0 | 0 |  | 7848 | 4038 | 11886 | 3615 | 556 | 1665 | 847 | 3237 | 820 | 126 | 418 | 595 | 162 | 58 | 0 | 89.4
17:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 176 |  | 0 | 210 | 0 | 27 | 0 | 55 | 244 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 23 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 26 | 0 | 55 | 72 | 37 | 19 | 6 | 0 | 0 | 0 | 280 | 250 | 211 | 8 | 78 | 38 | 25 | 0 | 51 | 0 | 41 | 0 | 21 | 11 | 8 | 12 | 154 | 71 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 85 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 9 | 265 | 16 | 11 | 100 | 248 | 175 | 0 | 123 | 25 | 114 | 0 | 90 | 155 | 133 | 402 | 59 | 105 | 87 | 0 | 245 | 54 | 105 | 17 | 9 | 90 | 400 | 104 | 17 | 162 | 90 | 0 | 17 | 10 | 116 | 55 | 0 |  | 865 | 0 | 160 | 0 | 16 | 205 | 0 | 0 | 26 | 0 | 8 | 85 | 20 | 16 | 0 | 0 | 0 | 34 | 30 | 85 | 0 | 34 | 32 | 0 | 37 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 93 | 0 | 0 | 217 | 0 | 60 | 144 | 0 | 374 | 75 | 10 | 94 | 105 | 71 | 0 | 2 | 113 | 540 | 220 | 0 | 17 | 0 | 16 | 35 | 0 | 0 |  | 7710 | 4120 | 11830 | 3578 | 865 | 1641 | 370 | 3397 | 790 | 125 | 422 | 660 | 154 | 45 | 0 | 89.43
18:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 0 | 176 |  | 0 | 210 | 0 | 31 | 0 | 55 | 242 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 23 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 35 | 0 | 55 | 85 | 37 | 19 | 2 | 0 | 0 | 0 | 280 | 270 | 180 | 8 | 84 | 25 | 40 | 0 | 51 | 0 | 36 | 22 | 21 | 11 | 8 | 12 | 144 | 71 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 85 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 270 | 16 | 11 | 10 | 238 | 14 | 0 | 169 | 25 | 114 | 0 | 76 | 200 | 133 | 365 | 115 | 105 | 94 | 0 | 244 | 54 | 110 | 52 | 9 | 100 | 360 | 104 | 6 | 162 | 102 | 0 | 17 | 2 | 116 | 55 | 0 |  | 852 | 0 | 155 | 0 | 16 | 205 | 0 | 0 | 29 | 36 | 8 | 87 | 18 | 16 | 0 | 0 | 0 | 34 | 32 | 85 | 0 | 34 | 32 | 0 | 37 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 93 | 0 | 0 | 150 | 0 | 20 | 142 | 0 | 363 | 74 | 10 | 94 | 105 | 96 | 0 | 1 | 113 | 480 | 173 | 0 | 17 | 0 | 7 | 108 | 0 | 0 |  | 7581 | 4003 | 11584 | 3476 | 852 | 1595 | 79 | 3724 | 730 | 125 | 355 | 638 | 144 | 16 | 0 | 89.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 0 | 177 |  | 0 | 210 | 0 | 31 | 0 | 55 | 243 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 18 | 33 | 23 | 48 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 55 | 86 | 37 | 21 | 13 | 0 | 0 | 0 | 280 | 270 | 210 | 8 | 85 | 35 | 50 | 0 | 51 | 0 | 40 | 25 | 21 | 11 | 18 | 12 | 170 | 100 | 0 | 14 | 0 | 44 | 42 | 0 | 0 | 85 | 0 | 64 | 86 | 0 | 140 | 0 | 0 | 10 | 270 | 16 | 11 | 100 | 247 | 56 | 0 | 169 | 97 | 124 | 0 | 90 | 200 | 127 | 379 | 115 | 105 | 105 | 0 | 270 | 54 | 110 | 52 | 15 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 32 | 0 | 116 | 55 | 0 |  | 839 | 0 | 245 | 0 | 49 | 205 | 0 | 0 | 12 | 50 | 40 | 87 | 27 | 16 | 0 | 0 | 0 | 34 | 33 | 85 | 0 | 34 | 32 | 16 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 95 | 0 | 0 | 140 | 0 | 25 | 141 | 0 | 367 | 74 | 12 | 94 | 105 | 96 | 0 | 0 | 113 | 490 | 223 | 0 | 17 | 0 | 0 | 112 | 0 | 0 |  | 8078 | 4228 | 12306 | 3696 | 839 | 1686 | 290 | 3910 | 740 | 81 | 345 | 689 | 170 | 0 | 0 | 89.54
19:30 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 0 | 177 |  | 0 | 210 | 0 | 31 | 0 | 55 | 243 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 23 | 51 | 0 | 56 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 51 | 55 | 86 | 37 | 21 | 17 | 0 | 0 | 0 | 280 | 275 | 209 | 8 | 85 | 35 | 50 | 0 | 51 | 0 | 40 | 25 | 21 | 11 | 18 | 20 | 162 | 104 | 0 | 14 | 0 | 44 | 42 | 0 | 0 | 110 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 300 | 16 | 11 | 195 | 245 | 187 | 0 | 187 | 98 | 124 | 0 | 90 | 200 | 133 | 403 | 115 | 105 | 105 | 0 | 270 | 54 | 110 | 52 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 245 | 0 | 49 | 205 | 0 | 0 | 24 | 60 | 40 | 87 | 28 | 44 | 0 | 0 | 0 | 32 | 33 | 85 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 98 | 0 | 0 | 202 | 0 | 97 | 139 | 0 | 362 | 74 | 135 | 94 | 105 | 96 | 0 | 0 | 113 | 590 | 225 | 0 | 35 | 0 | 0 | 112 | 0 | 0 |  | 8437 | 4669 | 13106 | 3746 | 840 | 1743 | 712 | 3996 | 840 | 91 | 407 | 771 | 162 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 0 | 187 |  | 0 | 210 | 0 | 31 | 0 | 55 | 223 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 23 | 51 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 86 | 38 | 21 | 21 | 0 | 0 | 0 | 280 | 275 | 210 | 8 | 85 | 35 | 53 | 0 | 51 | 0 | 40 | 25 | 21 | 11 | 16 | 20 | 154 | 104 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 110 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 310 | 16 | 11 | 195 | 248 | 186 | 0 | 188 | 98 | 131 | 0 | 90 | 200 | 133 | 409 | 115 | 105 | 105 | 0 | 275 | 54 | 110 | 52 | 10 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 245 | 0 | 49 | 205 | 0 | 0 | 42 | 60 | 40 | 87 | 27 | 48 | 0 | 0 | 0 | 34 | 30 | 86 | 0 | 34 | 32 | 34 | 29 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 97 | 0 | 0 | 210 | 0 | 98 | 139 | 0 | 363 | 74 | 158 | 94 | 105 | 97 | 0 | 0 | 113 | 600 | 222 | 0 | 35 | 0 | 0 | 112 | 0 | 0 |  | 8496 | 4722 | 13218 | 3729 | 840 | 1766 | 735 | 4019 | 850 | 123 | 415 | 797 | 154 | 0 | 0 | 89.51
21:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 0 | 202 |  | 0 | 210 | 0 | 31 | 0 | 55 | 224 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 28 | 51 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 86 | 42 | 21 | 22 | 0 | 0 | 0 | 325 | 315 | 209 | 8 | 84 | 39 | 52 | 0 | 51 | 0 | 40 | 25 | 21 | 11 | 16 | 20 | 164 | 104 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 110 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 280 | 16 | 11 | 195 | 248 | 303 | 0 | 200 | 100 | 131 | 0 | 90 | 200 | 137 | 409 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 114 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 250 | 0 | 49 | 205 | 0 | 0 | 35 | 60 | 40 | 87 | 32 | 48 | 0 | 0 | 0 | 34 | 26 | 86 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 101 | 0 | 0 | 220 | 0 | 98 | 139 | 0 | 374 | 74 | 179 | 94 | 100 | 98 | 0 | 0 | 113 | 622 | 225 | 0 | 35 | 0 | 0 | 113 | 0 | 0 |  | 8802 | 4812 | 13614 | 3831 | 840 | 1772 | 875 | 4112 | 872 | 124 | 440 | 804 | 164 | 0 | 0 | 89.54
22:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 0 | 186 |  | 0 | 210 | 0 | 30 | 0 | 55 | 217 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 28 | 42 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 86 | 44 | 21 | 30 | 0 | 0 | 0 | 345 | 335 | 207 | 8 | 84 | 39 | 52 | 0 | 51 | 0 | 41 | 33 | 21 | 11 | 16 | 20 | 164 | 103 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 90 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 10 | 315 | 16 | 11 | 195 | 248 | 303 | 0 | 200 | 100 | 132 | 0 | 90 | 200 | 138 | 404 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 114 | 9 | 100 | 395 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 250 | 0 | 49 | 205 | 0 | 0 | 28 | 40 | 8 | 86 | 33 | 48 | 0 | 0 | 0 | 34 | 26 | 87 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 9 | 102 | 0 | 0 | 216 | 0 | 98 | 139 | 0 | 376 | 75 | 172 | 94 | 105 | 98 | 0 | 0 | 113 | 622 | 225 | 0 | 46 | 0 | 0 | 115 | 0 | 0 |  | 8790 | 4774 | 13564 | 3831 | 840 | 1761 | 868 | 4101 | 872 | 123 | 445 | 775 | 164 | 0 | 0 | 89.57
23:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 0 | 181 |  | 0 | 210 | 0 | 24 | 0 | 55 | 218 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 30 | 42 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 85 | 44 | 19 | 30 | 0 | 0 | 0 | 320 | 330 | 208 | 26 | 84 | 39 | 52 | 0 | 51 | 0 | 39 | 33 | 21 | 11 | 16 | 20 | 166 | 105 | 0 | 17 | 0 | 44 | 42 | 0 | 0 | 90 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 10 | 310 | 16 | 11 | 195 | 235 | 303 | 0 | 200 | 100 | 133 | 0 | 90 | 200 | 138 | 403 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 114 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 250 | 0 | 49 | 206 | 0 | 0 | 32 | 40 | 8 | 87 | 33 | 48 | 0 | 0 | 0 | 34 | 31 | 87 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 9 | 86 | 0 | 0 | 216 | 0 | 96 | 142 | 0 | 400 | 75 | 170 | 94 | 105 | 98 | 0 | 0 | 113 | 622 | 224 | 0 | 54 | 0 | 0 | 115 | 0 | 0 |  | 8755 | 4799 | 13554 | 3798 | 840 | 1789 | 864 | 4090 | 872 | 123 | 446 | 782 | 166 | 0 | 0 | 89.6
24:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 0 | 182 |  | 0 | 210 | 0 | 31 | 0 | 55 | 218 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 30 | 42 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 50 | 51 | 55 | 93 | 44 | 19 | 30 | 0 | 0 | 0 | 310 | 315 | 211 | 26 | 84 | 39 | 53 | 0 | 51 | 0 | 41 | 0 | 21 | 11 | 17 | 20 | 148 | 105 | 0 | 17 | 0 | 44 | 42 | 0 | 0 | 90 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 10 | 280 | 16 | 11 | 195 | 228 | 227 | 0 | 115 | 39 | 133 | 0 | 90 | 200 | 145 | 402 | 60 | 105 | 87 | 0 | 285 | 54 | 80 | 34 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 846 | 0 | 250 | 0 | 26 | 208 | 0 | 0 | 32 | 40 | 8 | 87 | 33 | 48 | 0 | 0 | 0 | 34 | 33 | 87 | 0 | 34 | 32 | 0 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 9 | 47 | 0 | 0 | 218 | 0 | 97 | 158 | 0 | 414 | 75 | 169 | 94 | 89 | 98 | 0 | 0 | 113 | 610 | 223 | 0 | 54 | 0 | 0 | 115 | 0 | 0 |  | 8265 | 4716 | 12981 | 3753 | 846 | 1778 | 727 | 3726 | 860 | 124 | 450 | 787 | 148 | 0 | 0 | 89.63
KWH | 0 | 0 | 0 | 4378500 | 7157218 | 1983227 | 0 | 0 | 4274000 |  | 0 | 4210450 | 0 | 736320 | 0 | 1310027 | 5415875 | 0 | 0 | 967680 | 2128176 | 2854080 | 0 | 0 | 0 | 0 | 1213200 | 1329668 | 946990 | 454572 | 600000 | 637200 | 805900 | 651900 | 974400 | 0 | 2077930 | 840000 | 2400000 | 0 | 556860 | 0 | 0 | 0 | 0 |  | 594240 | 504480 | 658561 | 1224600 | 1872840 | 996480 | 450336 | 385920 | 0 | 0 | 0 | 7561800 | 7865900 | 4714000 | 1137454 | 1925920 | 819504 | 1066560 | 0 | 1227807 | 0 | 692976 | 160968 | 379908 | 250200 | 299500 | 424160 | 3607680 | 2129280 | 0 | 342864 | 8600 | 886000 | 988296 | 91200 | 99144 | 2478355 | 0 | 1392096 | 2016960 | 0 | 3293450 | 0 | 140400 | 221940 | 7088500 | 388202 | 240000 | 2587008 | 6051925 | 3951226 | 0 | 3156000 | 1502416 | 2832190 | 76680 | 2036160 | 2962560 | 3233381 | 9534000 | 1755600 | 2468400 | 2294145 | 29279 | 4641818 | 1366128 | 2489010 | 507300 | 230160 | 2302080 | 9458100 | 2510400 | 185200 | 3875040 | 2456400 | 0 | 551160 | 217697 | 2773440 | 1338120 | 1522900 |  | 20883636 | 0 | 6020640 | 0 | 538560 | 4701120 | 0 | 0 | 360000 | 486272 | 260625 | 1707116 | 593090 | 742842 | 0 | 0 | 0 | 368112 | 348751 | 2045304 | 0 | 717968 | 356753 | 159610 | 478350 | 496560 | 0 | 215936 | 0 | 0 | 6036000 | 129000 | 24000 | 3092600 | 0 | 0 | 4833173 | 0 | 1101120 | 4635982 | 0 | 9467636 | 1948800 | 2005830 | 2273952 | 2490768 | 1863744 | 0 | 41372 | 2736000 | 14075500 | 5236473 | 0 | 614400 | 24360 | 309600 | 1608384 | 0 | 0 |  | 190427177 | 106029939 | 296457116 | 93039855 | 20883636 | 42215676 | 11147600 | 82799519 | 20111500 | 2917930 | 9687293 | 9153639 | 3607680 | 892788 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 8016084.16 | 2637691.91 | 0 | 0 | 4615920 |  | 0 | 4589390.5 | 0 | 8232057.6 | 0 | 17357857.75 | 6065780 | 0 | 0 | 14147481.6 | 29943436.32 | 46264636.8 | 0 | 0 | 0 | 0 | 15431904 | 17950518 | 12699135.9 | 340929 | 450000 | 0 | 0 | 0 | 16574544 | 0 | 561041.1 | 226800 | 4536000 | 0 | 9104661 | 0 | 0 | 0 | 0 |  | 7754832 | 8414726.4 | 11208708.22 | 16544346 | 23747611.2 | 11529273.6 | 571926.72 | 1285113.6 | 0 | 0 | 0 | 8393598 | 8573831 | 5468240 | 1467315.66 | 2349622.4 | 926039.52 | 1589174.4 | 0 | 2050437.69 | 0 | 11967695.52 | 2165019.6 | 520473.96 | 187650 | 524125 | 318120 | 25903142.4 | 2320915.2 | 0 | 466295.04 | 137084 | 1213820 | 1304550.72 | 158688 | 171519.12 | 2850108.25 | 0 | 2700666.24 | 4598668.8 | 0 | 3326384.5 | 0 | 209196 | 439441.2 | 7088500 | 291151.5 | 182400 | 54223687.68 | 82608776.25 | 82817696.96 | 0 | 42542880 | 31054938.72 | 39225831.5 | 896389.2 | 21013171.2 | 40468569.6 | 42906965.87 | 8771280 | 21348096 | 35693064 | 29020934.25 | 0 | 54494943.32 | 14877133.92 | 26458176.3 | 6884061 | 2966762.4 | 27118502.4 | 8701452 | 32509680 | 2676140 | 49174257.6 | 27953832 | 0 | 7198149.6 | 2601479.15 | 41518396.8 | 17623040.4 | 0 |  | 62650908 | 0 | 6743116.8 | 0 | 5606409.6 | 77568480 | 0 | 0 | 6483600 | 8752896 | 3745181.25 | 1911969.92 | 1150594.6 | 8096977.8 | 0 | 0 | 0 | 6173238.24 | 6099654.99 | 31988554.56 | 0 | 11889550.08 | 6032693.23 | 2175484.3 | 8069764.5 | 1027879.2 | 0 | 163463.552 | 0 | 0 | 31930440 | 5420580 | 843600 | 3587416 | 0 | 0 | 84387200.58 | 0 | 23101497.6 | 5377739.12 | 0 | 9372959.64 | 26191872 | 42062255.1 | 26900852.16 | 35991597.6 | 23669548.8 | 0 | 457160.6 | 33215040 | 126820255 | 5341202.46 | 0 | 4546560 | 275511.6 | 3631608 | 24656526.72 | 0 | 0 |  | 1262538534.22 | 774111839.602 | 2036650373.822 | 100829005.352 | 62650908 | 50643801.03 | 233260076.06 | 1073473503.29 | 158750695 | 787841.1 | 168219860.58 | 151456168.46 | 25903142.4 | 10675372.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 122 |  | 0 | 170 | 0 | 26 | 0 | 55 | 232 | 0 | 0 | 40 | 85 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 42 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 80 | 37 | 17 | 2 | 0 | 0 | 0 | 280 | 280 | 198 | 45 | 84 | 36 | 49 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 148 | 69 | 0 | 15 | 1 | 32 | 42 | 5 | 5 | 110 | 0 | 63 | 81 | 0 | 140 | 0 | 6 | 9 | 290 | 19 | 11 | 80 | 260 | 221 | 0 | 114 | 81 | 114 | 10 | 76 | 112 | 140 | 402 | 59 | 105 | 87 | 4 | 189 | 54 | 92 | 0 | 9 | 90 | 400 | 104 | 19 | 162 | 90 | 0 | 17 | 24 | 101 | 55 | 293 |  | 864 | 0 | 235 | 0 | 16 | 205 | 0 | 0 | 0 | 0 | 8 | 85 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 144 | 0 | 0 | 190 | 0 | 0 | 202 | 0 | 414 | 75 | 0 | 94 | 89 | 69 | 0 | 6 | 113 | 450 | 229 | 0 | 17 | 3 | 43 | 35 | 0 | 0 |  | 11838 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 0 | 202 | 0 | 0 | 210 | 0 | 31 | 0 | 55 | 224 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 28 | 51 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 51 | 51 | 55 | 86 | 42 | 21 | 22 | 0 | 0 | 0 | 325 | 315 | 209 | 8 | 84 | 39 | 52 | 0 | 51 | 0 | 40 | 25 | 21 | 11 | 16 | 20 | 164 | 104 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 110 | 0 | 63 | 86 | 0 | 140 | 0 | 0 | 10 | 280 | 16 | 11 | 195 | 248 | 303 | 0 | 200 | 100 | 131 | 0 | 90 | 200 | 137 | 409 | 115 | 105 | 105 | 0 | 290 | 54 | 110 | 114 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 116 | 55 | 0 |  | 840 | 0 | 250 | 0 | 49 | 205 | 0 | 0 | 35 | 60 | 40 | 87 | 32 | 48 | 0 | 0 | 0 | 34 | 26 | 86 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 101 | 0 | 0 | 220 | 0 | 98 | 139 | 0 | 374 | 74 | 179 | 94 | 100 | 98 | 0 | 0 | 113 | 622 | 225 | 0 | 35 | 0 | 0 | 113 | 0 | 0 |  | 13614 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 31 | 0 | 55 | 250 | 0 | 0 | 40 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 55 | 86 | 42 | 21 | 30 | 0 | 0 | 0 | 330 | 320 | 210 | 55 | 84 | 39 | 52 | 0 | 51 | 0 | 40 | 25 | 22 | 11 | 20 | 20 | 165 | 100 | 0 | 20 | 0 | 43 | 42 | 5 | 5 | 110 | 0 | 64 | 86 | 0 | 140 | 0 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 0 | 200 | 100 | 131 | 0 | 90 | 200 | 147 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 9 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 115 | 55 |  |  | 886 | 0 | 300 | 0 | 49 | 220 | 0 | 0 | 35 | 60 | 40 | 87 | 32 | 110 | 0 | 0 | 0 | 34 | 30 | 86 | 0 | 34 | 32 | 34 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 10 | 150 | 0 | 0 | 220 | 0 | 100 | 180 | 0 | 414 | 74 | 180 | 94 | 105 | 98 | 0 | 0 | 113 | 622 | 220 |  | 90 |  |  | 113
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 30 | 0 | 55 | 250 | 0 | 0 | 40 | 94 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 40 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 50 | 55 | 85 | 42 | 20 | 10 | 0 | 0 | 0 | 320 | 330 | 210 | 55 | 84 | 36 | 50 | 0 | 51 | 0 | 40 | 0 | 22 | 11 | 20 | 20 | 143 | 90 | 0 | 20 | 1.6 | 43 | 42 | 5 | 5 | 110 | 0 | 60 | 86 | 0 | 140 | 0 | 0 | 10 | 310 | 16 | 11 | 100 | 250 | 300 | 0 | 115 | 50 | 130 | 20 | 90 | 100 | 145 | 400 | 59 | 105 | 105 | 5 | 200 | 54 | 110 | 17 | 9 | 100 | 400 | 104 | 50 | 162 | 108 | 0 | 35 | 30 | 115 | 55 |  |  | 881 | 0 | 240 | 0 | 16 | 220 | 0 | 0 | 35 | 0 | 8 | 80 | 20 | 32 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 140 | 0 | 0 | 220 | 0 | 90 | 180 | 0 | 414 | 74 | 170 | 94 | 105 | 70 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 90
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 0 | 180 | 0 | 0 | 210 | 0 | 31 | 0 | 55 | 230 | 0 | 0 | 40 | 58 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 30 | 42 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 55 | 56 | 37 | 19 | 2 | 0 | 0 | 0 | 360 | 315 | 210 | 55 | 84 | 38 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 7 | 18 | 112 | 89 | 0 | 19 | 1 | 43 | 42 | 0 | 0 | 90 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 230 | 0 | 0 | 116 | 0 | 127 | 4 | 90 | 100 | 115 | 353 | 60 | 90 | 38 | 1 | 174 | 54 | 73 | 17 | 9 | 100 | 360 | 104 | 12 | 119 | 108 | 0 | 35 | 19 | 95 | 55 | 0 | 0 | 897 | 0 | 315 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 206 | 0 | 370 | 75 | 0 | 94 | 105 | 70 | 0 | 3 | 113 | 500 | 223 | 0 | 0 | 2 | 56 | 109 | 0 | 0 | 0 |  |  |  |  | 112788051 |  | 0
112788051
| Minimum Generation |  | 10793 | 8:00
| Highest Generation |  | 13614 | 21:00
| Day Peak Generation |  | 11838 | 12:00
| Evening Peak Generation |  | 13614 | 21:00
| HVDC Max Flow |  | 910 | 4:00
| HVDC EvPeak Flow |  | 840 | 21:00
| Load factor L.F |  | 90.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-07
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11838 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11043 | MW
Evening Peak Generation : |  | 13614 | MW Hour : | 21:00 | Available Max Generation : |  | 14175 | MW
E.P. Demand (at gen end) : |  | 13864 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13614 | MW Hour : | 21:00 | Reserve(Generation end) |  | 175 | MW
Total Gen. (MKWH) : |  | 296.4571 | System Load Factor : | 90.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 248 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-07
Actual : | 89.68 | Ft.(MSL) , | Rule curve : | 84.96 | Ft.( MSL )
Gas Consumed : | Total = | 1020.3 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151472806.382
: |  | Coal : | 158750695 | Oil : | 1626409608.39 | Total : | 1936633109.772
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4936.5143 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1330.65 |  |  | 0 | 0%
Khulna Area | 42 | 1008:00 | 1742.78 |  |  | 0 | 0%
Rajshahi Area | 56 | 1344:00 | 1561.5629 |  |  | 0 | 0%
Cumilla Area | 18 | 432:00 | 1383.4762 |  |  | 0 | 0%
Mymensingh Area | 86 | 2064:00 | 1017.3029 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 564.26 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 368.9995 |  |  | 0 | 0%
Rangpur Area | 48 | 1152:00 | 779.2162 |  |  | 0 | 0%
Total | 250 |  | 13684.762 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bakulia 132/33 kV T-1 & T-2 transformers tripped at 08:46 from 33 kV end due to Pathorghata-2 feeder | [5 empty] | About 44 MW power interruption occurred under
fault and were switched on at 08:56. | [5 empty] | Bakulia S/S area from 08:46 to 08:56.
b) Cumilla(N)-Megnaghat 230 kV Ckt-1 was under shut down from 09:36 to 13:32 for C/M.
c) Haripur S/S-Haripur-412 MW 132 kV Ckt was under shut down from 10:13 to 13:44 for C/M.
d) Mirsharai 230/132 kV T-1 transformer was under shut down from 10:10 to 1714 for D/W.
e) BSRM-Mirsharai EZ 230 kV Ckt was under shut down from 10:27 to 17:03 for D/W.
f) Mirpur-Aminbazar 132 kV Ckt-1 tripped at 11:52 from both end showing directional E/F at Mirpur end & | [5 empty] | About 30 MW power interruption occurred under
dist.Z1 at Aminbazar end and was switched on at 12:43. | [5 empty] | Mirpur & Uttara S/S area from 11:52 to 12:43.
g) Bogura confidence P/S-Mithapukur 132 kV Ckt-1 was shut down at 11:09 due to red hot maintenance
and was switched on at 12:27.
h) HVDC pole-2 tripped at 15:22 due to auxiliary problem and was switched on at 15:58.
i) Niamatpur 132/33 kV T-3 transformer was under shut down from 13:43 to 18:50 for maintenance work.
j) Sirajganj #1 CCPP GT & ST were synchronized at 01:53 & 05:15(7/7/22).
k) Benapole 132/33 kV T-2 transformer was shut down at 06:44(7/7/22) due to red hot maintenance at | [5 empty] | About 20 MW power interruption occurred under
33 kV Chutipur feeder and was switched on at 09:05(7/7/22). | [5 empty] | Benapole S/S area from 06:44 to 09:05.
l) Agargaon 230/132 kV T-2 transformer is under shut down since 06:51(7/7/22) for C/M.
m) Patuakhali 132/33 kV T-2 transformer is under shut down since 07:19(7/7/22) for C/M.
n) Gopalganj 132/33 kV T-2 transformer is under shut down since 07:22(7/7/22) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7157218 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 88 | 1983227 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 202 | 4274000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 210 | 4210450 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 31 | 736320 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1310027
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 454572
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 967680 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 224 | 5415875 | Gas shoratge
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2128176 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1213200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2854080 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1329668
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 946990
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1237200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 651900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 974400 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 248 | 6051925 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 303 | 3951226
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1502416
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2832190 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2468400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2510400
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3875040
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 217697
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1338120
| Dhaka area Total |  |  |  | 5847 | 3115 | 67776797
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 556860
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 76680
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 996480 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 124 | 2917930 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2294145
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 504480 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 658561 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 55 | 1224600 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2036160 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 450336
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 385920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 1872840 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29279
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 290 | 4641818 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1366128
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2489010
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2302080
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2456400 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1434 | 29659707
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4714000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7561800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7865900 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 1522900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 819504 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1066560
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1137454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1227807
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3233381 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 692976 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 84 | 1925920 | Gas shortage
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2962560
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 379908
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3607680
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 299500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 160968 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 424160 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 195 | 2587008
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 507300
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 230160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 551160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 116 | 2773440
| Cumilla Area Total |  |  |  | 2885 | 2186 | 46502246
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2129280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 342864
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 3156000
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1755600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 185200
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 594240
| Mymensingh Area Total |  |  |  | 614 | 457 | 8171784
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 886000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 988296 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2478355 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 91200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 99144 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 240000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1392096
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2016960
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3293450 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 140400 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 388202
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7088500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 409 | 9534000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 221940
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9458100
| Sylhet Area Total |  |  |  | 2477 | 1610 | 38316643
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 840 | 20883636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 538560 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 360000 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 205 | 4701120 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 486272 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6020640 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 260625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 1101120
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 74 | 1948800 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 100 | 2490768
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 309600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1751 | 39101141
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 742842 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 593090 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 1707116 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14075500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 225 | 5236473
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 614400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1049 | 22969421
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 368112 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 348751 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 717968 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 356753 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 101 | 3092600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 4833173
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 139 | 4635982 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 374 | 9467636 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 478350 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 496560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 215936
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 159610 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 2045304 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 179 | 2005830 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2273952 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2736000
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24360
| Rajshahi Area Total |  |  |  | 2129 | 1536 | 34256877
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6036000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 129000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 24000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1863744 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41372
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 1608384
| Rangpur Area Total |  |  |  | 720 | 476 | 9702500
| Total |  |  |  | 21396 | 13614 | 296457116
| Eastern Grid Total |  |  |  | 14205 | 8802 | 190427177
| Western Grid Total |  |  |  | 7191 | 4812 | 106029939
| National Grid Total |  |  |  | 21396 | 13614 | 296457116
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-06
(a) ENTIRE EASTERN GRID : |  | 8863.39 | MW | (b) ENTIRE WESTERN GRID : |  | 4188.49 | MW
i) Dhaka area |  | 4801.79 | MW | i) Khulna area |  | 1576.2 | MW
ii) Chittagong area |  | 1321.6 | MW | ii) Rajshahi area |  | 1369.4 | MW
iii) Comilla area |  | 1291 | MW | iii) Barisal area |  | 399.89 | MW
iv) Mymensingh area |  | 922 | MW | iv) Rangpur area |  | 843 | MW
v) Sylhet area |  | 527 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13051.88 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 15 | 12:00 | Chowmuhani | 224 | 23:00 | Kaptai | 4.2 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 140 | 15:00 | Chuadanga | 105 | 02:00 | Kazla | 85 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 00:00 | Coxsbazar | 109 | 21:00 | Keranigonj | 64 | 13:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 91 | 13:00 | Cumilla(N) | 171 | 21:00 | Khagrachori | 28 | 21:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 88 | 15:00 | Cumilla(S) | 170 | 19:00 | Khulna | 92 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 59 | 04:00 | Daudkandi | 162 | 21:00 | Khulshi | 183 | 15:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 48 | 00:00 | Dhaka | 42 | 12:00 | Kishoreganj | 132 | 05:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 123 | 18:00 | Dhamrai | 120 | 15:00 | Kodda | 316 | 19:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 94 | 02:00 | Dhanmondi | 148 | 13:00 | Kulaura | 48 | 20:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 131 | 16:00 | Dohazari | 110 | 20:00 | Kurigram | 69 | 22:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 57 | 13:00 | Faridpur | 152 | 22:00 | Kushtia | 140 | 21:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 10:00 | Fatullah | 70 | 00:00 | Lalbag | 92 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 53 | 19:30 | Fenchuganj | 46 | 20:00 | Lalmonirhat | 51 | 02:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 22:00 | Feni | 130 | 21:00 | Madanganj | 94 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 98 | 00:00 | GPH | 93 | 13:00 | Madaripur | 104 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 86 | 19:30 | Ghorashal | 72 | 22:00 | Madartek | 85 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 75 | 10:00 | Goalpara | 29 | 00:00 | Madunaghat | 59 | 21:00 | Rajshahi | 132 | 22:00
Baroirhat | 59 | 23:00 | Gollamari | 56 | 20:00 | Magura | 56 | 02:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 153 | 16:00 | Gopalganj | 103 | 19:30 | Mahasthangarh | 70 | 23:00 | Ramganj | 88 | 19:00
BashundharaCement | 13 | 23:00 | Gulshan | 122 | 13:00 | Manikganj | 98 | 01:00 | Rampur | 16 | 00:00
Beanibazar | 63 | 19:30 | Halishahar | 94.5 | 16:00 | Maniknagar | 77 | 13:00 | Rangamati | 14 | 19:00
Benapole | 56 | 21:00 | HaripurSBU | 145 | 00:00 | Matarbari | 41 | 20:00 | Rangpur | 105 | 08:00
Bhaluka | 134 | 18:30 | Hasnabad | 115 | 00:00 | Matuail | 62 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 58 | 00:00 | Hathazari | 102 | 19:00 | Millgate | 58 | 15:00 | SSM | 3 | 05:00
Bhangura | 32 | 23:00 | Ishurdi | 69 | 00:00 | Mirpur | 121 | 00:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 58 | 21:00 | Jaldhaka | 66 | 02:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 265 | 21:00 | Jamalpur | 152 | 04:00 | Mithapukur | 30 | 03:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 03:00 | Jashore | 129 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 171 | 22:00 | Jhenaidah | 114 | 22:00 | Mogbazar | 126 | 13:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 21:00 | Joydebpur | 196 | 19:30 | Mongla | 42 | 15:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 160 | 01:00 | Joypurhat | 56 | 23:00 | Motijheel | 39 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 140 | 13:00 | Juldah | 29 | 15:00 | Munshiganj | 106 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 71 | 00:00 | KSRM | 28 | 12:00 | Mymensingh | 211 | 00:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 22:00 | Kabirpur | 280 | 18:30 | Naogaon | 133 | 22:00 | Shikalbaha | 28 | 19:00
Chapai | 75 | 06:00 | Kachua | 74 | 02:00 | Narail | 46 | 21:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 34 | 11:00 | Kallyanpur | 102 | 00:00 | Narinda | 69 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 49 | 23:00 | Kalurghat | 6 | 09:00 | Narshingdi | 180 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 28 | 21:00 | Kamrangirchar | 61 | 13:00 | Natore | 153 | 21:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 395 | 07:00 | 378 | 12:00 | Kaliakoir | 397 | 07:00 | 385 | 08:00
| Bibiana | 408 | 11:00 | 401 | 15:00 | Payra | 418 | 18:30 | 410 | 03:00
| BIPTC | 406 | 16:00 | 393 | 00:00
| Gopalganj_I | 417 | 18:00 | 398 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 05:00 | 212 | 15:00 | Hasnabad | 224 | 02:00 | 215 | 17:00
| AKSML | 237 | 05:00 | 218 | 13:00 | Hathazari | 239 | 18:00 | 226 | 12:00
| Aminbazar | 227 | 06:00 | 216 | 12:00 | Ishurdi | 236 | 18:30 | 226 | 02:00
| Ashuganj | 240 | 06:00 | 232 | 12:00 | Jhenaidah | 233 | 18:30 | 220 | 03:00
| Baghabari | 234 | 18:00 | 229 | 10:00 | Kaliakoir | 229 | 05:00 | 217 | 12:00
| Barapukuria | 229 | 17:00 | 214 | 04:00 | Keranigonj | 225 | 05:00 | 212 | 15:00
| Barishal | 243 | 18:00 | 236 | 03:00 | Khulna(S) | 241 | 18:30 | 230 | 02:00
| Bheramara | 232 | 18:00 | 223 | 02:00 | Maniknagar | 226 | 05:00 | 215 | 15:00
| Bhulta | 228 | 05:00 | 218 | 12:00 | Meghnaghat | 230 | 05:00 | 220 | 12:00
| Bibiana | 238 | 03:00 | 233 | 15:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 18:30 | 223 | 02:00 | Rajshahi | 235 | 18:30 | 222 | 03:00
| Bogura | 233 | 18:30 | 219 | 04:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 10:00 | 241 | 14:00 | Rampura | 226 | 05:00 | 218 | 11:00
| BSRM | 236 | 05:00 | 222 | 15:00 | Shikalbaha | 239 | 18:30 | 226 | 13:00
| Cumilla(N) | 229 | 18:00 | 222 | 12:00 | Shyampur | 225 | 05:00 | 213 | 15:00
| Fenchuganj | 241 | 05:00 | 237 | 08:00 | Siddhirganj | 226 | 05:00 | 216 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 259 | 12:00 | 227 | 02:00
| GPH | 237 | 05:00 | 224 | 08:00 | Tongi | 226 | 05:00 | 215 | 15:00
| Haripur | 222 | 01:00 | 215 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 05:00 | 124 | 12:00 | Lalbag | 137 | 05:00 | 128 | 15:00
| Agargaon | 135 | 05:00 | 125 | 15:00 | Lalmonirhat | 132 | 18:30 | 113 | 02:00
| Agrabad | 138 | 05:00 | 130 | 12:00 | Madanganj | 130 | 04:00 | 125 | 12:00
| AKS | 137 | 20:00 | 129 | 11:00 | Madaripur | 137 | 09:00 | 129 | 22:00
| Aminbazar | 133 | 02:00 | 126 | 16:00 | Madartek | 136 | 05:00 | 124 | 12:00
| Amnura | 136 | 18:30 | 125 | 03:00 | Madunaghat | 140 | 18:00 | 131 | 12:00
| Ashuganj | 135 | 06:00 | 134 | 00:00 | Magura | 137 | 18:30 | 127 | 02:00
| Bagerhat | 135 | 18:00 | 128 | 02:00 | Mahasthangarh | 136 | 18:30 | 121 | 02:00
| Bakulia | 140 | 18:00 | 130 | 13:00 | Manikganj | 135 | 05:00 | 131 | 15:00
| Banani | 134 | 07:00 | 125 | 12:00 | Maniknagar | 133 | 05:00 | 125 | 12:00
| Bangabhaban | 133 | 07:00 | 125 | 12:00 | Matarbari | 129 | 18:30 | 112 | 13:00
| Barapukuria | 137 | 18:30 | 125 | 03:00 | Matuail | 131 | 04:00 | 124 | 15:00
| Barguna | 138 | 09:00 | 131 | 22:00 | Millgate | 134 | 05:00 | 125 | 11:00
| Barishal | 136 | 07:00 | 131 | 22:00 | Mirpur | 133 | 03:00 | 124 | 13:00
| Barishal-230 | 138 | 18:30 | 132 | 00:00 | Mithapukur | 135 | 18:00 | 115 | 02:00
| Baroaulia | 141 | 18:00 | 132 | 12:00 | Modern | 138 | 05:00 | 130 | 12:00
| Baroirhat | 135 | 18:30 | 125 | 13:00 | Mogbazar | 135 | 04:00 | 125 | 12:00
| Bashundhara | 134 | 05:00 | 123 | 15:00 | Mongla | 133 | 08:00 | 129 | 23:00
| BashundharaCement | 130 | 04:00 | 125 | 12:00 | Motijheel | 133 | 07:00 | 125 | 12:00
| Beanibazar | 133 | 07:00 | 126 | 22:00 | Munshiganj | 132 | 05:00 | 125 | 15:00
| Benapole | 135 | 18:30 | 126 | 02:00 | Mymensingh | 132 | 11:00 | 117 | 03:00
| Bhaluka | 131 | 02:00 | 113 | 03:00 | Naogaon | 133 | 19:00 | 118 | 02:00
| Bhandaria | 136 | 09:00 | 126 | 23:00 | Narail | 135 | 18:00 | 126 | 02:00
| Bhangura | 138 | 14:00 | 133 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:30 | 132 | 02:00 | Narshingdi | 126 | 00:00 | 119 | 11:00
| Bheramara(GK) | 139 | 18:30 | 132 | 03:00 | Natore | 136 | 18:00 | 126 | 02:00
| Bhulta | 123 | 00:00 | 116 | 15:00 | Nawabganj | 137 | 05:00 | 129 | 12:00
| Bog-Sherpur | 136 | 18:30 | 126 | 02:00 | Netrakona | 132 | 23:00 | 115 | 03:00
| Bogura | 138 | 18:30 | 126 | 02:00 | New | 133 | 07:00 | 125 | 12:00
| Bogura-230 | 138 | 18:30 | 127 | 04:00 | Niamatpur | 130 | 18:00 | 112 | 02:00
| Brahmanbaria | 133 | 07:00 | 128 | 14:00 | Noapara | 137 | 18:00 | 132 | 06:00
| Cantonment | 134 | 05:00 | 123 | 15:00 | Pabna | 136 | 18:00 | 130 | 02:00
| Chandpur | 139 | 18:00 | 131 | 02:00 | Palashbari | 134 | 18:00 | 118 | 01:00
| Chandraghona | 140 | 18:00 | 132 | 12:00 | Panchagarh | 132 | 19:00 | 109 | 04:00
| Chapai | 135 | 18:00 | 126 | 02:00 | Patuakhali | 137 | 18:00 | 133 | 00:00
| Charsaidpur | 133 | 04:00 | 127 | 12:00 | Payra | 138 | 09:00 | 135 | 01:00
| Chauddagram | 134 | 18:00 | 125 | 01:00 | PHP | 134 | 18:30 | 124 | 14:00
| Chhatak | 135 | 02:00 | 126 | 20:00 | Purbachal | 134 | 06:00 | 124 | 15:00
| Chowmuhani | 131 | 18:00 | 120 | 14:00 | Purbasadipur | 134 | 18:30 | 112 | 02:00
| Chuadanga | 134 | 18:30 | 121 | 03:00 | Rahim | 131 | 02:00 | 125 | 12:00
| Coxsbazar | 130 | 18:00 | 108 | 02:00 | Rajbari | 135 | 18:00 | 127 | 2:00
| Cumilla(N) | 135 | 20:00 | 130 | 00:00 | Rajendrapur | 138 | 07:00 | 130 | 17:00
| Cumilla(S) | 136 | 20:00 | 126 | 14:00 | Rajshahi | 134 | 18:00 | 126 | 02:00
| Daudkandi | 134 | 19:30 | 127 | 12:00 | Rajshahi-230 | 135 | 18:30 | 126 | 03:00
| Dhaka | 136 | 05:00 | 124 | 12:00 | Ramganj | 135 | 18:00 | 125 | 00:00
| Dhamrai | 132 | 06:00 | 122 | 15:00 | Rampur | 138 | 06:00 | 130 | 12:00
| Dhanmondi | 131 | 04:00 | 124 | 12:00 | Rampura | 133 | 04:00 | 127 | 09:00
| Dohazari | 136 | 05:00 | 125 | 13:00 | Rangamati | 139 | 18:00 | 131 | 13:00
| Faridpur | 135 | 18:00 | 128 | 02:00 | Rangpur | 133 | 18:30 | 121 | 03:00
| Fatullah | 132 | 05:00 | 125 | 12:00 | Ruppur | 135 | 16:00 | 131 | 02:00
| Fenchuganj | 138 | 07:00 | 133 | 22:00 | Saidpur | 134 | 18:00 | 110 | 02:00
| Feni | 135 | 18:00 | 126 | 01:00 | Satkhira | 135 | 18:30 | 126 | 02:00
| Ghorashal | 138 | 09:00 | 135 | 00:00 | Satmasjid | 134 | 05:00 | 124 | 15:00
| Goalpara | 138 | 18:30 | 132 | 02:00 | Savar | 134 | 05:00 | 125 | 15:00
| Gollamari | 136 | 18:00 | 130 | 03:00 | Shahjadpur | 141 | 18:00 | 135 | 00:00
| Gopalganj | 139 | 18:00 | 133 | 01:00 | Shahjibazar | 136 | 18:00 | 133 | 22:00
| Gopalganj_I | 139 | 18:30 | 136 | 08:00 | Shahmirpur | 140 | 18:00 | 132 | 12:00
| Gulshan | 135 | 06:00 | 124 | 12:00 | Shariatpur | 136 | 09:00 | 127 | 22:00
| Halishahar | 140 | 05:00 | 130 | 14:00 | Sherpur | 137 | 23:00 | 114 | 03:00
| Haripur | 131 | 02:00 | 125 | 12:00 | Shikalbaha | 140 | 18:00 | 132 | 13:00
| HaripurSBU | 139 | 00:00 | 126 | 12:00 | Shikalbaha-230 | 140 | 06:00 | 132 | 13:00
| Hasnabad | 134 | 01:00 | 129 | 11:00 | Shitalakhya | 136 | 04:00 | 127 | 15:00
| Hathazari | 139 | 18:00 | 132 | 14:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 137 | 18:30 | 132 | 02:00 | Shyampur | 131 | 07:00 | 124 | 12:00
| Jaldhaka | 132 | 18:00 | 110 | 02:00 | Shyampur-230 | 132 | 05:00 | 125 | 12:00
| Jamalpur | 138 | 18:30 | 120 | 03:00 | Siddhirganj | 132 | 07:00 | 125 | 12:00
| Jashore | 135 | 18:30 | 128 | 03:00 | Sirajganj | 136 | 18:30 | 128 | 03:00
| Jhenaidah | 138 | 18:30 | 129 | 04:00 | Sonargaon | 131 | 07:00 | 125 | 11:00
| Jhenaidah-230 | 138 | 18:30 | 129 | 02:00 | Sreemongol | 138 | 06:00 | 134 | 19:00
| Joydebpur | 140 | 05:00 | 135 | 17:00 | Srinagar | 137 | 05:00 | 128 | 12:00
| Joypurhat | 135 | 19:00 | 116 | 02:00 | SSM | 140 | 00:00 | 133 | 12:00
| Juldah | 141 | 18:00 | 132 | 12:00 | Sunamganj | 133 | 11:00 | 123 | 22:00
| Kabirpur | 139 | 06:00 | 122 | 12:00 | Sylhet | 136 | 02:00 | 130 | 19:00
| Kachua | 137 | 18:00 | 129 | 01:00 | Tangail | 135 | 01:00 | 130 | 17:00
| Kaliakoir | 140 | 05:00 | 134 | 10:00 | Thakurgaon | 134 | 19:00 | 105 | 02:00
| Kallyanpur | 133 | 05:00 | 126 | 12:00 | TK | 140 | 05:00 | 131 | 14:00
Page 7 of 7

## L-Curve
Date | 2022-07-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 602 | 8265 | 4716 | 12981 |  |  |  | QF-LDC-11
0:30 | 638 | 8245 | 4754.5 | 12999.5 | Date: | 2022-07-06
1:00 | 674 | 8225 | 4793 | 13018
1:30 | 548 | 8123 | 4758.5 | 12881.5
2:00 | 422 | 8021 | 4724 | 12745
2:30 | 382 | 7989.5 | 4664.5 | 12654 | [5 empty] | Gen. at Eve. Peak | 13614 | 13614 MW (21:00 )
3:00 | 342 | 7958 | 4605 | 12563 | [6 empty] | 21:00
3:30 | 353 | 7899.5 | 4566.5 | 12466 | [5 empty] | Gen. at Day Peak | 11838 | 11838 MW (12:00 )
4:00 | 364 | 7841 | 4528 | 12369 | [6 empty] | 12:00
4:30 | 375 | 7816.5 | 4504 | 12320.5 | [5 empty] | Highest Generation | 13614
5:00 | 386 | 7792 | 4480 | 12272 | [6 empty] | 21:00
5:30 | 345 | 7560 | 4297 | 11857
6:00 | 304 | 7328 | 4114 | 11442
6:30 | 276 | 7254.5 | 4058.5 | 11313
7:00 | 248 | 7181 | 4003 | 11184
7:30 | 295 | 7089 | 3899.5 | 10988.5
8:00 | 342 | 6997 | 3796 | 10793
8:30 | 361.5 | 7186.5 | 3813 | 10999.5
9:00 | 381 | 7376 | 3830 | 11206
9:30 | 402 | 7492.5 | 3864 | 11356.5
10:00 | 423 | 7609 | 3898 | 11507
10:30 | 442.5 | 7705 | 3910 | 11615
11:00 | 462 | 7801 | 3922 | 11723
11:30 | 477.5 | 7813 | 3967.5 | 11780.5
12:00 | 493 | 7825 | 4013 | 11838
12:30 | 590.5 | 7842 | 4030.5 | 11872.5
13:00 | 688 | 7859 | 4048 | 11907
13:30 | 714 | 7854.5 | 4136 | 11990.5
14:00 | 740 | 7850 | 4224 | 12074
14:30 | 827 | 7773.5 | 4271.5 | 12045
15:00 | 914 | 7697 | 4319 | 12016
15:30 | 758 | 7772.5 | 4178.5 | 11951
16:00 | 602 | 7848 | 4038 | 11886
16:30 | 673 | 7779 | 4079 | 11858
17:00 | 744 | 7710 | 4120 | 11830
17:30 | 754 | 7645.5 | 4061.5 | 11707
18:00 | 764 | 7581 | 4003 | 11584
18:30 | 742 | 7829.5 | 4115.5 | 11945
19:00 | 720 | 8078 | 4228 | 12306
19:30 | 616 | 8437 | 4669 | 13106
20:00 | 582 | 8496 | 4722 | 13218 |  |  |  | Executive Engineer
20:30 | 476 | 8649 | 4767 | 13416 |  |  |  | Network Operation Division
21:00 | 370 | 8802 | 4812 | 13614
21:30 | 358 | 8796 | 4793 | 13589
22:00 | 346 | 8790 | 4774 | 13564 |  |  |  |  | Page 6 of 7
22:30 | 398 | 8772.5 | 4786.5 | 13559
23:00 | 450 | 8755 | 4799 | 13554
23:30 | 526 | 8510 | 4757.5 | 13267.5
24:00 | 602 | 8265 | 4716 | 12981
13614 MW (21:00 )
11838 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-06 |  | Energy |  | 296457116
[13 empty] | 2022-07-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3753 | 846 | 1778 | 727 | 3726 | 860 | 124 | 450 | 787 | 148 | 0 | 0
0:30 | 3844.5 | 859 | 1832.5 | 785 | 3543 | 878.5 | 124.5 | 444 | 752.5 | 153 | 0 | 0 | Date: | 2022-07-06
1:00 | 3936 | 872 | 1887 | 843 | 3360 | 897 | 125 | 438 | 718 | 158 | 0 | 0
1:30 | 3934 | 880.5 | 1861 | 815 | 3277.5 | 884.5 | 125 | 439 | 725 | 157 | 0 | 0 | [8 empty] | Total Energy | 296.4571 | Total Energy Gen 296.457 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 296.457 MKWHr
2:00 | 3932 | 889 | 1835 | 787 | 3195 | 872 | 125 | 440 | 732 | 156 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3927.5 | 889.5 | 1858.5 | 615.5 | 3267 | 861 | 125 | 439.5 | 734 | 154 | 0 | 0 | [8 empty] | Energy Requirement | 296.4571
3:00 | 3923 | 890 | 1882 | 444 | 3339 | 850 | 125 | 439 | 736 | 152 | 0 | 0
3:30 | 3926.5 | 900 | 1898 | 339.5 | 3324.5 | 845 | 125 | 439 | 733.5 | 152 | 0 | 0 | [6 empty] | Shortage
4:00 | 3930 | 910 | 1914 | 235 | 3310 | 840 | 125 | 439 | 731 | 152 | 0 | 0
4:30 | 3921 | 909.5 | 1909 | 209.5 | 3309 | 845 | 125 | 439.5 | 731.5 | 139 | 0 | 0
5:00 | 3912 | 909 | 1904 | 184 | 3308 | 850 | 125 | 440 | 732 | 126 | 0 | 0
5:30 | 3927 | 909.5 | 1877.5 | 92 | 3230.5 | 795 | 124 | 413 | 563.5 | 130 | 2.5 | 0
6:00 | 3942 | 910 | 1851 | 0 | 3153 | 740 | 123 | 386 | 395 | 134 | 5 | 0
6:30 | 3955.5 | 909.5 | 1862 | 0 | 3075.5 | 740 | 122 | 333 | 329 | 131 | 19 | 0 |  |  |  |  | Coal
7:00 | 3969 | 909 | 1873 | 0 | 2998 | 740 | 121 | 280 | 263 | 128 | 33 | 0
7:30 | 3965.5 | 909.5 | 1845 | 0 | 2879 | 711 | 121 | 265 | 263.5 | 130 | 29 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3962 | 910 | 1817 | 0 | 2760 | 682 | 121 | 250 | 264 | 132 | 25 | 0
8:30 | 3954.5 | 910 | 1816 | 0 | 2915 | 696 | 120 | 250 | 297.5 | 132 | 38.5 | 0
9:00 | 3947 | 910 | 1815 | 0 | 3070 | 710 | 119 | 250 | 331 | 132 | 52 | 0
9:30 | 3937.5 | 909.5 | 1798 | 43 | 3179.5 | 700 | 120 | 260 | 331 | 135 | 73 | 0
10:00 | 3928 | 909 | 1781 | 86 | 3289 | 690 | 121 | 270 | 331 | 138 | 94 | 0
10:30 | 3971 | 887 | 1745 | 164 | 3270.5 | 690 | 121 | 315 | 342 | 140 | 110.5 | 0
11:00 | 4014 | 865 | 1709 | 242 | 3252 | 690 | 121 | 360 | 353 | 142 | 127 | 0
11:30 | 4017.5 | 864.5 | 1710 | 312 | 3217.5 | 695 | 122 | 377.5 | 372 | 145 | 118.5 | 0
12:00 | 4021 | 864 | 1711 | 382 | 3183 | 700 | 123 | 395 | 391 | 148 | 110 | 0
12:30 | 3958.5 | 864.5 | 1684 | 482 | 3174 | 710 | 123 | 407 | 418 | 150 | 103 | 0
13:00 | 3896 | 865 | 1657 | 582 | 3165 | 720 | 123 | 419 | 445 | 152 | 96 | 0
13:30 | 3896 | 865 | 1657 | 582 | 3165 | 720 | 123 | 419 | 445 | 152 | 96 | 0
14:00 | 3896 | 865 | 1657 | 582 | 3165 | 720 | 123 | 419 | 445 | 152 | 96 | 0
14:30 | 3719.5 | 864.5 | 1654.5 | 697 | 3211.5 | 755 | 125 | 415.5 | 482.5 | 158 | 89.5 | 0
15:00 | 3543 | 864 | 1652 | 812 | 3258 | 790 | 127 | 412 | 520 | 164 | 83 | 0
15:30 | 3579 | 710 | 1658.5 | 829.5 | 3247.5 | 805 | 126.5 | 415 | 557.5 | 163 | 70.5 | 0
16:00 | 3615 | 556 | 1665 | 847 | 3237 | 820 | 126 | 418 | 595 | 162 | 58 | 0
16:30 | 3578 | 710.5 | 1653 | 608.5 | 3317 | 805 | 125.5 | 420 | 627.5 | 158 | 51.5 | 0
17:00 | 3578 | 865 | 1641 | 370 | 3397 | 790 | 125 | 422 | 660 | 154 | 45 | 0
17:30 | 3527 | 858.5 | 1618 | 224.5 | 3560.5 | 760 | 125 | 388.5 | 649 | 149 | 30.5 | 0
18:00 | 3476 | 852 | 1595 | 79 | 3724 | 730 | 125 | 355 | 638 | 144 | 16 | 0
18:30 | 3586 | 845.5 | 1640.5 | 184.5 | 3817 | 735 | 103 | 350 | 663.5 | 157 | 8 | 0
19:00 | 3696 | 839 | 1686 | 290 | 3910 | 740 | 81 | 345 | 689 | 170 | 0 | 0
19:30 | 3746 | 840 | 1743 | 712 | 3996 | 840 | 91 | 407 | 771 | 162 | 0 | 0
20:00 | 3729 | 840 | 1766 | 735 | 4019 | 850 | 123 | 415 | 797 | 154 | 0 | 0
20:30 | 3780 | 840 | 1769 | 805 | 4065.5 | 861 | 123.5 | 427.5 | 800.5 | 159 | 0 | 0
21:00 | 3831 | 840 | 1772 | 875 | 4112 | 872 | 124 | 440 | 804 | 164 | 0 | 250
21:30 | 3831 | 840 | 1766.5 | 871.5 | 4106.5 | 872 | 123.5 | 442.5 | 789.5 | 164 | 0 | 0
22:00 | 3831 | 840 | 1761 | 868 | 4101 | 872 | 123 | 445 | 775 | 164 | 0 | 0
22:30 | 3814.5 | 840 | 1775 | 866 | 4095.5 | 872 | 123 | 445.5 | 778.5 | 165 | 0 | 0
23:00 | 3798 | 840 | 1789 | 864 | 4090 | 872 | 123 | 446 | 782 | 166 | 0 | 0
23:30 | 3775.5 | 843 | 1783.5 | 795.5 | 3908 | 866 | 123.5 | 448 | 784.5 | 157 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31° C
24:00 | 3753 | 846 | 1778 | 727 | 3726 | 860 | 124 | 450 | 787 | 148 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 296.457 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 296.457 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-07-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 90 | 90 | 90 | 88 | 86 | 86 | 84 | 86 | 86 | 88 | 88 | 88 | 92 | 91 | 90 | 90 |  | 46 | 56 | 88 | 89 | 88 | 88 | 89 | 2077930
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 |  | 12 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 22 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 556860
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 3 | 5 | 16 | 18 | 10 | 4 | 18 | 0 | [10 empty] | 0 | 76680
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 60 | 60 | 60 | 60 | 60 | 30 | [11 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 658561
12 | Hathazari 100 MW peaking PP | 25 | 26 | 26 | 26 | 26 | [7 empty] | 0 | 2 | 9 | 26 | 26 | 35 |  | 43 | 43 | 51 | 51 | 51 | 51 | 50 | 504480
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 17 | 51 | 105 | 105 | 87 | 87 | 87 | 87 | 87 | 87 | 94 |  | 105 | 105 | 105 | 105 | 105 | 105 | 87 | 2294145
| Daudkandi 200 MW PP (B.Trac) | 195 | 195 | 100 | 50 | 50 |  |  |  |  | 0 | 30 | 80 | 190 | 191 | 191 | 192 | 100 | 10 |  | 100 | 195 | 195 | 195 | 195 | 195 | 195 | 2587008
14 | Titas 50 MW Peaking PP | 47 | 47 | 48 | 48 | 48 | [7 empty] | 27 | 40 | 40 | 40 | 41 | 36 |  | 40 | 40 | 40 | 40 | 41 | 39 | 41 | 692976
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 187 | 187 | 187 | 187 | 186 | 186 | 244 | 252 | 238 | 231 | 232 | 232 | 245 | 245 | 244 | 244 | 244 | 242 |  | 243 | 243 | 223 | 224 | 217 | 218 | 218 | 5415875
18 | Kodda 300 MW PP Unit-2 (Summit) | 250 | 250 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 248 | 248 | 238 |  | 247 | 245 | 248 | 248 | 248 | 235 | 228 | 6051925
19 | Ashuganj 195MW PP (APSCL-United) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 45 | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 1137454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7157218
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 31 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 38 | 25 |  | 35 | 35 | 35 | 39 | 39 | 39 | 39 | 819504
33 | Ashuganj 225 MW CCPP | 210 | 209 | 209 | 210 | 213 | 210 | 214 | 212 | 196 | 192 | 177 | 198 | 143 | 119 | 133 | 207 | 211 | 180 |  | 210 | 209 | 210 | 209 | 207 | 208 | 211 | 4714000
34 | Ashuganj 450 MW CCPP(South) | 355 | 355 | 350 | 355 | 355 | 355 | 355 | 345 | 360 | 295 | 275 | 280 | 280 | 280 | 220 | 250 | 250 | 270 |  | 270 | 275 | 275 | 315 | 335 | 330 | 315 | 7865900
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 330 | 310 | 330 | 275 | 275 | 280 | 280 | 280 | 280 | 280 | 295 | 280 | 280 |  | 280 | 280 | 280 | 325 | 345 | 320 | 310 | 7561800
| Ashuganj 420 MW CCPP(East) | [5 empty] | 0 | 27 | 130 | 193 | 243 | 287 | 293 | 240 | 124 | 0 | [10 empty] | 0 | 1522900
35 | Ashuganj 55 MW PP (Precision) | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 49 | 10 | 10 | 10 | 10 | 25 | 40 |  | 50 | 50 | 53 | 52 | 52 | 52 | 53 | 1066560
36 | Chandpur 150 MW CCPP | 85 | 85 | 86 | 86 | 84 | 85 | 85 | 85 | 84 | 84 | 84 | 84 | 70 | 70 | 70 | 70 | 78 | 84 |  | 85 | 85 | 85 | 84 | 84 | 84 | 84 | 1925920
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 200 | 200 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 190 | 190 | 170 | 170 | 180 | 180 | 200 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4210450
41 | Haripur 360MW CCPP(HPL) | 172 | 182 | 187 | 202 | 211 | 222 | 208 | 197 | 192 | 165 | 153 | 122 | 121 | 138 | 150 | 172 | 176 | 176 |  | 177 | 177 | 187 | 202 | 186 | 181 | 182 | 4274000
42 | RPCL 210MW CCPP | 117 | 108 | 108 | 110 | 109 | 109 | 89 | 88 | 81 | 78 | 78 | 69 | 69 | 70 | 69 | 71 | 71 | 71 |  | 100 | 104 | 104 | 104 | 103 | 105 | 105 | 2129280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 4 | 9 | 21 | 34 | 19 | 11 | 27 | 15 | 14 | 17 | 6 |  | 0 | [6 empty] | 185200
44 | Fenchugonj CCPP Phase-1 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 44 | 43 | 44 | 43 | 43 |  | 44 | 44 | 43 | 43 | 43 | 44 | 44 | 886000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 988296
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 65 | 40 | 64 | 63 | 64 | 63 | 62 | 62 | 61 | 62 | 63 | 63 |  | 64 | 63 | 63 | 63 | 40 | 40 | 40 | 1392096
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 81 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 65 | 65 | 65 | 2016960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3293450
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | [9 empty] | 140400
53 | Sylhet 10MW PP (Desh) | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 221940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | [8 empty] | 0 | 91200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 16 | 18 | 19 | 19 | 19 | 20 | 22 | 23 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 388202
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 260 | 270 | 290 | 280 | 260 | 295 | 270 | 290 | 300 | 280 | 290 | 310 | 290 | 300 | 290 | 265 | 270 |  | 270 | 300 | 310 | 280 | 315 | 310 | 280 | 7088500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 384 | 400 | 400 | 360 | 400 | 400 | 400 | 400 | 398 | 400 | 380 | 400 | 400 | 360 |  | 400 | 400 | 400 | 400 | 395 | 400 | 400 | 9458100
58 | Nababganj 55 MW PP (Southern power ) | 55 |  | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 946990
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 594240
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 450336
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 454572
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 15 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 342864
63 | Impoprt (Tripura) | 158 | 156 | 152 | 152 | 126 | 134 | 128 | 132 | 132 | 138 | 142 | 148 | 152 | 166 | 164 | 162 | 154 | 144 |  | 170 | 162 | 154 | 164 | 164 | 166 | 148 | 3607680
64 | Malancha, Ctg. EPZ (United) | 29 | 27 | 29 | 29 | 29 | 29 | 25 | 7 | 2 | 3 | 2 | 2 | 4 | 3 | 3 | 2 | 6 | 2 |  | 13 | 17 | 21 | 22 | 30 | 30 | 30 | 385920
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 0 | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 379908
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250200
67 | Jangalia 33MW PP (Summit) | 16 | 21 | 25 | 32 | 30 | 25 | 23 | 16 | [7 empty] | 0 | 8 | 8 |  | 18 | 18 | 16 | 16 | 16 | 16 | 17 | 299500
68 | Cumilla 25 MW PP (Summit) | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 10 | 10 | 10 | 12 | 12 | 12 |  | 12 | 20 | 20 | 20 | 20 | 20 | 20 | 424160
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 20 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 18 | 28 | 28 | 28 | 28 | 28 | 28 | 637200
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805900
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 25 | 25 | 25 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 28 | 28 | 30 | 30 | 651900
73 | Ghorashal 108MW PP (Regent) | 85 | 86 | 82 | 82 | 82 | 79 | 82 | 82 | 79 | 79 | 82 | 82 | 84 | 86 | 86 | 83 | 86 | 83 |  | 87 | 87 | 86 | 88 | 88 | 85 | 89 | 1983227
| Feni Lanka Power | [16 empty] | 17 | 52 |  | 52 | 52 | 52 | 114 | 114 | 114 | 34 | 507300
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 15 | 9 | 10 | 9 | 9 | 9 | 9 | 230160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 72 | 137 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3875040
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 967680
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 42 | 24 | 24 | 24 | 34 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 |  | 48 | 51 | 51 | 51 | 42 | 42 | 42 | 974400
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 82 | 48 | 48 | 115 | 115 | 115 | 115 | 115 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2854080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 0 | 22 |  | 25 | 25 | 25 | 25 | 33 | 33 | 0 | 160968
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2468400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 0 | 0 | 0 | [8 empty] | 29279
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1366128
| Karnaphuli Power Ltd. | 89 | 92 | 106 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 106 | 92 | 89 | 92 | 92 | 92 | 105 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 2489010
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 32 | 31 | 32 | 31 | 32 | 32 | 32 | 31 | 31 | 32 | 26 | 26 | 27 | 32 | 32 | 29 | 27 | 31 |  | 31 | 31 | 31 | 31 | 30 | 24 | 31 | 736320
| Meghnaghat 104 MW PP (OPCL) | 87 | 75 | 91 | 91 | 91 | 91 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2510400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1224600
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | [8 empty] | 0 | 99144
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1227807
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 94 | 85 | 85 | 94 | 85 | 85 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2128176
95 | Patenga 50MW PP (Baraka) | 45 | 44 | 45 | 44 | 44 | 45 | 45 | 44 | 44 | 43 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 38 | 42 | 44 | 44 | 44 | 996480
96 | Chattogram 108 MW PP (ECPV) | 88 | 90 | 91 | 88 | 86 | 56 | 11 | 11 | 57 | 85 | 83 | 80 | 84 | 78 | 78 | 78 | 72 | 85 |  | 86 | 86 | 86 | 86 | 86 | 85 | 93 | 1872840
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1310027
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329668
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 85 | 85 | 85 | 85 |  | 85 | 110 | 110 | 110 | 90 | 90 | 90 | 2478355
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 8600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1213200
104 | Keranigonj 300 MW PP (APR) | 302 | 254 | 154 | 54 | 53 |  |  |  |  | 35 | 131 | 221 | 300 | 255 | 300 | 300 | 175 | 14 |  | 56 | 187 | 186 | 303 | 303 | 303 | 227 | 3951226
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 0
106 | Mymensingh 200 MW PP (United) | 114 | 115 | 115 | 116 | 116 | 116 | 115 | 115 | 115 | 115 | 114 | 114 | 114 | 114 | 115 | 115 | 123 | 169 |  | 169 | 187 | 188 | 200 | 200 | 200 | 115 | 3156000
112 | Aurahati 100MW PP (Aggreko) | 80 | 81 | 80 | 81 | 81 |  |  |  |  | 51 | 81 | 81 | 81 | 83 | 83 | 82 | 25 | 25 |  | 97 | 98 | 98 | 100 | 100 | 100 | 39 | 1502416
114 | Kodda 149 MW PP Unit-1 (Summit) | 100 | 96 | 96 | 95 | 96 | 102 | 132 | 125 | 115 | 113 | 113 | 114 | 114 | 126 | 131 | 121 | 114 | 114 |  | 124 | 124 | 131 | 131 | 132 | 133 | 133 | 2832190
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 76 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 76 | 90 | 76 | 90 | 90 | 90 | 90 | 90 | 76 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2036160
116 | Chandpur 200MW (Desh energy) | 116 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 72 | 81 | 112 | 120 | 112 | 120 | 120 | 155 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2962560
117 | Ashuganj 150MW PP (Midland) | 125 | 133 | 125 | 132 | 137 | 138 | 135 | 125 | 138 | 138 | 138 | 140 | 133 | 130 | 137 | 132 | 133 | 133 |  | 127 | 133 | 133 | 137 | 138 | 138 | 145 | 3233381
118 | Bibiyana-III 400 MW CCPP | 403 | 402 | 403 | 402 | 402 | 401 | 403 | 398 | 370 | 402 | 402 | 402 | 391 | 403 | 404 | 403 | 402 | 365 |  | 379 | 403 | 409 | 409 | 404 | 403 | 402 | 9534000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 58 | 58 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 60 | 1755600
| Anwara 300 MW PP (United) | 174 | 177 | 177 | 178 | 178 | 100 | 50 | 15 | 100 | 189 | 195 | 189 | 190 | 190 | 191 | 195 | 245 | 244 |  | 270 | 270 | 275 | 290 | 290 | 290 | 285 | 4641818
| Juldah unit-2 (Acorn) | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 90 | 90 | 100 | 90 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2302080
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 90 | 72 | 90 | 90 | 90 | 90 | 102 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2456400
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 551160
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 5 | 8 | 11 | 27 | 24 | 35 | 17 | 33 | 10 | 10 | 2 | [8 empty] | 217697
| Chandpur 115(Doreen) | 109 | 116 | 114 | 115 | 116 | 116 | 116 | 115 | 116 | 116 | 116 | 101 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2773440
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1338120
120 | Eastern Zone Total | 8225 | 8021 | 7958 | 7841 | 7792 | 7328 | 7181 | 6997 | 7376 | 7609 | 7801 | 7825 | 7859 | 7850 | 7697 | 7848 | 7710 | 7581 |  | 8078 | 8437 | 8496 | 8802 | 8790 | 8755 | 8265 | 190427177
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 49 | 49 | 49 | 49 | 49 | 49 | 26 | 538560
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | [9 empty] | 17 | 23 | 26 | 29 |  | 12 | 24 | 42 | 35 | 28 | 32 | 32 | 360000
| Khulna 225 MW CCPP | 207 | 207 | 207 | 207 | 207 | 189 | 150 | 120 | 120 | 140 | 208 | 205 | 206 | 206 | 203 | 205 | 205 | 205 |  | 205 | 205 | 205 | 205 | 205 | 206 | 208 | 4701120
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 73 | 75 | 75 | 75 | 75 | 64 | 75 | 74 |  | 74 | 74 | 74 | 74 | 75 | 75 | 75 | 1948800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 21 | 10 | 22 | 36 | 34 | 43 | 32 | 22 | 23 | 29 | 16 | 7 | [8 empty] | 309600
131
132 | United Payra Power Ltd. | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 46 | 54 | 54 | 614400
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 208 | 222 | 222 | 216 | 216 | 223 | 223 | 216 | 220 | 222 | 229 | 220 | 221 | 209 | 219 | 220 | 173 |  | 223 | 225 | 222 | 225 | 225 | 224 | 223 | 5236473
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 44 | 48 | 48 | 48 | 48 | 48 | 742842
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 20 | 20 | 20 | 87 | 85 | 86 | 86 | 85 | 85 | 85 | 87 |  | 87 | 87 | 87 | 87 | 86 | 87 | 87 | 1707116
140 | Bhola 33 MW PP (Venture) | 31 | 29 | 29 | 27 | 23 | 20 | 21 | 19 | 19 | 20 | 20 | 20 | 23 | 24 | 24 | 24 | 20 | 18 |  | 27 | 28 | 27 | 32 | 33 | 33 | 33 | 593090
141 | Noapara 100 MW PP (Bangla Trac) | 98 | 95 | 10 | [9 empty] | 1 | 38 | 79 | 95 | 60 | 20 |  | 25 | 97 | 98 | 98 | 98 | 96 | 97 | 1101120
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 260625
143 | Gopalganj 100 MW Peaking PP | 41 | 41 | 41 | 36 | 36 | [12 empty] | 36 |  | 50 | 60 | 60 | 60 | 40 | 40 | 40 | 486272
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 89 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 100 | 105 | 105 | 89 | 2490768
146 | Bheramara HVDC | 872 | 889 | 890 | 910 | 909 | 910 | 909 | 910 | 910 | 909 | 865 | 864 | 865 | 865 | 864 | 556 | 865 | 852 |  | 839 | 840 | 840 | 840 | 840 | 840 | 846 | 20883636
147 | Bheramara 410 MW CCPP | 280 | 280 | 270 | 270 | 270 | 265 | 260 | 260 | 245 | 250 | 240 | 235 | 235 | 245 | 225 | 175 | 160 | 155 |  | 245 | 245 | 245 | 250 | 250 | 250 | 250 | 6020640
148 | Payra 1320 MW | 622 | 622 | 600 | 590 | 600 | 520 | 520 | 460 | 460 | 440 | 440 | 450 | 470 | 490 | 540 | 570 | 540 | 480 |  | 490 | 590 | 600 | 622 | 622 | 622 | 610 | 14075500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 275 | 250 | 250 | 250 | 250 | 220 | 220 | 222 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6036000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | [11 empty] | 34 | 34 |  | 34 | 32 | 34 | 34 | 34 | 34 | 34 | 368112
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 24360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 148 | 147 | 146 | 148 | 150 | 150 | 148 | 147 | 146 | 146 | 144 | 143 | 129 | 114 | 103 | 93 | 93 |  | 95 | 98 | 97 | 101 | 102 | 86 | 47 | 3092600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 216 | 218 | 217 | 217 | 218 | 197 | 130 | 130 | 130 | 130 | 152 | 190 | 213 | 215 | 209 | 213 | 217 | 150 |  | 140 | 202 | 210 | 220 | 216 | 216 | 218 | 4833173
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 211 | 211 | 212 | 212 | 212 | 212 | 210 | 210 | 209 | 211 | 207 | 202 | 196 | 181 | 173 | 162 | 144 | 142 |  | 141 | 139 | 139 | 139 | 139 | 142 | 158 | 4635982
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 415 | 414 | 414 | 376 | 370 | 370 | 370 | 414 | 370 | 414 | 414 | 414 | 414 | 390 | 374 | 363 |  | 367 | 362 | 363 | 374 | 376 | 400 | 414 | 9467636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 10 | 21 | 25 | 25 | 25 | [7 empty] | 4 | 4 | 4 | 18 | 30 | 32 |  | 33 | 33 | 30 | 26 | 26 | 31 | 33 | 348751
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 20 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 215936
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 8 | 34 | 34 | 34 | 33 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 717968
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | [9 empty] | 24 | 24 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 356753
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | [10 empty] | 34 | 37 | 37 |  | 37 | 37 | 29 | 37 | 37 | 37 | 37 | 478350
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 16 | 34 | 34 | 34 | 34 | 34 | 0 | 159610
170 | Chapainawabganj 100 MW Peaking PP | 85 | 85 | 85 | 85 | 85 | 86 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 85 | 85 | 85 |  | 85 | 85 | 86 | 86 | 87 | 87 | 87 | 2045304
171 | Baghabari 200 MW PP (Paramount) | 168 | 162 | 100 | 50 | [8 empty] | 10 | 125 | 159 | 178 | 10 | 10 |  | 12 | 135 | 158 | 179 | 172 | 170 | 169 | 2005830
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2273952
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2736000
173 | Rangpur 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 15 | 15 | 15 | 15 | 129000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 24000
176 | Rangpur 113 MW PP (Confidence) | 70 | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 63 | 71 | 96 |  | 96 | 96 | 97 | 98 | 98 | 98 | 98 | 1863744
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 4 | 6 | 6 | 6 | 6 | 5 | 3 | 2 | 1 | [8 empty] | 41372
178 | Energypac Power Venture Thakurgaon Ltd. | 52 |  | 90 | 72 | 72 | 72 | 72 | 52 | 52 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 108 |  | 112 | 112 | 112 | 113 | 115 | 115 | 115 | 1608384
178