## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-09 | Saturday
|  |  | Date (day): | 2022-07-09 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12824.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14230 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-08 | 2022-07-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 300 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 92 | 90 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 337 | 330 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 60 | 87 | 85 | 87 |  | 13 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 15 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 91 | 92 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 336 | 330 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 94 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 44 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 30
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 49 | 40 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 210 | 212 | 285 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 105 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 50 | 0 | 50 | 50 |  | Fuel Shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 133 | 130 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 17 | 72 | 90 |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2408 | 3037 | 3105 | 3469 | 1393 | 986
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 44 | 44 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 124 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 87 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 50 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 55 | 55 | 55 | 55 | 45 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 42 | 30 | 40
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 79 | 80 | 80 |  | 28 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 262 | 200 | 265 |  | 35 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 36 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 65 | 95 | 75 | 95 |  | 25 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 72 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 815 | 1381 | 1330 | 1419 | 356 | 639
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 208 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 325 | 320 | 325 | 35 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 325 | 320 | 325 | 35 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 217 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 36 | 35 | 36 |  | 9 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 50 | 52 | 50 | 52
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 107 | 137 | 135 | 137
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 40 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 84 | 84 | 84 | 84 |  | 79 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 154 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 20 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 39 | 8 | 40 |  | 12 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 98 | 17 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 48 | 40 | 48 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 72 | 36 | 72 | 43 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1765 | 2003 | 1918 | 2222 | 539 | 140
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 206 | 186 | 170 | 190
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 20 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 188 | 115 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 60 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 20 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 447 | 535 | 438.6 | 549 | 0 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 33 | 33 | 32 | 33 |  | 37 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 45 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 60 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 65 | 86 | 80 | 86 |  |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 140 | 130 | 140 |  | 89 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 24 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 401 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1501 | 1586 | 1593 | 1645 | 118 | 657
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 489 | 492 | 501 | 501
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 41 | 16 | 49 | 66 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 203 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 315 | 380 | 300 | 410
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 8 | 8 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 90 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 50 | 55 |  | 50 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 89 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1074 | 1336 | 1425 | 1543 | 98 | 118
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 32 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 32 | 20 | 32 |  | 8 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 87 | 85 | 87 | 107 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 622 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 221 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 90 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 728 | 994 | 996 | 1161 | 107 | 8
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 16 | 32 |  | 39 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 214 | 200 | 214
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 140 | 220 | 220 |  |  | Running by HSD
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 168 | 211 | 180 | 211
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 392 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36 |  | 14 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 85 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 170 | 180 |  | 20 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 94 | 94 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1003 | 1505 | 1613 | 1787 | 171 | 160
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 97 | 70 | 97 |  | 16 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 72 | 111 | 113 | 113
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 398 | 408 | 406 | 435 | 244 | 16
|  | Total |  |  |  |  | 22678 | 21396 | 10139 | 12785 | 12824.6 | 14230 | 3026 | 2732
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9646.2613 | 12163.67 | 12201.3455 | 13538.4454
| A. |  | 2022-07-08 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 13071 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9692 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12785 | MW
| 3 | Day peak Generation : |  |  | 10139 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12163.67 | MW
| 4 | Evening peak Generation : |  |  | 12785 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 272.9578 | MKWHr | By Solar | 1.2689 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 145.4647 | MKWHr |  | By Oil: | 89.347 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 18.8923 | MKWHr |  | By Hydro: | 2.8918 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3026 | MW | Dhaka | 3618.32 | 3618.32 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2732 | MW | Chittagong | 1200.5 | 1200.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5758 | MW | Khulna | 1651 | 1651 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1096.25 | MMCFD |  |  | Rajshahi | 1451 | 1451 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163344329.36 | ii) Oil : | Taka | 1249838472.09 | Comilla | 1258 | 1258 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 149758135 | Total | Taka | 1562940936.45 | Mymensingh | 1152 | 1152 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.1345 | MKWHr. | Sylhet | 534 | 534 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -376 | MW (E to W) at | 21:00 | hrs | Barisal | 387.85 | 387.85 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -376 | MW at | 21:00 | hrs | Rangpur | 911 | 911 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34° C |  |  | Total | 12163.67 | 12163.67 |  | 0
| B. |  | 2022-07-09 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14230 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1730 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 261.0338 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9066 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8233 | MKWHr. | ii) HVDC Flow at Peak Time |  | 492 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2698 | MKWHr. | iii) Maximum HVDC Flow : |  | 492 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.87 |  | (b) Today: | 90.15 |  | (c) Rule Curve: |  | 85.28
.

## YesterdayGen
2022-07-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 317 |  | 0 | 225 | 0 | 31 | 0 | 50 | 333 | 0 | 0 | 8 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 32 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 50 | 51 | 55 | 86 | 44 | 21 | 37 | 0 | 0 | 0 | 325 | 325 | 207 | 92 | 84 | 35 | 50 | 0 | 43 | 0 | 49 | 8 | 22 | 8 | 33 | 20 | 158 | 145 | 0 | 20 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 51 | 65 | 0 | 140 | 0 | 0 | 10 | 310 | 16 | 11 | 196 | 268 | 306 | 100 | 116 | 20 | 149 | 0 | 90 | 200 | 132 | 402 | 60 | 105 | 105 | 0 | 174 | 54 | 97 | 17 | 8 | 90 | 400 | 104 | 0 | 96 | 108 | 0 | 35 | 0 | 45 | 55 | 0 |  | 483 | 0 | 290 | 0 | 16 | 206 | 0 | 0 | 30 | 40 | 8 | 87 | 33 | 48 | 0 | 0 | 0 | 24 | 23 | 88 | 0 | 34 | 32 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 180 | 0 | 0 | 212 | 0 | 97 | 174 | 0 | 414 | 75 | 169 | 94 | 105 | 102 | 0 | 0 | 113 | 622 | 224 | 0 | 54 | 0 | 0 | 108 | 0 | 0 |  | 8543 | 4528 | 13071 | 4144 | 483 | 2009 | 888 | 3414 | 872 | 114 | 433 | 768 | 158 | 0 | 0 | 89.82
2:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 328 |  | 0 | 225 | 0 | 31 | 0 | 55 | 334 | 0 | 0 | 8 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 50 | 51 | 55 | 85 | 45 | 21 | 37 | 0 | 0 | 0 | 310 | 305 | 208 | 92 | 84 | 36 | 52 | 0 | 43 | 0 | 49 | 8 | 22 | 8 | 25 | 20 | 154 | 147 | 0 | 20 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 51 | 65 | 0 | 140 | 0 | 0 | 10 | 310 | 0 | 11 | 195 | 256 | 227 | 100 | 116 | 0 | 141 | 0 | 90 | 200 | 127 | 402 | 60 | 105 | 105 | 0 | 176 | 54 | 99 | 17 | 7 | 90 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 483 | 0 | 290 | 0 | 16 | 207 | 0 | 0 | 30 | 20 | 8 | 87 | 31 | 32 | 0 | 0 | 0 | 24 | 23 | 88 | 0 | 34 | 32 | 8 | 37 | 22 | 0 | 11 | 0 | 0 | 245 | 15 | 0 | 176 | 0 | 0 | 214 | 0 | 70 | 168 | 0 | 414 | 75 | 120 | 94 | 105 | 70 | 0 | 0 | 113 | 622 | 224 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8300 | 4333 | 12633 | 4081 | 483 | 2020 | 712 | 3226 | 867 | 118 | 436 | 750 | 154 | 0 | 0 | 89.83
3:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 327 |  | 0 | 225 | 0 | 31 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 50 | 51 | 55 | 86 | 45 | 21 | 37 | 0 | 0 | 0 | 340 | 340 | 206 | 92 | 84 | 36 | 51 | 0 | 43 | 0 | 49 | 8 | 22 | 8 | 33 | 20 | 152 | 157 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 51 | 65 | 0 | 140 | 0 | 0 | 10 | 290 | 0 | 11 | 140 | 256 | 174 | 100 | 115 | 0 | 131 | 0 | 90 | 200 | 133 | 405 | 59 | 105 | 105 | 0 | 176 | 54 | 94 | 17 | 9 | 90 | 400 | 104 | 0 | 17 | 96 | 0 | 35 | 0 | 35 | 55 | 0 |  | 483 | 0 | 290 | 0 | 16 | 207 | 0 | 0 | 30 | 20 | 8 | 88 | 31 | 16 | 0 | 0 | 0 | 24 | 23 | 88 | 0 | 34 | 32 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 175 | 0 | 0 | 215 | 0 | 0 | 169 | 0 | 414 | 75 | 40 | 94 | 105 | 70 | 0 | 0 | 113 | 600 | 225 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8235 | 4152 | 12387 | 4169 | 483 | 1999 | 454 | 3190 | 850 | 118 | 437 | 750 | 152 | 0 | 0 | 89.84
4:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 333 |  | 0 | 225 | 0 | 31 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 50 | 51 | 55 | 78 | 45 | 21 | 37 | 0 | 0 | 0 | 310 | 305 | 208 | 92 | 84 | 36 | 51 | 0 | 43 | 0 | 49 | 8 | 22 | 8 | 33 | 20 | 152 | 158 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 52 | 65 | 0 | 140 | 0 | 0 | 9 | 300 | 5 | 11 | 60 | 259 | 83 | 70 | 115 | 0 | 132 | 0 | 90 | 200 | 132 | 402 | 59 | 105 | 105 | 0 | 176 | 54 | 101 | 17 | 9 | 90 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 482 | 0 | 290 | 0 | 16 | 207 | 0 | 0 | 30 | 0 | 8 | 88 | 30 | 16 | 0 | 0 | 0 | 24 | 25 | 88 | 0 | 34 | 32 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 175 | 0 | 0 | 215 | 0 | 0 | 170 | 0 | 414 | 75 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 600 | 225 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8005 | 4093 | 12098 | 4111 | 482 | 2013 | 213 | 3205 | 850 | 118 | 437 | 732 | 152 | 0 | 0 | 89.85
5:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 333 |  | 0 | 225 | 0 | 31 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 43 | 51 | 55 | 85 | 45 | 21 | 37 | 0 | 0 | 0 | 300 | 280 | 210 | 92 | 84 | 36 | 52 | 0 | 51 | 0 | 49 | 8 | 22 | 8 | 33 | 20 | 138 | 160 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 52 | 65 | 0 | 140 | 0 | 0 | 9 | 280 | 16 | 11 | 20 | 260 | 23 | 25 | 116 | 0 | 132 | 0 | 90 | 200 | 132 | 401 | 59 | 105 | 105 | 0 | 191 | 54 | 110 | 17 | 9 | 90 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 486 | 0 | 290 | 0 | 16 | 208 | 0 | 0 | 30 | 0 | 8 | 87 | 28 | 16 | 0 | 0 | 0 | 24 | 25 | 88 | 0 | 34 | 16 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 174 | 0 | 0 | 217 | 0 | 0 | 169 | 0 | 414 | 74 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 570 | 226 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7838 | 4049 | 11887 | 4087 | 486 | 2001 | 68 | 3235 | 820 | 118 | 440 | 711 | 138 | 0 | 0 | 89.86
6:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 332 |  | 0 | 225 | 0 | 31 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 28 | 33 | 8 | 25 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 55 | 63 | 45 | 21 | 38 | 0 | 0 | 0 | 260 | 265 | 208 | 92 | 84 | 36 | 51 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 128 | 160 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 9 | 270 | 16 | 11 | 0 | 260 | 21 | 25 | 116 | 0 | 122 | 1 | 90 | 200 | 133 | 353 | 59 | 90 | 68 | 0 | 100 | 37 | 110 | 17 | 9 | 90 | 400 | 104 | 3 | 17 | 108 | 0 | 24 | 1 | 36 | 36 | 0 |  | 487 | 0 | 290 | 0 | 16 | 170 | 0 | 0 | 0 | 0 | 8 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 8 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 15 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 380 | 74 | 0 | 94 | 105 | 70 | 0 | 0 | 113 | 520 | 200 | 0 | 0 | 0 | 3 | 108 | 0 | 0 |  | 7200 | 3653 | 10853 | 3947 | 487 | 1926 | 46 | 2931 | 770 | 116 | 385 | 309 | 128 | 8 | 0 | 89.87
7:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 337 |  | 0 | 225 | 0 | 32 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 25 | 24 | 33 | 8 | 25 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 63 | 45 | 21 | 38 | 0 | 0 | 0 | 270 | 265 | 181 | 55 | 85 | 36 | 52 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 116 | 160 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 75 | 0 | 40 | 65 | 0 | 140 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 233 | 0 | 0 | 116 | 0 | 108 | 4 | 90 | 200 | 133 | 352 | 59 | 70 | 68 | 2 | 65 | 37 | 110 | 17 | 9 | 90 | 400 | 104 | 8 | 17 | 108 | 0 | 17 | 4 | 36 | 54 | 0 |  | 487 | 0 | 290 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 88 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 249 | 0 | 0 | 176 | 0 | 0 | 130 | 0 | 0 | 169 | 0 | 380 | 35 | 0 | 94 | 105 | 70 | 0 | 0 | 95 | 480 | 225 | 0 | 0 | 0 | 34 | 108 | 0 | 0 |  | 6927 | 3421 | 10348 | 3903 | 487 | 1924 | 0 | 2748 | 729 | 123 | 250 | 146 | 116 | 52 | 0 | 89.88
8:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 338 |  | 0 | 225 | 0 | 32 | 0 | 55 | 335 | 0 | 0 | 8 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 20 | 33 | 17 | 8 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 55 | 32 | 45 | 21 | 38 | 0 | 0 | 0 | 270 | 230 | 181 | 8 | 85 | 35 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 110 | 160 | 0 | 22 | 1 | 32 | 42 | 0 | 0 | 75 | 0 | 52 | 65 | 0 | 135 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 258 | 0 | 0 | 115 | 0 | 60 | 12 | 90 | 200 | 125 | 353 | 59 | 70 | 17 | 4 | 0 | 37 | 110 | 17 | 9 | 75 | 360 | 104 | 10 | 17 | 108 | 0 | 17 | 10 | 35 | 54 | 222 |  | 486 | 0 | 285 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 88 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 380 | 17 | 0 | 94 | 85 | 70 | 0 | 2 | 95 | 450 | 160 | 0 | 0 | 2 | 46 | 99 | 0 | 0 |  | 6830 | 3204 | 10034 | 3981 | 486 | 1813 | 0 | 2466 | 700 | 125 | 250 | 146 | 110 | 87 | 0 | 89.89
9:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 328 |  | 0 | 225 | 0 | 32 | 0 | 55 | 335 | 0 | 0 | 25 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 20 | 33 | 25 | 8 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 55 | 11 | 45 | 21 | 38 | 0 | 0 | 0 | 270 | 220 | 191 | 8 | 84 | 35 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 30 | 20 | 110 | 169 | 0 | 22 | 1 | 33 | 42 | 11 | 10 | 110 | 0 | 50 | 65 | 0 | 20 | 0 | 4 | 9 | 265 | 8 | 11 | 0 | 210 | 0 | 0 | 115 | 0 | 24 | 15 | 90 | 170 | 100 | 364 | 59 | 70 | 17 | 4 | 0 | 35 | 110 | 17 | 9 | 75 | 361 | 104 | 12 | 17 | 80 | 0 | 17 | 24 | 36 | 45 | 286 |  | 488 | 0 | 290 | 0 | 21 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 340 | 0 | 0 | 70 | 50 | 69 | 0 | 3 | 70 | 410 | 166 | 0 | 0 | 2 | 60 | 72 | 0 | 0 |  | 6667 | 3025 | 9692 | 3958 | 488 | 1807 | 0 | 2161 | 660 | 121 | 250 | 146 | 110 | 121 | 0 | 89.9
10:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 328 |  | 0 | 225 | 0 | 32 | 0 | 55 | 335 | 0 | 0 | 64 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 17 | 33 | 25 | 8 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 55 | 11 | 45 | 21 | 38 | 0 | 0 | 0 | 270 | 220 | 196 | 8 | 84 | 35 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 25 | 20 | 110 | 179 | 0 | 22 | 1 | 32 | 42 | 11 | 10 | 110 | 0 | 60 | 65 | 0 | 20 | 0 | 15 | 9 | 290 | 8 | 11 | 0 | 210 | 0 | 0 | 115 | 0 | 17 | 20 | 90 | 170 | 100 | 402 | 59 | 70 | 17 | 2 | 0 | 35 | 110 | 17 | 9 | 50 | 398 | 104 | 24 | 17 | 68 | 0 | 17 | 21 | 35 | 37 | 192 |  | 489 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 340 | 0 | 0 | 70 | 50 | 69 | 0 | 6 | 70 | 380 | 165 | 0 | 0 | 2 | 62 | 72 | 0 | 0 |  | 6698 | 3007 | 9705 | 3965 | 489 | 1844 | 0 | 2142 | 630 | 121 | 250 | 146 | 110 | 138 | 0 | 89.91
11:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 0 | 322 |  | 0 | 225 | 0 | 55 | 0 | 55 | 335 | 0 | 0 | 84 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 17 | 33 | 25 | 8 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 55 | 11 | 44 | 0 | 30 | 0 | 0 | 0 | 310 | 305 | 197 | 8 | 84 | 33 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 25 | 18 | 112 | 206 | 0 | 22 | 1 | 33 | 42 | 11 | 25 | 110 | 0 | 40 | 65 | 0 | 20 | 0 | 19 | 9 | 285 | 8 | 11 | 0 | 210 | 0 | 0 | 115 | 0 | 17 | 19 | 90 | 170 | 100 | 403 | 59 | 70 | 17 | 5 | 0 | 35 | 110 | 17 | 9 | 50 | 365 | 104 | 18 | 17 | 68 | 0 | 17 | 30 | 35 | 36 | 216 |  | 488 | 0 | 315 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 340 | 0 | 0 | 70 | 50 | 69 | 0 | 6 | 70 | 370 | 167 | 0 | 0 | 5 | 65 | 72 | 0 | 0 |  | 6846 | 3018 | 9864 | 4081 | 488 | 1842 | 0 | 2185 | 620 | 121 | 250 | 146 | 112 | 149 | 0 | 89.92
12:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 322 |  | 0 | 225 | 0 | 60 | 0 | 55 | 335 | 0 | 0 | 91 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 17 | 33 | 25 | 8 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 19 | 44 | 21 | 30 | 0 | 0 | 0 | 275 | 275 | 183 | 8 | 84 | 32 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 20 | 20 | 126 | 206 | 0 | 22 | 2 | 33 | 42 | 11 | 45 | 110 | 0 | 61 | 65 | 0 | 20 | 0 | 24 | 9 | 300 | 8 | 11 | 0 | 210 | 0 | 0 | 114 | 0 | 24 | 19 | 76 | 200 | 107 | 402 | 59 | 70 | 17 | 5 | 0 | 35 | 110 | 17 | 9 | 65 | 360 | 104 | 20 | 17 | 72 | 0 | 17 | 30 | 36 | 36 | 217 |  | 489 | 0 | 315 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 168 | 0 | 340 | 0 | 0 | 70 | 50 | 69 | 0 | 7 | 70 | 400 | 221 | 0 | 0 | 4 | 76 | 72 | 0 | 0 |  | 6936 | 3203 | 10139 | 4123 | 489 | 1942 | 0 | 2258 | 650 | 122 | 250 | 146 | 126 | 163 | 0 | 89.93
13:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 323 |  | 0 | 225 | 0 | 65 | 0 | 55 | 336 | 0 | 0 | 93 | 94 | 40 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 15 | 25 | 14 | 33 | 25 | 12 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 69 | 45 | 21 | 29 | 0 | 0 | 0 | 305 | 305 | 182 | 8 | 84 | 36 | 49 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 16 | 20 | 134 | 195 | 0 | 22 | 1 | 33 | 42 | 19 | 44 | 110 | 0 | 55 | 40 | 0 | 20 | 0 | 26 | 9 | 300 | 8 | 11 | 0 | 210 | 105 | 0 | 114 | 0 | 117 | 15 | 76 | 200 | 122 | 402 | 59 | 80 | 60 | 6 | 15 | 35 | 110 | 17 | 9 | 78 | 400 | 104 | 11 | 17 | 108 | 0 | 17 | 20 | 36 | 37 | 218 |  | 491 | 0 | 315 | 0 | 16 | 153 | 0 | 0 | 0 | 0 | 8 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 140 | 0 | 0 | 193 | 0 | 414 | 0 | 0 | 76 | 60 | 68 | 0 | 7 | 90 | 470 | 221 | 0 | 0 | 2 | 93 | 72 | 0 | 0 |  | 7414 | 3445 | 10859 | 4254 | 491 | 2002 | 105 | 2593 | 670 | 122 | 293 | 180 | 134 | 155 | 0 | 89.94
14:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 322 |  | 0 | 225 | 0 | 73 | 0 | 55 | 280 | 0 | 0 | 99 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 15 | 25 | 14 | 33 | 25 | 32 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 79 | 44 | 21 | 25 | 0 | 0 | 0 | 305 | 310 | 181 | 8 | 84 | 36 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 16 | 20 | 136 | 188 | 0 | 22 | 1 | 33 | 42 | 22 | 41 | 110 | 0 | 60 | 40 | 0 | 20 | 0 | 26 | 9 | 270 | 8 | 11 | 0 | 210 | 0 | 0 | 114 | 0 | 130 | 14 | 76 | 200 | 130 | 353 | 59 | 88 | 105 | 2 | 45 | 35 | 110 | 17 | 9 | 75 | 350 | 104 | 42 | 17 | 108 | 0 | 17 | 29 | 35 | 36 | 217 |  | 491 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 350 | 17 | 0 | 84 | 67 | 66 | 0 | 1 | 113 | 470 | 163 | 0 | 0 | 1 | 37 | 106 | 0 | 0 |  | 7317 | 3273 | 10590 | 4070 | 491 | 1845 | 0 | 2830 | 670 | 123 | 250 | 178 | 136 | 127 | 0 | 89.94
15:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 322 |  | 0 | 225 | 0 | 72 | 0 | 55 | 280 | 0 | 0 | 100 | 94 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 15 | 25 | 14 | 33 | 25 | 32 | 0 | 89 | 35 | 90 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 84 | 44 | 21 | 25 | 0 | 0 | 0 | 320 | 320 | 181 | 8 | 84 | 36 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 30 | 20 | 136 | 201 | 0 | 20 | 1 | 33 | 42 | 22 | 41 | 110 | 0 | 61 | 40 | 0 | 20 | 0 | 27 | 9 | 280 | 8 | 11 | 0 | 224 | 0 | 0 | 114 | 0 | 128 | 16 | 76 | 200 | 123 | 402 | 59 | 88 | 105 | 4 | 50 | 35 | 110 | 17 | 9 | 75 | 400 | 104 | 45 | 17 | 108 | 0 | 19 | 15 | 35 | 37 | 218 |  | 491 | 0 | 325 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 374 | 35 | 0 | 94 | 67 | 66 | 0 | 1 | 113 | 450 | 220 | 0 | 0 | 1 | 75 | 106 | 0 | 0 |  | 7476 | 3422 | 10898 | 4194 | 491 | 1940 | 0 | 2891 | 650 | 124 | 250 | 194 | 136 | 158 | 0 | 89.95
16:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 322 |  | 0 | 225 | 0 | 72 | 0 | 30 | 280 | 0 | 0 | 99 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 15 | 25 | 14 | 33 | 25 | 32 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 54 | 44 | 21 | 25 | 0 | 0 | 0 | 320 | 320 | 181 | 8 | 85 | 36 | 51 | 0 | 51 | 0 | 0 | 12 | 0 | 8 | 33 | 20 | 130 | 204 | 0 | 20 | 0 | 33 | 42 | 25 | 41 | 110 | 0 | 61 | 40 | 0 | 20 | 0 | 26 | 9 | 250 | 8 | 11 | 0 | 215 | 0 | 0 | 113 | 0 | 133 | 12 | 76 | 200 | 125 | 353 | 59 | 88 | 51 | 1 | 50 | 35 | 96 | 17 | 14 | 90 | 320 | 104 | 14 | 17 | 108 | 0 | 35 | 26 | 35 | 36 | 292 |  | 491 | 0 | 340 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 168 | 0 | 332 | 35 | 0 | 94 | 67 | 62 | 0 | 2 | 113 | 460 | 170 | 0 | 0 | 0 | 63 | 106 | 0 | 0 |  | 7245 | 3355 | 10600 | 4189 | 491 | 1817 | 0 | 2799 | 660 | 114 | 250 | 162 | 130 | 118 | 0 | 89.95
17:00 | 0 | 0 | 0 | 180 | 310 | 84 | 0 | 0 | 312 |  | 0 | 225 | 0 | 68 | 0 | 30 | 250 | 0 | 0 | 95 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 14 | 33 | 25 | 25 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 37 | 44 | 18 | 25 | 0 | 0 | 0 | 280 | 280 | 180 | 8 | 84 | 36 | 50 | 0 | 51 | 0 | 0 | 16 | 0 | 8 | 33 | 20 | 126 | 204 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 40 | 0 | 140 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 212 | 0 | 0 | 120 | 0 | 84 | 5 | 50 | 200 | 123 | 403 | 59 | 50 | 17 | 1 | 15 | 35 | 68 | 51 | 27 | 75 | 396 | 90 | 13 | 17 | 68 | 0 | 35 | 10 | 42 | 37 | 0 |  | 491 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 34 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 170 | 0 | 340 | 17 | 0 | 50 | 67 | 92 | 0 | 1 | 50 | 470 | 220 | 0 | 0 | 1 | 43 | 52 | 0 | 0 |  | 6753 | 3237 | 9990 | 3985 | 491 | 1786 | 0 | 2461 | 670 | 115 | 250 | 162 | 126 | 74 | 0 | 89.96
18:00 | 0 | 0 | 0 | 180 | 310 | 87 | 0 | 0 | 312 |  | 0 | 225 | 0 | 83 | 0 | 30 | 250 | 0 | 0 | 50 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 14 | 33 | 25 | 25 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 2 | 0 | 10 | 30 | 44 | 21 | 28 | 0 | 0 | 0 | 280 | 280 | 180 | 8 | 85 | 36 | 51 | 0 | 51 | 0 | 0 | 16 | 10 | 8 | 33 | 20 | 120 | 204 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 40 | 0 | 140 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 210 | 0 | 0 | 120 | 0 | 79 | 1 | 30 | 100 | 127 | 352 | 59 | 50 | 17 | 0 | 15 | 35 | 51 | 51 | 27 | 40 | 360 | 52 | 4 | 32 | 51 | 0 | 35 | 2 | 71 | 42 | 0 |  | 491 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 21 | 0 | 8 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 0 | 0 | 0 | 52 | 10 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 346 | 17 | 0 | 35 | 67 | 72 | 0 | 0 | 35 | 430 | 160 | 0 | 0 | 0 | 13 | 52 | 0 | 0 |  | 6340 | 3036 | 9376 | 3815 | 491 | 1739 | 0 | 2122 | 630 | 119 | 250 | 200 | 120 | 20 | 0 | 89.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 88 | 0 | 0 | 322 |  | 0 | 225 | 0 | 87 | 0 | 30 | 300 | 0 | 0 | 55 | 85 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 15 | 33 | 25 | 48 | 0 | 85 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 33 | 30 | 45 | 43 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 280 | 180 | 8 | 85 | 36 | 52 | 0 | 51 | 0 | 26 | 21 | 22 | 8 | 33 | 20 | 148 | 206 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 40 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 212 | 0 | 0 | 120 | 0 | 103 | 0 | 76 | 114 | 133 | 353 | 65 | 66 | 23 | 0 | 171 | 35 | 58 | 90 | 41 | 44 | 360 | 60 | 0 | 72 | 61 | 0 | 35 | 0 | 71 | 53 | 0 |  | 492 | 0 | 300 | 0 | 40 | 120 | 0 | 0 | 34 | 0 | 8 | 88 | 27 | 0 | 0 | 0 | 0 | 34 | 5 | 71 | 0 | 0 | 25 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 166 | 0 | 382 | 18 | 0 | 40 | 105 | 74 | 0 | 0 | 90 | 430 | 170 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 7108 | 3430 | 10538 | 3888 | 492 | 1828 | 0 | 2824 | 630 | 120 | 250 | 488 | 148 | 0 | 0 | 90
19:30 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 322 |  | 0 | 225 | 0 | 87 | 0 | 55 | 335 | 0 | 0 | 99 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 15 | 33 | 25 | 49 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 79 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 325 | 208 | 8 | 85 | 36 | 51 | 0 | 51 | 0 | 46 | 34 | 22 | 8 | 33 | 20 | 152 | 207 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 40 | 0 | 140 | 0 | 0 | 9 | 265 | 8 | 11 | 0 | 212 | 0 | 0 | 177 | 0 | 133 | 0 | 90 | 200 | 137 | 402 | 115 | 105 | 87 | 0 | 254 | 35 | 110 | 98 | 48 | 95 | 400 | 104 | 0 | 72 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 385 | 0 | 49 | 160 | 0 | 0 | 48 | 0 | 8 | 88 | 30 | 32 | 0 | 0 | 0 | 34 | 23 | 88 | 0 | 34 | 32 | 52 | 37 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 213 | 0 | 0 | 138 | 0 | 0 | 211 | 0 | 367 | 35 | 0 | 94 | 105 | 95 | 0 | 0 | 90 | 580 | 220 | 0 | 0 | 0 | 0 | 111 | 0 | 0 |  | 8260 | 4084 | 12344 | 4345 | 492 | 1854 | 0 | 3779 | 780 | 119 | 298 | 663 | 152 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 332 |  | 0 | 225 | 0 | 86 | 0 | 55 | 337 | 0 | 0 | 96 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 19 | 33 | 25 | 49 | 0 | 30 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 34 | 55 | 79 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 325 | 207 | 8 | 85 | 36 | 51 | 0 | 51 | 0 | 48 | 32 | 22 | 8 | 33 | 20 | 150 | 185 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 40 | 0 | 140 | 0 | 0 | 9 | 275 | 8 | 11 | 0 | 213 | 0 | 0 | 188 | 0 | 132 | 0 | 90 | 180 | 133 | 403 | 115 | 105 | 77 | 0 | 258 | 35 | 109 | 98 | 48 | 95 | 398 | 104 | 0 | 72 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 390 | 0 | 49 | 203 | 0 | 0 | 37 | 10 | 8 | 87 | 29 | 32 | 0 | 0 | 0 | 34 | 27 | 88 | 0 | 34 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 140 | 0 | 0 | 212 | 0 | 394 | 53 | 0 | 94 | 105 | 96 | 0 | 0 | 113 | 590 | 220 | 0 | 0 | 0 | 0 | 111 | 0 | 0 |  | 8165 | 4215 | 12380 | 4333 | 492 | 1900 | 0 | 3795 | 790 | 65 | 343 | 652 | 150 | 0 | 0 | 89.99
21:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 337 |  | 0 | 225 | 0 | 87 | 0 | 55 | 336 | 0 | 0 | 92 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 19 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 34 | 55 | 79 | 44 | 21 | 42 | 0 | 0 | 0 | 325 | 325 | 208 | 8 | 84 | 36 | 52 | 0 | 51 | 0 | 48 | 39 | 22 | 8 | 33 | 20 | 154 | 186 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 212 | 105 | 50 | 188 | 25 | 133 | 0 | 90 | 200 | 137 | 401 | 115 | 105 | 87 | 0 | 262 | 54 | 110 | 98 | 48 | 95 | 400 | 104 | 0 | 72 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 380 | 0 | 41 | 203 | 0 | 0 | 35 | 35 | 8 | 87 | 32 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 140 | 0 | 0 | 211 | 0 | 392 | 53 | 0 | 94 | 89 | 97 | 0 | 0 | 113 | 622 | 221 | 0 | 0 | 0 | 0 | 111 | 0 | 0 |  | 8542 | 4243 | 12785 | 4327 | 492 | 1969 | 180 | 3834 | 822 | 124 | 343 | 680 | 154 | 0 | 0 | 90
22:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 337 |  | 0 | 225 | 0 | 87 | 0 | 55 | 0 | 0 | 0 | 98 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 25 | 33 | 25 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 34 | 55 | 79 | 44 | 21 | 40 | 0 | 0 | 0 | 320 | 325 | 207 | 8 | 84 | 36 | 51 | 0 | 51 | 0 | 40 | 43 | 22 | 8 | 33 | 20 | 158 | 187 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 200 | 156 | 0 | 188 | 42 | 131 | 0 | 90 | 200 | 135 | 401 | 115 | 105 | 87 | 0 | 262 | 54 | 110 | 98 | 49 | 98 | 400 | 104 | 0 | 72 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 390 | 0 | 48 | 205 | 0 | 0 | 34 | 50 | 8 | 87 | 33 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 24 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 198 | 0 | 0 | 212 | 0 | 403 | 55 | 0 | 113 | 90 | 96 | 0 | 0 | 113 | 622 | 221 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 8203 | 4361 | 12564 | 4010 | 492 | 1958 | 198 | 3862 | 822 | 123 | 403 | 736 | 158 | 0 | 0 | 90.01
23:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 327 |  | 0 | 225 | 0 | 88 | 0 | 55 | 0 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 25 | 33 | 22 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 34 | 55 | 80 | 44 | 21 | 40 | 0 | 0 | 0 | 335 | 320 | 206 | 8 | 84 | 36 | 50 | 0 | 51 | 0 | 40 | 43 | 22 | 8 | 33 | 20 | 158 | 205 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 55 | 86 | 0 | 140 | 0 | 0 | 9 | 300 | 8 | 11 | 100 | 200 | 250 | 0 | 200 | 64 | 131 | 0 | 90 | 200 | 138 | 403 | 115 | 105 | 105 | 0 | 262 | 54 | 110 | 98 | 48 | 92 | 395 | 104 | 0 | 26 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 395 | 0 | 49 | 205 | 0 | 0 | 34 | 62 | 8 | 87 | 34 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 213 | 0 | 0 | 210 | 0 | 414 | 55 | 0 | 113 | 105 | 97 | 0 | 0 | 113 | 622 | 221 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 8459 | 4384 | 12843 | 4033 | 492 | 1989 | 414 | 3819 | 822 | 123 | 418 | 788 | 158 | 0 | 0 | 90.02
24:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 327 |  | 0 | 225 | 0 | 87 | 0 | 55 | 42 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 33 | 27 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 34 | 55 | 78 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 84 | 33 | 51 | 0 | 51 | 0 | 40 | 8 | 22 | 8 | 33 | 20 | 158 | 205 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 300 | 8 | 11 | 100 | 200 | 255 | 0 | 115 | 70 | 132 | 0 | 90 | 200 | 138 | 402 | 61 | 105 | 105 | 0 | 262 | 54 | 110 | 17 | 42 | 98 | 400 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 60 | 55 | 0 |  | 491 | 0 | 390 | 0 | 16 | 207 | 0 | 0 | 34 | 64 | 8 | 87 | 34 | 32 | 0 | 0 | 0 | 34 | 33 | 88 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 214 | 0 | 18 | 211 | 0 | 392 | 55 | 80 | 113 | 105 | 96 | 0 | 0 | 113 | 622 | 225 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 8248 | 4420 | 12668 | 4050 | 491 | 1974 | 523 | 3543 | 822 | 123 | 421 | 777 | 158 | 0 | 0 | 90.03
KWH | 0 | 0 | 0 | 4359600 | 7354173 | 2131681 | 0 | 0 | 7806000 |  | 0 | 5033150 | 0 | 1410240 | 0 | 1234894 | 6964612 | 0 | 0 | 1415040 | 2176704 | 1558080 | 0 | 0 | 0 | 0 | 330840 | 615332 | 505790 | 400320 | 600000 | 479340 | 806600 | 583600 | 796800 | 0 | 2039836 | 852000 | 2400000 | 0 | 603156 | 0 | 0 | 0 | 0 |  | 566160 | 512120 | 445773 | 1245840 | 1431360 | 1073280 | 486384 | 829920 | 0 | 0 | 0 | 7735900 | 7244000 | 4726000 | 802909 | 2019910 | 837576 | 1219200 | 0 | 1168571 | 0 | 485560 | 382411 | 383940 | 239220 | 718400 | 509850 | 3269760 | 4271040 | 0 | 464364 | 10400 | 772000 | 983088 | 142800 | 280728 | 2288290 | 0 | 1264704 | 1512960 | 0 | 2367370 | 0 | 163800 | 170460 | 7036000 | 304656 | 264000 | 847296 | 5494907 | 1577279 | 502852 | 3093600 | 166083 | 2517984 | 132975 | 1922880 | 4524000 | 3057745 | 9331000 | 1669200 | 2116800 | 1609156 | 36721 | 2767527 | 1048219 | 2493189 | 852720 | 487200 | 1897920 | 9241500 | 2498880 | 205030 | 756000 | 2357291 | 0 | 704880 | 222597 | 1121280 | 1137240 | 2042500 |  | 11823272 | 0 | 7962624 | 0 | 514560 | 3902400 | 0 | 0 | 350880 | 279040 | 192000 | 2095707 | 618978 | 310656 | 0 | 0 | 0 | 300936 | 269924 | 1007208 | 0 | 337216 | 279300 | 429134 | 414903 | 489360 | 0 | 268300 | 0 | 0 | 5500400 | 92000 | 0 | 4641691 | 0 | 0 | 4151091 | 0 | 241920 | 4452391 | 0 | 9221745 | 921600 | 547650 | 2121888 | 2054880 | 1810012 | 0 | 29355 | 2335968 | 13391900 | 4971764 | 0 | 164400 | 29220 | 602640 | 2305920 | 0 | 0 |  | 181522943 | 91434833 | 272957776 | 99576360 | 11823272 | 45888316 | 3883080 | 71414699 | 18892300 | 2891836 | 8145491 | 5903724 | 3269760 | 1268938 | 0
Fuel Cost | 0 | 0 | 0 | 6495804 | 8236673.76 | 2835135.73 | 0 | 0 | 8430480 |  | 0 | 5486133.5 | 0 | 15766483.2 | 0 | 16362345.5 | 7800365.44 | 0 | 0 | 20687884.8 | 30626225.28 | 25256476.8 | 0 | 0 | 0 | 0 | 4208284.8 | 8306982 | 6782643.9 | 300240 | 450000 | 0 | 0 | 0 | 13553568 | 0 | 550755.72 | 230040 | 4536000 | 0 | 9861600.6 | 0 | 0 | 0 | 0 |  | 7388388 | 8542161.6 | 7587056.46 | 16831298.4 | 18149644.8 | 12417849.6 | 617707.68 | 2763633.6 | 0 | 0 | 0 | 8586849 | 7895960 | 5482160 | 1035752.61 | 2464290.2 | 946460.88 | 1816608 | 0 | 1951513.57 | 0 | 8385621.2 | 5143427.95 | 525997.8 | 179415 | 1257200 | 382387.5 | 23476876.8 | 4655433.6 | 0 | 631535.04 | 165776 | 1057640 | 1297676.16 | 248472 | 485659.44 | 2631533.5 | 0 | 2453525.76 | 3449548.8 | 0 | 2391043.7 | 0 | 244062 | 337510.8 | 7036000 | 228492 | 200640 | 17759324.16 | 75005480.55 | 33059767.84 | 10393950.84 | 41701728 | 3432935.61 | 34874078.4 | 1554477.75 | 19844121.6 | 61797840 | 40576276.15 | 8584520 | 20297472 | 30608928 | 20355823.4 | 0 | 32490766.98 | 11415104.91 | 26502599.07 | 11571410.4 | 6280008 | 22357497.6 | 8502180 | 32360496 | 2962683.5 | 9593640 | 26825971.58 | 0 | 9205732.8 | 2660034.15 | 16785561.6 | 14977450.8 | 0 |  | 35469816 | 0 | 8918138.88 | 0 | 5356569.6 | 64389600 | 0 | 0 | 6319348.8 | 5022720 | 2759040 | 2347191.84 | 1200817.32 | 3386150.4 | 0 | 0 | 0 | 5046696.72 | 4720970.76 | 15752733.12 | 0 | 5584296.96 | 4722963 | 5849096.42 | 6999413.61 | 1012975.2 | 0 | 203103.1 | 0 | 0 | 29097116 | 3865840 | 0 | 5384361.56 | 0 | 0 | 72478048.86 | 0 | 5075481.6 | 5164773.56 | 0 | 9129527.55 | 12386304 | 11484220.5 | 25101935.04 | 29693016 | 22987152.4 | 0 | 324372.75 | 28358651.52 | 120661019 | 5071199.28 | 0 | 1216560 | 330478.2 | 7068967.2 | 35349753.6 | 0 | 0 |  | 1022444794.17 | 615290420.35 | 1637735214.52 | 108177766.46 | 35469816 | 55166562.9 | 81205680.55 | 929543140.61 | 149758135 | 780795.72 | 140733488.86 | 98356162.07 | 23476876.8 | 15066789.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 322 |  | 0 | 225 | 0 | 60 | 0 | 55 | 335 | 0 | 0 | 91 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 17 | 33 | 25 | 8 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 19 | 44 | 21 | 30 | 0 | 0 | 0 | 275 | 275 | 183 | 8 | 84 | 32 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 20 | 20 | 126 | 206 | 0 | 22 | 2 | 33 | 42 | 11 | 45 | 110 | 0 | 61 | 65 | 0 | 20 | 0 | 24 | 9 | 300 | 8 | 11 | 0 | 210 | 0 | 0 | 114 | 0 | 24 | 19 | 76 | 200 | 107 | 402 | 59 | 70 | 17 | 5 | 0 | 35 | 110 | 17 | 9 | 65 | 360 | 104 | 20 | 17 | 72 | 0 | 17 | 30 | 36 | 36 | 217 |  | 489 | 0 | 315 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 168 | 0 | 340 | 0 | 0 | 70 | 50 | 69 | 0 | 7 | 70 | 400 | 221 | 0 | 0 | 4 | 76 | 72 | 0 | 0 |  | 10139 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 337 | 0 | 0 | 225 | 0 | 87 | 0 | 55 | 336 | 0 | 0 | 92 | 94 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 19 | 33 | 25 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 51 | 34 | 55 | 79 | 44 | 21 | 42 | 0 | 0 | 0 | 325 | 325 | 208 | 8 | 84 | 36 | 52 | 0 | 51 | 0 | 48 | 39 | 22 | 8 | 33 | 20 | 154 | 186 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 212 | 105 | 50 | 188 | 25 | 133 | 0 | 90 | 200 | 137 | 401 | 115 | 105 | 87 | 0 | 262 | 54 | 110 | 98 | 48 | 95 | 400 | 104 | 0 | 72 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 492 | 0 | 380 | 0 | 41 | 203 | 0 | 0 | 35 | 35 | 8 | 87 | 32 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 140 | 0 | 0 | 211 | 0 | 392 | 53 | 0 | 94 | 89 | 97 | 0 | 0 | 113 | 622 | 221 | 0 | 0 | 0 | 0 | 111 | 0 | 0 |  | 12785 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 360 | 0 | 0 | 225 | 0 | 87 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 28 | 33 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 55 | 80 | 44 | 21 | 40 | 0 | 0 | 0 | 325 | 325 | 210 | 8 | 84 | 36 | 52 | 0 | 51 | 0 | 50 | 40 | 22 | 11 | 33 | 20 | 165 | 190 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 64 | 86 | 0 | 140 | 0 | 0 | 10 | 341 | 8 | 11 | 200 | 285 | 300 | 50 | 200 | 100 | 133 | 0 | 90 | 200 | 137 | 400 | 115 | 105 | 105 | 0 | 265 | 54 | 110 | 98 | 48 | 95 | 400 | 104 | 0 | 72 | 108 | 0 | 35 |  | 72 | 55 |  |  | 501 | 0 | 410 | 0 | 49 | 220 | 0 | 0 | 35 | 60 | 8 | 87 | 32 | 110 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 10 | 214 | 0 | 0 | 220 | 0 | 100 | 211 | 0 | 414 | 55 | 180 | 94 | 105 | 97 | 0 | 0 | 113 | 622 | 220 |  | 90 |  |  | 113
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 0 | 330 | 0 | 0 | 225 | 0 | 85 | 0 | 55 | 330 | 0 | 0 | 100 | 94 | 130 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 26 | 33 | 25 | 40 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 55 | 80 | 44 | 21 | 30 | 0 | 0 | 0 | 320 | 320 | 210 | 8 | 84 | 35 | 50 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 143 | 170 | 0 | 20 | 1.6 | 32 | 42 | 0 | 0 | 110 | 0 | 60 | 80 | 0 | 130 | 0 | 0 | 10 | 310 | 8 | 11 | 100 | 285 | 200 | 0 | 115 | 0 | 130 | 20 | 90 | 200 | 135 | 400 | 60 | 105 | 105 | 5 | 200 | 36 | 110 | 17 | 40 | 75 | 400 | 104 | 50 | 17 | 108 | 0 | 35 | 30 | 36 | 55 |  |  | 501 | 0 | 300 | 0 | 16 | 220 | 0 | 0 | 35 | 0 | 8 | 85 | 20 | 32 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 0 | 200 | 0 | 0 | 220 | 0 | 90 | 180 | 0 | 414 | 50 | 170 | 94 | 105 | 70 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 113
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 | 0 | 0 | 225 | 0 | 88 | 0 | 15 | 335 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 13 | 33 | 24 | 0 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 21 | 42 | 0 | 0 | 0 | 275 | 305 | 208 | 8 | 85 | 31 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 20 | 110 | 173 | 0 | 22 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 30 | 0 | 0 | 116 | 0 | 17 | 5 | 10 | 100 | 10 | 377 | 60 | 17 | 0 | 3 | 0 | 36 | 17 | 17 | 39 | 72 | 360 | 17 | 25 | 17 | 60 | 0 | 35 | 0 | 36 | 17 | 197 | 0 | 491 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 213 | 0 | 397 | 55 | 0 | 35 | 105 | 70 | 0 | 2 | 35 | 470 | 185 | 0 | 0 | 2 | 35 | 34 | 0 | 0 | 0 |  |  |  |  | 89346994 |  | 0
89346994
| Minimum Generation |  | 9692 | 9:00
| Highest Generation |  | 13071 | 1:00
| Day Peak Generation |  | 10139 | 12:00
| Evening Peak Generation |  | 12785 | 21:00
| HVDC Max Flow |  | 492 | 19:00
| HVDC EvPeak Flow |  | 492 | 21:00
| Load factor L.F |  | 87.01%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-09
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10139 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9066 | MW
Evening Peak Generation : |  | 12785 | MW Hour : | 21:00 | Available Max Generation : |  | 14230 | MW
E.P. Demand (at gen end) : |  | 12785 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 13071 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1730 | MW
Total Gen. (MKWH) : |  | 272.9578 | System Load Factor : | 87.01% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -376 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-09
Actual : | 90.15 | Ft.(MSL) , | Rule curve : | 85.28 | Ft.( MSL )
Gas Consumed : | Total = | 1096.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163344329.36
: |  | Coal : | 149758135 | Oil : | 1249838472.09 | Total : | 1562940936.45
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4295.6812 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1143.7404 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1518.4884 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1358.6324 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1205.467 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 889.1362 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 489.4961 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 328.0574 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 675.9709 |  |  | 0 | 0%
Total | 0 |  | 11904.6701 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari-AKSML 230 kV Ckt tripped at 10:03 showing dist.E/F,R-phase and was switched on at 10:34.
b) Netrokona 132/33 kV T-1 transformer was under shut down from 09:58 to 10:40 for C/M.
c) Netrokona 132/33 kV T-2 transformer was under shut down from 09:56 to10:03 for C/M.
d) Bhandaria 132/33 kV T-2 transformer was under shut down from 08:34 to 09:57 for C/M. | [5 empty] | About 15 MW power interruption occurred under
Bhandaria S/S area from 08:34 to 09:57.
e) Barishal(N) 132/33 kV T-5 transformer was under shut down from 09:08 to 13:09 for C/M.
f) Kaptai #2 & 3 tripped at 19:38 showing unit breaker conditional trip and was switched on at 19:55 & 20:16 respectively.
g) Siddirganj-335 MW CCPP tripped at 21:46 due to tripping of GBC and GT & ST were synchronized at
23:43 & 01:00(9/7/22) respectively.
h) Narail 132/33 kV T-2 transformer was shut down at 07:33(9/7/22) due to red hot maintenance and was | [5 empty] | About 10 MW power interruption occurred under
switched on at 08:24(9/7/22). | [5 empty] | Narail S/S area from 07:33 to 08:24(9/7/22).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4359600
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7354173 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 92 | 2131681 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7806000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5033150 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 87 | 1410240 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1234894
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 400320 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 92 | 1415040 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 336 | 6964612
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 2176704 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 330840 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1558080 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 615332 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 505790 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 1079340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 806600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 583600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 796800 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 212 | 5494907 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 105 | 1577279 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 502852 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 166083 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2517984 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2116800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2498880
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 756000 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 222597
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1137240
| Dhaka area Total |  |  |  | 5847 | 3037 | 63553418
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 603156
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 132975
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1073280 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 124 | 2891836 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1609156 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 512120 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 445773 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 55 | 1245840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1922880 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 486384
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 829920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 79 | 1431360 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36721
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 262 | 2767527 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1048219
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2493189
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 95 | 1897920
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2357291
| Chattogram area Total |  |  |  | 2382 | 1381 | 26185547
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4726000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7735900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 325 | 7244000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 2042500 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 837576 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1219200
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 802909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1168571
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3057745 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 485560
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 84 | 2019910 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4524000
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 383940
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 239220 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3269760
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 718400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 39 | 382411 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 509850 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 847296 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 852720 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 487200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 704880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1121280 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 2003 | 45380828
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 186 | 4271040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 464364
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 188 | 3093600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1669200
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 205030
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 566160
| Mymensingh Area Total |  |  |  | 614 | 535 | 10279794
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 33 | 772000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 983088 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2288290 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 142800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 280728 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1264704 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1512960
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 2367370 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 163800 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 304656 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7036000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9331000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 170460
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9241500
| Sylhet Area Total |  |  |  | 2477 | 1586 | 36123356
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 492 | 11823272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 41 | 514560 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 350880 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 203 | 3902400 | Engine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 279040 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 380 | 7962624 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 192000 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 241920 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 921600 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 2054880 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 602640
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1336 | 28845816
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 310656 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 618978 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2095707 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 13391900 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 4971764
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 164400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 994 | 21553405
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 300936 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 32 | 269924 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 337216 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 279300 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4641691
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4151091
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 211 | 4452391
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 9221745
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 414903 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 489360
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 268300
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 429134
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 1007208 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 547650 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 2121888 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2335968
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29220
| Rajshahi Area Total |  |  |  | 2129 | 1505 | 31297925
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5500400
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 92000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 97 | 1810012 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29355
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 111 | 2305920
| Rangpur Area Total |  |  |  | 720 | 408 | 9737687
| Total |  |  |  | 21396 | 12785 | 272957776
| Eastern Grid Total |  |  |  | 14205 | 8542 | 181522943
| Western Grid Total |  |  |  | 7191 | 4243 | 91434833
| National Grid Total |  |  |  | 21396 | 12785 | 272957776
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-08
(a) ENTIRE EASTERN GRID : |  | 7762.82 | MW | (b) ENTIRE WESTERN GRID : |  | 4400.85 | MW
i) Dhaka area |  | 3618.32 | MW | i) Khulna area |  | 1651 | MW
ii) Chittagong area |  | 1200.5 | MW | ii) Rajshahi area |  | 1451 | MW
iii) Comilla area |  | 1258 | MW | iii) Barisal area |  | 387.85 | MW
iv) Mymensingh area |  | 1152 | MW | iv) Rangpur area |  | 911 | MW
v) Sylhet area |  | 534 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12163.67 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 16 | 04:00 | Chowmuhani | 191 | 01:00 | Kaptai | 4 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 134 | 00:00 | Chuadanga | 113 | 23:00 | Kazla | 61 | 01:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 30 | 00:00 | Coxsbazar | 105 | 20:00 | Keranigonj | 46 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 72 | 00:00 | Cumilla(N) | 155 | 23:00 | Khagrachori | 28 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 72 | 00:00 | Cumilla(S) | 166 | 00:00 | Khulna | 90 | 00:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 66 | 21:00 | Daudkandi | 140 | 23:00 | Khulshi | 153 | 03:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 37 | 06:00 | Dhaka | 18 | 12:00 | Kishoreganj | 164 | 22:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 162 | 10:00 | Dhamrai | 98 | 00:00 | Kodda | 194 | 00:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 101 | 00:00 | Dhanmondi | 94 | 12:00 | Kulaura | 50 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 106 | 00:00 | Dohazari | 100 | 00:00 | Kurigram | 68 | 01:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 41 | 00:00 | Faridpur | 151 | 00:00 | Kushtia | 131 | 01:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 6 | 10:00 | Fatullah | 55 | 00:00 | Lalbag | 71 | 00:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 54 | 23:00 | Fenchuganj | 48 | 21:00 | Lalmonirhat | 53 | 20:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 124 | 22:00 | Madanganj | 88 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 112 | 00:00 | GPH | 66 | 06:00 | Madaripur | 101 | 21:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 60 | 00:00 | Ghorashal | 66 | 00:00 | Madartek | 79 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 67 | 00:00 | Goalpara | 26 | 00:00 | Madunaghat | 59 | 23:00 | Rajshahi | 132 | 22:00
Baroirhat | 63 | 02:00 | Gollamari | 53 | 00:00 | Magura | 64 | 22:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 127 | 19:00 | Gopalganj | 104.8 | 23:00 | Mahasthangarh | 76 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 13 | 01:00 | Gulshan | 82 | 19:30 | Manikganj | 86 | 00:00 | Rampur | 16 | 00:00
Beanibazar | 70 | 22:00 | Halishahar | 77 | 10:00 | Maniknagar | 56 | 00:00 | Rangamati | 14 | 19:00
Benapole | 58 | 22:00 | HaripurSBU | 175 | 18:00 | Matarbari | 42 | 22:00 | Rangpur | 105 | 08:00
Bhaluka | 116 | 21:00 | Hasnabad | 84 | 00:00 | Matuail | 40 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 58 | 23:00 | Hathazari | 95 | 23:00 | Millgate | 32 | 01:00 | SSM | 3 | 05:00
Bhangura | 38 | 22:00 | Ishurdi | 76 | 00:00 | Mirpur | 104 | 00:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 65 | 22:00 | Jaldhaka | 69 | 20:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 215 | 01:00 | Jamalpur | 165 | 20:00 | Mithapukur | 36 | 00:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 66 | 00:00 | Jashore | 127 | 00:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 174 | 00:00 | Jhenaidah | 126 | 20:00 | Mogbazar | 90 | 13:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 44 | 23:00 | Joydebpur | 151 | 00:00 | Mongla | 36 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 184 | 22:00 | Joypurhat | 61 | 00:00 | Motijheel | 27 | 19:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 120 | 00:00 | Juldah | 23 | 02:00 | Munshiganj | 112 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 72 | 00:00 | KSRM | 7.75 | 03:00 | Mymensingh | 229 | 23:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 19:30 | Kabirpur | 154 | 00:00 | Naogaon | 132 | 00:00 | Shikalbaha | 28 | 19:00
Chapai | 74 | 00:00 | Kachua | 84 | 22:00 | Narail | 49 | 23:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 37 | 12:00 | Kallyanpur | 96 | 00:00 | Narinda | 47 | 00:00 | Shitalakhya | 114 | 12:00
Chauddagram | 49 | 22:00 | Kalurghat | 2 | 00:00 | Narshingdi | 175 | 00:00 | Sholosohor | N/A | N/A
Chhatak | 32 | 21:00 | Kamrangirchar | 47 | 00:00 | Natore | 156 | 00:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 396 | 19:30 | 377 | 12:00 | Kaliakoir | 392 | 06:00 | 338 | 03:00
| Bibiana | 410 | 18:30 | 400 | 11:00 | Payra | 419 | 18:30 | 410 | 04:00
| BIPTC | 407 | 19:30 | 394 | 00:00
| Gopalganj_I | 419 | 18:30 | 396 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 19:30 | 213 | 12:00 | Hasnabad | 227 | 19:30 | 214 | 09:00
| AKSML | 238 | 18:00 | 222 | 13:00 | Hathazari | 237 | 18:00 | 225 | 12:00
| Aminbazar | 226 | 21:00 | 216 | 11:00 | Ishurdi | 238 | 18:00 | 227 | 21:00
| Ashuganj | 242 | 18:30 | 230 | 11:00 | Jhenaidah | 233 | 18:00 | 221 | 21:00
| Baghabari | 235 | 18:30 | 227 | 21:00 | Kaliakoir | 227 | 04:00 | 217 | 12:00
| Barapukuria | 227 | 18:00 | 213 | 21:00 | Keranigonj | 226 | 19:30 | 213 | 12:00
| Barishal | 242 | 18:30 | 234 | 23:00 | Khulna(S) | 241 | 18:00 | 227 | 21:00
| Bheramara | 235 | 18:00 | 233 | 09:00 | Maniknagar | 226 | 00:00 | 216 | 12:00
| Bhulta | 229 | 19:30 | 218 | 11:00 | Meghnaghat | 226 | 03:00 | 220 | 09:00
| Bibiana | 239 | 18:30 | 232 | 12:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 238 | 04:00 | 223 | 21:00 | Rajshahi | 238 | 18:30 | 221 | 21:00
| Bogura | 233 | 18:00 | 219 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 11:00 | 240 | 21:00 | Rampura | 227 | 19:30 | 216 | 12:00
| BSRM | 234 | 18:00 | 225 | 12:00 | Shikalbaha | 237 | 18:00 | 227 | 12:00
| Cumilla(N) | 232 | 22:00 | 221 | 13:00 | Shyampur | 226 | 19:30 | 214 | 12:00
| Fenchuganj | 242 | 18:00 | 235 | 01:00 | Siddhirganj | 228 | 21:00 | 218 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 260 | 00:00 | 227 | 21:00
| GPH | 232 | 00:00 | 223 | 12:00 | Tongi | 225 | 18:00 | 214 | 09:00
| Haripur | 227 | 21:00 | 215 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 05:00 | 132 | 00:00 | Lalbag | 139 | 06:00 | 135 | 00:00
| Agargaon | 137 | 06:00 | 133 | 00:00 | Lalmonirhat | 126 | 07:00 | 114 | 22:00
| Agrabad | 138 | 19:30 | 130 | 11:00 | Madanganj | 135 | 19:00 | 131 | 00:00
| AKS | 138 | 20:00 | 128 | 17:00 | Madaripur | 136 | 06:00 | 129 | 23:00
| Aminbazar | 135 | 05:00 | 131 | 00:00 | Madartek | 136 | 06:00 | 131 | 00:00
| Amnura | 134 | 18:00 | 126 | 00:00 | Madunaghat | 139 | 19:30 | 131 | 17:00
| Ashuganj | 138 | 18:00 | 133 | 23:00 | Magura | 135 | 06:00 | 124 | 21:00
| Bagerhat | 134 | 06:00 | 125 | 00:00 | Mahasthangarh | 134 | 19:00 | 122 | 23:00
| Bakulia | 140 | 05:00 | 130 | 12:00 | Manikganj | 138 | 06:00 | 132 | 00:00
| Banani | 139 | 18:00 | 134 | 00:00 | Maniknagar | 133 | 09:00 | 130 | 00:00
| Bangabhaban | 132 | 06:00 | 130 | 00:00 | Matarbari | 131 | 10:00 | 117 | 01:00
| Barapukuria | 133 | 07:00 | 122 | 22:00 | Matuail | 135.4 | 19:30 | 131 | 01:00
| Barguna | 136 | 09:00 | 127 | 23:00 | Millgate | 137 | 07:00 | 132 | 00:00
| Barishal | 135 | 08:00 | 128 | 22:00 | Mirpur | 134 | 18:00 | 130 | 00:00
| Barishal-230 | 136 | 07:00 | 129 | 23:00 | Mithapukur | 131 | 19:00 | 117 | 23:00
| Baroaulia | 140 | 20:00 | 131 | 12:00 | Modern | 139 | 05:00 | 132 | 12:00
| Baroirhat | 133 | 19:00 | 126 | 02:00 | Mogbazar | 137 | 06:00 | 132 | 13:00
| Bashundhara | 138 | 06:00 | 133 | 13:00 | Mongla | 134 | 07:00 | 125 | 21:00
| BashundharaCement | 139 | 08:00 | 131 | 00:00 | Motijheel | 132 | 07:00 | 130 | 00:00
| Beanibazar | 131 | 11:00 | 123 | 00:00 | Munshiganj | 136 | 17:00 | 131 | 00:00
| Benapole | 135 | 05:00 | 125 | 19:30 | Mymensingh | 135 | 18:00 | 115 | 03:00
| Bhaluka | 133 | 16:00 | 113 | 03:00 | Naogaon | 131 | 18:00 | 116 | 23:00
| Bhandaria | 138 | 09:00 | 121 | 23:00 | Narail | 135 | 18:30 | 123 | 21:00
| Bhangura | 139 | 18:00 | 131 | 23:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 06:00 | 132 | 21:00 | Narshingdi | 140 | 18:00 | 125 | 00:00
| Bheramara(GK) | 140 | 18:00 | 132 | 00:00 | Natore | 136 | 19:00 | 125 | 23:00
| Bhulta | 130 | 10:00 | 123 | 00:00 | Nawabganj | 139 | 06:00 | 133 | 01:00
| Bog-Sherpur | 135 | 19:00 | 124 | 23:00 | Netrakona | 134 | 18:00 | 112 | 02:00
| Bogura | 135 | 19:00 | 125 | 23:00 | New | 138 | 06:00 | 134 | 12:00
| Bogura-230 | 137 | 16:00 | 125 | 23:00 | Niamatpur | 129 | 18:00 | 111 | 22:00
| Brahmanbaria | 133 | 18:00 | 127 | 00:00 | Noapara | 136 | 18:00 | 128 | 21:00
| Cantonment | 137 | 06:00 | 132 | 00:00 | Pabna | 136 | 18:00 | 128 | 21:00
| Chandpur | 138 | 07:00 | 132 | 15:00 | Palashbari | 129 | 19:00 | 114 | 23:00
| Chandraghona | 139 | 22:00 | 132 | 12:00 | Panchagarh | 132 | 19:00 | 110 | 23:00
| Chapai | 135 | 19:00 | 125 | 23:00 | Patuakhali | 135 | 08:00 | 128 | 22:00
| Charsaidpur | 136 | 09:00 | 131 | 00:00 | Payra | 137 | 08:00 | 133 | 21:00
| Chauddagram | 134 | 18:00 | 127 | 00:00 | PHP | 133 | 19:00 | 125 | 14:00
| Chhatak | 132 | 08:00 | 123 | 00:00 | Purbachal | 138 | 06:00 | 134 | 00:00
| Chowmuhani | 130 | 07:00 | 120 | 01:00 | Purbasadipur | 132 | 16:00 | 113 | 23:00
| Chuadanga | 131 | 18:00 | 117 | 21:00 | Rahim | 136 | 18:00 | 132 | 00:00
| Coxsbazar | 123 | 08:00 | 116 | 01:00 | Rajbari | 135 | 08:00 | 127 | 00:00
| Cumilla(N) | 136 | 22:00 | 130 | 06:00 | Rajendrapur | 139 | 07:00 | 132 | 00:00
| Cumilla(S) | 136 | 07:00 | 126 | 19:30 | Rajshahi | 132 | 18:00 | 124 | 23:00
| Daudkandi | 134 | 00:00 | 130 | 15:00 | Rajshahi-230 | 133 | 18:00 | 125 | 13:00
| Dhaka | 136 | 06:00 | 133 | 00:00 | Ramganj | 131 | 08:00 | 124 | 23:00
| Dhamrai | 135 | 06:00 | 131 | 00:00 | Rampur | 139 | 19:30 | 132 | 10:00
| Dhanmondi | 136 | 19:00 | 132 | 00:00 | Rampura | 136 | 05:00 | 132 | 00:00
| Dohazari | 135 | 19:30 | 127 | 18:30 | Rangamati | 138 | 19:30 | 131 | 12:00
| Faridpur | 135 | 07:00 | 126 | 00:00 | Rangpur | 128 | 05:00 | 114 | 23:00
| Fatullah | 140 | 13:00 | 134 | 00:00 | Ruppur | 137 | 16:00 | 130 | 22:00
| Fenchuganj | 137 | 16:00 | 131 | 00:00 | Saidpur | 131 | 16:00 | 117 | 23:00
| Feni | 135 | 19:30 | 125 | 01:00 | Satkhira | 133 | 18:00 | 121 | 21:00
| Ghorashal | 140 | 07:00 | 136 | 01:00 | Satmasjid | 137 | 06:00 | 133 | 00:00
| Goalpara | 137 | 06:00 | 130 | 21:00 | Savar | 135 | 06:00 | 130 | 11:00
| Gollamari | 136 | 06:00 | 129 | 01:00 | Shahjadpur | 141 | 18:00 | 135 | 20:00
| Gopalganj | 138 | 18:00 | 131 | 20:00 | Shahjibazar | 136 | 08:00 | 131 | 00:00
| Gopalganj_I | 138 | 18:00 | 130 | 21:00 | Shahmirpur | 140 | 19:00 | 130 | 12:00
| Gulshan | 135 | 18:00 | 131 | 12:00 | Shariatpur | 134 | 09:00 | 125 | 23:00
| Halishahar | 139 | 19:30 | 131 | 10:00 | Sherpur | 134 | 17:00 | 115 | 05:00
| Haripur | 136 | 18:00 | 132 | 00:00 | Shikalbaha | 140 | 05:00 | 132 | 16:00
| HaripurSBU | 137 | 18:00 | 133 | 00:00 | Shikalbaha-230 | 139 | 19:30 | 131 | 12:00
| Hasnabad | 140 | 06:00 | 136 | 00:00 | Shitalakhya | 140 | 06:00 | 136 | 01:00
| Hathazari | 140 | 19:00 | 132 | 10:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 18:00 | 131 | 21:00 | Shyampur | 135 | 17:00 | 132 | 01:00
| Jaldhaka | 128 | 07:00 | 111 | 23:00 | Shyampur-230 | 136 | 18:00 | 132 | 00:00
| Jamalpur | 137 | 18:00 | 115 | 03:00 | Siddhirganj | 136 | 18:00 | 131 | 00:00
| Jashore | 135 | 04:00 | 126 | 19:30 | Sirajganj | 136 | 19:00 | 126 | 23:00
| Jhenaidah | 137 | 18:00 | 127 | 21:00 | Sonargaon | 137 | 18:00 | 132 | 01:00
| Jhenaidah-230 | 137 | 06:00 | 127 | 21:00 | Sreemongol | 136 | 07:00 | 132 | 00:00
| Joydebpur | 145 | 19:00 | 140 | 12:00 | Srinagar | 139 | 06:00 | 134 | 00:00
| Joypurhat | 132 | 19:00 | 112 | 23:00 | SSM | 140 | 19:30 | 133 | 13:00
| Juldah | 140 | 19:30 | 131 | 18:30 | Sunamganj | 132 | 08:00 | 120 | 00:00
| Kabirpur | 139 | 05:00 | 131 | 12:00 | Sylhet | 132 | 08:00 | 127 | 22:00
| Kachua | 136 | 07:00 | 130 | 01:00 | Tangail | 137 | 17:00 | 129 | 00:00
| Kaliakoir | 141 | 18:00 | 135 | 00:00 | Thakurgaon | 132 | 19:00 | 111 | 23:00
| Kallyanpur | 135 | 06:00 | 131 | 01:00 | TK | 140 | 19:30 | 132 | 18:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 172 | 8248 | 4420 | 12668 |  |  |  | QF-LDC-11
0:30 | 157 | 8395.5 | 4474 | 12869.5 | Date: | 2022-07-08
1:00 | 142 | 8543 | 4528 | 13071
1:30 | 146 | 8421.5 | 4430.5 | 12852
2:00 | 150 | 8300 | 4333 | 12633
2:30 | 173 | 8267.5 | 4242.5 | 12510 | [5 empty] | Gen. at Eve. Peak | 12785 | 12785 MW (21:00 )
3:00 | 196 | 8235 | 4152 | 12387 | [6 empty] | 21:00
3:30 | 196 | 8120 | 4122.5 | 12242.5 | [5 empty] | Gen. at Day Peak | 10139 | 10139 MW (12:00 )
4:00 | 196 | 8005 | 4093 | 12098 | [6 empty] | 12:00
4:30 | 149 | 7921.5 | 4071 | 11992.5 | [5 empty] | Highest Generation | 13071
5:00 | 102 | 7838 | 4049 | 11887 | [6 empty] | 1:00
5:30 | 108 | 7519 | 3851 | 11370
6:00 | 114 | 7200 | 3653 | 10853
6:30 | 150 | 7063.5 | 3537 | 10600.5
7:00 | 186 | 6927 | 3421 | 10348
7:30 | 186 | 6878.5 | 3312.5 | 10191
8:00 | 186 | 6830 | 3204 | 10034
8:30 | 181 | 6748.5 | 3114.5 | 9863
9:00 | 176 | 6667 | 3025 | 9692
9:30 | 160 | 6682.5 | 3016 | 9698.5
10:00 | 144 | 6698 | 3007 | 9705
10:30 | 199 | 6772 | 3012.5 | 9784.5
11:00 | 254 | 6846 | 3018 | 9864
11:30 | 198 | 6891 | 3110.5 | 10001.5
12:00 | 142 | 6936 | 3203 | 10139
12:30 | 146 | 7175 | 3324 | 10499
13:00 | 150 | 7414 | 3445 | 10859
13:30 | 218 | 7365.5 | 3359 | 10724.5
14:00 | 286 | 7317 | 3273 | 10590
14:30 | 243 | 7396.5 | 3347.5 | 10744
15:00 | 200 | 7476 | 3422 | 10898
15:30 | 181 | 7360.5 | 3388.5 | 10749
16:00 | 162 | 7245 | 3355 | 10600
16:30 | 104 | 6999 | 3296 | 10295
17:00 | 46 | 6753 | 3237 | 9990
17:30 | 69 | 6546.5 | 3136.5 | 9683
18:00 | 92 | 6340 | 3036 | 9376
18:30 | 51 | 6724 | 3233 | 9957
19:00 | 10 | 7108 | 3430 | 10538
19:30 | 350 | 8260 | 4084 | 12344
20:00 | 332 | 8165 | 4215 | 12380 |  |  |  | Executive Engineer
20:30 | 354 | 8353.5 | 4229 | 12582.5 |  |  |  | Network Operation Division
21:00 | 376 | 8542 | 4243 | 12785
21:30 | 296 | 8372.5 | 4302 | 12674.5
22:00 | 216 | 8203 | 4361 | 12564 |  |  |  |  | Page 6 of 7
22:30 | 241 | 8331 | 4372.5 | 12703.5
23:00 | 266 | 8459 | 4384 | 12843
23:30 | 219 | 8353.5 | 4402 | 12755.5
24:00 | 172 | 8248 | 4420 | 12668
12785 MW (21:00 )
10139 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-08 |  | Energy |  | 272957776
[13 empty] | 2022-07-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4050 | 491 | 1974 | 523 | 3543 | 822 | 123 | 421 | 777 | 158 | 0 | 0
0:30 | 4097 | 487 | 1991.5 | 705.5 | 3478.5 | 847 | 118.5 | 427 | 772.5 | 158 | 0 | 0 | Date: | 2022-07-08
1:00 | 4144 | 483 | 2009 | 888 | 3414 | 872 | 114 | 433 | 768 | 158 | 0 | 0
1:30 | 4112.5 | 483 | 2014.5 | 800 | 3320 | 869.5 | 116 | 434.5 | 759 | 156 | 0 | 0 | [8 empty] | Total Energy | 272.9578 | Total Energy Gen 272.958 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.958 MKWHr
2:00 | 4081 | 483 | 2020 | 712 | 3226 | 867 | 118 | 436 | 750 | 154 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4125 | 483 | 2009.5 | 583 | 3208 | 858.5 | 118 | 436.5 | 750 | 153 | 0 | 0 | [8 empty] | Energy Requirement | 272.9578
3:00 | 4169 | 483 | 1999 | 454 | 3190 | 850 | 118 | 437 | 750 | 152 | 0 | 0
3:30 | 4140 | 482.5 | 2006 | 333.5 | 3197.5 | 850 | 118 | 437 | 741 | 152 | 0 | 0 | [6 empty] | Shortage
4:00 | 4111 | 482 | 2013 | 213 | 3205 | 850 | 118 | 437 | 732 | 152 | 0 | 0
4:30 | 4099 | 484 | 2007 | 140.5 | 3220 | 835 | 118 | 438.5 | 721.5 | 145 | 0 | 0
5:00 | 4087 | 486 | 2001 | 68 | 3235 | 820 | 118 | 440 | 711 | 138 | 0 | 0
5:30 | 4017 | 486.5 | 1963.5 | 57 | 3083 | 795 | 117 | 412.5 | 510 | 133 | 4 | 0
6:00 | 3947 | 487 | 1926 | 46 | 2931 | 770 | 116 | 385 | 309 | 128 | 8 | 0
6:30 | 3925 | 487 | 1925 | 23 | 2839.5 | 749.5 | 119.5 | 317.5 | 227.5 | 122 | 30 | 0 |  |  |  |  | Coal
7:00 | 3903 | 487 | 1924 | 0 | 2748 | 729 | 123 | 250 | 146 | 116 | 52 | 0
7:30 | 3942 | 486.5 | 1868.5 | 0 | 2607 | 714.5 | 124 | 250 | 146 | 113 | 69.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3981 | 486 | 1813 | 0 | 2466 | 700 | 125 | 250 | 146 | 110 | 87 | 0
8:30 | 3969.5 | 487 | 1810 | 0 | 2313.5 | 680 | 123 | 250 | 146 | 110 | 104 | 0
9:00 | 3958 | 488 | 1807 | 0 | 2161 | 660 | 121 | 250 | 146 | 110 | 121 | 0
9:30 | 3961.5 | 488.5 | 1825.5 | 0 | 2151.5 | 645 | 121 | 250 | 146 | 110 | 129.5 | 0
10:00 | 3965 | 489 | 1844 | 0 | 2142 | 630 | 121 | 250 | 146 | 110 | 138 | 0
10:30 | 4023 | 488.5 | 1843 | 0 | 2163.5 | 625 | 121 | 250 | 146 | 111 | 143.5 | 0
11:00 | 4081 | 488 | 1842 | 0 | 2185 | 620 | 121 | 250 | 146 | 112 | 149 | 0
11:30 | 4102 | 488.5 | 1892 | 0 | 2221.5 | 635 | 121.5 | 250 | 146 | 119 | 156 | 0
12:00 | 4123 | 489 | 1942 | 0 | 2258 | 650 | 122 | 250 | 146 | 126 | 163 | 0
12:30 | 4188.5 | 490 | 1972 | 52.5 | 2425.5 | 660 | 122 | 271.5 | 163 | 130 | 159 | 0
13:00 | 4254 | 491 | 2002 | 105 | 2593 | 670 | 122 | 293 | 180 | 134 | 155 | 0
13:30 | 4254 | 491 | 2002 | 105 | 2593 | 670 | 122 | 293 | 180 | 134 | 155 | 0
14:00 | 4254 | 491 | 2002 | 105 | 2593 | 670 | 122 | 293 | 180 | 134 | 155 | 0
14:30 | 4224 | 491 | 1971 | 52.5 | 2742 | 660 | 123 | 271.5 | 187 | 135 | 156.5 | 0
15:00 | 4194 | 491 | 1940 | 0 | 2891 | 650 | 124 | 250 | 194 | 136 | 158 | 0
15:30 | 4191.5 | 491 | 1878.5 | 0 | 2845 | 655 | 119 | 250 | 178 | 133 | 138 | 0
16:00 | 4189 | 491 | 1817 | 0 | 2799 | 660 | 114 | 250 | 162 | 130 | 118 | 0
16:30 | 3985 | 491 | 1801.5 | 0 | 2630 | 665 | 114.5 | 250 | 162 | 128 | 96 | 0
17:00 | 3985 | 491 | 1786 | 0 | 2461 | 670 | 115 | 250 | 162 | 126 | 74 | 0
17:30 | 3900 | 491 | 1762.5 | 0 | 2291.5 | 650 | 117 | 250 | 181 | 123 | 47 | 0
18:00 | 3815 | 491 | 1739 | 0 | 2122 | 630 | 119 | 250 | 200 | 120 | 20 | 0
18:30 | 3851.5 | 491.5 | 1783.5 | 0 | 2473 | 630 | 119.5 | 250 | 344 | 134 | 10 | 0
19:00 | 3888 | 492 | 1828 | 0 | 2824 | 630 | 120 | 250 | 488 | 148 | 0 | 0
19:30 | 4345 | 492 | 1854 | 0 | 3779 | 780 | 119 | 298 | 663 | 152 | 0 | 0
20:00 | 4333 | 492 | 1900 | 0 | 3795 | 790 | 65 | 343 | 652 | 150 | 0 | 0
20:30 | 4330 | 492 | 1934.5 | 90 | 3814.5 | 806 | 94.5 | 343 | 666 | 152 | 0 | 0
21:00 | 4327 | 492 | 1969 | 180 | 3834 | 822 | 124 | 343 | 680 | 154 | 0 | 0
21:30 | 4168.5 | 492 | 1963.5 | 189 | 3848 | 822 | 123.5 | 373 | 708 | 156 | 0 | 0
22:00 | 4010 | 492 | 1958 | 198 | 3862 | 822 | 123 | 403 | 736 | 158 | 0 | 0
22:30 | 4021.5 | 492 | 1973.5 | 306 | 3840.5 | 822 | 123 | 410.5 | 762 | 158 | 0 | 0
23:00 | 4033 | 492 | 1989 | 414 | 3819 | 822 | 123 | 418 | 788 | 158 | 0 | 0
23:30 | 4041.5 | 491.5 | 1981.5 | 468.5 | 3681 | 822 | 123 | 419.5 | 782.5 | 158 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34° C
24:00 | 4050 | 491 | 1974 | 523 | 3543 | 822 | 123 | 421 | 777 | 158 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 272.958 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.958 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 79 | 83 | 83 | 83 | 83 | 81 | 88 | 90 | 86 | 86 | 86 | 87 | 87 | 88 | 89 | 79 | 80 | 84 |  | 85 | 84 | 30 | 89 | 88 | 88 | 88 | 2039836
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603156
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 4 | 12 | 15 | 20 | 19 | 19 | 15 | 14 | 16 | 12 | 5 | 1 | [8 empty] | 132975
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 0 | [13 empty] | 30 | 51 | 34 | 34 | 34 | 34 | 34 | 445773
12 | Hathazari 100 MW peaking PP | 50 | 50 | 50 | 50 | 43 | 0 | [11 empty] | 2 |  | 33 | 51 | 51 | 51 | 51 | 51 | 43 | 512120
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 17 | 17 | 17 | 17 | 17 | 60 | 105 | 105 | 51 | 17 | 17 |  | 23 | 87 | 77 | 87 | 87 | 105 | 105 | 1609156
| Daudkandi 200 MW PP (B.Trac) | 196 | 195 | 140 | 60 | 20 | 0 | [18 empty] | 100 | 100 | 847296
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | 0 | [13 empty] | 26 | 46 | 48 | 48 | 40 | 40 | 40 | 485560
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 333 | 334 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 336 | 280 | 280 | 280 | 250 | 250 |  | 300 | 335 | 337 | 336 | 0 | 0 | 42 | 6964612
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 256 | 256 | 259 | 260 | 260 | 233 | 258 | 210 | 210 | 210 | 210 | 210 | 210 | 224 | 215 | 212 | 210 |  | 212 | 212 | 213 | 212 | 200 | 200 | 200 | 5494907
19 | Ashuganj 195MW PP (APSCL-United) | 92 | 92 | 92 | 92 | 92 | 92 | 55 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 802909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4359600
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 270 | 310 | 310 | 310 | 310 | 310 | 310 | 7354173
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 33 | 32 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 33 | 837576
33 | Ashuganj 225 MW CCPP | 207 | 208 | 206 | 208 | 210 | 208 | 181 | 181 | 191 | 196 | 197 | 183 | 182 | 181 | 181 | 181 | 180 | 180 |  | 180 | 208 | 207 | 208 | 207 | 206 | 208 | 4726000
34 | Ashuganj 450 MW CCPP(South) | 325 | 305 | 340 | 305 | 280 | 265 | 265 | 230 | 220 | 220 | 305 | 275 | 305 | 310 | 320 | 320 | 280 | 280 |  | 280 | 325 | 325 | 325 | 325 | 320 | 305 | 7244000
| Ashuganj 450 MW CCPP(North) | 325 | 310 | 340 | 310 | 300 | 260 | 270 | 270 | 270 | 270 | 310 | 275 | 305 | 305 | 320 | 320 | 280 | 280 |  | 280 | 320 | 320 | 325 | 320 | 335 | 320 | 7735900
| Ashuganj 420 MW CCPP(East) | [7 empty] | 222 | 286 | 192 | 216 | 217 | 218 | 217 | 218 | 292 | 0 | [8 empty] | 0 | 2042500
35 | Ashuganj 55 MW PP (Precision) | 50 | 52 | 51 | 51 | 52 | 51 | 52 | 50 | 48 | 48 | 48 | 50 | 49 | 50 | 52 | 51 | 50 | 51 |  | 52 | 51 | 51 | 52 | 51 | 50 | 51 | 1219200
36 | Chandpur 150 MW CCPP | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 85 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 84 | 85 |  | 85 | 85 | 85 | 84 | 84 | 84 | 84 | 2019910
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5033150
41 | Haripur 360MW CCPP(HPL) | 317 | 328 | 327 | 333 | 333 | 332 | 337 | 338 | 328 | 328 | 322 | 322 | 323 | 322 | 322 | 322 | 312 | 312 |  | 322 | 322 | 332 | 337 | 337 | 327 | 327 | 7806000
42 | RPCL 210MW CCPP | 145 | 147 | 157 | 158 | 160 | 160 | 160 | 160 | 169 | 179 | 206 | 206 | 195 | 188 | 201 | 204 | 204 | 204 |  | 206 | 207 | 185 | 186 | 187 | 205 | 205 | 4271040
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 3 | 8 | 10 | 12 | 24 | 18 | 20 | 11 | 42 | 45 | 14 | 13 | 4 | [8 empty] | 205030
44 | Fenchugonj CCPP Phase-1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 772000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 983088
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 51 | 51 | 52 | 52 | 40 | 40 | 52 | 50 | 60 | 40 | 61 | 55 | 60 | 61 | 61 | 60 | 40 |  | 60 | 56 | 56 | 56 | 56 | 55 | 56 | 1264704
48 | Shahjibazar 86MW PP (Shahjibazar) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 86 | 86 | 86 | 86 | 1512960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 2367370
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [8 empty] | 4 | 15 | 19 | 24 | 26 | 26 | 27 | 26 | 0 | [9 empty] | 163800
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 170460
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | [8 empty] | 11 | 11 | 11 | 11 | 19 | 22 | 22 | 25 | [10 empty] | 142800
56 | Shahjahanulla 25 MW PP | 16 | 0 | 0 | 5 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 304656
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 310 | 290 | 300 | 280 | 270 | 280 | 280 | 265 | 290 | 285 | 300 | 300 | 270 | 280 | 250 | 270 | 270 |  | 280 | 265 | 275 | 290 | 270 | 300 | 300 | 7036000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 360 | 361 | 398 | 365 | 360 | 400 | 350 | 400 | 320 | 396 | 360 |  | 360 | 400 | 398 | 400 | 400 | 395 | 400 | 9241500
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 0 | [9 empty] | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 505790
59 | Tangail Palli Power Gen 22 MW | 21 | 24 | 24 | 24 | 23 | 23 | 24 | 18 | 18 | 18 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566160
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 21 | 21 | 21 | 21 | 21 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 486384
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 22 | 22 | 22 | 400320
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 464364
63 | Impoprt (Tripura) | 158 | 154 | 152 | 152 | 138 | 128 | 116 | 110 | 110 | 110 | 112 | 126 | 134 | 136 | 136 | 130 | 126 | 120 |  | 148 | 152 | 150 | 154 | 158 | 158 | 158 | 3269760
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 30 | 30 | 29 | 25 | 25 | 25 | 25 | 28 |  | 42 | 42 | 42 | 42 | 40 | 40 | 42 | 829920
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 10 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 383940
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 239220
67 | Jangalia 33MW PP (Summit) | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 25 | 20 | 16 | 16 | 30 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 718400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 509850
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 20 | 20 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 | 19 | 19 | 25 | 25 | 25 | 479340
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806600
72 | Rupganj 33 MW PP(Summit) | 32 | 33 | 33 | 33 | 33 | 8 | 8 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 22 | 27 | 583600
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 92 | 92 | 92 | 89 | 92 | 89 | 89 | 86 | 89 | 89 | 89 | 89 | 89 | 84 | 87 |  | 88 | 92 | 92 | 92 | 92 | 92 | 92 | 2131681
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 |  | 90 | 98 | 98 | 98 | 98 | 98 | 17 | 852720
| Chowmuhani 113 MW | 8 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 14 | 27 | 27 |  | 41 | 48 | 48 | 48 | 49 | 48 | 42 | 487200
| Manikgonj 162MW PP(MPGL) | 96 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 |  | 72 | 72 | 72 | 72 | 72 | 26 | 17 | 756000
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 64 | 84 | 91 | 93 | 99 | 100 | 99 | 95 | 50 |  | 55 | 99 | 96 | 92 | 98 | 100 | 100 | 1415040
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 12 | 32 | 32 | 32 | 25 | 25 |  | 48 | 49 | 49 | 49 | 50 | 50 | 50 | 796800
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 40 | 48 | 48 | 16 | 16 | 16 |  | 64 | 115 | 115 | 115 | 115 | 132 | 132 | 1558080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 16 | 16 |  | 21 | 34 | 32 | 39 | 43 | 43 | 8 | 382411
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 88 | 88 | 88 | 50 | 50 |  | 66 | 105 | 105 | 105 | 105 | 105 | 105 | 2116800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 4 | 4 | 2 | 5 | 5 | 6 | 2 | 4 | 1 | 1 | 0 | [8 empty] | 36721
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 37 | 37 | 37 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 1048219
| Karnaphuli Power Ltd. | 97 | 99 | 94 | 101 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 96 | 68 | 51 |  | 58 | 110 | 109 | 110 | 110 | 110 | 110 | 2493189
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 55 | 60 | 65 | 73 | 72 | 72 | 68 | 83 |  | 87 | 87 | 86 | 87 | 87 | 88 | 87 | 1410240
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 90 | 52 |  | 60 | 104 | 104 | 104 | 104 | 104 | 104 | 2498880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 10 |  | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 1245840
92 | Fenchuganj 44MW (Energyprima) | [8 empty] | 10 | 10 | 25 | 45 | 44 | 41 | 41 | 41 | 0 | [9 empty] | 280728
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1168571
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 50 |  | 85 | 94 | 94 | 94 | 94 | 94 | 94 | 2176704
95 | Patenga 50MW PP (Baraka) | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 45 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1073280
96 | Chattogram 108 MW PP (ECPV) | 86 | 85 | 86 | 78 | 85 | 63 | 63 | 32 | 11 | 11 | 11 | 19 | 69 | 79 | 84 | 54 | 37 | 30 |  | 43 | 79 | 79 | 79 | 79 | 80 | 78 | 1431360
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 1234894
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 615332
101 | Kushiara 163 MW CCPP (KP) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2288290
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 12 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 330840
104 | Keranigonj 300 MW PP (APR) | 306 | 227 | 174 | 83 | 23 | 21 | 0 | [5 empty] | 105 | [9 empty] | 105 | 156 | 250 | 255 | 1577279
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | 100 | 100 | 70 | 25 | 25 | 0 | [15 empty] | 50 |  |  | 0 | 502852
106 | Mymensingh 200 MW PP (United) | 116 | 116 | 115 | 115 | 116 | 116 | 116 | 115 | 115 | 115 | 115 | 114 | 114 | 114 | 114 | 113 | 120 | 120 |  | 120 | 177 | 188 | 188 | 188 | 200 | 115 | 3093600
112 | Aurahati 100MW PP (Aggreko) | 20 | 0 | [20 empty] | 25 | 42 | 64 | 70 | 166083
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 141 | 131 | 132 | 132 | 122 | 108 | 60 | 24 | 17 | 17 | 24 | 117 | 130 | 128 | 133 | 84 | 79 |  | 103 | 133 | 132 | 133 | 131 | 131 | 132 | 2517984
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 76 | 76 | 50 | 30 |  | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 1922880
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 170 | 170 | 170 | 200 | 200 | 200 | 200 | 200 | 200 | 100 |  | 114 | 200 | 180 | 200 | 200 | 200 | 200 | 4524000
117 | Ashuganj 150MW PP (Midland) | 132 | 127 | 133 | 132 | 132 | 133 | 133 | 125 | 100 | 100 | 100 | 107 | 122 | 130 | 123 | 125 | 123 | 127 |  | 133 | 137 | 133 | 137 | 135 | 138 | 138 | 3057745
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 405 | 402 | 401 | 353 | 352 | 353 | 364 | 402 | 403 | 402 | 402 | 353 | 402 | 353 | 403 | 352 |  | 353 | 402 | 403 | 401 | 401 | 403 | 402 | 9331000
| Jamalpur 115 MW PP (United) | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 |  | 65 | 115 | 115 | 115 | 115 | 115 | 61 | 1669200
| Anwara 300 MW PP (United) | 174 | 176 | 176 | 176 | 191 | 100 | 65 | [5 empty] | 15 | 45 | 50 | 50 | 15 | 15 |  | 171 | 254 | 258 | 262 | 262 | 262 | 262 | 2767527
| Juldah unit-2 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 50 | 50 | 65 | 78 | 75 | 75 | 90 | 75 | 40 |  | 44 | 95 | 95 | 95 | 98 | 92 | 98 | 1897920
| Anlima Energy Ltd. | 108 | 108 | 96 | 108 | 108 | 108 | 108 | 108 | 80 | 68 | 68 | 72 | 108 | 108 | 108 | 108 | 68 | 51 |  | 61 | 108 | 108 | 108 | 108 | 108 | 108 | 2357291
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 704880
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 4 | 10 | 24 | 21 | 30 | 30 | 20 | 29 | 15 | 26 | 10 | 2 | [8 empty] | 222597
| Chandpur 115(Doreen) | 45 | 35 | 35 | 36 | 35 | 36 | 36 | 35 | 36 | 35 | 35 | 36 | 36 | 35 | 35 | 35 | 42 | 71 |  | 71 | 72 | 72 | 72 | 72 | 72 | 60 | 1121280
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 36 | 54 | 54 | 45 | 37 | 36 | 36 | 37 | 36 | 37 | 36 | 37 | 42 |  | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 1137240
120 | Eastern Zone Total | 8543 | 8300 | 8235 | 8005 | 7838 | 7200 | 6927 | 6830 | 6667 | 6698 | 6846 | 6936 | 7414 | 7317 | 7476 | 7245 | 6753 | 6340 |  | 7108 | 8260 | 8165 | 8542 | 8203 | 8459 | 8248 | 181522943
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 40 | 49 | 49 | 41 | 48 | 49 | 16 | 514560
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 0 | [11 empty] | 21 |  | 34 | 48 | 37 | 35 | 34 | 34 | 34 | 350880
| Khulna 225 MW CCPP | 206 | 207 | 207 | 207 | 208 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 153 | 120 | 120 | 120 | 120 | 120 |  | 120 | 160 | 203 | 203 | 205 | 205 | 207 | 3902400
129 | Rupsha 105 MW PP (Orion rupsha) | 75 | 75 | 75 | 75 | 74 | 74 | 35 | 17 | [5 empty] | 17 | 35 | 35 | 17 | 17 |  | 18 | 35 | 53 | 53 | 55 | 55 | 55 | 921600
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 34 | 46 | 60 | 62 | 65 | 76 | 93 | 37 | 75 | 63 | 43 | 13 | [8 empty] | 602640
131
132 | United Payra Power Ltd. | 54 | 17 | 17 | 17 | 17 | 0 | [20 empty] | 164400
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 225 | 225 | 226 | 200 | 225 | 160 | 166 | 165 | 167 | 221 | 221 | 163 | 220 | 170 | 220 | 160 |  | 170 | 220 | 220 | 221 | 221 | 221 | 225 | 4971764
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 32 | 16 | 16 | 16 | 0 | [14 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 310656
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 88 | 88 | 87 | 88 | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 87 |  | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 2095707
140 | Bhola 33 MW PP (Venture) | 33 | 31 | 31 | 30 | 28 | 24 | 21 | 20 | 18 | 20 | 20 | 20 | 24 | 24 | 25 | 24 | 23 | 22 |  | 27 | 30 | 29 | 32 | 33 | 34 | 34 | 618978
141 | Noapara 100 MW PP (Bangla Trac) | 97 | 70 | 0 | [22 empty] | 18 | 241920
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192000
143 | Gopalganj 100 MW Peaking PP | 40 | 20 | 20 | 0 | [17 empty] | 10 | 35 | 50 | 62 | 64 | 279040
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 50 | 50 | 50 | 50 | 60 | 67 | 67 | 67 | 67 | 67 |  | 105 | 105 | 105 | 89 | 90 | 105 | 105 | 2054880
146 | Bheramara HVDC | 483 | 483 | 483 | 482 | 486 | 487 | 487 | 486 | 488 | 489 | 488 | 489 | 491 | 491 | 491 | 491 | 491 | 491 |  | 492 | 492 | 492 | 492 | 492 | 492 | 491 | 11823272
147 | Bheramara 410 MW CCPP | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 285 | 290 | 300 | 315 | 315 | 315 | 320 | 325 | 340 | 350 | 300 |  | 300 | 385 | 390 | 380 | 390 | 395 | 390 | 7962624
148 | Payra 1320 MW | 622 | 622 | 600 | 600 | 570 | 520 | 480 | 450 | 410 | 380 | 370 | 400 | 470 | 470 | 450 | 460 | 470 | 430 |  | 430 | 580 | 590 | 622 | 622 | 622 | 622 | 13391900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 245 | 250 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5500400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | [14 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 300936
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 2 | 2 | 5 | 4 | 2 | 1 | 1 | 0 | 1 | 0 | [8 empty] | 29220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 176 | 175 | 175 | 174 | 175 | 176 | 130 | 130 | 130 | 130 | 180 | 205 | 214 | 214 | 214 | 160 | 150 |  | 160 | 213 | 214 | 214 | 214 | 214 | 214 | 4641691
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 212 | 214 | 215 | 215 | 217 | 200 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 130 | 130 | 130 | 130 | 130 |  | 130 | 138 | 140 | 140 | 198 | 213 | 214 | 4151091
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 174 | 168 | 169 | 170 | 169 | 169 | 169 | 130 | 130 | 130 | 130 | 168 | 193 | 150 | 150 | 168 | 170 | 150 |  | 166 | 211 | 212 | 211 | 212 | 210 | 211 | 4452391
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 380 | 380 | 380 | 340 | 340 | 340 | 340 | 414 | 350 | 374 | 332 | 340 | 346 |  | 382 | 367 | 394 | 392 | 403 | 414 | 392 | 9221745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 23 | 23 | 23 | 25 | 25 | 0 | [11 empty] | 5 |  | 5 | 23 | 27 | 32 | 32 | 32 | 33 | 269924
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 20 | 20 | 19 | 19 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 489360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 268300
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 8 | 0 | [13 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 337216
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 16 | 0 | [13 empty] | 25 | 32 | 32 | 32 | 24 | 32 | 32 | 279300
168 | Santahar 50 MW Peaking PP | 37 | 37 | 36 | 36 | 36 | 0 | [11 empty] | 10 |  | 36 | 37 | 36 | 36 | 36 | 36 | 29 | 414903
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 52 |  | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 429134
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 45 | [8 empty] | 16 | 16 | 16 | 16 |  | 71 | 88 | 88 | 88 | 88 | 88 | 88 | 1007208
171 | Baghabari 200 MW PP (Paramount) | 169 | 120 | 40 | 0 | [21 empty] | 80 | 547650
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 70 | 70 | 70 | 70 | 76 | 84 | 94 | 94 | 50 | 35 |  | 40 | 94 | 94 | 94 | 113 | 113 | 113 | 2121888
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 95 | 95 | 70 | 70 | 70 | 70 | 90 | 113 | 113 | 113 | 50 | 35 |  | 90 | 90 | 113 | 113 | 113 | 113 | 113 | 2335968
173 | Rangpur 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 102 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 68 | 66 | 66 | 62 | 92 | 72 |  | 74 | 95 | 96 | 97 | 96 | 97 | 96 | 1810012
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 3 | 6 | 6 | 7 | 7 | 1 | 1 | 2 | 1 | 0 | [8 empty] | 29355
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 99 | 72 | 72 | 72 | 72 | 72 | 106 | 106 | 106 | 52 | 52 |  | 100 | 111 | 111 | 111 | 112 | 112 | 108 | 2305920
178