## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-10 | Sunday |  | EID MUBARAK
|  |  | Date (day): | 2022-07-10 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13310.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14873 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-09 | 2022-07-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 300 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 92 | 90 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 347 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 323 | 300 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 80 | 82 | 85 | 87 |  | 13 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 96 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 96 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 332 | 330 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 48 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 37 | 51 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 25 | 30
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 24 | 40 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 225 | 285 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel Shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 56 | 130 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 61 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 17 | 72 | 90 |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 36 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 1898 | 2932 | 3567 | 3921 | 921 | 986
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 11 | 16 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 44 | 44 | 44 |  | 6 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 123 | 125 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 50 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 10 | 55 | 55 | 45 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 50 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 30 | 40
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 80 | 80 |  | 28 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 200 | 265 |  | 35 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 36 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 50 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 90 | 75 | 90 |  | 25 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 82 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 601 | 821 | 1330 | 1414 | 356 | 639
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 203 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 280 | 320 | 320 | 40 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 270 | 320 | 330 | 30 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 217 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 31 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 47 | 48 | 50 | 52
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 55 | 55 | 55 | 140 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 25 | 123 | 135 | 135 |  | 15 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 84 | 136 | 136 | 136 |  | 27 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 75 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 144 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 31 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 8 | 40 |  | 12 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 58 | 75 | 40 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 72 | 36 | 72 | 43 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1666 | 1937 | 2017 | 2399 | 387 | 88
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 200 | 201 | 170 | 190
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 20 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 60 | 169 | 115 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 115 | 60 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 399 | 531 | 438.6 | 549 | 0 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 33 | 33 | 32 | 33 |  | 37 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 60 | 60 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 84 | 80 | 86
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 130 | 140 |  | 89 | ST under maint
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 310 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 382 | 396 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1488 | 1580 | 1593 | 1645 | 118 | 657
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 493 | 493 | 501 | 501
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 48 | 16 | 49 | 66 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 30 | 30 |  | 24 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 85 | 0 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 400 | 300 | 410
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 12 | 90 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 50 | 70 |  | 35 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 49 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 978 | 1186 | 1420 | 1553 | 98 | 108
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 32 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 32 | 20 | 32 |  | 8 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 85 | 85 | 87 | 107 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 520 | 622 | 622 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 224 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 90 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 728 | 893 | 996 | 1161 | 107 | 8
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 16 | 32 |  | 39 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 210 | 200 | 214
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 209 | 150 | 210
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 207 | 208 | 180 | 211
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 410 | 410 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 36 |  | 14 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 20 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 85 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 170 | 180 |  | 20 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 39 | 113 | 94 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1078 | 1471 | 1543 | 1796 | 171 | 141
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 97 | 70 | 97 |  | 16 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 112 | 113 | 113
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 311 | 409 | 406 | 435 | 244 | 16
|  | Total |  |  |  |  | 22678 | 21396 | 9147 | 11760 | 13310.6 | 14873 | 2402 | 2651
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8768.5195 | 11273.4 | 12759.84 | 14257.5917
| A. |  | 2022-07-09 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12204 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8857 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11760 | MW
| 3 | Day peak Generation : |  |  | 9147 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11273.4 | MW
| 4 | Evening peak Generation : |  |  | 11760 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 252.0322 | MKWHr | By Solar | 1.6291 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 153.7835 | MKWHr |  | By Oil: | 61.2492 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.3644 | MKWHr |  | By Hydro: | 2.9468 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2402 | MW | Dhaka | 3126.36 | 3126.36 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2651 | MW | Chittagong | 972.34 | 972.34 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5053 | MW | Khulna | 1574.6 | 1574.6 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1180.17 | MMCFD |  |  | Rajshahi | 1402.2 | 1402.2 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 174220982.582 | ii) Oil : | Taka | 829096447.24 | Comilla | 1302 | 1302 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 138309316 | Total | Taka | 1141626745.822 | Mymensingh | 1105 | 1105 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.2375 | MKWHr. | Sylhet | 494 | 494 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -510 | MW (E to W) at | 21:00 | hrs | Barisal | 391.9 | 391.9 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -536 | MW at | 20:00 | hrs | Rangpur | 905 | 905 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 11273.4 | 11273.4 |  | 0
| B. |  | 2022-07-10 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14873 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 3373 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 237.4935 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8130 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8931 | MKWHr. | ii) HVDC Flow at Peak Time |  | 493 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1661 | MKWHr. | iii) Maximum HVDC Flow : |  | 493 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.15 |  | (b) Today: | 90.36 |  | (c) Rule Curve: |  | 85.44
.

## YesterdayGen
2022-07-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 327 |  | 0 | 225 | 0 | 88 | 0 | 55 | 40 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 22 | 33 | 27 | 50 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 43 | 34 | 55 | 80 | 40 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 86 | 33 | 50 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 154 | 171 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 10 | 213 | 129 | 0 | 115 | 70 | 131 | 0 | 90 | 200 | 127 | 403 | 60 | 105 | 105 | 0 | 262 | 54 | 110 | 17 | 42 | 100 | 400 | 96 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 489 | 0 | 395 | 0 | 16 | 207 | 0 | 0 | 28 | 63 | 8 | 87 | 34 | 32 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 216 | 0 | 20 | 212 | 0 | 400 | 55 | 50 | 113 | 105 | 70 | 0 | 0 | 113 | 622 | 224 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7835 | 4369 | 12204 | 4014 | 489 | 1960 | 279 | 3426 | 822 | 124 | 423 | 729 | 154 | 0 | 0 | 90.05
2:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 0 | 331 |  | 0 | 225 | 0 | 87 | 0 | 55 | 170 | 0 | 0 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 22 | 33 | 27 | 50 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 43 | 34 | 55 | 80 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 85 | 33 | 50 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 150 | 173 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 86 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 213 | 0 | 0 | 116 | 0 | 131 | 0 | 90 | 200 | 132 | 402 | 60 | 105 | 105 | 0 | 200 | 54 | 110 | 17 | 39 | 100 | 400 | 94 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 490 | 0 | 395 | 0 | 16 | 207 | 0 | 0 | 28 | 10 | 8 | 87 | 33 | 32 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 216 | 0 | 0 | 213 | 0 | 381 | 55 | 0 | 113 | 105 | 70 | 0 | 0 | 113 | 580 | 224 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7695 | 4186 | 11881 | 4145 | 490 | 1944 | 0 | 3368 | 780 | 121 | 423 | 676 | 150 | 0 | 0 | 90.07
3:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 331 |  | 0 | 225 | 0 | 88 | 0 | 55 | 233 | 0 | 0 | 100 | 94 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 22 | 33 | 27 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 55 | 72 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 210 | 8 | 85 | 33 | 52 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 144 | 173 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 30 | 0 | 140 | 0 | 0 | 9 | 290 | 8 | 11 | 0 | 253 | 0 | 0 | 116 | 0 | 132 | 0 | 90 | 200 | 130 | 402 | 60 | 105 | 105 | 0 | 100 | 54 | 110 | 17 | 39 | 100 | 400 | 93 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 40 | 0 |  | 490 | 0 | 400 | 0 | 16 | 170 | 0 | 0 | 0 | 0 | 0 | 88 | 32 | 16 | 0 | 0 | 0 | 34 | 0 | 88 | 0 | 34 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 195 | 0 | 0 | 213 | 0 | 389 | 55 | 0 | 113 | 105 | 70 | 0 | 0 | 113 | 580 | 225 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7513 | 4042 | 11555 | 4216 | 490 | 1905 | 0 | 3259 | 780 | 123 | 365 | 468 | 144 | 0 | 0 | 90.09
4:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 87 | 0 | 55 | 335 | 0 | 0 | 100 | 94 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 13 | 33 | 27 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 55 | 78 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 210 | 8 | 84 | 33 | 52 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 0 | 20 | 136 | 173 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 30 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 263 | 0 | 0 | 116 | 0 | 128 | 0 | 90 | 200 | 118 | 401 | 60 | 105 | 68 | 0 | 30 | 54 | 103 | 17 | 39 | 100 | 400 | 92 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 490 | 0 | 400 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 214 | 0 | 381 | 55 | 0 | 113 | 105 | 69 | 0 | 0 | 113 | 580 | 225 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7417 | 3745 | 11162 | 4273 | 490 | 1886 | 0 | 3131 | 780 | 123 | 250 | 223 | 136 | 0 | 0 | 90.11
5:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 88 | 0 | 15 | 335 | 0 | 0 | 100 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 13 | 33 | 27 | 8 | 0 | 88 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 55 | 27 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 210 | 8 | 84 | 33 | 50 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 132 | 173 | 0 | 20 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 57 | 30 | 0 | 140 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 275 | 0 | 0 | 116 | 0 | 106 | 0 | 90 | 200 | 125 | 401 | 60 | 105 | 0 | 0 | 0 | 54 | 110 | 17 | 39 | 100 | 400 | 93 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 490 | 0 | 400 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 214 | 0 | 348 | 55 | 0 | 113 | 105 | 70 | 0 | 0 | 113 | 540 | 225 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7146 | 3652 | 10798 | 4306 | 490 | 1840 | 0 | 2883 | 740 | 123 | 250 | 164 | 132 | 0 | 0 | 90.13
6:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 87 | 0 | 15 | 335 | 0 | 0 | 37 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 13 | 33 | 27 | 0 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 211 | 8 | 84 | 31 | 52 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 120 | 173 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 56 | 30 | 0 | 140 | 0 | 0 | 9 | 270 | 8 | 11 | 0 | 30 | 0 | 0 | 116 | 0 | 32 | 1 | 10 | 200 | 10 | 402 | 60 | 50 | 0 | 0 | 0 | 54 | 17 | 17 | 38 | 100 | 360 | 42 | 1 | 17 | 99 | 0 | 35 | 1 | 36 | 55 | 0 |  | 490 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 215 | 0 | 350 | 55 | 0 | 113 | 105 | 70 | 0 | 0 | 113 | 480 | 224 | 0 | 0 | 0 | 6 | 52 | 0 | 0 |  | 6099 | 3472 | 9571 | 4218 | 490 | 1839 | 0 | 1850 | 680 | 115 | 250 | 130 | 120 | 9 | 0 | 90.15
7:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 87 | 0 | 15 | 335 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 25 | 13 | 33 | 24 | 0 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 84 | 31 | 51 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 33 | 20 | 116 | 173 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 61 | 30 | 0 | 140 | 0 | 0 | 7 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 116 | 0 | 16 | 6 | 10 | 155 | 10 | 402 | 60 | 17 | 0 | 1 | 0 | 54 | 17 | 17 | 38 | 100 | 360 | 17 | 10 | 17 | 100 | 0 | 35 | 4 | 36 | 17 | 0 |  | 490 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 214 | 0 | 399 | 55 | 0 | 35 | 105 | 70 | 0 | 1 | 35 | 480 | 225 | 0 | 0 | 0 | 29 | 34 | 0 | 0 |  | 5881 | 3318 | 9199 | 4144 | 490 | 1913 | 0 | 1440 | 680 | 115 | 250 | 130 | 116 | 51 | 0 | 90.17
8:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 88 | 0 | 15 | 335 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 13 | 33 | 24 | 0 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 21 | 42 | 0 | 0 | 0 | 275 | 305 | 208 | 8 | 85 | 31 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 20 | 110 | 173 | 0 | 22 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 9 | 280 | 8 | 11 | 0 | 30 | 0 | 0 | 116 | 0 | 17 | 5 | 10 | 100 | 10 | 377 | 60 | 17 | 0 | 3 | 0 | 36 | 17 | 17 | 39 | 72 | 360 | 17 | 25 | 17 | 60 | 0 | 35 | 0 | 36 | 17 | 197 |  | 491 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 213 | 0 | 397 | 55 | 0 | 35 | 105 | 70 | 0 | 2 | 35 | 470 | 185 | 0 | 0 | 2 | 35 | 34 | 0 | 0 |  | 5807 | 3259 | 9066 | 4235 | 491 | 1853 | 0 | 1269 | 670 | 115 | 250 | 130 | 110 | 73 | 0 | 90.19
9:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 0 | 332 |  | 0 | 225 | 0 | 81 | 0 | 15 | 270 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 13 | 33 | 24 | 0 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 270 | 305 | 208 | 8 | 86 | 33 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 33 | 20 | 110 | 171 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 8 | 270 | 8 | 11 | 0 | 30 | 0 | 0 | 116 | 0 | 17 | 8 | 10 | 51 | 10 | 377 | 60 | 17 | 0 | 4 | 0 | 36 | 17 | 17 | 39 | 30 | 360 | 17 | 38 | 17 | 34 | 0 | 35 | 25 | 35 | 17 | 218 |  | 491 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 213 | 0 | 350 | 17 | 0 | 35 | 105 | 70 | 0 | 3 | 35 | 440 | 185 | 0 | 0 | 3 | 76 | 34 | 0 | 0 |  | 5672 | 3185 | 8857 | 4188 | 491 | 1791 | 0 | 1105 | 640 | 123 | 250 | 130 | 110 | 159 | 0 | 90.21
10:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 332 |  | 0 | 225 | 0 | 80 | 0 | 15 | 250 | 0 | 37 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 25 | 10 | 33 | 24 | 0 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 270 | 305 | 207 | 8 | 85 | 33 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 28 | 20 | 106 | 171 | 0 | 20 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 8 | 280 | 8 | 0 | 0 | 30 | 0 | 0 | 60 | 0 | 17 | 14 | 10 | 51 | 10 | 378 | 60 | 17 | 0 | 5 | 0 | 36 | 20 | 17 | 39 | 30 | 360 | 17 | 50 | 17 | 55 | 0 | 35 | 31 | 35 | 17 | 217 |  | 491 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 211 | 0 | 396 | 0 | 0 | 35 | 67 | 70 | 0 | 4 | 35 | 400 | 185 | 0 | 0 | 4 | 94 | 34 | 0 | 0 |  | 5676 | 3120 | 8796 | 4156 | 491 | 1849 | 0 | 1017 | 600 | 123 | 250 | 130 | 106 | 204 | 0 | 90.23
11:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 0 | 327 |  | 0 | 225 | 0 | 80 | 0 | 15 | 329 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 25 | 8 | 33 | 24 | 0 | 0 | 88 | 35 | 100 | 0 | 3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 44 | 21 | 33 | 0 | 0 | 0 | 300 | 335 | 203 | 8 | 87 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 118 | 200 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 8 | 310 | 8 | 0 | 0 | 30 | 0 | 0 | 60 | 0 | 17 | 17 | 10 | 51 | 10 | 377 | 60 | 17 | 0 | 5 | 0 | 36 | 34 | 17 | 47 | 30 | 383 | 17 | 23 | 17 | 68 | 0 | 32 | 35 | 35 | 17 | 217 |  | 492 | 0 | 320 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 208 | 0 | 408 | 0 | 0 | 35 | 15 | 70 | 0 | 7 | 35 | 400 | 185 | 0 | 0 | 5 | 94 | 34 | 0 | 0 |  | 5890 | 3101 | 8991 | 4350 | 492 | 1870 | 0 | 1000 | 600 | 123 | 250 | 130 | 118 | 188 | 0 | 90.25
12:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 0 | 327 |  | 0 | 225 | 0 | 80 | 0 | 15 | 330 | 0 | 37 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 25 | 8 | 25 | 24 | 0 | 0 | 88 | 35 | 100 | 0 | 11 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 21 | 42 | 0 | 0 | 0 | 275 | 315 | 204 | 8 | 84 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 31 | 18 | 118 | 200 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 30 | 0 | 0 | 60 | 0 | 17 | 12 | 10 | 75 | 25 | 405 | 59 | 50 | 0 | 5 | 0 | 36 | 50 | 17 | 58 | 70 | 382 | 17 | 56 | 17 | 82 | 0 | 17 | 36 | 35 | 17 | 217 |  | 493 | 0 | 320 | 0 | 16 | 85 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 207 | 0 | 410 | 0 | 0 | 39 | 15 | 70 | 0 | 7 | 70 | 400 | 220 | 0 | 0 | 4 | 49 | 34 | 0 | 0 |  | 6052 | 3095 | 9147 | 4353 | 493 | 1895 | 0 | 1179 | 600 | 123 | 215 | 130 | 118 | 171 | 0 | 90.26
13:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 0 | 328 |  | 0 | 225 | 0 | 75 | 0 | 15 | 326 | 0 | 94 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 10 | 25 | 8 | 25 | 26 | 0 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 38 | 21 | 42 | 0 | 0 | 0 | 305 | 330 | 202 | 8 | 85 | 32 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 31 | 18 | 134 | 199 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 49 | 30 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 8 | 0 | 114 | 0 | 0 | 45 | 0 | 17 | 19 | 10 | 155 | 60 | 403 | 59 | 50 | 0 | 5 | 0 | 36 | 68 | 17 | 68 | 80 | 378 | 17 | 52 | 17 | 90 | 0 | 17 | 34 | 35 | 17 | 217 |  | 492 | 0 | 390 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 191 | 0 | 130 | 0 | 0 | 0 | 206 | 0 | 404 | 0 | 0 | 70 | 15 | 70 | 0 | 7 | 70 | 400 | 220 | 0 | 0 | 4 | 107 | 34 | 0 | 0 |  | 6473 | 3168 | 9641 | 4670 | 492 | 1894 | 0 | 1498 | 600 | 123 | 0 | 0 | 134 | 230 | 0 | 90.27
14:00 | 0 | 0 | 0 | 180 | 310 | 87 | 0 | 0 | 322 |  | 0 | 225 | 0 | 80 | 0 | 15 | 250 | 0 | 32 | 20 | 60 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 10 | 25 | 7 | 33 | 24 | 8 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 44 | 0 | 42 | 21 | 42 | 0 | 0 | 0 | 305 | 310 | 206 | 55 | 84 | 31 | 48 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 18 | 138 | 200 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 50 | 30 | 0 | 140 | 0 | 0 | 8 | 300 | 8 | 11 | 0 | 148 | 0 | 0 | 53 | 0 | 22 | 13 | 90 | 180 | 65 | 378 | 59 | 58 | 0 | 3 | 15 | 36 | 82 | 17 | 66 | 90 | 397 | 23 | 49 | 17 | 90 | 0 | 17 | 31 | 35 | 28 | 217 |  | 492 | 0 | 390 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 209 | 0 | 180 | 0 | 0 | 0 | 205 | 0 | 335 | 0 | 0 | 74 | 67 | 70 | 0 | 7 | 100 | 440 | 220 | 0 | 0 | 4 | 84 | 100 | 0 | 0 |  | 6671 | 3340 | 10011 | 4586 | 492 | 1876 | 0 | 1963 | 640 | 123 | 0 | 0 | 138 | 193 | 0 | 90.27
15:00 | 0 | 0 | 0 | 180 | 310 | 83 | 0 | 0 | 322 |  | 0 | 225 | 0 | 80 | 0 | 0 | 250 | 0 | 133 | 70 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 10 | 25 | 7 | 33 | 12 | 8 | 0 | 84 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 305 | 310 | 206 | 55 | 124 | 31 | 47 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 32 | 20 | 140 | 200 | 0 | 22 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 50 | 30 | 0 | 140 | 0 | 0 | 8 | 270 | 8 | 11 | 0 | 177 | 0 | 0 | 110 | 0 | 51 | 13 | 50 | 200 | 80 | 353 | 59 | 50 | 0 | 4 | 15 | 36 | 109 | 17 | 66 | 100 | 392 | 83 | 40 | 17 | 90 | 0 | 17 | 26 | 35 | 38 | 217 |  | 492 | 0 | 390 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 211 | 0 | 150 | 0 | 0 | 0 | 180 | 0 | 341 | 10 | 0 | 94 | 50 | 70 | 0 | 7 | 113 | 410 | 218 | 0 | 0 | 1 | 84 | 107 | 0 | 0 |  | 6951 | 3294 | 10245 | 4634 | 492 | 1847 | 0 | 2227 | 610 | 119 | 0 | 0 | 140 | 176 | 0 | 90.28
16:00 | 0 | 0 | 0 | 180 | 310 | 83 | 0 | 6 | 322 |  | 0 | 225 | 0 | 80 | 0 | 5 | 250 | 0 | 132 | 77 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 10 | 25 | 7 | 33 | 20 | 8 | 0 | 84 | 35 | 95 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 305 | 310 | 204 | 55 | 130 | 31 | 48 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 31 | 20 | 134 | 200 | 0 | 22 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 50 | 30 | 0 | 140 | 0 | 0 | 8 | 270 | 8 | 11 | 0 | 145 | 0 | 0 | 112 | 0 | 44 | 10 | 20 | 200 | 60 | 353 | 59 | 50 | 0 | 4 | 15 | 36 | 68 | 17 | 65 | 100 | 396 | 82 | 30 | 17 | 90 | 0 | 17 | 18 | 35 | 55 | 218 |  | 492 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 25 | 0 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 211 | 0 | 150 | 0 | 0 | 0 | 180 | 0 | 335 | 35 | 0 | 94 | 15 | 68 | 0 | 5 | 113 | 370 | 216 | 0 | 0 | 2 | 25 | 72 | 0 | 0 |  | 6808 | 3221 | 10029 | 4710 | 492 | 1839 | 0 | 2055 | 570 | 119 | 0 | 15 | 134 | 95 | 0 | 90.28
17:00 | 0 | 0 | 0 | 180 | 310 | 91 | 0 | 15 | 322 |  | 0 | 225 | 0 | 80 | 0 | 15 | 250 | 0 | 134 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 7 | 33 | 16 | 8 | 0 | 85 | 35 | 95 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 305 | 310 | 204 | 55 | 130 | 30 | 47 | 0 | 51 | 0 | 0 | 9 | 21 | 8 | 23 | 20 | 108 | 200 | 0 | 22 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 50 | 30 | 0 | 140 | 0 | 0 | 8 | 280 | 8 | 11 | 0 | 145 | 0 | 0 | 112 | 0 | 33 | 4 | 20 | 155 | 40 | 353 | 59 | 50 | 0 | 1 | 15 | 36 | 51 | 34 | 26 | 100 | 397 | 35 | 15 | 17 | 51 | 0 | 17 | 9 | 40 | 55 | 0 |  | 491 | 0 | 395 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 23 | 0 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 0 | 0 | 24 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 150 | 0 | 0 | 0 | 180 | 0 | 329 | 53 | 0 | 50 | 15 | 40 | 0 | 2 | 70 | 370 | 210 | 0 | 0 | 1 | 34 | 52 | 0 | 0 |  | 6347 | 3104 | 9451 | 4475 | 491 | 1842 | 0 | 1763 | 570 | 120 | 0 | 15 | 108 | 67 | 0 | 90.29
18:00 | 0 | 0 | 0 | 180 | 310 | 53 | 0 | 31 | 322 |  | 0 | 225 | 0 | 44 | 0 | 15 | 250 | 0 | 90 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 7 | 33 | 16 | 8 | 0 | 91 | 35 | 95 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 45 | 21 | 42 | 0 | 0 | 0 | 305 | 310 | 171 | 26 | 130 | 27 | 49 | 0 | 51 | 0 | 0 | 24 | 21 | 10 | 31 | 15 | 110 | 201 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 30 | 0 | 140 | 0 | 0 | 8 | 260 | 8 | 11 | 0 | 145 | 0 | 0 | 112 | 0 | 33 | 1 | 20 | 120 | 40 | 352 | 58 | 50 | 0 | 0 | 15 | 17 | 51 | 34 | 26 | 20 | 360 | 35 | 3 | 35 | 51 | 0 | 17 | 2 | 71 | 55 | 0 |  | 492 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 24 | 0 | 8 | 86 | 20 | 0 | 0 | 0 | 30 | 0 | 0 | 22 | 0 | 0 | 0 | 24 | 10 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 323 | 53 | 0 | 35 | 15 | 40 | 0 | 1 | 35 | 320 | 172 | 0 | 0 | 0 | 10 | 52 | 0 | 0 |  | 6051 | 2838 | 8889 | 4254 | 492 | 1710 | 0 | 1604 | 520 | 126 | 0 | 56 | 110 | 17 | 0 | 90.29
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 86 | 0 | 105 | 274 |  | 0 | 225 | 0 | 43 | 0 | 15 | 250 | 0 | 190 | 38 | 64 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 7 | 33 | 24 | 10 | 0 | 92 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 17 | 36 | 10 | 6 | 44 | 21 | 42 | 0 | 0 | 0 | 310 | 305 | 197 | 55 | 130 | 28 | 48 | 0 | 51 | 0 | 16 | 24 | 21 | 10 | 31 | 19 | 144 | 201 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 30 | 0 | 140 | 0 | 0 | 8 | 265 | 8 | 11 | 0 | 153 | 0 | 0 | 110 | 0 | 38 | 0 | 20 | 120 | 63 | 376 | 63 | 52 | 6 | 0 | 15 | 19 | 51 | 34 | 26 | 23 | 381 | 35 | 0 | 62 | 52 | 0 | 17 | 0 | 72 | 55 | 0 |  | 491 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 35 | 36 | 8 | 84 | 27 | 32 | 0 | 0 | 0 | 34 | 0 | 45 | 0 | 8 | 30 | 24 | 29 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 403 | 53 | 0 | 38 | 29 | 52 | 0 | 0 | 90 | 350 | 210 | 0 | 6 | 0 | 0 | 75 | 0 | 0 |  | 6561 | 3238 | 9799 | 4417 | 491 | 1853 | 0 | 1923 | 550 | 127 | 0 | 294 | 144 | 0 | 0 | 90.31
19:30 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 313 | 323 |  | 0 | 225 | 0 | 75 | 0 | 15 | 335 | 0 | 92 | 50 | 94 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 8 | 33 | 24 | 30 | 0 | 90 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 30 | 39 | 50 | 10 | 44 | 21 | 40 | 0 | 0 | 0 | 280 | 270 | 206 | 55 | 137 | 29 | 48 | 0 | 51 | 0 | 43 | 34 | 21 | 10 | 31 | 20 | 136 | 206 | 0 | 22 | 0 | 32 | 42 | 0 | 0 | 110 | 0 | 59 | 50 | 0 | 140 | 0 | 0 | 8 | 250 | 8 | 11 | 0 | 153 | 0 | 0 | 172 | 0 | 100 | 0 | 90 | 200 | 80 | 402 | 115 | 105 | 17 | 0 | 15 | 35 | 60 | 98 | 75 | 100 | 381 | 54 | 0 | 72 | 95 | 0 | 17 | 0 | 72 | 55 | 0 |  | 492 | 0 | 380 | 0 | 48 | 0 | 0 | 0 | 36 | 51 | 8 | 83 | 27 | 64 | 0 | 0 | 0 | 34 | 0 | 80 | 0 | 8 | 32 | 43 | 29 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 192 | 0 | 156 | 0 | 0 | 0 | 162 | 0 | 356 | 65 | 0 | 113 | 102 | 88 | 0 | 0 | 113 | 500 | 190 | 0 | 17 | 0 | 0 | 113 | 0 | 0 |  | 7702 | 3811 | 11513 | 4744 | 492 | 1844 | 0 | 3083 | 699 | 125 | 0 | 390 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 270 | 89 | 0 | 267 | 333 |  | 0 | 225 | 0 | 71 | 0 | 15 | 335 | 0 | 92 | 66 | 74 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 9 | 33 | 24 | 24 | 0 | 92 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 270 | 205 | 55 | 136 | 29 | 48 | 0 | 51 | 0 | 0 | 34 | 21 | 10 | 31 | 20 | 142 | 203 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 61 | 84 | 0 | 140 | 0 | 0 | 8 | 265 | 8 | 11 | 0 | 208 | 0 | 0 | 168 | 0 | 99 | 0 | 50 | 175 | 93 | 402 | 115 | 105 | 15 | 0 | 0 | 50 | 80 | 98 | 57 | 100 | 400 | 54 | 0 | 72 | 100 | 0 | 17 | 0 | 72 | 55 | 0 |  | 491 | 0 | 315 | 0 | 48 | 0 | 0 | 0 | 48 | 20 | 8 | 86 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 8 | 0 | 52 | 22 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 179 | 0 | 0 | 0 | 177 | 0 | 356 | 70 | 0 | 107 | 105 | 95 | 0 | 0 | 113 | 520 | 223 | 0 | 17 | 0 | 0 | 113 | 0 | 0 |  | 7580 | 3783 | 11363 | 4675 | 491 | 1934 | 0 | 3048 | 720 | 127 | 0 | 226 | 142 | 0 | 0 | 90.3
21:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 347 | 323 |  | 0 | 225 | 0 | 82 | 0 | 0 | 332 | 0 | 96 | 96 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 12 | 33 | 24 | 24 | 0 | 90 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 270 | 203 | 55 | 136 | 31 | 48 | 0 | 51 | 0 | 0 | 34 | 21 | 10 | 33 | 20 | 144 | 201 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 84 | 0 | 140 | 0 | 0 | 8 | 285 | 8 | 11 | 0 | 225 | 0 | 0 | 169 | 0 | 56 | 0 | 50 | 200 | 123 | 403 | 115 | 105 | 0 | 0 | 0 | 54 | 110 | 114 | 75 | 90 | 396 | 61 | 0 | 72 | 108 | 0 | 17 | 0 | 72 | 55 | 0 |  | 493 | 0 | 400 | 0 | 48 | 0 | 0 | 0 | 30 | 20 | 8 | 85 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 52 | 29 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 209 | 0 | 0 | 12 | 208 | 0 | 410 | 70 | 0 | 113 | 105 | 97 | 0 | 0 | 113 | 520 | 224 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 7801 | 3959 | 11760 | 4945 | 493 | 2009 | 12 | 3094 | 720 | 125 | 0 | 218 | 144 | 0 | 0 | 90.31
22:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 387 | 323 |  | 0 | 225 | 0 | 87 | 0 | 0 | 331 | 0 | 97 | 99 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 13 | 33 | 24 | 24 | 0 | 88 | 35 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 305 | 203 | 55 | 136 | 32 | 49 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 33 | 20 | 152 | 203 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 61 | 84 | 0 | 140 | 0 | 0 | 8 | 285 | 8 | 0 | 0 | 225 | 0 | 0 | 169 | 0 | 40 | 0 | 10 | 200 | 130 | 402 | 115 | 70 | 0 | 0 | 0 | 54 | 110 | 114 | 75 | 90 | 400 | 52 | 0 | 72 | 108 | 0 | 17 | 0 | 72 | 55 | 0 |  | 493 | 0 | 400 | 0 | 48 | 0 | 0 | 0 | 32 | 20 | 8 | 85 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 52 | 29 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 210 | 0 | 0 | 52 | 209 | 0 | 410 | 70 | 0 | 113 | 105 | 96 | 0 | 0 | 113 | 520 | 221 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 7825 | 4004 | 11829 | 5064 | 493 | 2008 | 52 | 2997 | 720 | 123 | 0 | 220 | 152 | 0 | 0 | 90.31
23:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 398 | 326 |  | 0 | 225 | 0 | 87 | 0 | 0 | 336 | 0 | 192 | 99 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 13 | 33 | 24 | 24 | 0 | 82 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 270 | 208 | 55 | 137 | 33 | 49 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 150 | 207 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 62 | 84 | 0 | 140 | 0 | 0 | 8 | 285 | 8 | 8 | 0 | 225 | 0 | 0 | 187 | 0 | 34 | 0 | 10 | 200 | 133 | 402 | 115 | 70 | 0 | 0 | 0 | 54 | 110 | 114 | 75 | 94 | 400 | 52 | 0 | 72 | 108 | 0 | 17 | 0 | 54 | 54 | 0 |  | 493 | 0 | 405 | 0 | 49 | 0 | 0 | 0 | 32 | 20 | 8 | 87 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 211 | 0 | 0 | 95 | 210 | 0 | 374 | 70 | 0 | 113 | 105 | 96 | 0 | 0 | 113 | 540 | 224 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 7882 | 4047 | 11929 | 5130 | 493 | 1981 | 95 | 3003 | 740 | 117 | 0 | 220 | 150 | 0 | 0 | 90.32
24:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 398 | 326 |  | 0 | 225 | 0 | 89 | 0 | 0 | 334 | 0 | 196 | 99 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 23 | 35 | 22 | 25 | 12 | 25 | 18 | 24 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 315 | 207 | 55 | 136 | 33 | 50 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 33 | 20 | 154 | 207 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 61 | 84 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 8 | 0 | 225 | 0 | 0 | 115 | 0 | 35 | 0 | 10 | 200 | 135 | 402 | 59 | 70 | 0 | 0 | 0 | 54 | 110 | 114 | 75 | 90 | 400 | 50 | 0 | 72 | 108 | 0 | 34 | 0 | 45 | 54 | 0 |  | 493 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 32 | 20 | 8 | 87 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 211 | 0 | 0 | 98 | 210 | 0 | 413 | 71 | 0 | 113 | 105 | 95 | 0 | 0 | 113 | 580 | 224 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7788 | 4043 | 11831 | 5153 | 493 | 2026 | 98 | 2789 | 780 | 118 | 0 | 220 | 154 | 0 | 0 | 90.32
KWH | 0 | 0 | 0 | 4331250 | 7418109 | 2054318 | 0 | 1972220 | 7798000 |  | 0 | 5037000 | 0 | 1929600 | 0 | 486821 | 6767021 | 0 | 1588000 | 1352640 | 1053648 | 507360 | 0 | 0 | 0 | 0 | 330480 | 611496 | 513257 | 343584 | 600000 | 298260 | 782500 | 585500 | 418080 | 0 | 2106764 | 840000 | 2300000 | 0 | 331227 | 0 | 0 | 0 | 0 |  | 350880 | 116544 | 334395 | 460440 | 352320 | 1052160 | 510336 | 1052640 | 0 | 0 | 0 | 7617400 | 7410000 | 4966000 | 669090 | 2471490 | 735984 | 1187040 | 0 | 1184753 | 0 | 123640 | 390182 | 411660 | 239580 | 773600 | 500000 | 3166080 | 4455360 | 0 | 475128 | 15000 | 772000 | 989152 | 0 | 0 | 2615727 | 0 | 1257312 | 1175040 | 0 | 3371830 | 0 | 0 | 193680 | 6913500 | 192560 | 204912 | 56064 | 3806290 | 298105 | 0 | 2733600 | 81723 | 1292112 | 119070 | 949440 | 3889440 | 2005600 | 9314000 | 165800 | 1584000 | 520218 | 35039 | 850582 | 1111527 | 1845846 | 902880 | 1228080 | 1935360 | 9188900 | 1211520 | 390970 | 776160 | 2133982 | 0 | 659160 | 258690 | 1095360 | 1020240 | 1859200 |  | 11893090 | 0 | 9023904 | 0 | 525120 | 1763520 | 0 | 0 | 260160 | 246016 | 82875 | 2098217 | 632043 | 361820 | 0 | 0 | 120000 | 136376 | 85139 | 756992 | 0 | 165904 | 118678 | 409858 | 297554 | 470880 | 0 | 255906 | 0 | 0 | 4877400 | 0 | 0 | 5188127 | 0 | 2089358 | 2076161 | 0 | 307200 | 5098455 | 0 | 9131418 | 1070880 | 104775 | 1992384 | 1860048 | 1720387 | 0 | 53177 | 2155104 | 12487000 | 5091573 | 0 | 26400 | 37920 | 719280 | 1857600 | 0 | 0 |  | 164383508 | 87648699 | 252032207 | 108576815 | 11893090 | 45206702 | 847867 | 53578808 | 17364400 | 2946764 | 3839681 | 2982854 | 3166080 | 1629146 | 0
Fuel Cost | 0 | 0 | 0 | 6453562.5 | 8308282.08 | 2732242.94 | 0 | 2070831 | 8421840 |  | 0 | 5490330 | 0 | 21572928 | 0 | 6450378.25 | 7579063.52 | 0 | 2779000 | 19775596.8 | 14824827.36 | 8224305.6 | 0 | 0 | 0 | 0 | 4203705.6 | 8255196 | 6882776.37 | 257688 | 450000 | 0 | 0 | 0 | 7111540.8 | 0 | 568826.28 | 226800 | 4347000 | 0 | 5415561.45 | 0 | 0 | 0 | 0 |  | 4578984 | 1943953.92 | 5691402.9 | 6220544.4 | 4467417.6 | 12173491.2 | 648126.72 | 3505291.2 | 0 | 0 | 0 | 8455314 | 8076900 | 5760560 | 863126.1 | 3015217.8 | 831661.92 | 1768689.6 | 0 | 1978537.51 | 0 | 2135262.8 | 5247947.9 | 563974.2 | 179685 | 1353800 | 375000 | 22732454.4 | 4856342.4 | 0 | 646174.08 | 239100 | 1057640 | 1305680.64 | 0 | 0 | 3008086.05 | 0 | 2439185.28 | 2679091.2 | 0 | 3405548.3 | 0 | 0 | 383486.4 | 6913500 | 144420 | 155733.12 | 1175101.44 | 51955858.5 | 6248280.8 | 0 | 36848928 | 1689214.41 | 17895751.2 | 1391928.3 | 9798220.8 | 53129750.4 | 26614312 | 8568880 | 2016128 | 22904640 | 6580757.7 | 0 | 9985832.68 | 12104529.03 | 19621342.98 | 12252081.6 | 15829951.2 | 22798540.8 | 8453788 | 15689184 | 5649516.5 | 9849470.4 | 24284715.16 | 0 | 8608629.6 | 3091345.5 | 16397539.2 | 13436560.8 | 0 |  | 35679270 | 0 | 10106772.48 | 0 | 5466499.2 | 29098080 | 0 | 0 | 4685481.6 | 4428288 | 1190913.75 | 2350003.04 | 1226163.42 | 3943838 | 0 | 0 | 246000 | 2287025.52 | 1489081.11 | 11839354.88 | 0 | 2747370.24 | 2006844.98 | 5586364.54 | 5019735.98 | 974721.6 | 0 | 193720.842 | 0 | 0 | 25801446 | 0 | 0 | 6018227.32 | 0 | 2674378.24 | 36249771.06 | 0 | 6445056 | 5914207.8 | 0 | 9040103.82 | 14392627.2 | 2197131.75 | 23569902.72 | 26877693.6 | 21848914.9 | 0 | 587605.85 | 26162962.56 | 112507870 | 5193404.46 | 0 | 195360 | 428875.2 | 8437154.4 | 28477008 | 0 | 0 |  | 727074392.19 | 493585230.062 | 1220659622.252 | 120042368.282 | 35679270 | 54178614.3 | 17754784.4 | 696243074.49 | 138309316 | 795626.28 | 65347851.06 | 49750737.29 | 22732454.4 | 19825525.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 0 | 327 |  | 0 | 225 | 0 | 80 | 0 | 15 | 330 | 0 | 37 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 25 | 8 | 25 | 24 | 0 | 0 | 88 | 35 | 100 | 0 | 11 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 21 | 42 | 0 | 0 | 0 | 275 | 315 | 204 | 8 | 84 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 31 | 18 | 118 | 200 | 0 | 22 | 2 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 30 | 0 | 140 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 30 | 0 | 0 | 60 | 0 | 17 | 12 | 10 | 75 | 25 | 405 | 59 | 50 | 0 | 5 | 0 | 36 | 50 | 17 | 58 | 70 | 382 | 17 | 56 | 17 | 82 | 0 | 17 | 36 | 35 | 17 | 217 |  | 493 | 0 | 320 | 0 | 16 | 85 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 207 | 0 | 410 | 0 | 0 | 39 | 15 | 70 | 0 | 7 | 70 | 400 | 220 | 0 | 0 | 4 | 49 | 34 | 0 | 0 |  | 9147 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 347 | 323 | 0 | 0 | 225 | 0 | 82 | 0 | 0 | 332 | 0 | 96 | 96 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 12 | 33 | 24 | 24 | 0 | 90 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 10 | 0 | 44 | 21 | 42 | 0 | 0 | 0 | 280 | 270 | 203 | 55 | 136 | 31 | 48 | 0 | 51 | 0 | 0 | 34 | 21 | 10 | 33 | 20 | 144 | 201 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 60 | 84 | 0 | 140 | 0 | 0 | 8 | 285 | 8 | 11 | 0 | 225 | 0 | 0 | 169 | 0 | 56 | 0 | 50 | 200 | 123 | 403 | 115 | 105 | 0 | 0 | 0 | 54 | 110 | 114 | 75 | 90 | 396 | 61 | 0 | 72 | 108 | 0 | 17 | 0 | 72 | 55 | 0 |  | 493 | 0 | 400 | 0 | 48 | 0 | 0 | 0 | 30 | 20 | 8 | 85 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 8 | 0 | 52 | 29 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 209 | 0 | 0 | 12 | 208 | 0 | 410 | 70 | 0 | 113 | 105 | 97 | 0 | 0 | 113 | 520 | 224 | 0 | 0 | 0 | 0 | 112 | 0 | 0 |  | 11760 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 412 | 320 | 0 | 0 | 225 | 0 | 87 | 0 | 55 | 335 | 0 | 100 | 100 | 94 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 28 | 33 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 55 | 80 | 44 | 21 | 40 | 0 | 0 | 0 | 320 | 330 | 210 | 55 | 136 | 35 | 52 | 0 | 51 | 0 | 50 | 40 | 22 | 11 | 33 | 20 | 165 | 190 | 0 | 22 | 0 | 33 | 42 | 0 | 0 | 110 | 0 | 64 | 86 | 0 | 140 | 0 | 0 | 10 | 341 | 8 | 11 | 200 | 285 | 300 | 50 | 200 | 100 | 133 | 0 | 90 | 200 | 135 | 400 | 115 | 105 | 105 | 0 | 265 | 54 | 110 | 114 | 113 | 90 | 400 | 104 | 0 | 72 | 108 | 0 | 35 |  | 72 | 55 |  |  | 501 | 0 | 410 | 0 | 49 | 220 | 0 | 0 | 30 | 60 | 8 | 87 | 32 | 110 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 10 | 214 | 0 | 210 | 0 | 0 | 100 | 211 | 0 | 414 | 70 | 180 | 113 | 105 | 97 | 0 | 0 | 113 | 622 | 220 |  | 90 |  |  | 113
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 85 | 0 | 55 | 330 | 0 | 100 | 100 | 94 | 130 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 26 | 33 | 25 | 40 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 51 | 55 | 80 | 44 | 21 | 30 | 0 | 0 | 0 | 320 | 320 | 210 | 55 | 136 | 35 | 50 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 143 | 170 | 0 | 20 | 1.6 | 32 | 42 | 0 | 0 | 110 | 0 | 60 | 80 | 0 | 130 | 0 | 0 | 10 | 310 | 8 | 11 | 100 | 285 | 200 | 0 | 115 | 0 | 130 | 20 | 90 | 200 | 135 | 400 | 60 | 105 | 105 | 5 | 200 | 36 | 110 | 17 | 40 | 75 | 400 | 104 | 50 | 17 | 108 | 0 | 35 | 30 | 36 | 55 |  |  | 501 | 0 | 300 | 0 | 16 | 220 | 0 | 0 | 30 | 0 | 8 | 85 | 20 | 32 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 0 | 200 | 0 | 150 | 0 | 0 | 90 | 180 | 0 | 414 | 50 | 170 | 94 | 105 | 70 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 113
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 230 | 42 | 0 | 396 | 292 | 0 | 0 | 225 | 0 | 88 | 0 | 15 | 250 | 0 | 74 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 25 | 0 | 0 | 14 | 0 | 0 | 92 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 7 | 21 | 42 | 0 | 0 | 0 | 280 | 270 | 180 | 55 | 136 | 33 | 51 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 94 | 150 | 0 | 13 | 1 | 33 | 42 | 0 | 0 | 110 | 0 | 40 | 60 | 0 | 130 | 0 | 0 | 8 | 250 | 8 | 8 | 0 | 140 | 0 | 0 | 24 | 0 | 20 | 4 | 10 | 51 | 70 | 353 | 59 | 17 | 0 | 3 | 0 | 35 | 34 | 17 | 8 | 40 | 340 | 36 | 12 | 0 | 34 | 0 | 35 | 13 | 36 | 50 | 0 | 0 | 493 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 30 | 0 | 0 | 0 | 115 | 0 | 215 | 0 | 0 | 70 | 15 | 68 | 0 | 2 | 113 | 400 | 163 | 0 | 0 | 2 | 42 | 0 | 0 | 0 | 0 |  |  |  |  | 61249210 |  | 0
61249210
| Minimum Generation |  | 8857 | 9:00
| Highest Generation |  | 12204 | 1:00
| Day Peak Generation |  | 9147 | 12:00
| Evening Peak Generation |  | 11760 | 21:00
| HVDC Max Flow |  | 493 | 12:00
| HVDC EvPeak Flow |  | 493 | 21:00
| Load factor L.F |  | 86.05%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  | EID MUBARAK | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-10
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9147 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8130 | MW
Evening Peak Generation : |  | 11760 | MW Hour : | 21:00 | Available Max Generation : |  | 14873 | MW
E.P. Demand (at gen end) : |  | 11760 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 12204 | MW Hour : | 1:00 | Reserve(Generation end) |  | 3373 | MW
Total Gen. (MKWH) : |  | 252.0322 | System Load Factor : | 86.05% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -536 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-10
Actual : | 90.36 | Ft.(MSL) , | Rule curve : | 85.44 | Ft.( MSL )
Gas Consumed : | Total = | 1180.17 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 174220982.582
: |  | Coal : | 138309316 | Oil : | 829096447.24 | Total : | 1141626745.822
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3982.4209 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1052.3728 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1408.8473 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1259.4333 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1118.4503 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 826.4842 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 452.9491 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 308.0436 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 625.5011 |  |  | 0 | 0%
Total | 0 |  | 11034.5026 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sonargaon 132/33 kV T-1 transformer was under shut down from 08:55 to 09:56 for C/M. | [5 empty] | About 15 MW power interruption occurred under
Sonargaon S/S area from 08:55 to 09:56.
b) Bhandaria 132/33 kV T-2 transformer was shut down from 10:10 to for C/M.
c) Baroierhat 132/33 kV T-1 transformer was shut down from 10:53 to 12:02 for C/M | [5 empty] | About 20 MW power interruption occurred under
Baroierhat S/S area from 10:53 to 12:02.
d) Khulna-225 MW CCPP GT & ST were shut down at 12:40 & 12:25 respectively for low demand.
e) Khulna© 132/33 kV T-2 transformer was shut down at 12:32 for changing fuse of 33 kV bus PT and was
switched on at 12:58.
f) Siddirganj GT-1 was synchronized at 11:12.
g) Haripur-412 MW CCPP GT & ST were synchronized at 15:22 & 18:04 respectively.
h)Baghabari-71 MW was synchronized at 15:47 and shut down at 18:47 due to gas booster problem.
i) Siddirganj GT-2 was synchronized at 14:23 and tripped at 19:26 showing E/F relay.
j) Shahjadpur 132/33 kV T-3 transformer tripped at 15:21 for C/M and was switched on at 15:58. | [5 empty] | About 15 MW power interruption occurred under
Shahjadpur S/S area from 15:21 to 15:58.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4331250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7418109 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 92 | 2054318 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 1972220
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 7798000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5037000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 82 | 1929600 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 486821
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 343584
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 96 | 1588000 | GT-2 under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 96 | 1352640 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 6767021
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 1053648 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 330480 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 507360 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 611496 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 513257 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 898260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 782500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 585500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 24 | 418080 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 225 | 3806290 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 298105 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 81723 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 56 | 1292112 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1584000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 61 | 1211520 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 776160 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 258690
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1020240
| Dhaka area Total |  |  |  | 5847 | 2932 | 57107984
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 331227 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119070
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1052160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 2946764 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 520218 | Low demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 116544 | Reserve.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 334395 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 460440 | Low demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 949440 | Low demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 510336
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1052640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 352320 | Reserve.
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 850582 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1111527
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1845846
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1935360 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2133982 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 821 | 18957890
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4966000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7617400 | Machine problem
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7410000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 1859200 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 31 | 735984 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1187040 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 669090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1184753
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 2005600 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 123640 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 2471490 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3889440
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 411660
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 239580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 3166080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 773600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 390182 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 500000 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 56064 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 902880
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 1228080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 659160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1095360 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 1937 | 43542283
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 201 | 4455360
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 475128
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 169 | 2733600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 165800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 390970
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 350880
| Mymensingh Area Total |  |  |  | 614 | 531 | 8586738
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 33 | 772000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 989152 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2615727 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204912
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1257312 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1175040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3371830 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 192560 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6913500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9314000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 193680
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 9188900
| Sylhet Area Total |  |  |  | 2477 | 1580 | 36188613
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 493 | 11893090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 525120 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 260160 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 1763520 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 246016 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 9023904
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 82875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 12 | 307200 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1070880 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1860048
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 719280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1186 | 27752093
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 361820 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 632043 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2098217 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 12487000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 5091573
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 26400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 893 | 20697053
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 120000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 136376 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 85139 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 165904 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 118678 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 210 | 5188127
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 209 | 4165519
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 208 | 5098455
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 9131418 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 297554 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 470880
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255906
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 409858
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 756992 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 104775 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1992384
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2155104
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37920
| Rajshahi Area Total |  |  |  | 2129 | 1471 | 30690989
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4877400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 97 | 1720387 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53177
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 112 | 1857600
| Rangpur Area Total |  |  |  | 720 | 409 | 8508564
| Total |  |  |  | 21396 | 11760 | 252032207
| Eastern Grid Total |  |  |  | 14205 | 7801 | 164383508
| Western Grid Total |  |  |  | 7191 | 3959 | 87648699
| National Grid Total |  |  |  | 21396 | 11760 | 252032207
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-09
(a) ENTIRE EASTERN GRID : |  | 6999.7 | MW | (b) ENTIRE WESTERN GRID : |  | 4273.7 | MW
i) Dhaka area |  | 3126.36 | MW | i) Khulna area |  | 1574.6 | MW
ii) Chittagong area |  | 972.34 | MW | ii) Rajshahi area |  | 1402.2 | MW
iii) Comilla area |  | 1302 | MW | iii) Barisal area |  | 391.9 | MW
iv) Mymensingh area |  | 1105 | MW | iv) Rangpur area |  | 905 | MW
v) Sylhet area |  | 494 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11273.4 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 10 | 00:00 | Chowmuhani | 210 | 21:00 | Kaptai | 4 | 18:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 6 | 10:00 | Chuadanga | 111 | 23:00 | Kazla | 55 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 28 | 00:00 | Coxsbazar | 103 | 13:00 | Keranigonj | 46 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 67 | 21:00 | Cumilla(N) | 156 | 23:00 | Khagrachori | 26 | 20:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 70 | 00:00 | Cumilla(S) | 158 | 00:00 | Khulna | 87 | 00:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 64 | 00:00 | Daudkandi | 176 | 08:00 | Khulshi | 140 | 00:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 40 | 21:00 | Dhaka | 18 | 11:00 | Kishoreganj | 160 | 19:30 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 130 | 01:00 | Dhamrai | 88 | 00:00 | Kodda | 148 | 00:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 98 | 00:00 | Dhanmondi | 84 | 17:00 | Kulaura | 50 | 19:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 103 | 00:00 | Dohazari | 104 | 19:30 | Kurigram | 70 | 20:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 38 | 00:00 | Faridpur | 150 | 21:00 | Kushtia | 122 | 00:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 6 | 11:00 | Fatullah | 42 | 00:00 | Lalbag | 48 | 00:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 53 | 21:00 | Fenchuganj | 50 | 19:00 | Lalmonirhat | 55 | 20:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 129 | 23:00 | Madanganj | 80 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 111 | 23:00 | GPH | 27 | 08:00 | Madaripur | 114 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 62 | 22:00 | Ghorashal | 62 | 00:00 | Madartek | 76 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 46 | 00:00 | Goalpara | 26 | 00:00 | Madunaghat | 63 | 21:00 | Rajshahi | 132 | 22:00
Baroirhat | 55 | 00:00 | Gollamari | 48 | 00:00 | Magura | 62 | 23:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 122 | 19:30 | Gopalganj | 105.2 | 23:00 | Mahasthangarh | 74 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 2 | 00:00 | Gulshan | 78 | 19:30 | Manikganj | 83 | 00:00 | Rampur | 16 | 00:00
Beanibazar | 74 | 19:30 | Halishahar | 62 | 00:00 | Maniknagar | 53 | 00:00 | Rangamati | 14 | 19:00
Benapole | 54 | 00:00 | HaripurSBU | 83 | 00:00 | Matarbari | 43 | 00:00 | Rangpur | 105 | 08:00
Bhaluka | 110 | 00:00 | Hasnabad | 67 | 00:00 | Matuail | 32 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 58 | 00:00 | Hathazari | 91 | 00:00 | Millgate | 28 | 00:00 | SSM | 3 | 05:00
Bhangura | 35 | 20:00 | Ishurdi | 67 | 00:00 | Mirpur | 100.5 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 63 | 00:00 | Jaldhaka | 73 | 20:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 144 | 00:00 | Jamalpur | 149 | 22:00 | Mithapukur | 34 | 00:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 58 | 00:00 | Jashore | 124 | 22:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 155 | 00:00 | Jhenaidah | 126 | 00:00 | Mogbazar | 86 | 19:30 | Shahjadpur | 85 | 22:00
Borhanuddin | 44 | 00:00 | Joydebpur | 123 | 00:00 | Mongla | 22 | 05:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 180 | 20:00 | Joypurhat | 60 | 21:00 | Motijheel | 25 | 18:30 | Shahmirpur | 46.5 | 18:30
Cantonment | 114 | 21:00 | Juldah | 16 | 00:00 | Munshiganj | 101 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 69 | 22:00 | KSRM | 6.55 | 00:00 | Mymensingh | 223 | 23:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 22:00 | Kabirpur | 121 | 00:00 | Naogaon | 140 | 11:00 | Shikalbaha | 28 | 19:00
Chapai | 68 | 01:00 | Kachua | 84 | 23:00 | Narail | 47 | 23:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 20 | 00:00 | Kallyanpur | 87 | 00:00 | Narinda | 42 | 00:00 | Shitalakhya | 114 | 12:00
Chauddagram | 50 | 23:00 | Kalurghat | 0 | 00:00 | Narshingdi | 158 | 01:00 | Sholosohor | N/A | N/A
Chhatak | 32 | 21:00 | Kamrangirchar | 32 | 00:00 | Natore | 145 | 00:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 405 | 18:30 | 375 | 09:00 | Kaliakoir | 403 | 18:30 | 392 | 11:00
| Bibiana | 416 | 19:30 | 405 | 13:00 | Payra | 417 | 18:00 | 406 | 00:00
| BIPTC | 408 | 06:00 | 396 | 23:00
| Gopalganj_I | 416 | 18:30 | 395 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 18:30 | 223 | 11:00 | Hasnabad | 232 | 18:30 | 224 | 13:00
| AKSML | 228 | 14:00 | 220 | 09:00 | Hathazari | 234 | 00:00 | 221 | 07:00
| Aminbazar | 232 | 17:00 | 226 | 09:00 | Ishurdi | 237 | 18:00 | 225 | 21:00
| Ashuganj | 240 | 17:00 | 233 | 11:00 | Jhenaidah | 230 | 18:00 | 212 | 20:00
| Baghabari | 234 | 18:00 | 226 | 03:00 | Kaliakoir | 234 | 18:30 | 225 | 09:00
| Barapukuria | 222 | 15:00 | 210 | 00:00 | Keranigonj | 230 | 18:30 | 222 | 11:00
| Barishal | 242 | 18:30 | 233 | 00:00 | Khulna(S) | 239 | 08:00 | 222 | 21:00
| Bheramara | 235 | 18:00 | 223 | 13:00 | Maniknagar | 233 | 18:30 | 225 | 09:00
| Bhulta | 234 | 18:00 | 226 | 09:00 | Meghnaghat | 234 | 21:00 | 228 | 13:00
| Bibiana | 241 | 18:00 | 235 | 00:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 18:00 | 220 | 20:00 | Rajshahi | 232 | 18:30 | 219 | 21:00
| Bogura | 230 | 18:30 | 218 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 18:30 | 239 | 00:00 | Rampura | 231 | 20:00 | 222 | 09:00
| BSRM | 232 | 00:00 | 222 | 09:00 | Shikalbaha | 238 | 02:00 | 219 | 10:00
| Cumilla(N) | 233 | 18:30 | 227 | 08:00 | Shyampur | 231 | 18:30 | 223 | 11:00
| Fenchuganj | 243 | 18:30 | 237 | 00:00 | Siddhirganj | 233 | 18:00 | 225 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 18:30 | 226 | 00:00
| GPH | 231 | 06:00 | 223 | 13:00 | Tongi | 234 | 18:00 | 225 | 13:00
| Haripur | 231 | 19:30 | 224 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 18:00 | 133 | 00:00 | Lalbag | 140 | 18:30 | 136 | 12:00
| Agargaon | 138 | 18:30 | 133 | 13:00 | Lalmonirhat | 126 | 05:00 | 115 | 20:00
| Agrabad | 138 | 01:00 | 128 | 09:00 | Madanganj | 138 | 20:00 | 132 | 07:00
| AKS | 136 | 00:00 | 126 | 09:00 | Madaripur | 136 | 18:30 | 129 | 00:00
| Aminbazar | 136 | 17:00 | 131 | 00:00 | Madartek | 136 | 18:00 | 131 | 11:00
| Amnura | 133 | 17:00 | 124 | 13:00 | Madunaghat | 139 | 01:00 | 129 | 09:00
| Ashuganj | 138 | 18:30 | 133 | 00:00 | Magura | 140 | 18:00 | 125 | 22:00
| Bagerhat | 135 | 07:00 | 121 | 20:00 | Mahasthangarh | 133 | 18:30 | 122 | 00:00
| Bakulia | 136 | 00:00 | 128 | 08:00 | Manikganj | 138 | 18:00 | 130 | 22:00
| Banani | 140 | 18:00 | 134 | 00:00 | Maniknagar | 134 | 18:30 | 130 | 11:00
| Bangabhaban | 134 | 19:30 | 130 | 00:00 | Matarbari | 123 | 15:00 | 115 | 06:00
| Barapukuria | 132 | 15:00 | 124 | 23:00 | Matuail | 137 | 18:00 | 132 | 11:00
| Barguna | 136 | 18:30 | 127 | 00:00 | Millgate | 138 | 18:00 | 134 | 04:00
| Barishal | 137 | 07:00 | 128 | 00:00 | Mirpur | 135 | 18:30 | 129 | 09:00
| Barishal-230 | 137 | 18:30 | 129 | 00:00 | Mithapukur | 130 | 06:00 | 117 | 00:00
| Baroaulia | 138 | 00:00 | 130 | 11:00 | Modern | 137 | 00:00 | 129 | 08:00
| Baroirhat | 131 | 19:30 | 127 | 00:00 | Mogbazar | 137 | 05:00 | 133 | 11:00
| Bashundhara | 139 | 18:00 | 133 | 12:00 | Mongla | 136 | 18:30 | 121 | 13:00
| BashundharaCement | 136 | 18:00 | 132 | 07:00 | Motijheel | 134 | 19:30 | 130 | 00:00
| Beanibazar | 130 | 07:00 | 123 | 00:00 | Munshiganj | 138 | 18:30 | 133 | 10:00
| Benapole | 137 | 06:00 | 126 | 20:00 | Mymensingh | 134 | 18:30 | 114 | 01:00
| Bhaluka | 134 | 18:00 | 112 | 00:00 | Naogaon | 131 | 18:30 | 116 | 00:00
| Bhandaria | 134 | 18:30 | 121 | 00:00 | Narail | 138 | 18:30 | 125 | 20:00
| Bhangura | 138 | 06:00 | 132 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 18:00 | 132 | 00:00 | Narshingdi | 141 | 18:30 | 128 | 00:00
| Bheramara(GK) | 139 | 08:00 | 131 | 22:00 | Natore | 134 | 18:00 | 125 | 00:00
| Bhulta | 133 | 19:30 | 129 | 00:00 | Nawabganj | 139 | 18:30 | 133 | 11:00
| Bog-Sherpur | 134 | 18:30 | 123 | 05:00 | Netrakona | 132 | 18:00 | 112 | 00:00
| Bogura | 134 | 06:00 | 126 | 00:00 | New | 140 | 18:00 | 134 | 09:00
| Bogura-230 | 135 | 18:30 | 126 | 00:00 | Niamatpur | 129 | 18:30 | 111 | 23:00
| Brahmanbaria | 133 | 18:00 | 127 | 00:00 | Noapara | 138 | 07:00 | 126 | 13:00
| Cantonment | 137 | 20:00 | 132 | 11:00 | Pabna | 136 | 18:00 | 128 | 22:00
| Chandpur | 137 | 19:30 | 130 | 00:00 | Palashbari | 128 | 18:30 | 115 | 00:00
| Chandraghona | 137 | 00:00 | 130 | 09:00 | Panchagarh | 129 | 06:00 | 111 | 00:00
| Chapai | 133 | 17:00 | 124 | 13:00 | Patuakhali | 135 | 07:00 | 129 | 00:00
| Charsaidpur | 137 | 03:00 | 132 | 13:00 | Payra | 137 | 08:00 | 133 | 00:00
| Chauddagram | 135 | 19:30 | 127 | 00:00 | PHP | 133 | 20:00 | 126 | 00:00
| Chhatak | 129 | 05:00 | 123 | 00:00 | Purbachal | 139 | 18:30 | 133 | 11:00
| Chowmuhani | 129 | 19:00 | 121 | 01:00 | Purbasadipur | 129 | 18:00 | 114 | 00:00
| Chuadanga | 136 | 18:00 | 120 | 22:00 | Rahim | 138 | 19:00 | 133 | 11:00
| Coxsbazar | 123 | 01:00 | 114 | 10:00 | Rajbari | 136 | 18:00 | 127 | 00:00
| Cumilla(N) | 136 | 18:30 | 131 | 09:00 | Rajendrapur | 139 | 18:30 | 131 | 22:00
| Cumilla(S) | 136 | 19:30 | 126 | 00:00 | Rajshahi | 132 | 18:00 | 123 | 13:00
| Daudkandi | 135 | 18:30 | 129 | 13:00 | Rajshahi-230 | 133 | 18:30 | 124 | 23:00
| Dhaka | 137 | 18:30 | 132 | 09:00 | Ramganj | 132 | 19:30 | 125 | 00:00
| Dhamrai | 136 | 18:30 | 131 | 11:00 | Rampur | 137 | 00:00 | 129 | 09:00
| Dhanmondi | 137 | 18:00 | 134 | 10:00 | Rampura | 135 | 04:00 | 132 | 09:00
| Dohazari | 132 | 00:00 | 125 | 09:00 | Rangamati | 137 | 00:00 | 129 | 09:00
| Faridpur | 135 | 09:00 | 128 | 00:00 | Rangpur | 126 | 06:00 | 114 | 00:00
| Fatullah | 138 | 18:30 | 133 | 11:00 | Ruppur | 137 | 17:00 | 131 | 00:00
| Fenchuganj | 139 | 02:00 | 131 | 00:00 | Saidpur | 128 | 05:00 | 122 | 17:00
| Feni | 135 | 19:30 | 127 | 00:00 | Satkhira | 134 | 18:00 | 119 | 21:00
| Ghorashal | 140 | 17:00 | 137 | 00:00 | Satmasjid | 137 | 06:00 | 133 | 01:00
| Goalpara | 138 | 07:00 | 126 | 13:00 | Savar | 136 | 19:30 | 130 | 00:00
| Gollamari | 137 | 06:00 | 126 | 13:00 | Shahjadpur | 141 | 18:30 | 135 | 13:00
| Gopalganj | 138 | 08:00 | 128 | 13:00 | Shahjibazar | 134 | 06:00 | 132 | 00:00
| Gopalganj_I | 138 | 18:00 | 131 | 00:00 | Shahmirpur | 137 | 00:00 | 129 | 08:00
| Gulshan | 136 | 18:30 | 132 | 09:00 | Shariatpur | 134 | 08:00 | 126 | 00:00
| Halishahar | 138 | 01:00 | 128 | 08:00 | Sherpur | 135 | 18:30 | 110 | 00:00
| Haripur | 138 | 19:30 | 133 | 11:00 | Shikalbaha | 137 | 00:00 | 131 | 06:00
| HaripurSBU | 138 | 17:00 | 133 | 11:00 | Shikalbaha-230 | 139 | 02:00 | 129 | 10:00
| Hasnabad | 140 | 20:00 | 135 | 07:00 | Shitalakhya | 141 | 19:30 | 132 | 11:00
| Hathazari | 138 | 00:00 | 131 | 07:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 18:00 | 131 | 00:00 | Shyampur | 136 | 18:30 | 132 | 10:00
| Jaldhaka | 126 | 06:00 | 111 | 00:00 | Shyampur-230 | 137 | 18:00 | 133 | 11:00
| Jamalpur | 135 | 18:00 | 113 | 01:00 | Siddhirganj | 138 | 18:30 | 132 | 09:00
| Jashore | 138 | 08:00 | 126 | 13:00 | Sirajganj | 135 | 17:00 | 127 | 00:00
| Jhenaidah | 141 | 18:00 | 128 | 22:00 | Sonargaon | 136 | 00:00 | 134 | 09:00
| Jhenaidah-230 | 142 | 18:00 | 128 | 20:00 | Sreemongol | 136 | 18:00 | 131 | 00:00
| Joydebpur | 144 | 19:30 | 137 | 11:00 | Srinagar | 140 | 18:30 | 134 | 13:00
| Joypurhat | 131 | 18:00 | 115 | 00:00 | SSM | 140 | 00:00 | 132 | 08:00
| Juldah | 138 | 00:00 | 129 | 09:00 | Sunamganj | 128 | 06:00 | 120 | 00:00
| Kabirpur | 139 | 17:00 | 130 | 18:30 | Sylhet | 131 | 08:00 | 127 | 00:00
| Kachua | 136 | 18:30 | 130 | 00:00 | Tangail | 138 | 18:00 | 128 | 00:00
| Kaliakoir | 141 | 18:00 | 134 | 16:00 | Thakurgaon | 129 | 15:00 | 112 | 00:00
| Kallyanpur | 136 | 19:00 | 130 | 13:00 | TK | 139 | 03:00 | 129 | 08:00
Page 7 of 7

## L-Curve
Date | 2022-07-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 488 | 7788 | 4043 | 11831 |  |  |  | QF-LDC-11
0:30 | 320 | 7811.5 | 4206 | 12017.5 | Date: | 2022-07-09
1:00 | 152 | 7835 | 4369 | 12204
1:30 | 182 | 7765 | 4277.5 | 12042.5
2:00 | 212 | 7695 | 4186 | 11881
2:30 | 264 | 7604 | 4114 | 11718 | [5 empty] | Gen. at Eve. Peak | 11760 | 11760 MW (21:00 )
3:00 | 316 | 7513 | 4042 | 11555 | [6 empty] | 21:00
3:30 | 364 | 7465 | 3893.5 | 11358.5 | [5 empty] | Gen. at Day Peak | 9147 | 9147 MW (12:00 )
4:00 | 412 | 7417 | 3745 | 11162 | [6 empty] | 12:00
4:30 | 383 | 7281.5 | 3698.5 | 10980 | [5 empty] | Highest Generation | 12204
5:00 | 354 | 7146 | 3652 | 10798 | [6 empty] | 1:00
5:30 | 211 | 6622.5 | 3562 | 10184.5
6:00 | 68 | 6099 | 3472 | 9571
6:30 | 66 | 5990 | 3395 | 9385
7:00 | 64 | 5881 | 3318 | 9199
7:30 | 54 | 5844 | 3288.5 | 9132.5
8:00 | 44 | 5807 | 3259 | 9066
8:30 | 28 | 5739.5 | 3222 | 8961.5
9:00 | 12 | 5672 | 3185 | 8857
9:30 | 9 | 5674 | 3152.5 | 8826.5
10:00 | 6 | 5676 | 3120 | 8796
10:30 | 27 | 5783 | 3110.5 | 8893.5
11:00 | 48 | 5890 | 3101 | 8991
11:30 | 137 | 5971 | 3098 | 9069
12:00 | 226 | 6052 | 3095 | 9147
12:30 | 239 | 6262.5 | 3131.5 | 9394
13:00 | 252 | 6473 | 3168 | 9641
13:30 | 270 | 6572 | 3254 | 9826
14:00 | 288 | 6671 | 3340 | 10011
14:30 | 300 | 6811 | 3317 | 10128
15:00 | 312 | 6951 | 3294 | 10245
15:30 | 298 | 6879.5 | 3257.5 | 10137
16:00 | 284 | 6808 | 3221 | 10029
16:30 | 234 | 6577.5 | 3162.5 | 9740
17:00 | 184 | 6347 | 3104 | 9451
17:30 | 195 | 6199 | 2971 | 9170
18:00 | 206 | 6051 | 2838 | 8889
18:30 | 179 | 6306 | 3038 | 9344
19:00 | 152 | 6561 | 3238 | 9799
19:30 | 498 | 7702 | 3811 | 11513
20:00 | 536 | 7580 | 3783 | 11363 |  |  |  | Executive Engineer
20:30 | 523 | 7690.5 | 3871 | 11561.5 |  |  |  | Network Operation Division
21:00 | 510 | 7801 | 3959 | 11760
21:30 | 512 | 7813 | 3981.5 | 11794.5
22:00 | 514 | 7825 | 4004 | 11829 |  |  |  |  | Page 6 of 7
22:30 | 509 | 7853.5 | 4025.5 | 11879
23:00 | 504 | 7882 | 4047 | 11929
23:30 | 496 | 7835 | 4045 | 11880
24:00 | 488 | 7788 | 4043 | 11831
11760 MW (21:00 )
9147 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-09 |  | Energy |  | 252032207
[13 empty] | 2022-07-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 5153 | 493 | 2026 | 98 | 2789 | 780 | 118 | 0 | 220 | 154 | 0 | 0
0:30 | 4583.5 | 491 | 1993 | 188.5 | 3107.5 | 801 | 121 | 211.5 | 474.5 | 154 | 0 | 0 | Date: | 2022-07-09
1:00 | 4014 | 489 | 1960 | 279 | 3426 | 822 | 124 | 423 | 729 | 154 | 0 | 0
1:30 | 4079.5 | 489.5 | 1952 | 139.5 | 3397 | 801 | 122.5 | 423 | 702.5 | 152 | 0 | 0 | [8 empty] | Total Energy | 252.0322 | Total Energy Gen 252.032 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.032 MKWHr
2:00 | 4145 | 490 | 1944 | 0 | 3368 | 780 | 121 | 423 | 676 | 150 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4180.5 | 490 | 1924.5 | 0 | 3313.5 | 780 | 122 | 394 | 572 | 147 | 0 | 0 | [8 empty] | Energy Requirement | 252.0322
3:00 | 4216 | 490 | 1905 | 0 | 3259 | 780 | 123 | 365 | 468 | 144 | 0 | 0
3:30 | 4244.5 | 490 | 1895.5 | 0 | 3195 | 780 | 123 | 307.5 | 345.5 | 140 | 0 | 0 | [6 empty] | Shortage
4:00 | 4273 | 490 | 1886 | 0 | 3131 | 780 | 123 | 250 | 223 | 136 | 0 | 0
4:30 | 4289.5 | 490 | 1863 | 0 | 3007 | 760 | 123 | 250 | 193.5 | 134 | 0 | 0
5:00 | 4306 | 490 | 1840 | 0 | 2883 | 740 | 123 | 250 | 164 | 132 | 0 | 0
5:30 | 4262 | 490 | 1839.5 | 0 | 2366.5 | 710 | 119 | 250 | 147 | 126 | 4.5 | 0
6:00 | 4218 | 490 | 1839 | 0 | 1850 | 680 | 115 | 250 | 130 | 120 | 9 | 0
6:30 | 4181 | 490 | 1876 | 0 | 1645 | 680 | 115 | 250 | 130 | 118 | 30 | 0 |  |  |  |  | Coal
7:00 | 4144 | 490 | 1913 | 0 | 1440 | 680 | 115 | 250 | 130 | 116 | 51 | 0
7:30 | 4189.5 | 490.5 | 1883 | 0 | 1354.5 | 675 | 115 | 250 | 130 | 113 | 62 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4235 | 491 | 1853 | 0 | 1269 | 670 | 115 | 250 | 130 | 110 | 73 | 0
8:30 | 4211.5 | 491 | 1822 | 0 | 1187 | 655 | 119 | 250 | 130 | 110 | 116 | 0
9:00 | 4188 | 491 | 1791 | 0 | 1105 | 640 | 123 | 250 | 130 | 110 | 159 | 0
9:30 | 4172 | 491 | 1820 | 0 | 1061 | 620 | 123 | 250 | 130 | 108 | 181.5 | 0
10:00 | 4156 | 491 | 1849 | 0 | 1017 | 600 | 123 | 250 | 130 | 106 | 204 | 0
10:30 | 4253 | 491.5 | 1859.5 | 0 | 1008.5 | 600 | 123 | 250 | 130 | 112 | 196 | 0
11:00 | 4350 | 492 | 1870 | 0 | 1000 | 600 | 123 | 250 | 130 | 118 | 188 | 0
11:30 | 4351.5 | 492.5 | 1882.5 | 0 | 1089.5 | 600 | 123 | 232.5 | 130 | 118 | 179.5 | 0
12:00 | 4353 | 493 | 1895 | 0 | 1179 | 600 | 123 | 215 | 130 | 118 | 171 | 0
12:30 | 4511.5 | 492.5 | 1894.5 | 0 | 1338.5 | 600 | 123 | 107.5 | 65 | 126 | 200.5 | 0
13:00 | 4670 | 492 | 1894 | 0 | 1498 | 600 | 123 | 0 | 0 | 134 | 230 | 0
13:30 | 4670 | 492 | 1894 | 0 | 1498 | 600 | 123 | 0 | 0 | 134 | 230 | 0
14:00 | 4670 | 492 | 1894 | 0 | 1498 | 600 | 123 | 0 | 0 | 134 | 230 | 0
14:30 | 4652 | 492 | 1870.5 | 0 | 1862.5 | 605 | 121 | 0 | 0 | 137 | 203 | 0
15:00 | 4634 | 492 | 1847 | 0 | 2227 | 610 | 119 | 0 | 0 | 140 | 176 | 0
15:30 | 4672 | 492 | 1843 | 0 | 2141 | 590 | 119 | 0 | 7.5 | 137 | 135.5 | 0
16:00 | 4710 | 492 | 1839 | 0 | 2055 | 570 | 119 | 0 | 15 | 134 | 95 | 0
16:30 | 4475 | 491.5 | 1840.5 | 0 | 1909 | 570 | 119.5 | 0 | 15 | 121 | 81 | 0
17:00 | 4475 | 491 | 1842 | 0 | 1763 | 570 | 120 | 0 | 15 | 108 | 67 | 0
17:30 | 4364.5 | 491.5 | 1776 | 0 | 1683.5 | 545 | 123 | 0 | 35.5 | 109 | 42 | 0
18:00 | 4254 | 492 | 1710 | 0 | 1604 | 520 | 126 | 0 | 56 | 110 | 17 | 0
18:30 | 4335.5 | 491.5 | 1781.5 | 0 | 1763.5 | 535 | 126.5 | 0 | 175 | 127 | 8.5 | 0
19:00 | 4417 | 491 | 1853 | 0 | 1923 | 550 | 127 | 0 | 294 | 144 | 0 | 0
19:30 | 4744 | 492 | 1844 | 0 | 3083 | 699 | 125 | 0 | 390 | 136 | 0 | 0
20:00 | 4675 | 491 | 1934 | 0 | 3048 | 720 | 127 | 0 | 226 | 142 | 0 | 0
20:30 | 4810 | 492 | 1971.5 | 6 | 3071 | 720 | 126 | 0 | 222 | 143 | 0 | 0
21:00 | 4945 | 493 | 2009 | 12 | 3094 | 720 | 125 | 0 | 218 | 144 | 0 | 0
21:30 | 5004.5 | 493 | 2008.5 | 32 | 3045.5 | 720 | 124 | 0 | 219 | 148 | 0 | 0
22:00 | 5064 | 493 | 2008 | 52 | 2997 | 720 | 123 | 0 | 220 | 152 | 0 | 0
22:30 | 5097 | 493 | 1994.5 | 73.5 | 3000 | 730 | 120 | 0 | 220 | 151 | 0 | 0
23:00 | 5130 | 493 | 1981 | 95 | 3003 | 740 | 117 | 0 | 220 | 150 | 0 | 0
23:30 | 5141.5 | 493 | 2003.5 | 96.5 | 2896 | 760 | 117.5 | 0 | 220 | 152 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.6° C
24:00 | 5153 | 493 | 2026 | 98 | 2789 | 780 | 118 | 0 | 220 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 252.032 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.032 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 89 | 86 | 88 | 88 | 88 | 80 | 80 | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 84 | 84 | 85 | 91 |  | 92 | 90 | 92 | 90 | 88 | 82 | 83 | 2106764
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 8 | [5 empty] | 3 | 11 | 25 | 25 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 16 | 20 | 25 | 25 | 331227
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 5 | 8 | 14 | 17 | 12 | 19 | 13 | 13 | 10 | 4 | 1 | [8 empty] | 119070
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | [17 empty] | 36 | 39 | 51 | 51 | 51 | 51 | 51 | 334395
12 | Hathazari 100 MW peaking PP | 43 | 43 | [17 empty] | 17 | 30 | [5 empty] | 116544
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 68 | [15 empty] | 6 | 17 | 15 | 0 |  |  |  | 520218
| Daudkandi 200 MW PP (B.Trac) | 10 | [25 empty] | 56064
14 | Titas 50 MW Peaking PP | [19 empty] | 16 | 43 | [5 empty] | 123640
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [9 empty] | 37 | 0 | 37 | 94 | 32 | 133 | 132 | 134 | 90 |  | 190 | 92 | 92 | 96 | 97 | 192 | 196 | 1588000
17 | Siddhirganj 335 MW CCPP | 40 | 170 | 233 | 335 | 335 | 335 | 335 | 335 | 270 | 250 | 329 | 330 | 326 | 250 | 250 | 250 | 250 | 250 |  | 250 | 335 | 335 | 332 | 331 | 336 | 334 | 6767021
18 | Kodda 300 MW PP Unit-2 (Summit) | 213 | 213 | 253 | 263 | 275 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 114 | 148 | 177 | 145 | 145 | 145 |  | 153 | 153 | 208 | 225 | 225 | 225 | 225 | 3806290
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 55 | 55 | 55 | 55 | 26 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4331250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 270 | 300 | 270 | 310 | 310 | 310 | 310 | 7418109
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 32 | 31 | 31 | 31 | 30 | 27 |  | 28 | 29 | 29 | 31 | 32 | 33 | 33 | 735984
33 | Ashuganj 225 MW CCPP | 208 | 208 | 210 | 210 | 210 | 211 | 208 | 208 | 208 | 207 | 203 | 204 | 202 | 206 | 206 | 204 | 204 | 171 |  | 197 | 206 | 205 | 203 | 203 | 208 | 207 | 4966000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 335 | 315 | 330 | 310 | 310 | 310 | 310 | 310 |  | 305 | 270 | 270 | 270 | 305 | 270 | 315 | 7410000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 275 | 270 | 270 | 300 | 275 | 305 | 305 | 305 | 305 | 305 | 305 |  | 310 | 280 | 280 | 280 | 320 | 280 | 280 | 7617400
| Ashuganj 420 MW CCPP(East) | [7 empty] | 197 | 218 | 217 | 217 | 217 | 217 | 217 | 217 | 218 | 0 | [9 empty] | 1859200
35 | Ashuganj 55 MW PP (Precision) | 50 | 50 | 52 | 52 | 50 | 52 | 51 | 52 | 52 | 51 | 47 | 47 | 48 | 48 | 47 | 48 | 47 | 49 |  | 48 | 48 | 48 | 48 | 49 | 49 | 50 | 1187040
36 | Chandpur 150 MW CCPP | 86 | 85 | 85 | 84 | 84 | 84 | 84 | 85 | 86 | 85 | 87 | 84 | 85 | 84 | 124 | 130 | 130 | 130 |  | 130 | 137 | 136 | 136 | 136 | 137 | 136 | 2471490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [15 empty] | 6 | 15 | 31 |  | 105 | 313 | 267 | 347 | 387 | 398 | 398 | 1972220
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5037000
41 | Haripur 360MW CCPP(HPL) | 327 | 331 | 331 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 327 | 327 | 328 | 322 | 322 | 322 | 322 | 322 |  | 274 | 323 | 333 | 323 | 323 | 326 | 326 | 7798000
42 | RPCL 210MW CCPP | 171 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 171 | 171 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 201 |  | 201 | 206 | 203 | 201 | 203 | 207 | 207 | 4455360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 10 | 25 | 38 | 50 | 23 | 56 | 52 | 49 | 40 | 30 | 15 | 3 |  | 0 | [6 empty] | 390970
44 | Fenchugonj CCPP Phase-1 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 32 | 33 | 33 | 33 | 33 | 33 | 772000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 989152
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 57 | 56 | 61 | 40 | 40 | 40 | 40 | 40 | 49 | 50 | 50 | 50 | 50 | 60 |  | 60 | 59 | 61 | 60 | 61 | 62 | 61 | 1257312
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 50 | 84 | 84 | 84 | 84 | 84 | 1175040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3371830
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193680
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  |  | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 0 | 8 | 8 | 204912
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192560
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 280 | 270 | 270 | 300 | 280 | 270 | 280 | 310 | 290 | 290 | 300 | 270 | 270 | 280 | 260 |  | 265 | 250 | 265 | 285 | 285 | 285 | 290 | 6913500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 360 | 360 | 360 | 360 | 360 | 383 | 382 | 378 | 397 | 392 | 396 | 397 | 360 |  | 381 | 381 | 400 | 396 | 400 | 400 | 400 | 9188900
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | [10 empty] | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 513257
59 | Tangail Palli Power Gen 22 MW | 22 | 23 | 22 | 22 | 22 | [8 empty] | 1 | 15 | 23 | 19 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 350880
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 510336
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 343584
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475128
63 | Impoprt (Tripura) | 154 | 150 | 144 | 136 | 132 | 120 | 116 | 110 | 110 | 106 | 118 | 118 | 134 | 138 | 140 | 134 | 108 | 110 |  | 144 | 136 | 142 | 144 | 152 | 150 | 154 | 3166080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 33 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 40 | 42 | 42 | 42 | 42 | 42 | 1052640
65 | Feni 22MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  |  | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 411660
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 8 | 11 | 8 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 11 | 10 | 239580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 28 | 33 | 31 | 31 | 33 | 32 | 31 | 23 | 31 |  | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 773600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 20 | 20 | 15 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 500000
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 13 | 13 | 13 | 13 | 13 | 13 | 10 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 | 9 | 12 | 13 | 13 | 12 | 298260
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 782500
72 | Rupganj 33 MW PP(Summit) | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 26 | 24 | 12 | 20 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 18 | 585500
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 89 | 86 | 86 | 89 | 87 | 83 | 83 | 91 | 53 |  | 86 | 92 | 89 | 92 | 92 | 92 | 92 | 2054318
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 |  | 34 | 98 | 98 | 114 | 114 | 114 | 114 | 902880
| Chowmuhani 113 MW | 42 | 39 | 39 | 39 | 39 | 38 | 38 | 39 | 39 | 39 | 47 | 58 | 68 | 66 | 66 | 65 | 26 | 26 |  | 26 | 75 | 57 | 75 | 75 | 75 | 75 | 1228080
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 62 | 72 | 72 | 72 | 72 | 72 | 72 | 776160
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 37 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 20 | 70 | 77 | 40 | 32 |  | 38 | 50 | 66 | 96 | 99 | 99 | 99 | 1352640
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 8 | [8 empty] | 8 | 8 | 8 | 8 | 8 |  | 10 | 30 | 24 | 24 | 24 | 24 | 24 | 418080
79 | Kodda 150MW PP | 132 | 132 | 98 | 64 | 16 | [14 empty] | 16 | 16 | [5 empty] | 507360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 24 |  | 24 | 34 | 34 | 34 | 43 | 43 | 43 | 390182
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 50 | 17 | 17 | 17 | 17 | 17 | 50 | 50 | 58 | 50 | 50 | 50 | 50 |  | 52 | 105 | 105 | 105 | 70 | 70 | 70 | 1584000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 3 | 4 | 4 | 1 | [9 empty] | 35039
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 |  | 19 | 35 | 50 | 54 | 54 | 54 | 54 | 1111527
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 103 | 110 | 17 | 17 | 17 | 17 | 20 | 34 | 50 | 68 | 82 | 109 | 68 | 51 | 51 |  | 51 | 60 | 80 | 110 | 110 | 110 | 110 | 1845846
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 88 | 87 | 88 | 87 | 88 | 87 | 87 | 88 | 81 | 80 | 80 | 80 | 75 | 80 | 80 | 80 | 80 | 44 |  | 43 | 75 | 71 | 82 | 87 | 87 | 89 | 1929600
| Meghnaghat 104 MW PP (OPCL) | 96 | 94 | 93 | 92 | 93 | 42 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 83 | 82 | 35 | 35 |  | 35 | 54 | 54 | 61 | 52 | 52 | 50 | 1211520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | [8 empty] | 44 | 10 | 10 | 10 | 10 |  | 10 | 50 | 10 | 10 | 10 | 10 | 10 | 460440
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1184753
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 94 | 94 | 94 | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 32 | 60 | 64 | 24 | 24 | 24 |  | 64 | 94 | 74 | 48 | 24 | 24 | 24 | 1053648
95 | Patenga 50MW PP (Baraka) | 40 | 44 | 44 | 44 | 44 | 44 | 45 | 45 | 44 | 44 | 44 | 39 | 38 | 42 | 44 | 44 | 44 | 45 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1052160
96 | Chattogram 108 MW PP (ECPV) | 80 | 80 | 72 | 78 | 27 | [14 empty] | 6 | 10 | [5 empty] | 352320
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 5 | 15 | 15 |  | 15 | 15 | 15 | 0 |  |  |  | 486821
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 23 | 611496
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2615727
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 15000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 330480
104 | Keranigonj 300 MW PP (APR) | 129 | [25 empty] | 298105
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 115 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 60 | 60 | 60 | 45 | 53 | 110 | 112 | 112 | 112 |  | 110 | 172 | 168 | 169 | 169 | 187 | 115 | 2733600
112 | Aurahati 100MW PP (Aggreko) | 70 | [25 empty] | 81723
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 131 | 132 | 128 | 106 | 32 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 51 | 44 | 33 | 33 |  | 38 | 100 | 99 | 56 | 40 | 34 | 35 | 1292112
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 90 | 50 | 20 | 20 | 20 |  | 20 | 90 | 50 | 50 | 10 | 10 | 10 | 949440
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 155 | 100 | 51 | 51 | 51 | 75 | 155 | 180 | 200 | 200 | 155 | 120 |  | 120 | 200 | 175 | 200 | 200 | 200 | 200 | 3889440
117 | Ashuganj 150MW PP (Midland) | 127 | 132 | 130 | 118 | 125 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 60 | 65 | 80 | 60 | 40 | 40 |  | 63 | 80 | 93 | 123 | 130 | 133 | 135 | 2005600
118 | Bibiyana-III 400 MW CCPP | 403 | 402 | 402 | 401 | 401 | 402 | 402 | 377 | 377 | 378 | 377 | 405 | 403 | 378 | 353 | 353 | 353 | 352 |  | 376 | 402 | 402 | 403 | 402 | 402 | 402 | 9314000
| Jamalpur 115 MW PP (United) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 59 | 58 |  | 63 | 115 | 115 | 115 | 115 | 115 | 59 | 165800
| Anwara 300 MW PP (United) | 262 | 200 | 100 | 30 | [9 empty] | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 0 |  |  |  |  | 850582
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 72 | 30 | 30 | 30 | 70 | 80 | 90 | 100 | 100 | 100 | 20 |  | 23 | 100 | 100 | 90 | 90 | 94 | 90 | 1935360
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 99 | 100 | 60 | 34 | 55 | 68 | 82 | 90 | 90 | 90 | 90 | 51 | 51 |  | 52 | 95 | 100 | 108 | 108 | 108 | 108 | 2133982
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 32 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 659160
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 0 | 25 | 31 | 35 | 36 | 34 | 31 | 26 | 18 | 9 | 2 | [8 empty] | 258690
| Chandpur 115(Doreen) | 36 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 71 |  | 72 | 72 | 72 | 72 | 72 | 54 | 45 | 1095360
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 40 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 38 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 1020240
120 | Eastern Zone Total | 7835 | 7695 | 7513 | 7417 | 7146 | 6099 | 5881 | 5807 | 5672 | 5676 | 5890 | 6052 | 6473 | 6671 | 6951 | 6808 | 6347 | 6051 |  | 6561 | 7702 | 7580 | 7801 | 7825 | 7882 | 7788 | 164383508
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 49 | 48 | 48 | 48 | 48 | 49 | 16 | 525120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 28 | 28 | [15 empty] | 24 |  | 35 | 36 | 48 | 30 | 32 | 32 | 32 | 260160
| Khulna 225 MW CCPP | 207 | 207 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 85 | [14 empty] | 1763520
129 | Rupsha 105 MW PP (Orion rupsha) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 0 |  |  |  |  | 10 | 35 | 53 | 53 |  | 53 | 65 | 70 | 70 | 70 | 70 | 71 | 1070880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 29 | 35 | 76 | 94 | 94 | 49 | 107 | 84 | 84 | 25 | 34 | 10 | [8 empty] | 719280
131
132 | United Payra Power Ltd. | [19 empty] | 6 | 17 | 17 |  |  |  |  | 26400
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 225 | 225 | 225 | 224 | 225 | 185 | 185 | 185 | 185 | 220 | 220 | 220 | 218 | 216 | 210 | 172 |  | 210 | 190 | 223 | 224 | 221 | 224 | 224 | 5091573
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 16 | 16 | 16 | 16 | 16 | [12 empty] | 32 | 64 | 64 | 32 | 32 | 32 | 32 | 361820
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 88 | 88 | 87 | 87 | 87 | 88 | 87 | 87 | 86 | 86 | 82 | 85 | 86 | 86 | 86 | 86 |  | 84 | 83 | 86 | 85 | 85 | 87 | 87 | 2098217
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 30 | 29 | 25 | 22 | 21 | 20 | 20 | 22 | 22 | 22 | 24 | 26 | 25 | 23 | 20 |  | 27 | 27 | 25 | 32 | 33 | 34 | 34 | 632043
141 | Noapara 100 MW PP (Bangla Trac) | 20 | [8 empty] | 0 | [12 empty] | 12 | 52 | 95 | 98 | 307200
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | [13 empty] | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 82875
143 | Gopalganj 100 MW Peaking PP | 63 | 10 | [17 empty] | 36 | 51 | 20 | 20 | 20 | 20 | 20 | 246016
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 67 | 15 | 15 | 15 | 67 | 50 | 15 | 15 | 15 |  | 29 | 102 | 105 | 105 | 105 | 105 | 105 | 1860048
146 | Bheramara HVDC | 489 | 490 | 490 | 490 | 490 | 490 | 490 | 491 | 491 | 491 | 492 | 493 | 492 | 492 | 492 | 492 | 491 | 492 |  | 491 | 492 | 491 | 493 | 493 | 493 | 493 | 11893090
147 | Bheramara 410 MW CCPP | 395 | 395 | 400 | 400 | 400 | 350 | 300 | 300 | 300 | 300 | 320 | 320 | 390 | 390 | 390 | 400 | 395 | 400 |  | 350 | 380 | 315 | 400 | 400 | 405 | 400 | 9023904
148 | Payra 1320 MW | 622 | 580 | 580 | 580 | 540 | 480 | 480 | 470 | 440 | 400 | 400 | 400 | 400 | 440 | 410 | 370 | 370 | 320 |  | 350 | 500 | 520 | 520 | 520 | 540 | 580 | 12487000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 4877400
153 | Baghabari 71 MW GTPP | [15 empty] | 50 | 50 | 30 |  | 0 | [6 empty] | 120000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | [16 empty] | 34 | 34 | 0 |  |  |  |  | 136376
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 4 | 4 | 4 | 1 | 2 | 1 | 0 | [8 empty] | 37920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 180 | 180 | 180 | 191 | 209 | 211 | 211 | 210 | 150 |  | 150 | 192 | 205 | 210 | 214 | 214 | 214 | 5188127
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [12 empty] | 130 | 180 | 150 | 150 | 150 | 130 |  | 130 | 156 | 179 | 209 | 210 | 211 | 211 | 2089358
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 216 | 216 | 195 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | [13 empty] | 2076161
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 212 | 213 | 213 | 214 | 214 | 215 | 214 | 213 | 213 | 211 | 208 | 207 | 206 | 205 | 180 | 180 | 180 | 140 |  | 140 | 162 | 177 | 208 | 209 | 210 | 210 | 5098455
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 400 | 381 | 389 | 381 | 348 | 350 | 399 | 397 | 350 | 396 | 408 | 410 | 404 | 335 | 341 | 335 | 329 | 323 |  | 403 | 356 | 356 | 410 | 410 | 374 | 413 | 9131418
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 30 | 30 | [24 empty] | 85139
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | 20 | 20 | 22 | 22 | 470880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255906
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 8 | [15 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 165904
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 24 | [16 empty] | 30 | 32 | 0 |  |  |  |  | 118678
168 | Santahar 50 MW Peaking PP | 29 | 29 | 29 | 29 | 18 | [12 empty] | 10 |  | 29 | 29 | 22 | 29 | 29 | 29 | 29 | 297554
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 |  | 24 | 43 | 52 | 52 | 52 | 52 | 8 | 409858
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | [12 empty] | 15 | 15 | 22 |  | 45 | 80 | 85 | 88 | 88 | 88 | 88 | 756992
171 | Baghabari 200 MW PP (Paramount) | 50 | [25 empty] | 104775
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 39 | 70 | 74 | 94 | 94 | 50 | 35 |  | 38 | 113 | 107 | 113 | 113 | 113 | 113 | 1992384
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 100 | 113 | 113 | 70 | 35 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2155104
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 40 | 40 |  | 52 | 88 | 95 | 97 | 96 | 96 | 95 | 1720387
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 7 | 7 | 7 | 7 | 7 | 5 | 2 | 1 | [8 empty] | 53177
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 100 | 107 | 72 | 52 | 52 |  | 75 | 113 | 113 | 112 | 112 | 112 | 108 | 1857600
178