## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-17 | Sunday
|  |  | Date (day): | 2022-07-17 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13927.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15251 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-16 | 2022-07-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 89 | 89 | 90 |  | 18 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 398 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 324 | 330 | 330 |  | 30 | Machine problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 71 | 80 | 78 | 78 |  | 22 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 94 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 52 | 98 | 70 | 98 |  | 2 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 132 | 130 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55 |  |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 46 | 46 | 46 |  | 34 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 49 | 42 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 257 | 273 | 280 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 122 | 135 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 52 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2988 | 3653 | 3653 | 4031 | 821 | 999
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 20 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 37 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 124 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 26 | 70 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 0 | 52 | 46 |  | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 40 | 55 | 55 | 55 |  | 45 | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 32 | 7 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 30 | 80 | 70 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 50 | 200 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 781 | 1158 | 1233 | 1439 | 357 | 588
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 206 | 200 | 190
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 285 | 340 | 320 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 265 | 310 | 300 |  |  | FGMO
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 36 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 46 | 44 | 47 | 47 |  | 8 | Engine problem
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 187 | 155 | 150 | 95 | 100 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 60 | 10 | 145 | 145 |  | 5
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 47 | 40 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 84 | 85 | 85 |  | 78 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 120 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 80 | 60 | 78
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 14 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 17 | 97 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 111 | 9 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 95 | 95 | 95 | 20 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1725 | 1905 | 1933 | 2150 | 351 | 169
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 176 | 131 | 100 | 90 |  | 112 | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 19 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 167 | 116 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 105 | 60 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 15 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 441 | 437 | 371.6 | 419 | 0 | 150
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 44 | 44 |  | 26 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 80 | 0 | 0 |  |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 59 | 62 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 81 | 78 | 78
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 193 | 219 | 190 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 6 | 0 | 0 | 0 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 8 | 0 | 0 |  |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 60 | 260 | 341 | 341 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 366 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 398 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1426 | 1608 | 1567 | 1597 | 101 | 504
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 880 | 863 | 892 | 877
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 80 | 16 | 83 | 32 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 42 |  | 12 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 220 | 220
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 355 | 380 | 380
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 94 | 75 | 94 |  | 11 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 13 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1339 | 1573 | 1838 | 1969 | 64 | 72
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 64 | 110
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 24 | 26 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 20 | 87 | 87 | 107 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1020 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 224 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1089 | 1337 | 1514 | 1582 | 107 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 198 | 167 | 180 | 160 | 50 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 169 | 165 | 190 | 170 | 50 |  | Gas shortage
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 171 | 180 | 160 | 60 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 367 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30 |  | 20 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 25 | 8 | 52 |  |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 85 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 170 |  | 30 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 113 | 94 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 76 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1246 | 1458 | 1455 | 1633 | 331 | 159
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 198 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 15 | 15
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 68 | 101 | 68 | 97 |  | 16 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 108 | 72 | 109 |  | 6 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 270 | 409 | 363 | 431 | 244 | 22
|  | Total |  |  |  |  | 22678 | 21396 | 11305 | 13538 | 13927.6 | 15251 | 2376 | 2673
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10883.171 | 13032.85 | 13407.9127 | 14681.932
| A. |  | 2022-07-16 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13538 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10450 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13538 | MW
| 3 | Day peak Generation : |  |  | 11305 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13032.85 | MW
| 4 | Evening peak Generation : |  |  | 13538 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 290.5095 | MKWHr | By Solar | 1.4364 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 167.5257 | MKWHr |  | By Oil: | 69.105 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 26.5157 | MKWHr |  | By Hydro: | 2.7288 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2376 | MW | Dhaka | 4135.92 | 4135.92 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2673 | MW | Chittagong | 1335.8 | 1335.8 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5049 | MW | Khulna | 1733.6 | 1733.6 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1243.5 | MMCFD |  |  | Rajshahi | 1510.6 | 1510.6 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 194474597.898 | ii) Oil : | Taka | 919718852.21 | Comilla | 1353 | 1353 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 220912817 | Total | Taka | 1335106267.108 | Mymensingh | 1027 | 1027 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.6645 | MKWHr. | Sylhet | 608 | 608 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -450 | MW (E to W) at | 21:00 | hrs | Barisal | 397.93 | 397.93 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -840 | MW at | 20:00 | hrs | Rangpur | 931 | 931 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 13032.85 | 13032.85 |  | 0
| B. |  | 2022-07-17 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15251 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11900 | MW
| 4 | Reserve(Generation end) |  |  |  | 651 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 313.2987 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10783 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5025 | MKWHr. | ii) HVDC Flow at Peak Time |  | 863 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6954 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.27 |  | (b) Today: | 91.34 |  | (c) Rule Curve: |  | 86.24
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 408 | 328 |  | 0 | 420 | 0 | 78 | 0 | 30 | 335 | 0 | 190 | 90 | 48 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 16 | 25 | 30 | 24 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 34 | 34 | 55 | 11 | 44 | 21 | 42 | 0 | 0 | 0 | 310 | 310 | 138 | 187 | 85 | 35 | 47 | 0 | 51 | 0 | 40 | 8 | 22 | 7 | 33 | 20 | 76 | 205 | 0 | 15 | 0 | 43 | 42 | 50 | 47 | 80 | 0 | 51 | 81 | 0 | 220 | 0 | 25 | 10 | 0 | 23 | 11 | 0 | 145 | 0 | 0 | 115 | 0 | 130 | 0 | 50 | 139 | 113 | 403 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 20 | 100 | 400 | 72 | 0 | 0 | 108 | 0 | 35 | 0 | 65 | 55 | 0 |  | 917 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 31 | 16 | 0 | 0 | 70 | 0 | 0 | 87 | 0 | 34 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 214 | 0 | 179 | 0 | 0 | 0 | 175 | 0 | 414 | 70 | 0 | 94 | 105 | 93 | 0 | 0 | 76 | 1000 | 223 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7841 | 4676 | 12517 | 5138 | 917 | 2144 | 0 | 2563 | 1198 | 125 | 0 | 356 | 76 | 0 | 0 | 91.26
2:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 408 | 275 |  | 0 | 420 | 0 | 77 | 0 | 30 | 335 | 0 | 190 | 97 | 48 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 16 | 25 | 30 | 24 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 34 | 55 | 11 | 44 | 21 | 42 | 0 | 0 | 0 | 310 | 310 | 138 | 187 | 85 | 35 | 47 | 0 | 51 | 0 | 40 | 8 | 22 | 7 | 33 | 20 | 70 | 206 | 0 | 15 | 0 | 43 | 42 | 50 | 48 | 80 | 0 | 51 | 81 | 0 | 220 | 0 | 26 | 10 | 0 | 15 | 11 | 0 | 145 | 0 | 0 | 115 | 0 | 130 | 0 | 50 | 120 | 125 | 403 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 11 | 100 | 400 | 104 | 0 | 0 | 108 | 0 | 35 | 0 | 82 | 55 | 0 |  | 916 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 16 | 0 | 0 | 65 | 0 | 0 | 87 | 0 | 34 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 158 | 0 | 0 | 0 | 165 | 0 | 414 | 70 | 0 | 94 | 25 | 66 | 0 | 0 | 76 | 840 | 224 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7812 | 4286 | 12098 | 5011 | 916 | 2087 | 0 | 2496 | 1038 | 124 | 0 | 356 | 70 | 0 | 0 | 91.26
3:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 408 | 251 |  | 0 | 420 | 0 | 76 | 0 | 30 | 335 | 0 | 190 | 97 | 48 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 16 | 25 | 30 | 24 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 34 | 0 | 11 | 44 | 21 | 42 | 0 | 0 | 0 | 320 | 320 | 137 | 187 | 85 | 35 | 47 | 0 | 51 | 0 | 41 | 8 | 22 | 7 | 33 | 20 | 72 | 208 | 0 | 15 | 0 | 43 | 42 | 50 | 48 | 80 | 0 | 51 | 81 | 0 | 218 | 0 | 26 | 10 | 0 | 15 | 11 | 0 | 145 | 0 | 0 | 116 | 0 | 130 | 0 | 20 | 120 | 130 | 403 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 8 | 100 | 400 | 104 | 0 | 0 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 918 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 16 | 0 | 0 | 65 | 0 | 0 | 87 | 0 | 34 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 163 | 0 | 0 | 0 | 169 | 0 | 414 | 70 | 0 | 94 | 0 | 65 | 0 | 0 | 76 | 800 | 184 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7755 | 4192 | 11947 | 5055 | 918 | 2023 | 0 | 2401 | 998 | 123 | 0 | 357 | 72 | 0 | 0 | 91.26
4:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 408 | 251 |  | 0 | 420 | 0 | 74 | 0 | 30 | 335 | 0 | 185 | 97 | 48 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 30 | 24 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 34 | 0 | 11 | 44 | 21 | 42 | 0 | 0 | 0 | 310 | 310 | 137 | 187 | 85 | 35 | 48 | 0 | 51 | 0 | 41 | 8 | 22 | 7 | 33 | 20 | 72 | 208 | 0 | 15 | 0 | 43 | 42 | 50 | 48 | 80 | 0 | 51 | 81 | 0 | 220 | 0 | 26 | 10 | 0 | 15 | 11 | 0 | 145 | 0 | 0 | 116 | 0 | 130 | 0 | 20 | 120 | 130 | 403 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 9 | 100 | 400 | 104 | 0 | 0 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 915 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 16 | 0 | 0 | 65 | 0 | 0 | 87 | 0 | 34 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 180 | 0 | 164 | 0 | 0 | 0 | 168 | 0 | 414 | 53 | 0 | 94 | 0 | 65 | 0 | 0 | 76 | 700 | 183 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7714 | 4067 | 11781 | 5032 | 915 | 2021 | 0 | 2365 | 897 | 122 | 0 | 357 | 72 | 0 | 0 | 91.27
5:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 408 | 253 |  | 0 | 420 | 0 | 77 | 0 | 30 | 335 | 0 | 188 | 98 | 48 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 30 | 24 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 34 | 34 | 0 | 11 | 44 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 139 | 185 | 85 | 35 | 48 | 0 | 51 | 0 | 41 | 8 | 22 | 7 | 33 | 20 | 70 | 208 | 0 | 15 | 0 | 43 | 42 | 50 | 48 | 80 | 0 | 51 | 81 | 0 | 218 | 0 | 26 | 10 | 0 | 15 | 11 | 0 | 145 | 0 | 0 | 116 | 0 | 130 | 0 | 20 | 120 | 131 | 402 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 8 | 100 | 400 | 104 | 0 | 0 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 916 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 16 | 0 | 0 | 65 | 0 | 0 | 87 | 0 | 34 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 180 | 0 | 158 | 0 | 0 | 0 | 155 | 0 | 414 | 53 | 0 | 94 | 0 | 65 | 0 | 0 | 76 | 690 | 183 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7715 | 4039 | 11754 | 5014 | 916 | 2018 | 0 | 2370 | 887 | 122 | 0 | 357 | 70 | 0 | 0 | 91.27
6:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 251 |  | 0 | 420 | 0 | 77 | 0 | 15 | 335 | 0 | 190 | 43 | 48 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 30 | 8 | 0 | 86 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 34 | 17 | 0 | 0 | 44 | 20 | 42 | 0 | 0 | 0 | 310 | 310 | 30 | 187 | 85 | 35 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 66 | 208 | 0 | 15 | 0 | 43 | 42 | 50 | 48 | 80 | 0 | 51 | 81 | 0 | 219 | 0 | 25 | 10 | 0 | 15 | 0 | 0 | 45 | 0 | 0 | 116 | 0 | 118 | 1 | 20 | 120 | 20 | 402 | 59 | 105 | 17 | 0 | 0 | 35 | 110 | 17 | 8 | 100 | 400 | 30 | 1 | 0 | 108 | 0 | 35 | 2 | 96 | 42 | 0 |  | 916 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 180 | 0 | 157 | 0 | 0 | 0 | 155 | 0 | 414 | 17 | 0 | 94 | 0 | 67 | 0 | 0 | 76 | 680 | 183 | 0 | 0 | 0 | 5 | 34 | 0 | 0 |  | 7071 | 3801 | 10872 | 4895 | 916 | 2014 | 0 | 1796 | 877 | 121 | 0 | 178 | 66 | 9 | 0 | 91.27
7:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 252 |  | 0 | 420 | 0 | 78 | 0 | 15 | 335 | 0 | 195 | 7 | 48 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 30 | 8 | 0 | 88 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 18 | 20 | 36 | 0 | 0 | 0 | 310 | 310 | 34 | 187 | 85 | 32 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 62 | 207 | 0 | 15 | 0 | 43 | 42 | 50 | 49 | 80 | 0 | 56 | 81 | 0 | 219 | 0 | 25 | 10 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 116 | 0 | 70 | 5 | 20 | 120 | 20 | 401 | 59 | 105 | 17 | 1 | 0 | 35 | 110 | 17 | 9 | 100 | 400 | 17 | 13 | 0 | 108 | 0 | 35 | 6 | 95 | 55 | 0 |  | 915 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 19 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 180 | 0 | 157 | 0 | 0 | 0 | 155 | 0 | 414 | 17 | 0 | 94 | 0 | 67 | 0 | 1 | 75 | 680 | 183 | 0 | 0 | 1 | 17 | 0 | 0 | 0 |  | 6887 | 3747 | 10634 | 4904 | 915 | 2006 | 0 | 1622 | 877 | 123 | 0 | 81 | 62 | 44 | 0 | 91.28
8:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 252 |  | 0 | 420 | 0 | 77 | 0 | 15 | 280 | 0 | 185 | 7 | 48 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 15 | 8 | 0 | 90 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 21 | 20 | 11 | 0 | 0 | 0 | 310 | 305 | 26 | 185 | 85 | 32 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 60 | 207 | 0 | 15 | 1 | 43 | 42 | 50 | 49 | 80 | 0 | 56 | 81 | 0 | 219 | 0 | 25 | 10 | 0 | 24 | 11 | 0 | 15 | 0 | 0 | 114 | 0 | 70 | 11 | 20 | 120 | 20 | 354 | 59 | 105 | 17 | 1 | 0 | 35 | 110 | 17 | 9 | 100 | 400 | 17 | 28 | 0 | 108 | 0 | 35 | 4 | 95 | 55 | 0 |  | 915 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 161 | 0 | 0 | 0 | 158 | 0 | 370 | 17 | 0 | 94 | 0 | 66 | 0 | 0 | 76 | 680 | 183 | 0 | 0 | 2 | 49 | 0 | 0 | 0 |  | 6710 | 3740 | 10450 | 4790 | 915 | 1933 | 0 | 1621 | 878 | 125 | 0 | 32 | 60 | 96 | 0 | 91.28
9:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 408 | 252 |  | 0 | 420 | 0 | 72 | 0 | 15 | 280 | 0 | 145 | 7 | 48 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 16 | 25 | 32 | 8 | 0 | 91 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 36 | 20 | 2 | 0 | 0 | 0 | 320 | 320 | 39 | 187 | 85 | 32 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 0 | 33 | 20 | 60 | 201 | 0 | 15 | 1 | 43 | 42 | 50 | 48 | 80 | 0 | 60 | 78 | 0 | 218 | 0 | 25 | 10 | 10 | 24 | 11 | 0 | 15 | 0 | 0 | 114 | 0 | 70 | 11 | 20 | 120 | 40 | 353 | 59 | 105 | 17 | 4 | 0 | 35 | 110 | 17 | 9 | 100 | 391 | 17 | 47 | 0 | 108 | 0 | 35 | 24 | 95 | 55 | 0 |  | 915 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 165 | 0 | 0 | 0 | 162 | 0 | 370 | 17 | 0 | 94 | 0 | 66 | 0 | 1 | 76 | 680 | 183 | 0 | 0 | 4 | 17 | 0 | 0 | 0 |  | 6788 | 3717 | 10505 | 4793 | 915 | 1931 | 0 | 1661 | 878 | 126 | 0 | 32 | 60 | 109 | 0 | 91.28
10:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 409 | 252 |  | 0 | 420 | 0 | 71 | 0 | 25 | 280 | 0 | 143 | 26 | 84 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 15 | 25 | 0 | 25 | 32 | 17 | 0 | 91 | 35 | 100 | 0 | 2 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 37 | 20 | 2 | 0 | 0 | 0 | 325 | 305 | 105 | 187 | 84 | 32 | 46 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 60 | 202 | 0 | 15 | 2 | 44 | 42 | 47 | 48 | 80 | 0 | 63 | 75 | 0 | 219 | 0 | 25 | 10 | 10 | 24 | 0 | 0 | 117 | 0 | 0 | 115 | 0 | 70 | 8 | 20 | 120 | 50 | 403 | 59 | 90 | 17 | 5 | 0 | 35 | 110 | 17 | 9 | 100 | 400 | 41 | 47 | 0 | 108 | 0 | 35 | 0 | 94 | 49 | 0 |  | 880 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 170 | 0 | 0 | 0 | 167 | 0 | 304 | 17 | 0 | 94 | 0 | 65 | 0 | 4 | 76 | 680 | 220 | 0 | 0 | 1 | 94 | 0 | 0 | 0 |  | 7051 | 3741 | 10792 | 4903 | 880 | 1898 | 0 | 1854 | 878 | 126 | 0 | 32 | 60 | 161 | 0 | 91.29
11:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 408 | 252 |  | 0 | 420 | 0 | 71 | 0 | 30 | 280 | 0 | 97 | 50 | 93 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 16 | 25 | 32 | 33 | 0 | 46 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 0 | 31 | 21 | 2 | 0 | 0 | 0 | 340 | 320 | 172 | 187 | 85 | 29 | 46 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 60 | 198 | 0 | 15 | 1 | 44 | 42 | 47 | 48 | 80 | 0 | 60 | 75 | 0 | 205 | 0 | 25 | 8 | 10 | 23 | 3 | 0 | 240 | 0 | 0 | 115 | 0 | 70 | 12 | 30 | 120 | 60 | 365 | 59 | 90 | 17 | 5 | 0 | 35 | 110 | 17 | 9 | 100 | 360 | 50 | 43 | 0 | 108 | 0 | 35 | 34 | 82 | 55 | 0 |  | 880 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 180 | 0 | 166 | 0 | 0 | 0 | 164 | 0 | 385 | 17 | 0 | 94 | 0 | 66 | 0 | 4 | 76 | 680 | 220 | 0 | 0 | 4 | 15 | 0 | 0 | 0 |  | 7254 | 3704 | 10958 | 4829 | 880 | 1980 | 0 | 2100 | 878 | 81 | 0 | 32 | 60 | 118 | 0 | 91.29
12:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 252 |  | 0 | 420 | 0 | 71 | 0 | 30 | 280 | 0 | 94 | 52 | 93 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 16 | 25 | 32 | 33 | 0 | 40 | 35 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 30 | 31 | 21 | 2 | 0 | 0 | 0 | 325 | 305 | 205 | 187 | 85 | 29 | 46 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 68 | 176 | 0 | 15 | 2 | 43 | 42 | 50 | 47 | 80 | 0 | 60 | 75 | 0 | 193 | 0 | 6 | 10 | 60 | 23 | 11 | 0 | 257 | 0 | 0 | 113 | 0 | 70 | 13 | 60 | 120 | 60 | 366 | 59 | 90 | 26 | 5 | 15 | 35 | 110 | 17 | 9 | 90 | 360 | 52 | 52 | 0 | 108 | 0 | 35 | 35 | 93 | 55 | 0 |  | 880 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 198 | 0 | 169 | 0 | 0 | 0 | 198 | 0 | 409 | 17 | 0 | 94 | 13 | 68 | 0 | 4 | 76 | 750 | 220 | 0 | 0 | 5 | 93 | 0 | 0 | 0 |  | 7361 | 3944 | 11305 | 4842 | 880 | 2036 | 0 | 2231 | 948 | 75 | 0 | 16 | 68 | 209 | 0 | 91.29
13:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 300 |  | 0 | 420 | 0 | 71 | 0 | 30 | 335 | 0 | 92 | 82 | 84 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 25 | 32 | 33 | 0 | 43 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 48 | 31 | 21 | 2 | 0 | 0 | 0 | 325 | 305 | 205 | 187 | 85 | 29 | 46 | 0 | 51 | 0 | 48 | 8 | 22 | 7 | 33 | 20 | 72 | 152 | 0 | 15 | 2 | 43 | 42 | 50 | 47 | 80 | 0 | 60 | 78 | 0 | 206 | 0 | 6 | 10 | 110 | 23 | 11 | 0 | 260 | 0 | 0 | 113 | 0 | 104 | 7 | 76 | 110 | 76 | 404 | 58 | 90 | 48 | 2 | 60 | 35 | 107 | 17 | 9 | 90 | 388 | 72 | 45 | 0 | 108 | 0 | 35 | 35 | 95 | 55 | 0 |  | 880 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 196 | 0 | 197 | 0 | 0 | 0 | 191 | 0 | 377 | 17 | 0 | 94 | 67 | 59 | 0 | 5 | 76 | 790 | 220 | 0 | 0 | 5 | 106 | 0 | 0 | 0 |  | 7789 | 4062 | 11851 | 4999 | 880 | 2101 | 0 | 2462 | 988 | 78 | 0 | 64 | 72 | 207 | 0 | 91.29
14:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 325 |  | 0 | 420 | 0 | 71 | 0 | 30 | 333 | 0 | 95 | 88 | 84 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 16 | 25 | 32 | 33 | 0 | 42 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 55 | 72 | 31 | 21 | 2 | 0 | 0 | 0 | 330 | 310 | 205 | 187 | 85 | 32 | 45 | 0 | 51 | 0 | 48 | 8 | 22 | 7 | 33 | 20 | 74 | 142 | 0 | 15 | 1 | 42 | 42 | 47 | 46 | 80 | 0 | 60 | 78 | 0 | 220 | 0 | 6 | 8 | 200 | 23 | 11 | 0 | 272 | 0 | 0 | 114 | 0 | 132 | 17 | 76 | 120 | 80 | 405 | 58 | 105 | 72 | 2 | 60 | 35 | 93 | 17 | 8 | 90 | 388 | 89 | 39 | 0 | 108 | 0 | 35 | 32 | 94 | 55 | 0 |  | 880 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 173 | 0 | 188 | 0 | 0 | 0 | 172 | 0 | 331 | 17 | 0 | 94 | 67 | 65 | 0 | 7 | 76 | 810 | 220 | 0 | 0 | 5 | 28 | 0 | 0 | 0 |  | 8082 | 3928 | 12010 | 4989 | 880 | 2167 | 0 | 2606 | 1008 | 77 | 0 | 78 | 74 | 131 | 0 | 91.29
15:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 405 | 325 |  | 0 | 420 | 0 | 71 | 0 | 55 | 327 | 0 | 95 | 89 | 84 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 22 | 25 | 16 | 25 | 32 | 33 | 0 | 44 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 70 | 31 | 21 | 2 | 0 | 0 | 0 | 340 | 320 | 203 | 182 | 85 | 32 | 45 | 0 | 51 | 0 | 42 | 8 | 22 | 7 | 33 | 20 | 72 | 141 | 0 | 15 | 2 | 42 | 42 | 0 | 0 | 80 | 0 | 60 | 78 | 0 | 220 | 0 | 6 | 10 | 290 | 23 | 11 | 0 | 260 | 0 | 0 | 114 | 0 | 132 | 15 | 76 | 120 | 40 | 402 | 58 | 105 | 87 | 3 | 60 | 35 | 99 | 17 | 8 | 90 | 384 | 91 | 42 | 0 | 108 | 0 | 35 | 22 | 94 | 55 | 0 |  | 880 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 159 | 0 | 169 | 0 | 0 | 0 | 173 | 0 | 398 | 17 | 0 | 94 | 67 | 65 | 0 | 6 | 76 | 840 | 220 | 0 | 0 | 3 | 86 | 0 | 0 | 0 |  | 8085 | 4060 | 12145 | 4959 | 880 | 2227 | 0 | 2630 | 1037 | 79 | 0 | 82 | 72 | 179 | 0 | 91.3
16:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 400 | 308 |  | 0 | 420 | 0 | 70 | 0 | 55 | 329 | 0 | 95 | 88 | 93 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 16 | 25 | 32 | 36 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 55 | 72 | 31 | 21 | 4 | 0 | 0 | 0 | 315 | 300 | 204 | 155 | 84 | 29 | 45 | 0 | 30 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 72 | 141 | 0 | 15 | 1 | 43 | 42 | 0 | 0 | 80 | 0 | 60 | 60 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 11 | 0 | 260 | 0 | 0 | 122 | 0 | 132 | 0 | 76 | 120 | 10 | 405 | 58 | 105 | 88 | 3 | 150 | 35 | 110 | 17 | 24 | 90 | 390 | 90 | 30 | 0 | 108 | 0 | 35 | 18 | 95 | 55 | 0 |  | 880 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 60 | 0 | 0 | 27 | 0 | 8 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 191 | 0 | 192 | 0 | 0 | 0 | 194 | 0 | 370 | 17 | 0 | 94 | 88 | 65 | 0 | 5 | 76 | 900 | 220 | 0 | 0 | 1 | 55 | 0 | 0 | 0 |  | 8112 | 4198 | 12310 | 4966 | 880 | 2121 | 0 | 2793 | 1097 | 122 | 0 | 146 | 72 | 113 | 0 | 91.3
17:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 401 | 310 |  | 0 | 420 | 0 | 71 | 0 | 55 | 328 | 0 | 0 | 88 | 48 | 62 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 0 | 25 | 16 | 25 | 32 | 41 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 33 | 0 | 10 | 60 | 31 | 21 | 12 | 0 | 0 | 0 | 285 | 265 | 205 | 155 | 84 | 32 | 46 | 0 | 30 | 0 | 47 | 8 | 22 | 7 | 33 | 19 | 70 | 141 | 0 | 15 | 1 | 43 | 42 | 0 | 0 | 80 | 0 | 55 | 30 | 0 | 220 | 0 | 0 | 10 | 265 | 8 | 11 | 0 | 243 | 0 | 0 | 124 | 0 | 120 | 4 | 50 | 147 | 10 | 406 | 58 | 88 | 51 | 1 | 80 | 43 | 85 | 17 | 90 | 90 | 393 | 75 | 15 | 6 | 108 | 0 | 35 | 4 | 94 | 55 | 0 |  | 881 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 16 | 0 | 0 | 60 | 0 | 5 | 84 | 0 | 24 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 162 | 0 | 172 | 0 | 0 | 0 | 174 | 0 | 303 | 30 | 0 | 94 | 88 | 70 | 0 | 3 | 76 | 890 | 220 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 7728 | 4088 | 11816 | 4734 | 881 | 2002 | 0 | 2634 | 1087 | 121 | 0 | 255 | 70 | 32 | 0 | 91.3
18:00 | 0 | 0 | 0 | 180 | 300 | 53 | 0 | 398 | 280 |  | 0 | 330 | 0 | 60 | 0 | 55 | 250 | 0 | 0 | 66 | 48 | 62 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 16 | 25 | 32 | 34 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 10 | 51 | 19 | 21 | 20 | 0 | 0 | 0 | 285 | 265 | 206 | 155 | 83 | 34 | 44 | 0 | 30 | 0 | 47 | 8 | 22 | 9 | 33 | 19 | 66 | 142 | 0 | 15 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 40 | 30 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 11 | 0 | 243 | 0 | 0 | 160 | 0 | 105 | 0 | 30 | 200 | 10 | 366 | 104 | 70 | 51 | 0 | 50 | 35 | 68 | 17 | 111 | 40 | 360 | 72 | 6 | 17 | 68 | 0 | 35 | 3 | 95 | 35 | 0 |  | 880 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 60 | 0 | 21 | 83 | 0 | 24 | 24 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 149 | 0 | 152 | 0 | 0 | 0 | 140 | 0 | 307 | 35 | 0 | 50 | 32 | 98 | 0 | 1 | 50 | 770 | 160 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 7239 | 3601 | 10840 | 4312 | 880 | 1804 | 0 | 2427 | 969 | 121 | 0 | 241 | 66 | 20 | 0 | 91.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 290 | 80 | 0 | 408 | 252 |  | 0 | 300 | 0 | 60 | 0 | 55 | 259 | 0 | 0 | 63 | 64 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 16 | 25 | 32 | 38 | 0 | 87 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 10 | 41 | 55 | 63 | 20 | 21 | 29 | 0 | 0 | 0 | 285 | 265 | 206 | 155 | 84 | 32 | 43 | 0 | 39 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 78 | 137 | 0 | 15 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 60 | 60 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 11 | 0 | 255 | 0 | 0 | 174 | 0 | 110 | 0 | 72 | 200 | 10 | 398 | 104 | 75 | 53 | 0 | 50 | 39 | 74 | 60 | 110 | 50 | 360 | 82 | 0 | 39 | 74 | 0 | 35 | 0 | 95 | 38 | 0 |  | 864 | 0 | 300 | 0 | 64 | 0 | 0 | 0 | 42 | 28 | 8 | 0 | 21 | 16 | 0 | 0 | 60 | 17 | 30 | 86 | 0 | 34 | 27 | 8 | 27 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 145 | 0 | 0 | 0 | 143 | 0 | 367 | 35 | 0 | 54 | 15 | 99 | 0 | 0 | 85 | 780 | 220 | 0 | 8 | 0 | 0 | 66 | 0 | 0 |  | 7716 | 4030 | 11746 | 4417 | 864 | 1945 | 0 | 2871 | 979 | 122 | 0 | 470 | 78 | 0 | 0 | 91.31
19:30 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 300 |  | 0 | 420 | 0 | 71 | 0 | 55 | 280 | 0 | 0 | 75 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 25 | 33 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 28 | 51 | 55 | 80 | 35 | 21 | 23 | 0 | 0 | 0 | 285 | 265 | 205 | 155 | 84 | 35 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 78 | 137 | 0 | 15 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 55 | 60 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 5 | 0 | 255 | 0 | 0 | 175 | 0 | 130 | 0 | 90 | 200 | 10 | 405 | 104 | 105 | 68 | 0 | 170 | 54 | 110 | 114 | 110 | 90 | 390 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 863 | 0 | 356 | 0 | 83 | 0 | 0 | 0 | 40 | 29 | 8 | 20 | 22 | 32 | 0 | 0 | 60 | 20 | 33 | 86 | 0 | 34 | 30 | 16 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 172 | 0 | 168 | 0 | 0 | 0 | 163 | 0 | 403 | 50 | 0 | 70 | 67 | 99 | 0 | 0 | 113 | 950 | 223 | 0 | 17 | 0 | 0 | 113 | 0 | 0 |  | 8726 | 4601 | 13327 | 4616 | 863 | 2192 | 0 | 3780 | 1150 | 123 | 0 | 525 | 78 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 407 | 303 |  | 0 | 420 | 0 | 73 | 0 | 55 | 280 | 0 | 0 | 96 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 19 | 25 | 33 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 25 | 51 | 55 | 80 | 37 | 21 | 22 | 0 | 0 | 0 | 285 | 265 | 206 | 155 | 84 | 35 | 43 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 74 | 137 | 0 | 19 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 213 | 0 | 0 | 10 | 285 | 8 | 5 | 0 | 256 | 0 | 0 | 170 | 0 | 130 | 0 | 90 | 200 | 10 | 404 | 104 | 105 | 69 | 0 | 190 | 54 | 108 | 114 | 110 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 94 | 55 | 0 |  | 864 | 0 | 355 | 0 | 80 | 0 | 0 | 0 | 49 | 30 | 8 | 20 | 21 | 32 | 0 | 0 | 60 | 34 | 31 | 86 | 0 | 34 | 32 | 25 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 173 | 0 | 164 | 0 | 0 | 0 | 163 | 0 | 343 | 94 | 0 | 90 | 105 | 101 | 0 | 0 | 113 | 980 | 223 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 8798 | 4697 | 13495 | 4626 | 864 | 2147 | 0 | 3935 | 1180 | 123 | 0 | 546 | 74 | 0 | 0 | 91.31
21:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 398 | 324 |  | 0 | 450 | 0 | 80 | 0 | 55 | 335 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 21 | 25 | 33 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 15 | 51 | 51 | 55 | 80 | 37 | 21 | 32 | 0 | 0 | 0 | 285 | 265 | 206 | 155 | 84 | 36 | 44 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 14 | 80 | 131 | 0 | 19 | 0 | 42 | 42 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 219 | 0 | 0 | 10 | 260 | 8 | 5 | 0 | 273 | 0 | 0 | 167 | 0 | 122 | 0 | 90 | 200 | 10 | 404 | 105 | 105 | 70 | 0 | 50 | 54 | 110 | 114 | 111 | 100 | 398 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 863 | 0 | 355 | 0 | 80 | 0 | 0 | 0 | 38 | 30 | 8 | 20 | 24 | 32 | 0 | 0 | 60 | 34 | 30 | 86 | 0 | 34 | 32 | 25 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 167 | 0 | 165 | 0 | 0 | 0 | 171 | 0 | 367 | 94 | 0 | 113 | 105 | 101 | 0 | 0 | 113 | 1020 | 224 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8761 | 4777 | 13538 | 4669 | 863 | 2212 | 0 | 3810 | 1220 | 124 | 0 | 560 | 80 | 0 | 0 | 91.31
22:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 405 | 332 |  | 0 | 450 | 0 | 76 | 0 | 55 | 335 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 25 | 21 | 25 | 33 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 51 | 51 | 55 | 39 | 37 | 21 | 32 | 0 | 0 | 0 | 280 | 265 | 207 | 155 | 84 | 36 | 44 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 80 | 131 | 0 | 13 | 0 | 44 | 42 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 8 | 0 | 273 | 0 | 0 | 167 | 0 | 114 | 0 | 90 | 200 | 10 | 404 | 105 | 105 | 17 | 0 | 15 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 54 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 864 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 38 | 30 | 8 | 89 | 36 | 32 | 0 | 0 | 65 | 34 | 30 | 86 | 0 | 34 | 32 | 43 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 166 | 0 | 171 | 0 | 0 | 0 | 174 | 0 | 332 | 94 | 0 | 113 | 105 | 101 | 0 | 0 | 113 | 1040 | 225 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8523 | 4879 | 13402 | 4762 | 864 | 2208 | 0 | 3563 | 1240 | 125 | 0 | 560 | 80 | 0 | 0 | 91.31
23:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 409 | 323 |  | 0 | 450 | 0 | 73 | 0 | 55 | 335 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 25 | 21 | 25 | 33 | 49 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 32 | 37 | 21 | 34 | 0 | 0 | 0 | 310 | 300 | 208 | 158 | 85 | 36 | 45 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 74 | 131 | 0 | 7 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 58 | 81 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 11 | 0 | 275 | 0 | 0 | 167 | 0 | 114 | 0 | 90 | 200 | 10 | 403 | 105 | 105 | 21 | 0 | 15 | 54 | 110 | 97 | 111 | 100 | 400 | 104 | 0 | 56 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 864 | 0 | 390 | 0 | 81 | 0 | 0 | 0 | 38 | 30 | 8 | 87 | 36 | 32 | 0 | 0 | 65 | 34 | 23 | 86 | 0 | 34 | 32 | 43 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 156 | 0 | 171 | 0 | 0 | 0 | 176 | 0 | 358 | 94 | 0 | 113 | 105 | 103 | 0 | 0 | 113 | 1050 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8599 | 4928 | 13527 | 4852 | 864 | 2253 | 0 | 3554 | 1250 | 126 | 0 | 554 | 74 | 0 | 0 | 91.31
24:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 409 | 322 |  | 0 | 450 | 0 | 70 | 0 | 55 | 335 | 0 | 0 | 94 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 49 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 55 | 73 | 37 | 21 | 41 | 0 | 0 | 0 | 280 | 265 | 207 | 158 | 85 | 36 | 45 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 82 | 131 | 0 | 3 | 0 | 43 | 42 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 220 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 273 | 0 | 0 | 117 | 0 | 123 | 0 | 90 | 200 | 10 | 401 | 59 | 105 | 87 | 0 | 220 | 39 | 110 | 17 | 46 | 100 | 400 | 104 | 0 | 154 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 864 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 33 | 30 | 0 | 88 | 37 | 32 | 0 | 0 | 65 | 34 | 15 | 88 | 0 | 34 | 32 | 43 | 28 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 173 | 0 | 0 | 0 | 176 | 0 | 319 | 94 | 0 | 94 | 105 | 103 | 0 | 0 | 76 | 1060 | 221 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8608 | 4800 | 13408 | 4765 | 864 | 2215 | 0 | 3554 | 1260 | 126 | 0 | 542 | 82 | 0 | 0 | 91.31
KWH | 0 | 0 | 0 | 4347000 | 7221864 | 1939318 | 0 | 9897980 | 6870000 |  | 0 | 9497800 | 0 | 1753920 | 0 | 923105 | 7569721 | 0 | 2642000 | 1742256 | 1710720 | 1883040 | 0 | 0 | 0 | 0 | 340200 | 298707 | 513979 | 205020 | 600000 | 377820 | 592600 | 746700 | 762720 | 0 | 1888800 | 840000 | 2400000 | 0 | 469409 | 0 | 0 | 0 | 0 |  | 522720 | 471288 | 482245 | 760320 | 834240 | 830880 | 462048 | 534240 | 0 | 0 | 0 | 7702800 | 7224000 | 3745000 | 4248727 | 2008610 | 787104 | 1093920 | 0 | 1118251 | 0 | 740784 | 207336 | 503820 | 195120 | 810900 | 506380 | 1695360 | 4055040 | 0 | 327024 | 15650 | 1024000 | 973096 | 708000 | 670752 | 1990963 | 0 | 1347072 | 1747200 | 0 | 5182010 | 0 | 328600 | 231840 | 3281220 | 450662 | 196080 | 0 | 4649344 | 0 | 0 | 3057600 | 0 | 2667168 | 119880 | 1252800 | 3474240 | 1493745 | 9459000 | 1676400 | 2404800 | 994436 | 30840 | 1038764 | 1002850 | 2564279 | 835620 | 979440 | 2233920 | 9334400 | 1901760 | 393550 | 712800 | 2541709 | 0 | 879840 | 237661 | 2225280 | 1297440 | 0 |  | 21502545 | 0 | 8651232 | 0 | 736320 | 0 | 0 | 0 | 204000 | 157568 | 34875 | 1827910 | 540600 | 470304 | 0 | 0 | 1500000 | 156384 | 166504 | 1101923 | 0 | 408688 | 245213 | 314400 | 348320 | 462000 | 0 | 259164 | 0 | 0 | 4837000 | 0 | 0 | 4577936 | 0 | 4253609 | 0 | 0 | 0 | 4313300 | 0 | 9049454 | 1106880 | 0 | 2311776 | 1117728 | 1841356 | 0 | 42569 | 1945056 | 21678700 | 4934755 | 0 | 97200 | 33900 | 562320 | 1208448 | 0 | 0 |  | 187509547 | 102999937 | 290509484 | 118278022 | 21502545 | 49247640 | 0 | 63147778 | 26515700 | 2728800 | 0 | 5957269 | 1695360 | 1436370 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 8088487.68 | 2579292.94 | 0 | 10392879 | 7419600 |  | 0 | 10352602 | 0 | 19608825.6 | 0 | 12231141.25 | 8478087.52 | 0 | 4623500 | 25471782.72 | 24069830.4 | 30524078.4 | 0 | 0 | 0 | 0 | 4327344 | 4032544.5 | 6892458.39 | 153765 | 450000 | 0 | 0 | 0 | 12973867.2 | 0 | 509976 | 226800 | 4536000 | 0 | 7674837.15 | 0 | 0 | 0 | 0 |  | 6821496 | 7861083.84 | 8207809.9 | 10271923.2 | 10578163.2 | 9613281.6 | 586800.96 | 1779019.2 | 0 | 0 | 0 | 8550108 | 7874160 | 4344200 | 5480857.83 | 2450504.2 | 889427.52 | 1629940.8 | 0 | 1867479.17 | 0 | 12793339.68 | 2788669.2 | 690233.4 | 146340 | 1419075 | 379785 | 12172684.8 | 4419993.6 | 0 | 444752.64 | 249461 | 1402880 | 1284486.72 | 1231920 | 1160400.96 | 2289607.45 | 0 | 2613319.68 | 3983616 | 0 | 5233830.1 | 0 | 489614 | 459043.2 | 3281220 | 337996.5 | 149020.8 | 0 | 63463545.6 | 0 | 0 | 41216448 | 0 | 36940276.8 | 1401397.2 | 12928896 | 47458118.4 | 19821996.15 | 8702280 | 20385024 | 34773408 | 12579615.4 | 0 | 12195089.36 | 10921036.5 | 27258285.77 | 11339363.4 | 12624981.6 | 26315577.6 | 8587648 | 24627792 | 5686797.5 | 9045432 | 28924648.42 | 0 | 11490710.4 | 2840048.95 | 33312441.6 | 17087284.8 | 0 |  | 64507635 | 0 | 9689379.84 | 0 | 7665091.2 | 0 | 0 | 0 | 3674040 | 2836224 | 501153.75 | 2047259.2 | 1048764 | 5126313.6 | 0 | 0 | 3075000 | 2622559.68 | 2912154.96 | 17234075.72 | 0 | 6767873.28 | 4146551.83 | 4285272 | 5876158.4 | 956340 | 0 | 196187.148 | 0 | 0 | 25587730 | 0 | 0 | 5310405.76 | 0 | 5444619.52 | 0 | 0 | 0 | 5003428 | 0 | 8958959.46 | 14876467.2 | 0 | 27348310.08 | 16151169.6 | 23385221.2 | 0 | 470387.45 | 23612979.84 | 195325087 | 5033450.1 | 0 | 719280 | 383409 | 6596013.6 | 18525507.84 | 0 | 0 |  | 902250418.35 | 527900459.258 | 1430150877.608 | 134472870.788 | 64507635 | 60001727.11 | 0 | 821030775.8 | 220912817 | 736776 | 0 | 98688076.41 | 12172684.8 | 17627514.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 252 |  | 0 | 420 | 0 | 71 | 0 | 30 | 280 | 0 | 94 | 52 | 93 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 16 | 25 | 32 | 33 | 0 | 40 | 35 | 100 | 0 | 20 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 30 | 31 | 21 | 2 | 0 | 0 | 0 | 325 | 305 | 205 | 187 | 85 | 29 | 46 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 20 | 68 | 176 | 0 | 15 | 2 | 43 | 42 | 50 | 47 | 80 | 0 | 60 | 75 | 0 | 193 | 0 | 6 | 10 | 60 | 23 | 11 | 0 | 257 | 0 | 0 | 113 | 0 | 70 | 13 | 60 | 120 | 60 | 366 | 59 | 90 | 26 | 5 | 15 | 35 | 110 | 17 | 9 | 90 | 360 | 52 | 52 | 0 | 108 | 0 | 35 | 35 | 93 | 55 | 0 |  | 880 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 198 | 0 | 169 | 0 | 0 | 0 | 198 | 0 | 409 | 17 | 0 | 94 | 13 | 68 | 0 | 4 | 76 | 750 | 220 | 0 | 0 | 5 | 93 | 0 | 0 | 0 |  | 11305 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 398 | 324 | 0 | 0 | 450 | 0 | 80 | 0 | 55 | 335 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 21 | 25 | 33 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 51 | 51 | 55 | 80 | 37 | 21 | 32 | 0 | 0 | 0 | 285 | 265 | 206 | 155 | 84 | 36 | 44 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 14 | 80 | 131 | 0 | 19 | 0 | 42 | 42 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 219 | 0 | 0 | 10 | 260 | 8 | 5 | 0 | 273 | 0 | 0 | 167 | 0 | 122 | 0 | 90 | 200 | 10 | 404 | 105 | 105 | 70 | 0 | 50 | 54 | 110 | 114 | 111 | 100 | 398 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 863 | 0 | 355 | 0 | 80 | 0 | 0 | 0 | 38 | 30 | 8 | 20 | 24 | 32 | 0 | 0 | 60 | 34 | 30 | 86 | 0 | 34 | 32 | 25 | 29 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 167 | 0 | 165 | 0 | 0 | 0 | 171 | 0 | 367 | 94 | 0 | 113 | 105 | 101 | 0 | 0 | 113 | 1020 | 224 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 13538 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 78 | 0 | 55 | 335 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 51 | 55 | 90 | 38 | 21 | 30 | 0 | 0 | 0 | 320 | 300 | 190 | 95 | 85 | 35 | 47 | 0 | 51 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 78 | 90 | 0 | 22 | 0 | 44 | 42 | 0 | 0 | 0 | 0 | 62 | 78 | 0 | 220 | 0 | 0 | 10 | 341 | 0 | 0 | 200 | 280 | 300 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 145 | 400 | 105 | 105 | 105 | 0 | 285 | 54 | 110 | 17 | 113 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 95 | 55 |  |  | 877 | 0 | 380 | 0 | 83 | 220 | 0 | 0 | 42 | 60 | 8 | 87 | 30 | 110 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 10 | 160 | 0 | 170 | 0 | 0 | 100 | 160 | 0 | 414 | 94 | 170 | 113 | 105 | 97 | 0 | 0 | 113 | 1100 | 220 |  | 35 |  |  | 109
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 78 | 0 | 55 | 335 | 0 | 0 | 70 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 21 | 33 | 33 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  |  | 55 | 70 | 38 | 21 | 7 | 0 | 0 | 0 | 340 | 310 | 200 | 150 | 85 | 35 | 47 | 0 | 51 | 0 | 40 | 8 | 22 | 11 | 33 | 20 | 60 | 100 | 0 | 22 | 1.6 | 44 | 42 | 0 | 0 | 0 | 0 | 62 | 78 | 0 | 190 | 0 | 0 | 10 | 341 | 0 | 0 | 100 | 280 | 200 | 0 | 116 | 0 | 135 | 20 | 90 | 120 | 145 | 400 | 60 | 105 | 105 | 5 | 200 | 54 | 110 | 17 | 9 | 100 | 400 | 104 | 50 | 162 | 108 | 0 | 35 | 30 | 95 | 55 |  |  | 892 | 0 | 380 | 0 | 16 | 220 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 64 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 0 | 180 | 0 | 190 | 0 | 0 | 50 | 180 | 0 | 414 | 75 | 100 | 94 | 105 | 68 | 0 | 8 | 75 | 1100 | 220 |  | 17 | 6 | 100 | 72
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 407 | 332 | 0 | 0 | 300 | 0 | 70 | 0 | 30 | 260 | 0 | 0 | 16 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 42 | 0 | 88 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 55 | 0 | 38 | 21 | 7 | 0 | 0 | 0 | 285 | 270 | 210 | 158 | 84 | 36 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 62 | 134 | 0 | 18 | 1 | 43 | 42 | 0 | 0 | 80 | 0 | 63 | 50 | 0 | 191 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 110 | 0 | 0 | 116 | 0 | 134 | 3 | 76 | 120 | 50 | 353 | 60 | 88 | 34 | 1 | 15 | 36 | 92 | 17 | 9 | 100 | 360 | 53 | 15 | 0 | 108 | 0 | 35 | 11 | 95 | 55 | 0 | 0 | 915 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 155 | 0 | 163 | 0 | 0 | 0 | 162 | 0 | 355 | 17 | 0 | 94 | 15 | 69 | 0 | 2 | 76 | 770 | 162 | 0 | 0 | 1 | 52 | 52 | 0 | 0 | 0 |  |  |  |  | 69105047 |  | 0
69105047
| Minimum Generation |  | 10450 | 8:00
| Highest Generation |  | 13538 | 21:00
| Day Peak Generation |  | 11305 | 12:00
| Evening Peak Generation |  | 13538 | 21:00
| HVDC Max Flow |  | 918 | 3:00
| HVDC EvPeak Flow |  | 863 | 21:00
| Load factor L.F |  | 89.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-17
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11305 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10783 | MW
Evening Peak Generation : |  | 13538 | MW Hour : | 21:00 | Available Max Generation : |  | 15251 | MW
E.P. Demand (at gen end) : |  | 13538 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14600 | MW
Maximum Generation : |  | 13538 | MW Hour : | 21:00 | Reserve(Generation end) |  | 651 | MW
Total Gen. (MKWH) : |  | 290.5095 | System Load Factor : | 89.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -840 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-17
Actual : | 91.34 | Ft.(MSL) , | Rule curve : | 86.24 | Ft.( MSL )
Gas Consumed : | Total = | 1243.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 194474597.898
: |  | Coal : | 220912817 | Oil : | 919718852.21 | Total : | 1335106267.108
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5073.2385 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1370.5279 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1790.6335 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1604.8589 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1421.4551 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1044.6477 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 580.2112 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 377.7347 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 801.244 |  |  | 0 | 0%
Total | 0 |  | 14064.5514 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shahjibazar 132/33 kV T-4 transformer was under shut down from 08:34 to 09:13 for R/H maintenance | [5 empty] | About 40 MW power interruption occurred under
at 33 kV PBS feeder. | [5 empty] | Shahjibazar S/S area from 08:34 to 09:13.
b) Keraniganj 132/33 kV T-2 transformer was under shut down from 09:53 to 12:45 for C/M.
c) Bibiyana-2 Gt was synchronized at 08:44 and ST was synchronized at 10:45.
d) Ashuganj 225 MW ST was synchronized at 08:57.
e) Netrokona 132/33 kV T-2 transformer was shut down at 09:50 to attend Buchholz relay.
f) Kaptai unit-2 tripped at 12:21 and was synchronized at 15:01 and Kaptai unit-3 tripped at 10:55 and
was synchronized at 12:33.
g) Keraniganj 132/33 kV T-2 transformer was under shut down from 16:08 to 17:19 for 33 kV PBS U/G cable flashing.
h) Chattak 132/33 kV T-2 transformer was under shut down from 15:19 to 16:18 for R/H maintenance at 33 kV | [5 empty] | About 4 MW power interruption occurred under
PBS Sunamganj feeder connector. | [5 empty] | Chattak S/S area from 15:19 to 16:18.
i) Siddhirganj-Ullon 132 kV Ckt-1 tripped at 16:55 showing Distance relay at Siddhirganj end.
j) Bhola 225 MW tripped at 17:58.
k) Siddhirganj-Ullon 132 kV Ckt-1 tripped at 18:35 from Siddhirganj end and SOTF operated at Siddhirganj
end and was switched on at 19:11.
l) Siddhirganj GT was shut down at 16:47 due to gas shortage.
m) Bhola 225 MW GT was synchronized at 19:02 and ST was synchronized at 21:26.
n) Mithapukur 132/33 kV T-1 transformer was under shut down from 18:43 to 19:31 for R/H maintenance at 33 kV | [5 empty] | About 15 MW power interruption occurred under
Mirjapur PBS feeder clamp. | [5 empty] | Mithapukur S/S area from 18:43 to 19:31.
o) Mongla 132/33 kV T-1 & T-2 transformers tripped at 04:14(17/7/2022) from 33 kV sides showing O/C,E/F | [5 empty] | About 25 MW power interruption occurred under
relay as fuse of 33/0.4 kV Transformer got burnt and was switched on at 05:14. | [5 empty] | Mongla S/S area from 04:14(17/7/2022) to 05:14.
p) Haripur-Bhulta 132 kV Ckt was under shut down from 06:00(17/7/2022) to 08:27 for R/H maintenance at Bhulta end.
q) Hathazari-Baroirhat 132 kV Ckt-1 & 2 were shut down at 6:26(17/6/2022) for D/W.
r) Noapara132/33 kV T-2 transformer tripped at 6:04(17/4/2022) operating PRD and was switched on at 12:20.
s) Bogura 132/33 kV T-1 transformer was under shut down from 06:40(17/7/2022) for R/H maintenance at
132 kV B,CT connector.
t) Bhaluka 132/33 kV t-1 transformer was under shut down from 07:03(17/7/2022) for Bus isolator | [5 empty] | About 65 MW power interruption occurred under
maintenance at 33 kV,PDB Shokhipur feeder and was switched on at 09:27. | [5 empty] | Bhaluka S/S area from 07:03(17/7/2022) to 09:27.
u) Thakurgaon 33 kV Bus section-3 was under shut down from 05:55(17/7/20220 to 07:16 for isolator | [5 empty] | About 30 MW power interruption occurred under
maintenance of capacitor bank. | [5 empty] | Thakurgaon S/S area from 05:55(17/7/2022) to 07:16.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7221864 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 89 | 1939318 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 9897980 | Machine problem
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 324 | 6870000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9497800
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 80 | 1753920 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 923105
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 205020 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 2642000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 98 | 1742256
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7569721
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1710720 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 340200 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1883040 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 298707
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 513979
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 977820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 592600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 746700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 762720 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 273 | 4649344 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 2667168 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2404800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1901760
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 712800
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 237661
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1297440
| Dhaka area Total |  |  |  | 5847 | 3653 | 76307443
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 469409
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119880
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 830880 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 124 | 2728800 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 70 | 994436 | Low demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 471288 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 482245 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 55 | 760320 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1252800 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 462048
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 534240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 834240 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30840
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 1038764 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1002850
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2564279
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2233920
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2541709 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1158 | 21752948
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 3745000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7702800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7224000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 787104 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1093920 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 155 | 4248727 | Engine problem
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1118251
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 1493745 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 740784 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 84 | 2008610 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3474240
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 503820
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 195120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 80 | 1695360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 810900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 207336 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 14 | 506380 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 835620
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 111 | 979440
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 879840 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 2225280 | Engine problem
| Cumilla Area Total |  |  |  | 2885 | 1905 | 42476277
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 4055040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 327024
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 167 | 3057600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1676400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 393550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 15 | 522720 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 437 | 10047984
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 973096 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 1990963 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 708000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 670752 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 196080 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1347072 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1747200
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5182010
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 328600 | Engine problem
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 450662 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 3281220 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9459000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 231840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 398 | 9334400
| Sylhet Area Total |  |  |  | 2477 | 1608 | 36924895
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 863 | 21502545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 80 | 736320 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 204000 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 157568 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 8651232 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 34875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 1106880 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1117728
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 562320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1573 | 34073468
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 470304 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 540600
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 20 | 1827910 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 21678700 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4934755
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 97200 | Transformer O/L
| Barisal Area Total |  |  |  | 1958 | 1337 | 29549469
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1500000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 156384 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 166504 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 408688 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 245213 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 4577936 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 165 | 4253609
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 171 | 4313300 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 367 | 9049454 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 348320 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 462000
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 259164
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 314400
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 1101923 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2311776
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1945056
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33900
| Rajshahi Area Total |  |  |  | 2129 | 1458 | 31447627
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4837000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 1841356 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42569
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1208448 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 409 | 7929373
| Total |  |  |  | 21396 | 13538 | 290509484
| Eastern Grid Total |  |  |  | 14205 | 8761 | 187509547
| Western Grid Total |  |  |  | 7191 | 4777 | 102999937
| National Grid Total |  |  |  | 21396 | 13538 | 290509484
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-16
(a) ENTIRE EASTERN GRID : |  | 8459.72 | MW | (b) ENTIRE WESTERN GRID : |  | 4573.13 | MW
i) Dhaka area |  | 4135.92 | MW | i) Khulna area |  | 1733.6 | MW
ii) Chittagong area |  | 1335.8 | MW | ii) Rajshahi area |  | 1510.6 | MW
iii) Comilla area |  | 1353 | MW | iii) Barisal area |  | 397.93 | MW
iv) Mymensingh area |  | 1027 | MW | iv) Rangpur area |  | 931 | MW
v) Sylhet area |  | 608 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13032.85 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 9 | 00:00 | Chowmuhani | 231 | 21:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 1 | 09:00 | Chuadanga | 112 | 21:00 | Kazla | 77 | 22:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 30 | 20:00 | Coxsbazar | 117 | 21:00 | Keranigonj | 48 | 13:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 80 | 13:00 | Cumilla(N) | 151 | 22:00 | Khagrachori | 26 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 78 | 19:30 | Cumilla(S) | 174 | 22:00 | Khulna | 88 | 13:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 70 | 21:00 | Daudkandi | 156 | 21:00 | Khulshi | 180 | 16:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 29 | 22:00 | Dhaka | 34 | 13:00 | Kishoreganj | 162 | 01:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 157 | 15:00 | Dhamrai | 100 | 15:00 | Kodda | 229 | 15:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 106 | 20:00 | Dhanmondi | 107 | 12:00 | Kulaura | 54 | 19:30 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 121 | 20:00 | Dohazari | 96 | 19:30 | Kurigram | 68 | 19:30 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 52 | 13:00 | Faridpur | 159 | 22:00 | Kushtia | 146 | 20:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 10 | 10:00 | Fatullah | 50 | 15:00 | Lalbag | 66 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 58 | 22:00 | Fenchuganj | 52 | 19:00 | Lalmonirhat | 57 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 134 | 22:00 | Madanganj | 91 | 22:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 108 | 21:00 | GPH | 93 | 03:00 | Madaripur | 117 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 80 | 21:00 | Ghorashal | 66 | 22:00 | Madartek | 79 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 68 | 07:00 | Goalpara | 28 | 20:00 | Madunaghat | 61 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 58 | 19:00 | Gollamari | 54 | 20:00 | Magura | 64 | 20:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 150 | 14:00 | Gopalganj | 103.2 | 23:00 | Mahasthangarh | 76 | 20:00 | Ramganj | 88 | 19:00
BashundharaCement | 8 | 16:00 | Gulshan | 108 | 16:00 | Manikganj | 87 | 22:00 | Rampur | 16 | 00:00
Beanibazar | 72 | 19:30 | Halishahar | 79.5 | 10:00 | Maniknagar | 61 | 14:00 | Rangamati | 14 | 19:00
Benapole | 60 | 21:00 | HaripurSBU | 101 | 11:00 | Matarbari | 44 | 23:00 | Rangpur | 105 | 08:00
Bhaluka | 130 | 15:00 | Hasnabad | 98 | 23:00 | Matuail | 42 | 16:00 | Ruppur | 5 | 09:00
Bhandaria | 53 | 23:00 | Hathazari | 101 | 19:30 | Millgate | 48 | 14:00 | SSM | 3 | 05:00
Bhangura | 38 | 21:00 | Ishurdi | 79 | 21:00 | Mirpur | 189 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 67 | 21:00 | Jaldhaka | 76 | 02:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 181 | 21:00 | Jamalpur | 142 | 19:30 | Mithapukur | 46 | 10:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 70 | 20:00 | Jashore | 126 | 20:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 171 | 20:00 | Jhenaidah | 126 | 23:00 | Mogbazar | 115 | 16:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 04:00 | Joydebpur | 170 | 16:00 | Mongla | 32 | 09:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 184 | 00:00 | Joypurhat | 64 | 23:00 | Motijheel | 32 | 12:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 137 | 13:00 | Juldah | 27 | 15:00 | Munshiganj | 103 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 76 | 22:00 | KSRM | 33 | 19:00 | Mymensingh | 235 | 20:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 00:00 | Kabirpur | 218 | 16:00 | Naogaon | 133 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 75 | 21:00 | Kachua | 84 | 22:00 | Narail | 58 | 20:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 24 | 21:00 | Kallyanpur | 90 | 00:00 | Narinda | 46 | 14:00 | Shitalakhya | 114 | 12:00
Chauddagram | 50 | 22:00 | Kalurghat | 4 | 12:00 | Narshingdi | 161 | 21:00 | Sholosohor | N/A | N/A
Chhatak | 35 | 22:00 | Kamrangirchar | 41 | 13:00 | Natore | 146 | 23:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 401 | 20:00 | 388 | 00:00 | Kaliakoir | 397 | 18:30 | 383 | 00:00
| Bibiana | 409 | 18:00 | 400 | 00:00 | Payra | 421 | 18:30 | 409 | 23:00
| BIPTC | 396 | 06:00 | 390 | 20:00
| Gopalganj_I | 415 | 18:30 | 394 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 20:00 | 219 | 15:00 | Hasnabad | 229 | 20:00 | 219 | 13:00
| AKSML | 228 | 19:00 | 207 | 12:00 | Hathazari | 237 | 20:00 | 214 | 12:00
| Aminbazar | 228 | 19:30 | 220 | 15:00 | Ishurdi | 237 | 18:00 | 225 | 19:30
| Ashuganj | 240 | 04:00 | 235 | 17:00 | Jhenaidah | 231 | 18:00 | 216 | 19:30
| Baghabari | 234 | 18:30 | 225 | 21:00 | Kaliakoir | 229 | 18:30 | 222 | 00:00
| Barapukuria | 219 | 18:30 | 205 | 23:00 | Keranigonj | 227 | 20:00 | 219 | 15:00
| Barishal | 246 | 18:00 | 233 | 00:00 | Khulna(S) | 241 | 18:00 | 225 | 22:00
| Bheramara | 234 | 18:00 | 221 | 21:00 | Maniknagar | 230 | 20:00 | 224 | 12:00
| Bhulta | 233 | 20:00 | 226 | 12:00 | Meghnaghat | 232 | 19:30 | 224 | 12:00
| Bibiana | 237 | 06:00 | 232 | 01:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 17:00 | 221 | 21:00 | Rajshahi | 235 | 18:30 | 218 | 21:00
| Bogura | 227 | 18:30 | 214 | 1:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 15:00 | 239 | 00:00 | Rampura | 230 | 20:00 | 224 | 13:00
| BSRM | 234 | 20:00 | 216 | 11:00 | Shikalbaha | 235 | 21:00 | 214 | 11:00
| Cumilla(N) | 231 | 20:00 | 221 | 12:00 | Shyampur | 228 | 20:00 | 220 | 15:00
| Fenchuganj | 241 | 08:00 | 236 | 01:00 | Siddhirganj | 232 | 20:00 | 226 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:30 | 226 | 00:00
| GPH | 235 | 20:00 | 212 | 11:00 | Tongi | 234 | 04:00 | 225 | 19:00
| Haripur | 230 | 20:00 | 225 | 00:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 132 | 05:00 | 126 | 12:00 | Lalbag | 138 | 20:00 | 132 | 15:00
| Agargaon | 135 | 05:00 | 129 | 15:00 | Lalmonirhat | 125 | 18:30 | 113 | 00:00
| Agrabad | 139 | 19:30 | 123 | 12:00 | Madanganj | 137 | 19:30 | 130 | 12:00
| AKS | 138 | 19:30 | 122 | 12:00 | Madaripur | 139 | 18:00 | 129 | 22:00
| Aminbazar | 132 | 18:00 | 125 | 12:00 | Madartek | 132 | 05:00 | 125 | 15:00
| Amnura | 135 | 17:00 | 121 | 13:00 | Madunaghat | 140 | 20:00 | 125 | 11:00
| Ashuganj | 138 | 18:30 | 130 | 00:00 | Magura | 140 | 18:00 | 126 | 21:00
| Bagerhat | 135 | 18:00 | 122 | 01:00 | Mahasthangarh | 130 | 18:00 | 119 | 22:00
| Bakulia | 138 | 20:00 | 123 | 11:00 | Manikganj | 136 | 18:30 | 128 | 09:00
| Banani | 136 | 04:00 | 129 | 15:00 | Maniknagar | 132 | 03:00 | 128 | 12:00
| Bangabhaban | 132 | 18:00 | 128 | 12:00 | Matarbari | 126 | 20:00 | 111 | 11:00
| Barapukuria | 133 | 18:30 | 124 | 00:00 | Matuail | 136 | 20:00 | 132 | 12:00
| Barguna | 137 | 18:00 | 128 | 00:00 | Millgate | 137 | 05:00 | 130 | 12:00
| Barishal | 139 | 18:00 | 129 | 00:00 | Mirpur | 133 | 21:00 | 124 | 15:00
| Barishal-230 | 139 | 18:00 | 130 | 00:00 | Mithapukur | 129 | 18:30 | 117 | 01:00
| Baroaulia | 141 | 20:00 | 125 | 11:00 | Modern | 139 | 19:30 | 124 | 11:00
| Baroirhat | 133 | 20:00 | 117 | 01:00 | Mogbazar | 135 | 04:00 | 126 | 15:00
| Bashundhara | 136 | 04:00 | 130 | 12:00 | Mongla | 134 | 18:00 | 123 | 00:00
| BashundharaCement | 137 | 19:30 | 130 | 12:00 | Motijheel | 132 | 18:00 | 128 | 12:00
| Beanibazar | 134 | 03:00 | 123 | 22:00 | Munshiganj | 137 | 19:30 | 131 | 11:00
| Benapole | 137 | 18:00 | 125 | 00:00 | Mymensingh | 131 | 18:30 | 116 | 01:00
| Bhaluka | 130 | 18:30 | 115 | 01:00 | Naogaon | 127 | 18:30 | 110 | 23:00
| Bhandaria | 137 | 18:00 | 125 | 23:00 | Narail | 137 | 08:00 | 124 | 23:00
| Bhangura | 139 | 19:00 | 131 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:00 | 131 | 21:00 | Narshingdi | 138 | 19:30 | 127 | 01:00
| Bheramara(GK) | 140 | 17:00 | 132 | 00:00 | Natore | 134 | 18:30 | 124 | 00:00
| Bhulta | 131 | 20:00 | 126 | 12:00 | Nawabganj | 138 | 20:00 | 133 | 09:00
| Bog-Sherpur | 132 | 18:00 | 122 | 00:00 | Netrakona | 129 | 18:00 | 113 | 02:00
| Bogura | 132 | 18:00 | 122 | 00:00 | New | 136 | 18:00 | 130 | 15:00
| Bogura-230 | 133 | 18:30 | 123 | 00:00 | Niamatpur | 125 | 18:00 | 102 | 23:00
| Brahmanbaria | 133 | 10:00 | 124 | 00:00 | Noapara | 138 | 18:00 | 126 | 22:00
| Cantonment | 134 | 05:00 | 110 | 01:00 | Pabna | 136 | 18:00 | 128 | 00:00
| Chandpur | 137 | 18:00 | 122 | 01:00 | Palashbari | 126 | 18:30 | 114 | 00:00
| Chandraghona | 140 | 20:00 | 124 | 11:00 | Panchagarh | 126 | 19:00 | 106 | 13:00
| Chapai | 135 | 17:00 | 123 | 13:00 | Patuakhali | 136 | 07:00 | 130 | 00:00
| Charsaidpur | 138 | 19:30 | 131 | 13:00 | Payra | 139 | 18:30 | 133 | 00:00
| Chauddagram | 131 | 19:00 | 119 | 00:00 | PHP | 133 | 20:00 | 118 | 00:00
| Chhatak | 132 | 06:00 | 124 | 20:00 | Purbachal | 136 | 06:00 | 129 | 15:00
| Chowmuhani | 128 | 07:00 | 115 | 00:00 | Purbasadipur | 128 | 18:30 | 110 | 07:00
| Chuadanga | 135 | 18:00 | 120 | 00:00 | Rahim | 137 | 20:00 | 134 | 00:00
| Coxsbazar | 126 | 20:00 | 109 | 01:00 | Rajbari | 137 | 18:30 | 127 | 00:00
| Cumilla(N) | 134 | 20:00 | 125 | 01:00 | Rajendrapur | 136 | 18:00 | 128 | 09:00
| Cumilla(S) | 134 | 20:00 | 124 | 00:00 | Rajshahi | 133 | 17:00 | 123 | 00:00
| Daudkandi | 133 | 18:00 | 125 | 12:00 | Rajshahi-230 | 135 | 18:00 | 124 | 00:00
| Dhaka | 132 | 05:00 | 126 | 12:00 | Ramganj | 131 | 18:00 | 118 | 03:00
| Dhamrai | 133 | 05:00 | 127 | 15:00 | Rampur | 136 | 20:00 | 125 | 11:00
| Dhanmondi | 137 | 20:00 | 133 | 11:00 | Rampura | 130 | 05:00 | 126 | 13:00
| Dohazari | 136 | 19:30 | 122 | 11:00 | Rangamati | 138 | 20:00 | 125 | 11:00
| Faridpur | 136 | 18:30 | 127 | 22:00 | Rangpur | 126 | 18:30 | 115 | 00:00
| Fatullah | 136 | 20:00 | 131 | 12:00 | Ruppur | 136 | 09:00 | 130 | 00:00
| Fenchuganj | 137 | 07:00 | 131 | 22:00 | Saidpur | 130 | 19:00 | 112 | 08:00
| Feni | 132 | 20:00 | 121 | 01:00 | Satkhira | 134 | 18:00 | 121 | 22:00
| Ghorashal | 140 | 18:00 | 137 | 15:00 | Satmasjid | 134 | 06:00 | 129 | 15:00
| Goalpara | 138 | 18:00 | 128 | 22:00 | Savar | 134 | 20:00 | 123 | 12:00
| Gollamari | 138 | 18:00 | 128 | 01:00 | Shahjadpur | 140 | 07:00 | 133 | 21:00
| Gopalganj | 140 | 18:00 | 131 | 18:30 | Shahjibazar | 136 | 09:00 | 130 | 00:00
| Gopalganj_I | 141 | 17:00 | 133 | 00:00 | Shahmirpur | 140 | 20:00 | 123 | 11:00
| Gulshan | 131 | 04:00 | 125 | 15:00 | Shariatpur | 138 | 18:00 | 126 | 22:00
| Halishahar | 140 | 20:00 | 124 | 11:00 | Sherpur | 133 | 18:30 | 115 | 01:00
| Haripur | 137 | 20:00 | 134 | 00:00 | Shikalbaha | 142 | 20:00 | 125 | 11:00
| HaripurSBU | 137 | 20:00 | 133 | 12:00 | Shikalbaha-230 | 138 | 19:30 | 126 | 12:00
| Hasnabad | 138 | 19:30 | 133 | 09:00 | Shitalakhya | 139 | 20:00 | 132 | 09:00
| Hathazari | 141 | 20:00 | 125 | 12:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 18:00 | 130 | 21:00 | Shyampur | 134 | 03:00 | 131 | 09:00
| Jaldhaka | 125 | 19:00 | 111 | 14:00 | Shyampur-230 | 135 | 04:00 | 131 | 12:00
| Jamalpur | 135 | 18:30 | 116 | 03:00 | Siddhirganj | 136 | 03:00 | 132 | 12:00
| Jashore | 138 | 18:00 | 126 | 00:00 | Sirajganj | 135 | 18:00 | 125 | 00:00
| Jhenaidah | 140 | 18:00 | 129 | 21:00 | Sonargaon | 138 | 20:00 | 131 | 12:00
| Jhenaidah-230 | 141 | 18:00 | 129 | 19:30 | Sreemongol | 136 | 11:00 | 132 | 00:00
| Joydebpur | 142 | 05:00 | 138 | 15:00 | Srinagar | 137 | 20:00 | 132 | 12:00
| Joypurhat | 125 | 18:00 | 109 | 23:00 | SSM | 142 | 20:00 | 128 | 10:00
| Juldah | 141 | 20:00 | 124 | 11:00 | Sunamganj | 131 | 03:00 | 121 | 22:00
| Kabirpur | 137 | 18:00 | 127 | 15:00 | Sylhet | 133 | 03:00 | 127 | 22:00
| Kachua | 134 | 20:00 | 123 | 00:00 | Tangail | 136 | 18:00 | 127 | 00:00
| Kaliakoir | 139 | 18:00 | 132 | 00:00 | Thakurgaon | 126 | 19:00 | 103 | 13:00
| Kallyanpur | 134 | 20:00 | 125 | 15:00 | TK | 140 | 20:00 | 126 | 11:00
| Kalurghat | 140 | 20:00 | 125 | 12:00 | Tongi | 137 | 18:00 | 132 | 12:00
| Kamrangirchar | 138 | 19:30 | 132 | 14:00 | Ullon | 131 | 05:00 | 126 | 12:00
| Kaptai | 136 | 23:00 | 126 | 13:00 | Uttara | 133 | 20:00 | 124 | 15:00
| Kazla | 132 | 04:00 | 128 | 12:00 | UttaraNew | 136 | 00:00 | 129 | 16:00
| Keranigonj | 137 | 05:00 | 132 | 12:00 | Zigatola | 137 | 06:00 | 132 | 16:00
| Khagrachori | 137 | 20:00 | 124 | 11:00
| Khulna | 137 | 18:00 | 128 | 00:00
| Khulna(S) | 137 | 18:00 | 127 | 23:00
| Khulshi | 138 | 20:00 | 122 | 11:00
| Kishoreganj | 132 | 18:30 | 117 | 01:00
| Kodda | 140 | 17:00 | 130 | 16:00
| KSRM | 138 | 20:00 | 124 | 11:00
| Kulaura | 135 | 08:00 | 131 | 19:30
| Kurigram | 124 | 18:00 | 112 | 01:00
| Kushtia | 138 | 18:00 | 129 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 298 | 8608 | 4800 | 13408 |  |  |  | QF-LDC-11
0:30 | 266 | 8224.5 | 4738 | 12962.5 | Date: | 2022-07-16
1:00 | 234 | 7841 | 4676 | 12517
1:30 | 246 | 7826.5 | 4481 | 12307.5
2:00 | 258 | 7812 | 4286 | 12098
2:30 | 231 | 7783.5 | 4239 | 12022.5 | [5 empty] | Gen. at Eve. Peak | 13538 | 13538 MW (21:00 )
3:00 | 204 | 7755 | 4192 | 11947 | [6 empty] | 21:00
3:30 | 201 | 7734.5 | 4129.5 | 11864 | [5 empty] | Gen. at Day Peak | 11305 | 11305 MW (12:00 )
4:00 | 198 | 7714 | 4067 | 11781 | [6 empty] | 12:00
4:30 | 176 | 7714.5 | 4053 | 11767.5 | [5 empty] | Highest Generation | 13538
5:00 | 154 | 7715 | 4039 | 11754 | [6 empty] | 21:00
5:30 | 162 | 7393 | 3920 | 11313
6:00 | 170 | 7071 | 3801 | 10872
6:30 | 157 | 6979 | 3774 | 10753
7:00 | 144 | 6887 | 3747 | 10634
7:30 | 88 | 6798.5 | 3743.5 | 10542
8:00 | 32 | 6710 | 3740 | 10450
8:30 | 47 | 6749 | 3728.5 | 10477.5
9:00 | 62 | 6788 | 3717 | 10505
9:30 | 118 | 6919.5 | 3729 | 10648.5
10:00 | 174 | 7051 | 3741 | 10792
10:30 | 202 | 7152.5 | 3722.5 | 10875
11:00 | 230 | 7254 | 3704 | 10958
11:30 | 201 | 7307.5 | 3824 | 11131.5
12:00 | 172 | 7361 | 3944 | 11305
12:30 | 102 | 7575 | 4003 | 11578
13:00 | 32 | 7789 | 4062 | 11851
13:30 | 31 | 7935.5 | 3995 | 11930.5
14:00 | 30 | 8082 | 3928 | 12010
14:30 | 31 | 8083.5 | 3994 | 12077.5
15:00 | 32 | 8085 | 4060 | 12145
15:30 | 123 | 8098.5 | 4129 | 12227.5
16:00 | 214 | 8112 | 4198 | 12310
16:30 | 163 | 7920 | 4143 | 12063
17:00 | 112 | 7728 | 4088 | 11816
17:30 | 116 | 7483.5 | 3844.5 | 11328
18:00 | 120 | 7239 | 3601 | 10840
18:30 | 202 | 7477.5 | 3815.5 | 11293
19:00 | 284 | 7716 | 4030 | 11746
19:30 | 742 | 8726 | 4601 | 13327
20:00 | 840 | 8798 | 4697 | 13495 |  |  |  | Executive Engineer
20:30 | 645 | 8779.5 | 4737 | 13516.5 |  |  |  | Network Operation Division
21:00 | 450 | 8761 | 4777 | 13538
21:30 | 378 | 8642 | 4828 | 13470
22:00 | 306 | 8523 | 4879 | 13402 |  |  |  |  | Page 6 of 7
22:30 | 257 | 8561 | 4903.5 | 13464.5
23:00 | 208 | 8599 | 4928 | 13527
23:30 | 253 | 8603.5 | 4864 | 13467.5
24:00 | 298 | 8608 | 4800 | 13408
13538 MW (21:00 )
11305 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-16 |  | Energy |  | 290509484
[13 empty] | 2022-07-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4765 | 864 | 2215 | 0 | 3554 | 1260 | 126 | 0 | 542 | 82 | 0 | 0
0:30 | 4951.5 | 890.5 | 2179.5 | 0 | 3058.5 | 1229 | 125.5 | 0 | 449 | 79 | 0 | 0 | Date: | 2022-07-16
1:00 | 5138 | 917 | 2144 | 0 | 2563 | 1198 | 125 | 0 | 356 | 76 | 0 | 0
1:30 | 5074.5 | 916.5 | 2115.5 | 0 | 2529.5 | 1118 | 124.5 | 0 | 356 | 73 | 0 | 0 | [8 empty] | Total Energy | 290.5095 | Total Energy Gen 290.509 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 290.509 MKWHr
2:00 | 5011 | 916 | 2087 | 0 | 2496 | 1038 | 124 | 0 | 356 | 70 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 5033 | 917 | 2055 | 0 | 2448.5 | 1018 | 123.5 | 0 | 356.5 | 71 | 0 | 0 | [8 empty] | Energy Requirement | 290.5095
3:00 | 5055 | 918 | 2023 | 0 | 2401 | 998 | 123 | 0 | 357 | 72 | 0 | 0
3:30 | 5043.5 | 916.5 | 2022 | 0 | 2383 | 947.5 | 122.5 | 0 | 357 | 72 | 0 | 0 | [6 empty] | Shortage
4:00 | 5032 | 915 | 2021 | 0 | 2365 | 897 | 122 | 0 | 357 | 72 | 0 | 0
4:30 | 5023 | 915.5 | 2019.5 | 0 | 2367.5 | 892 | 122 | 0 | 357 | 71 | 0 | 0
5:00 | 5014 | 916 | 2018 | 0 | 2370 | 887 | 122 | 0 | 357 | 70 | 0 | 0
5:30 | 4954.5 | 916 | 2016 | 0 | 2083 | 882 | 121.5 | 0 | 267.5 | 68 | 4.5 | 0
6:00 | 4895 | 916 | 2014 | 0 | 1796 | 877 | 121 | 0 | 178 | 66 | 9 | 0
6:30 | 4899.5 | 915.5 | 2010 | 0 | 1709 | 877 | 122 | 0 | 129.5 | 64 | 26.5 | 0 |  |  |  |  | Coal
7:00 | 4904 | 915 | 2006 | 0 | 1622 | 877 | 123 | 0 | 81 | 62 | 44 | 0
7:30 | 4847 | 915 | 1969.5 | 0 | 1621.5 | 877.5 | 124 | 0 | 56.5 | 61 | 70 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4790 | 915 | 1933 | 0 | 1621 | 878 | 125 | 0 | 32 | 60 | 96 | 0
8:30 | 4791.5 | 915 | 1932 | 0 | 1641 | 878 | 125.5 | 0 | 32 | 60 | 102.5 | 0
9:00 | 4793 | 915 | 1931 | 0 | 1661 | 878 | 126 | 0 | 32 | 60 | 109 | 0
9:30 | 4848 | 897.5 | 1914.5 | 0 | 1757.5 | 878 | 126 | 0 | 32 | 60 | 135 | 0
10:00 | 4903 | 880 | 1898 | 0 | 1854 | 878 | 126 | 0 | 32 | 60 | 161 | 0
10:30 | 4866 | 880 | 1939 | 0 | 1977 | 878 | 103.5 | 0 | 32 | 60 | 139.5 | 0
11:00 | 4829 | 880 | 1980 | 0 | 2100 | 878 | 81 | 0 | 32 | 60 | 118 | 0
11:30 | 4835.5 | 880 | 2008 | 0 | 2165.5 | 913 | 78 | 0 | 24 | 64 | 163.5 | 0
12:00 | 4842 | 880 | 2036 | 0 | 2231 | 948 | 75 | 0 | 16 | 68 | 209 | 0
12:30 | 4920.5 | 880 | 2068.5 | 0 | 2346.5 | 968 | 76.5 | 0 | 40 | 70 | 208 | 0
13:00 | 4999 | 880 | 2101 | 0 | 2462 | 988 | 78 | 0 | 64 | 72 | 207 | 0
13:30 | 4999 | 880 | 2101 | 0 | 2462 | 988 | 78 | 0 | 64 | 72 | 207 | 0
14:00 | 4999 | 880 | 2101 | 0 | 2462 | 988 | 78 | 0 | 64 | 72 | 207 | 0
14:30 | 4979 | 880 | 2164 | 0 | 2546 | 1012.5 | 78.5 | 0 | 73 | 72 | 193 | 0
15:00 | 4959 | 880 | 2227 | 0 | 2630 | 1037 | 79 | 0 | 82 | 72 | 179 | 0
15:30 | 4962.5 | 880 | 2174 | 0 | 2711.5 | 1067 | 100.5 | 0 | 114 | 72 | 146 | 0
16:00 | 4966 | 880 | 2121 | 0 | 2793 | 1097 | 122 | 0 | 146 | 72 | 113 | 0
16:30 | 4734 | 880.5 | 2061.5 | 0 | 2713.5 | 1092 | 121.5 | 0 | 200.5 | 71 | 72.5 | 0
17:00 | 4734 | 881 | 2002 | 0 | 2634 | 1087 | 121 | 0 | 255 | 70 | 32 | 0
17:30 | 4523 | 880.5 | 1903 | 0 | 2530.5 | 1028 | 121 | 0 | 248 | 68 | 26 | 0
18:00 | 4312 | 880 | 1804 | 0 | 2427 | 969 | 121 | 0 | 241 | 66 | 20 | 0
18:30 | 4364.5 | 872 | 1874.5 | 0 | 2649 | 974 | 121.5 | 0 | 355.5 | 72 | 10 | 0
19:00 | 4417 | 864 | 1945 | 0 | 2871 | 979 | 122 | 0 | 470 | 78 | 0 | 0
19:30 | 4616 | 863 | 2192 | 0 | 3780 | 1150 | 123 | 0 | 525 | 78 | 0 | 0
20:00 | 4626 | 864 | 2147 | 0 | 3935 | 1180 | 123 | 0 | 546 | 74 | 0 | 0
20:30 | 4647.5 | 863.5 | 2179.5 | 0 | 3872.5 | 1200 | 123.5 | 0 | 553 | 77 | 0 | 0
21:00 | 4669 | 863 | 2212 | 0 | 3810 | 1220 | 124 | 0 | 560 | 80 | 0 | 0
21:30 | 4715.5 | 863.5 | 2210 | 0 | 3686.5 | 1230 | 124.5 | 0 | 560 | 80 | 0 | 0
22:00 | 4762 | 864 | 2208 | 0 | 3563 | 1240 | 125 | 0 | 560 | 80 | 0 | 0
22:30 | 4807 | 864 | 2230.5 | 0 | 3558.5 | 1245 | 125.5 | 0 | 557 | 77 | 0 | 0
23:00 | 4852 | 864 | 2253 | 0 | 3554 | 1250 | 126 | 0 | 554 | 74 | 0 | 0
23:30 | 4808.5 | 864 | 2234 | 0 | 3554 | 1255 | 126 | 0 | 548 | 78 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.2° C
24:00 | 4765 | 864 | 2215 | 0 | 3554 | 1260 | 126 | 0 | 542 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 290.509 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 290.509 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 89 | 88 | 87 | 87 | 86 | 88 | 90 | 91 | 91 | 46 | 40 | 43 | 42 | 44 | 87 | 86 | 86 |  | 87 | 88 | 88 | 89 | 90 | 91 | 91 | 1888800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 |  |  |  |  | 2 | 8 | 20 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 469409
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 11 | 11 | 8 | 12 | 13 | 7 | 17 | 15 | 0 | 4 | 0 | [8 empty] | 119880
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 17 | 17 | [12 empty] | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 482245
12 | Hathazari 100 MW peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | [10 empty] | 33 |  |  | 10 | 28 | 25 | 51 | 51 | 51 | 51 | 471288
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 48 | 72 | 87 | 88 | 51 | 51 |  | 53 | 68 | 69 | 70 | 17 | 21 | 87 | 994436
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 40 | 40 | 41 | 41 | 41 | [7 empty] | 48 | 48 | 42 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 740784
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 190 | 190 | 190 | 185 | 188 | 190 | 195 | 185 | 145 | 143 | 97 | 94 | 92 | 95 | 95 | 95 | 0 | [9 empty] | 2642000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 335 | 333 | 327 | 329 | 328 | 250 |  | 259 | 280 | 280 | 335 | 335 | 335 | 335 | 7569721
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 145 | 145 | 145 | 145 | 45 | 15 | 15 | 15 | 117 | 240 | 257 | 260 | 272 | 260 | 260 | 243 | 243 |  | 255 | 255 | 256 | 273 | 273 | 275 | 273 | 4649344
19 | Ashuganj 195MW PP (APSCL-United) | 187 | 187 | 187 | 187 | 185 | 187 | 187 | 185 | 187 | 187 | 187 | 187 | 187 | 187 | 182 | 155 | 155 | 155 |  | 155 | 155 | 155 | 155 | 155 | 158 | 158 | 4248727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 7221864
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 32 | 32 | 32 | 32 | 29 | 29 | 29 | 32 | 32 | 29 | 32 | 34 |  | 32 | 35 | 35 | 36 | 36 | 36 | 36 | 787104
33 | Ashuganj 225 MW CCPP | 138 | 138 | 137 | 137 | 139 | 30 | 34 | 26 | 39 | 105 | 172 | 205 | 205 | 205 | 203 | 204 | 205 | 206 |  | 206 | 205 | 206 | 206 | 207 | 208 | 207 | 3745000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 320 | 310 | 310 | 310 | 310 | 305 | 320 | 305 | 320 | 305 | 305 | 310 | 320 | 300 | 265 | 265 |  | 265 | 265 | 265 | 265 | 265 | 300 | 265 | 7224000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 320 | 310 | 310 | 310 | 310 | 310 | 320 | 325 | 340 | 325 | 325 | 330 | 340 | 315 | 285 | 285 |  | 285 | 285 | 285 | 285 | 280 | 310 | 280 | 7702800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 47 | 47 | 47 | 48 | 48 | 48 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 46 | 44 |  | 43 | 35 | 43 | 44 | 44 | 45 | 45 | 1093920
36 | Chandpur 150 MW CCPP | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 83 |  | 84 | 84 | 84 | 84 | 84 | 85 | 85 | 2008610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 408 | 408 | 408 | 408 | 407 | 407 | 407 | 408 | 409 | 408 | 407 | 407 | 407 | 405 | 400 | 401 | 398 |  | 408 | 408 | 407 | 398 | 405 | 409 | 409 | 9897980
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 330 |  | 300 | 420 | 420 | 450 | 450 | 450 | 450 | 9497800
41 | Haripur 360MW CCPP(HPL) | 328 | 275 | 251 | 251 | 253 | 251 | 252 | 252 | 252 | 252 | 252 | 252 | 300 | 325 | 325 | 308 | 310 | 280 |  | 252 | 300 | 303 | 324 | 332 | 323 | 322 | 6870000
42 | RPCL 210MW CCPP | 205 | 206 | 208 | 208 | 208 | 208 | 207 | 207 | 201 | 202 | 198 | 176 | 152 | 142 | 141 | 141 | 141 | 142 |  | 137 | 137 | 137 | 131 | 131 | 131 | 131 | 4055040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 13 | 28 | 47 | 47 | 43 | 52 | 45 | 39 | 42 | 30 | 15 | 6 |  | 0 | [6 empty] | 393550
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 43 | 42 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 42 | 44 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 973096
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 51 | 51 | 51 | 51 | 51 | 56 | 56 | 60 | 63 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 40 |  | 60 | 55 | 59 | 59 | 59 | 58 | 59 | 1347072
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 75 | 75 | 75 | 78 | 78 | 78 | 60 | 30 | 30 |  | 60 | 60 | 81 | 81 | 81 | 81 | 81 | 1747200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 218 | 220 | 218 | 219 | 219 | 219 | 218 | 219 | 205 | 193 | 206 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 213 | 219 | 220 | 220 | 220 | 5182010
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 25 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 6 | 6 | 6 | 6 | 0 | [10 empty] | 328600
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 231840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 |  | 3 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 5 | 5 | 5 | 8 | 11 | 8 | 196080
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 47 | [12 empty] | 708000
56 | Shahjahanulla 25 MW PP | 23 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 450662
57 | Bibiana-II 341 MW CCPP (Summit) | [8 empty] | 10 | 10 | 10 | 60 | 110 | 200 | 290 | 300 | 265 | 270 |  | 270 | 300 | 285 | 260 | 270 | 300 | 300 | 3281220
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 391 | 400 | 360 | 360 | 388 | 388 | 384 | 390 | 393 | 360 |  | 360 | 390 | 400 | 398 | 400 | 400 | 400 | 9334400
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 2 | 17 | 17 |  |  | 25 | 35 | 55 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 0 | 513979
59 | Tangail Palli Power Gen 22 MW | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 24 | 24 | 24 | 24 | 20 | 24 | 22 | 17 | 3 |  | 22 | 24 | 24 | 15 | 11 | 24 | 24 | 522720
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 462048
61 | Narshingdi 22 MW PP (Doreen) |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 0 | 22 | 22 | [9 empty] | 0 | 22 | 205020
62 | Tangail 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 19 | 19 | 13 | 7 | 3 | 327024
63 | Impoprt (Tripura) | 76 | 70 | 72 | 72 | 70 | 66 | 62 | 60 | 60 | 60 | 60 | 68 | 72 | 74 | 72 | 72 | 70 | 66 |  | 78 | 78 | 74 | 80 | 80 | 74 | 82 | 1695360
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 36 | 11 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 12 | 20 |  | 29 | 23 | 22 | 32 | 32 | 34 | 41 | 534240
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503820
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 |  | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 195120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 |  | 20 | 20 | 20 | 14 | 20 | 20 | 20 | 506380
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 19 | 21 | 21 | 21 | 21 | 377820
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 592600
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 746700
73 | Ghorashal 108MW PP (Regent) | 86 | 82 | 82 | 83 | 80 | 80 | 80 | 80 | 80 | 82 | 86 | 86 | 80 | 86 | 82 | 82 | 86 | 53 |  | 80 | 89 | 89 | 89 | 89 | 86 | 89 | 1939318
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 60 | 114 | 114 | 114 | 114 | 97 | 17 | 835620
| Chowmuhani 113 MW | 20 | 11 | 8 | 9 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 24 | 90 | 111 |  | 110 | 110 | 110 | 111 | 113 | 111 | 46 | 979440
| Manikgonj 162MW PP(MPGL) | [16 empty] | 6 | 17 |  | 39 | 162 | 162 | 162 | 54 | 56 | 154 | 712800
77 | Siddhirganj 100 PP(Dutch Bangla) | 90 | 97 | 97 | 97 | 98 | 43 | 7 | 7 | 7 | 26 | 50 | 52 | 82 | 88 | 89 | 88 | 88 | 66 |  | 63 | 75 | 96 | 98 | 98 | 98 | 94 | 1742256
78 | Gazipur 52 MW PP | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 17 | 33 | 33 | 33 | 33 | 33 | 36 | 41 | 34 |  | 38 | 49 | 49 | 49 | 49 | 49 | 49 | 762720
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 98 | 64 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 48 | 62 | 62 |  | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 1883040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 207336
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 88 | 70 |  | 75 | 105 | 105 | 105 | 105 | 105 | 105 | 2404800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 4 | 5 | 5 | 5 | 2 | 2 | 3 | 3 | 1 | [9 empty] | 30840
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 43 | 35 |  | 39 | 54 | 54 | 54 | 54 | 54 | 39 | 1002850
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 107 | 93 | 99 | 110 | 85 | 68 |  | 74 | 110 | 108 | 110 | 110 | 110 | 110 | 2564279
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 78 | 77 | 76 | 74 | 77 | 77 | 78 | 77 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 71 | 60 |  | 60 | 71 | 73 | 80 | 76 | 73 | 70 | 1753920
| Meghnaghat 104 MW PP (OPCL) | 72 | 104 | 104 | 104 | 104 | 30 | 17 | 17 | 17 | 41 | 50 | 52 | 72 | 89 | 91 | 90 | 75 | 72 |  | 82 | 104 | 104 | 104 | 104 | 104 | 104 | 1901760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 0 | [5 empty] | 10 | 10 | 40 | 40 | 55 | 55 | 55 | 55 | 10 | 10 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 760320
92 | Fenchuganj 44MW (Energyprima) | 47 | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 48 | 48 | 48 | 47 | 47 | 46 | [12 empty] | 670752
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 30 | 30 | 30 |  | 39 | 51 | 51 | 51 | 51 | 51 | 51 | 1118251
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 84 | 93 | 93 | 84 | 84 | 84 | 93 | 48 | 48 |  | 64 | 93 | 93 | 93 | 93 | 93 | 93 | 1710720
95 | Patenga 50MW PP (Baraka) | 44 | 44 | 44 | 44 | 44 | 44 | 18 | 21 | 36 | 37 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 19 |  | 20 | 35 | 37 | 37 | 37 | 37 | 37 | 830880
96 | Chattogram 108 MW PP (ECPV) | 11 | 11 | 11 | 11 | 11 | [6 empty] | 30 | 48 | 72 | 70 | 72 | 60 | 51 |  | 63 | 80 | 80 | 80 | 39 | 32 | 73 | 834240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 25 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 923105
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 298707
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1990963
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | [9 empty] | 15650
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | [10 empty] | 17 | 17 | 35 | 17 | 17 |  | 17 | 54 | 54 | 35 | 17 | 17 | 35 | 340200
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 115 | 115 | 116 | 116 | 116 | 116 | 116 | 114 | 114 | 115 | 115 | 113 | 113 | 114 | 114 | 122 | 124 | 160 |  | 174 | 175 | 170 | 167 | 167 | 167 | 117 | 3057600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 130 | 130 | 130 | 130 | 118 | 70 | 70 | 70 | 70 | 70 | 70 | 104 | 132 | 132 | 132 | 120 | 105 |  | 110 | 130 | 130 | 122 | 114 | 114 | 123 | 2667168
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 60 | 76 | 76 | 76 | 76 | 50 | 30 |  | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 1252800
116 | Chandpur 200MW (Desh energy) | 139 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 120 | 120 | 120 | 147 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3474240
117 | Ashuganj 150MW PP (Midland) | 113 | 125 | 130 | 130 | 131 | 20 | 20 | 20 | 40 | 50 | 60 | 60 | 76 | 80 | 40 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1493745
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 403 | 402 | 402 | 401 | 354 | 353 | 403 | 365 | 366 | 404 | 405 | 402 | 405 | 406 | 366 |  | 398 | 405 | 404 | 404 | 404 | 403 | 401 | 9459000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 104 |  | 104 | 104 | 104 | 105 | 105 | 105 | 59 | 1676400
| Anwara 300 MW PP (United) | 0 | [10 empty] | 15 | 60 | 60 | 60 | 150 | 80 | 50 |  | 50 | 170 | 190 | 50 | 15 | 15 | 220 | 1038764
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 40 |  | 50 | 90 | 100 | 100 | 100 | 100 | 100 | 2233920
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 68 |  | 74 | 108 | 108 | 108 | 108 | 108 | 108 | 2541709
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 879840
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 4 | 24 |  | 34 | 35 | 35 | 32 | 22 | 18 | 4 | 3 | [8 empty] | 237661
| Chandpur 115(Doreen) | 65 | 82 | 96 | 95 | 96 | 96 | 95 | 95 | 95 | 94 | 82 | 93 | 95 | 94 | 94 | 95 | 94 | 95 |  | 95 | 95 | 94 | 95 | 96 | 95 | 95 | 2225280
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 42 | 55 | 55 | 55 | 49 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 |  | 38 | 55 | 55 | 55 | 55 | 55 | 55 | 1297440
120 | Eastern Zone Total | 7841 | 7812 | 7755 | 7714 | 7715 | 7071 | 6887 | 6710 | 6788 | 7051 | 7254 | 7361 | 7789 | 8082 | 8085 | 8112 | 7728 | 7239 |  | 7716 | 8726 | 8798 | 8761 | 8523 | 8599 | 8608 | 187509547
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 64 | 83 | 80 | 80 | 83 | 81 | 83 | 736320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 42 | 40 | 49 | 38 | 38 | 38 | 33 | 204000
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 70 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 35 |  | 35 | 50 | 94 | 94 | 94 | 94 | 94 | 1106880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 17 | 49 | 17 | 94 | 15 | 93 | 106 | 28 | 86 | 55 | 4 | 10 | [8 empty] | 562320
131
132 | United Payra Power Ltd. | [19 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 97200
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 224 | 184 | 183 | 183 | 183 | 183 | 183 | 183 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 160 |  | 220 | 223 | 223 | 224 | 225 | 220 | 221 | 4934755
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 470304
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 87 | 87 | 87 | 87 | 87 | 86 | 85 | 86 | 86 | 86 | 86 | 87 | 87 | 86 | 86 |  |  |  | 20 | 20 | 20 | 89 | 87 | 88 | 1827910
140 | Bhola 33 MW PP (Venture) | 31 | 28 | 28 | 25 | 25 | 22 | 19 | 17 | 16 | 17 | 17 | 17 | 19 | 18 | 21 | 20 | 18 | 17 |  | 21 | 22 | 21 | 24 | 36 | 36 | 37 | 540600
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 34875
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 28 | 29 | 30 | 30 | 30 | 30 | 30 | 157568
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 25 | [9 empty] | 13 | 67 | 67 | 67 | 88 | 88 | 32 |  | 15 | 67 | 105 | 105 | 105 | 105 | 105 | 1117728
146 | Bheramara HVDC | 917 | 916 | 918 | 915 | 916 | 916 | 915 | 915 | 915 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 881 | 880 |  | 864 | 863 | 864 | 863 | 864 | 864 | 864 | 21502545
147 | Bheramara 410 MW CCPP | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 320 | 320 | 350 | 350 | 350 | 360 | 355 | 250 |  | 300 | 356 | 355 | 355 | 355 | 390 | 355 | 8651232
148 | Payra 1320 MW | 1000 | 840 | 800 | 700 | 690 | 680 | 680 | 680 | 680 | 680 | 680 | 750 | 790 | 810 | 840 | 900 | 890 | 770 |  | 780 | 950 | 980 | 1020 | 1040 | 1050 | 1060 | 21678700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 198 | 198 | 198 | 197 | 197 | 197 | 197 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 197 | 197 | 197 | 199 |  | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 4837000
153 | Baghabari 71 MW GTPP | 70 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 65 | 65 | 65 | 1500000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 17 | 20 | 34 | 34 | 34 | 34 | 34 | 156384
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 4 | 1 | 4 | 5 | 5 | 5 | 3 | 1 | 0 | 0 | [8 empty] | 33900
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 198 | 196 | 173 | 159 | 191 | 162 | 149 |  | 152 | 172 | 173 | 167 | 166 | 156 | 161 | 4577936
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 179 | 158 | 163 | 164 | 158 | 157 | 157 | 161 | 165 | 170 | 166 | 169 | 197 | 188 | 169 | 192 | 172 | 152 |  | 145 | 168 | 164 | 165 | 171 | 171 | 173 | 4253609
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 165 | 169 | 168 | 155 | 155 | 155 | 158 | 162 | 167 | 164 | 198 | 191 | 172 | 173 | 194 | 174 | 140 |  | 143 | 163 | 163 | 171 | 174 | 176 | 176 | 4313300
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 370 | 370 | 304 | 385 | 409 | 377 | 331 | 398 | 370 | 303 | 307 |  | 367 | 403 | 343 | 367 | 332 | 358 | 319 | 9049454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 21 |  | 30 | 33 | 31 | 30 | 30 | 23 | 15 | 166504
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 17 | 17 | 17 | 17 | 18 |  | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 462000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 259164
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 0 | [9 empty] | 8 | 24 | 24 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 408688
167 | Katakhali 50 MW Peaking PP | [13 empty] | 14 | 24 | 24 | 24 | 24 |  | 27 | 30 | 32 | 32 | 32 | 32 | 32 | 245213
168 | Santahar 50 MW Peaking PP | 29 | 29 | 29 | 29 | 29 | 29 | 0 | [12 empty] | 27 | 29 | 29 | 29 | 29 | 29 | 28 | 348320
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 16 | 25 | 25 | 43 | 43 | 43 | 314400
170 | Chapainawabganj 100 MW Peaking PP | 87 | 87 | 87 | 87 | 87 | 0 | [9 empty] | 27 | 84 | 83 |  | 86 | 86 | 86 | 86 | 86 | 86 | 88 | 1101923
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 50 |  | 54 | 70 | 90 | 113 | 113 | 113 | 94 | 2311776
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 50 |  | 85 | 113 | 113 | 113 | 113 | 113 | 76 | 1945056
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 93 | 66 | 65 | 65 | 65 | 67 | 67 | 66 | 66 | 65 | 66 | 68 | 59 | 65 | 65 | 65 | 70 | 98 |  | 99 | 99 | 101 | 101 | 101 | 103 | 103 | 1841356
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 0 | 1 | 4 | 4 | 4 | 5 | 7 | 6 | 5 | 3 | 1 | [8 empty] | 42569
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 34 | 0 | [12 empty] | 66 | 113 | 109 | 108 | 108 | 108 | 108 | 1208448
178