## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-19 | Tuesday
|  |  | Date (day): | 2022-07-19 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11812.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12482 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-18 | 2022-07-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 89 | 89 | 89 |  | 19 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 358 | 249 | 270 | 270
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 238 | 152 | 180 | 180 |  | 30 | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 180 | 180 | 180 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 71 | 36 | 50 | 50 |  | 50 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 94 | 32 | 32 | 32 |  | 68 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 88 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 114 | 125 | 125 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 3 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 48 | 48 | 48 |  | 32 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 31 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 50 | 41 | 50 |  | 2
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 274 | 273 | 280 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 300 | 301 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 96 | 97 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 93 | 101 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 148 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3287 | 3120 | 2767 | 2758 | 1656 | 1102
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 38 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 126 | 119 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 0 | 52 |  | 46 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 55 | 31 | 31 | 31 | 69 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 8 | 5 | 10
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 68 | 82 | 82 | 82 |  | 26 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 278 | 278 | 278 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 76 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 96 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1252 | 1315 | 1277 | 1367 | 380 | 597
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 124 | 154 | 154 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 280 | 280 | 280 |  |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 280 | 280 | 280 |  |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 40 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 47 | 47 | 5 | 5 |  | 50 | Engine problem
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 158 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 103 | 132 | 140 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 40 | 49
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Grid problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 120 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 66 | 82 | 60 | 79
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 27 | 32 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 50 | 200 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 115 | 9 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 71 | 95 | 95 | 20 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1717 | 1803 | 1402 | 1614 | 655 | 301
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 92 | 105 | 105 | 105 |  | 97 | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 170 | 116 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 105 | 60 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 367 | 424 | 376.6 | 454 | 0 | 115
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 62 | 40 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 81 | 40 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 290 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1503 | 1550 | 1480 | 1553 | 275 | 518
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 876 | 858 | 890 | 875
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 20 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 42 |  | 12 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 70 | 0 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 240 | 240 | 240 | 170 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40 | 32
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 94 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1372 | 1559 | 1484 | 1481 | 647 | 63
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 30 | 26 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 87 | 87 | 87 | 107 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 840 | 1050 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 226 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 35 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1203 | 1442 | 1466 | 1504 | 107 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 16 | 32 |  | 39 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 187 | 140 | 180 | 190 | 20 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 207 | 211 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 139 | 190 | 210 | 10 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 418 | 414 | 414 | 414
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 30 |  | 20 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 87 | 85 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 1 | 178 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 107 | 94 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 75 | 95
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1200 | 1606 | 1175 | 1348 | 630 | 127
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 82 | 94 | 68 | 94 |  | 19 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 72 | 108 | 109 | 109 |  | 6 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 357 | 402 | 385 | 403 | 199 | 110
|  | Total |  |  |  |  | 22678 | 21396 | 12258 | 13221 | 11812.6 | 12482 | 4549 | 2943
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 12678.0875 | 13674.09 | 12217.4235 | 12909.7641
| A. |  | 2022-07-18 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13281 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11150 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14006 | MW
| 3 | Day peak Generation : |  |  | 12258 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13674.09 | MW
| 4 | Evening peak Generation : |  |  | 13221 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 785 | MW
| 5 | Total Energy Generation : |  | 299.9752 | MKWHr | By Solar | 1.3884 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 138.8155 | MKWHr |  | By Oil: | 104.0526 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 29.7982 | MKWHr |  | By Hydro: | 2.7622 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4549 | MW | Dhaka | 4902.21 | 4804.21 |  | 98
|  |  |  | For Plants S/D or M/C prob = |  |  | 2943 | MW | Chittagong | 1220 | 1120 |  | 100 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7492 | MW | Khulna | 1660 | 1660 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 981.81 | MMCFD |  |  | Rajshahi | 1506 | 1506 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 155986592.032 | ii) Oil : | Taka | 1483934510.27 | Comilla | 1312 | 1222 |  | 90 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 250313674 | Total | Taka | 1890234776.302 | Mymensingh | 1195 | 902 |  | 293 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 490 | 470 |  | 20 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 382 | MW (E to W) at | 21:00 | hrs | Barisal | 386.88 | 386.88 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 212 | MW at | 1:00 | hrs | Rangpur | 1002 | 818 |  | 184 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 13674.09 | 12889.09 |  | 785
| B. |  | 2022-07-19 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 2556.1938 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12482 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12100 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 325.2498 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10633 | MW at | 8:00 | 831 | 264 | 356 | 324 | 272 | 230 | 98 | 0.19385 | 181
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3775 | MKWHr. | ii) HVDC Flow at Peak Time |  | 858 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7808 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.41 |  | (b) Today: | 91.93 |  | (c) Rule Curve: |  | 86.88
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 367 | 240 |  | 0 | 225 | 0 | 86 | 0 | 55 | 0 | 0 | 0 | 98 | 93 | 128 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 55 | 74 | 37 | 19 | 30 | 0 | 0 | 0 | 310 | 305 | 212 | 187 | 0 | 39 | 48 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 84 | 106 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 200 | 273 | 50 | 98 | 116 | 102 | 142 | 0 | 90 | 140 | 80 | 403 | 59 | 105 | 105 | 0 | 278 | 36 | 110 | 17 | 12 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 909 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 38 | 60 | 40 | 87 | 35 | 32 | 0 | 0 | 0 | 34 | 19 | 89 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 192 | 0 | 0 | 216 | 0 | 0 | 203 | 0 | 414 | 94 | 0 | 70 | 67 | 96 | 0 | 0 | 55 | 1060 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8377 | 4857 | 13234 | 4174 | 909 | 1948 | 450 | 3490 | 1257 | 128 | 216 | 794 | 84 | 0 | 0 | 91.41
2:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 375 | 252 |  | 0 | 225 | 0 | 86 | 0 | 55 | 0 | 0 | 0 | 98 | 93 | 128 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 42 | 51 | 55 | 74 | 38 | 19 | 30 | 0 | 0 | 0 | 335 | 330 | 210 | 187 | 0 | 39 | 48 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 80 | 106 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 50 | 0 | 220 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 273 | 20 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 10 | 403 | 59 | 105 | 105 | 0 | 278 | 36 | 110 | 17 | 0 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 911 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 88 | 34 | 32 | 0 | 0 | 0 | 34 | 15 | 89 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 196 | 0 | 0 | 216 | 0 | 0 | 203 | 0 | 414 | 94 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 1060 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8081 | 4785 | 12866 | 4227 | 911 | 1938 | 220 | 3422 | 1257 | 128 | 216 | 683 | 80 | 0 | 0 | 91.41
3:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 383 | 262 |  | 0 | 225 | 0 | 86 | 0 | 55 | 0 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 42 | 51 | 55 | 74 | 38 | 19 | 31 | 0 | 0 | 0 | 325 | 320 | 211 | 187 | 0 | 38 | 48 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 78 | 107 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 140 | 273 | 0 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 10 | 403 | 59 | 105 | 105 | 0 | 190 | 36 | 110 | 17 | 0 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 910 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 29 | 32 | 0 | 0 | 0 | 34 | 15 | 89 | 0 | 34 | 32 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 197 | 0 | 0 | 200 | 0 | 0 | 211 | 0 | 0 | 203 | 0 | 414 | 35 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 1040 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7883 | 4698 | 12581 | 4217 | 910 | 1934 | 140 | 3255 | 1237 | 128 | 211 | 682 | 78 | 0 | 0 | 91.41
4:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 393 | 266 |  | 0 | 225 | 0 | 85 | 0 | 55 | 0 | 0 | 0 | 98 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 42 | 51 | 55 | 74 | 38 | 19 | 31 | 0 | 0 | 0 | 310 | 305 | 212 | 187 | 0 | 38 | 47 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 76 | 107 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 140 | 273 | 0 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 10 | 402 | 59 | 105 | 105 | 0 | 130 | 36 | 110 | 17 | 0 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 910 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 28 | 32 | 0 | 0 | 0 | 25 | 12 | 89 | 0 | 34 | 32 | 8 | 29 | 21 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 205 | 0 | 0 | 168 | 0 | 0 | 203 | 0 | 414 | 35 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 1010 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7803 | 4637 | 12440 | 4222 | 910 | 1935 | 140 | 3194 | 1208 | 128 | 168 | 627 | 76 | 0 | 0 | 91.41
5:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 394 | 267 |  | 0 | 225 | 0 | 85 | 0 | 30 | 0 | 0 | 0 | 98 | 93 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 42 | 51 | 55 | 74 | 38 | 19 | 40 | 0 | 0 | 0 | 310 | 305 | 211 | 187 | 0 | 38 | 48 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 76 | 107 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 220 | 0 | 0 | 10 | 285 | 0 | 0 | 20 | 273 | 0 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 10 | 401 | 59 | 105 | 105 | 0 | 100 | 36 | 110 | 17 | 1 | 100 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 911 | 0 | 375 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 34 | 32 | 8 | 29 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 208 | 0 | 0 | 130 | 0 | 0 | 203 | 0 | 414 | 35 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 1000 | 221 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7611 | 4554 | 12165 | 4229 | 911 | 1934 | 20 | 3137 | 1198 | 125 | 130 | 535 | 76 | 0 | 0 | 91.41
6:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 395 | 267 |  | 0 | 225 | 0 | 80 | 0 | 30 | 0 | 0 | 0 | 98 | 93 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 22 | 25 | 33 | 24 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 30 | 35 | 38 | 19 | 40 | 0 | 0 | 0 | 310 | 305 | 212 | 187 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 72 | 107 | 0 | 21 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 220 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 273 | 0 | 0 | 117 | 0 | 149 | 1 | 90 | 120 | 10 | 401 | 59 | 105 | 17 | 0 | 0 | 36 | 110 | 17 | 8 | 100 | 400 | 104 | 1 | 35 | 108 | 0 | 35 | 1 | 95 | 55 | 0 |  | 910 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 208 | 0 | 0 | 130 | 0 | 0 | 207 | 0 | 414 | 0 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 950 | 220 | 0 | 17 | 0 | 3 | 72 | 0 | 0 |  | 6942 | 4226 | 11168 | 4240 | 910 | 1927 | 0 | 2580 | 1148 | 124 | 130 | 161 | 72 | 6 | 0 | 91.41
7:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 396 | 267 |  | 0 | 225 | 0 | 79 | 0 | 30 | 0 | 0 | 0 | 98 | 93 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 33 | 24 | 0 | 89 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 40 | 11 | 38 | 19 | 35 | 0 | 0 | 0 | 345 | 335 | 210 | 187 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 66 | 106 | 0 | 21 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 50 | 0 | 220 | 0 | 0 | 10 | 320 | 0 | 0 | 0 | 273 | 0 | 0 | 117 | 0 | 149 | 5 | 90 | 120 | 18 | 403 | 59 | 105 | 17 | 1 | 0 | 36 | 110 | 17 | 8 | 100 | 400 | 104 | 5 | 35 | 108 | 0 | 35 | 2 | 95 | 55 | 0 |  | 910 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 205 | 0 | 0 | 130 | 0 | 0 | 202 | 0 | 414 | 0 | 0 | 70 | 105 | 82 | 0 | 1 | 55 | 920 | 223 | 0 | 17 | 0 | 36 | 72 | 0 | 0 |  | 7023 | 4181 | 11204 | 4281 | 910 | 1959 | 0 | 2550 | 1118 | 124 | 130 | 146 | 66 | 50 | 0 | 91.42
8:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 380 | 260 |  | 0 | 225 | 0 | 79 | 0 | 55 | 0 | 0 | 0 | 94 | 93 | 50 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 16 | 25 | 33 | 32 | 0 | 89 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 55 | 24 | 38 | 19 | 10 | 0 | 0 | 0 | 325 | 340 | 210 | 158 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 64 | 106 | 0 | 21 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 50 | 0 | 220 | 0 | 0 | 10 | 310 | 0 | 0 | 0 | 264 | 0 | 0 | 116 | 0 | 146 | 10 | 90 | 120 | 36 | 404 | 59 | 105 | 20 | 2 | 30 | 36 | 92 | 17 | 8 | 100 | 400 | 104 | 29 | 50 | 108 | 0 | 35 | 14 | 95 | 55 | 0 |  | 910 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 196 | 0 | 0 | 130 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 70 | 105 | 82 | 0 | 1 | 55 | 860 | 223 | 0 | 17 | 2 | 52 | 72 | 0 | 0 |  | 7102 | 4048 | 11150 | 4169 | 910 | 1886 | 0 | 2649 | 1058 | 124 | 130 | 180 | 64 | 110 | 0 | 91.43
9:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 369 | 243 |  | 0 | 225 | 0 | 73 | 0 | 55 | 0 | 0 | 0 | 94 | 93 | 114 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 16 | 25 | 33 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 55 | 66 | 38 | 19 | 2 | 0 | 0 | 0 | 310 | 305 | 211 | 158 | 0 | 36 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 64 | 97 | 0 | 21 | 0 | 44 | 42 | 0 | 0 | 0 | 0 | 62 | 50 | 0 | 220 | 0 | 0 | 8 | 300 | 0 | 0 | 0 | 262 | 0 | 97 | 116 | 0 | 139 | 15 | 90 | 120 | 76 | 403 | 59 | 105 | 77 | 2 | 110 | 36 | 92 | 17 | 8 | 100 | 400 | 104 | 24 | 144 | 108 | 0 | 35 | 27 | 95 | 55 | 0 |  | 911 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 186 | 0 | 0 | 150 | 0 | 0 | 191 | 0 | 418 | 0 | 0 | 70 | 105 | 82 | 0 | 2 | 55 | 840 | 222 | 0 | 17 | 3 | 49 | 72 | 0 | 0 |  | 7520 | 4063 | 11583 | 4076 | 911 | 1854 | 97 | 3030 | 1039 | 126 | 150 | 264 | 64 | 122 | 0 | 91.43
10:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 358 | 238 |  | 0 | 225 | 0 | 71 | 0 | 55 | 0 | 0 | 0 | 94 | 93 | 114 | 0 | 0 | 0 | 0 | 17 | 0 | 3 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 68 | 38 | 19 | 2 | 0 | 0 | 0 | 320 | 315 | 208 | 158 | 0 | 37 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 27 | 20 | 66 | 92 | 0 | 21 | 2 | 44 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 8 | 300 | 8 | 0 | 50 | 274 | 300 | 96 | 115 | 93 | 148 | 20 | 76 | 120 | 103 | 403 | 59 | 105 | 105 | 4 | 278 | 36 | 92 | 17 | 8 | 100 | 400 | 104 | 54 | 144 | 108 | 0 | 35 | 22 | 95 | 0 | 0 |  | 876 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 207 | 0 | 0 | 188 | 0 | 418 | 0 | 1 | 70 | 105 | 82 | 0 | 3 | 55 | 840 | 222 | 0 | 17 | 4 | 95 | 72 | 0 | 0 |  | 8126 | 4132 | 12258 | 4080 | 876 | 1815 | 540 | 3190 | 1040 | 126 | 207 | 321 | 66 | 204 | 0 | 91.42
11:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 370 | 248 |  | 0 | 225 | 0 | 66 | 0 | 55 | 0 | 0 | 0 | 87 | 84 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 19 | 25 | 21 | 25 | 33 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 33 | 64 | 38 | 19 | 2 | 0 | 0 | 0 | 345 | 330 | 206 | 158 | 0 | 38 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 23 | 17 | 66 | 80 | 0 | 21 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 54 | 20 | 0 | 220 | 0 | 0 | 8 | 300 | 8 | 0 | 50 | 273 | 298 | 50 | 115 | 50 | 135 | 19 | 76 | 120 | 107 | 400 | 58 | 90 | 105 | 4 | 278 | 36 | 72 | 17 | 8 | 100 | 388 | 104 | 35 | 144 | 90 | 0 | 35 | 32 | 94 | 0 | 0 |  | 877 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 213 | 0 | 0 | 183 | 0 | 416 | 0 | 0 | 70 | 88 | 78 | 0 | 4 | 55 | 840 | 220 | 0 | 17 | 3 | 51 | 52 | 0 | 0 |  | 7996 | 4051 | 12047 | 4095 | 877 | 1821 | 448 | 3087 | 1039 | 127 | 213 | 338 | 66 | 149 | 0 | 91.41
12:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 330 | 239 |  | 0 | 225 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 88 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 19 | 25 | 21 | 25 | 33 | 43 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 33 | 64 | 38 | 19 | 2 | 0 | 0 | 0 | 345 | 330 | 206 | 128 | 0 | 37 | 45 | 0 | 51 | 0 | 43 | 8 | 22 | 10 | 21 | 20 | 70 | 80 | 0 | 21 | 2 | 42 | 42 | 0 | 0 | 0 | 0 | 57 | 20 | 0 | 220 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 273 | 150 | 92 | 114 | 0 | 135 | 18 | 76 | 120 | 110 | 402 | 58 | 90 | 105 | 6 | 278 | 36 | 72 | 17 | 8 | 100 | 386 | 104 | 39 | 144 | 106 | 0 | 35 | 17 | 94 | 32 | 0 |  | 876 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 185 | 0 | 0 | 210 | 0 | 0 | 182 | 0 | 414 | 0 | 0 | 70 | 105 | 81 | 0 | 6 | 55 | 870 | 218 | 0 | 17 | 5 | 105 | 34 | 0 | 0 |  | 7825 | 4071 | 11896 | 4008 | 876 | 1786 | 242 | 3141 | 1069 | 128 | 210 | 378 | 70 | 198 | 0 | 91.42
13:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 309 | 217 |  | 0 | 225 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 88 | 84 | 125 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 21 | 25 | 30 | 49 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 31 | 72 | 38 | 19 | 7 | 0 | 0 | 0 | 310 | 305 | 204 | 124 | 0 | 37 | 45 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 25 | 20 | 76 | 68 | 0 | 21 | 3 | 42 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 270 | 250 | 94 | 115 | 100 | 135 | 18 | 76 | 120 | 112 | 403 | 59 | 105 | 105 | 4 | 278 | 36 | 72 | 17 | 8 | 100 | 394 | 104 | 50 | 144 | 108 | 0 | 35 | 35 | 94 | 55 | 0 |  | 874 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 86 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 175 | 0 | 0 | 209 | 0 | 0 | 165 | 0 | 414 | 17 | 0 | 70 | 105 | 81 | 0 | 7 | 55 | 920 | 218 | 0 | 17 | 3 | 79 | 34 | 0 | 0 |  | 8026 | 4100 | 12126 | 3859 | 874 | 1771 | 444 | 3267 | 1119 | 128 | 209 | 389 | 76 | 199 | 0 | 91.42
14:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 297 | 207 |  | 0 | 215 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 88 | 93 | 125 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 21 | 25 | 30 | 49 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 32 | 73 | 38 | 19 | 2 | 0 | 0 | 0 | 310 | 305 | 206 | 108 | 0 | 37 | 45 | 0 | 51 | 0 | 49 | 8 | 22 | 10 | 23 | 20 | 80 | 68 | 0 | 21 | 2 | 42 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 273 | 305 | 92 | 115 | 101 | 143 | 14 | 90 | 120 | 115 | 404 | 59 | 98 | 105 | 4 | 278 | 36 | 75 | 17 | 8 | 100 | 388 | 104 | 24 | 144 | 108 | 0 | 35 | 5 | 94 | 55 | 0 |  | 875 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 88 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 169 | 0 | 0 | 211 | 0 | 0 | 154 | 0 | 415 | 84 | 0 | 70 | 105 | 80 | 0 | 7 | 55 | 940 | 218 | 0 | 17 | 5 | 101 | 34 | 0 | 0 |  | 7980 | 4270 | 12250 | 3827 | 875 | 1708 | 498 | 3390 | 1139 | 128 | 211 | 443 | 80 | 162 | 0 | 91.38
15:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 286 | 192 |  | 0 | 210 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 87 | 93 | 125 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 21 | 25 | 30 | 49 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 31 | 73 | 38 | 19 | 3 | 0 | 0 | 0 | 315 | 310 | 207 | 108 | 0 | 34 | 44 | 0 | 51 | 0 | 49 | 8 | 22 | 10 | 25 | 20 | 78 | 70 | 0 | 21 | 2 | 42 | 42 | 0 | 0 | 0 | 0 | 55 | 20 | 0 | 220 | 0 | 0 | 10 | 295 | 8 | 0 | 200 | 273 | 270 | 92 | 114 | 100 | 149 | 9 | 63 | 120 | 113 | 404 | 58 | 90 | 105 | 0 | 278 | 36 | 92 | 17 | 8 | 83 | 397 | 104 | 30 | 144 | 108 | 0 | 35 | 14 | 81 | 55 | 0 |  | 875 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 85 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 209 | 0 | 0 | 149 | 0 | 414 | 93 | 79 | 70 | 105 | 80 | 0 | 6 | 55 | 960 | 220 | 0 | 17 | 2 | 40 | 34 | 0 | 0 |  | 8063 | 4347 | 12410 | 3848 | 875 | 1692 | 741 | 3344 | 1160 | 128 | 209 | 441 | 78 | 103 | 0 | 91.39
16:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 276 | 177 |  | 0 | 205 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 80 | 93 | 125 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 21 | 25 | 30 | 48 | 0 | 33 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 31 | 76 | 37 | 19 | 4 | 0 | 0 | 0 | 320 | 310 | 207 | 108 | 0 | 36 | 43 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 30 | 20 | 74 | 70 | 0 | 21 | 1 | 42 | 42 | 0 | 0 | 0 | 0 | 55 | 20 | 0 | 220 | 0 | 0 | 10 | 305 | 8 | 0 | 200 | 273 | 271 | 96 | 114 | 100 | 149 | 8 | 90 | 120 | 118 | 404 | 58 | 90 | 81 | 0 | 278 | 36 | 92 | 17 | 30 | 70 | 395 | 104 | 3 | 144 | 108 | 0 | 35 | 6 | 72 | 55 | 0 |  | 875 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 9 | 20 | 40 | 87 | 23 | 32 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 34 | 16 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 159 | 0 | 0 | 211 | 0 | 0 | 149 | 0 | 414 | 93 | 173 | 70 | 105 | 81 | 0 | 4 | 55 | 960 | 225 | 0 | 17 | 1 | 17 | 0 | 0 | 0 |  | 7921 | 4422 | 12343 | 3860 | 875 | 1690 | 840 | 3259 | 1160 | 68 | 211 | 477 | 74 | 40 | 0 | 91.39
17:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 265 | 169 |  | 0 | 200 | 0 | 71 | 0 | 55 | 0 | 0 | 0 | 39 | 93 | 125 | 0 | 0 | 0 | 0 | 35 | 9 | 0 | 19 | 25 | 21 | 25 | 30 | 48 | 0 | 40 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 31 | 76 | 38 | 19 | 12 | 0 | 0 | 0 | 310 | 305 | 210 | 108 | 0 | 36 | 43 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 30 | 20 | 72 | 81 | 0 | 21 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 55 | 20 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 150 | 273 | 250 | 93 | 114 | 99 | 149 | 4 | 90 | 148 | 122 | 403 | 58 | 96 | 105 | 0 | 278 | 36 | 92 | 0 | 107 | 77 | 400 | 104 | 15 | 144 | 108 | 0 | 35 | 7 | 72 | 55 | 0 |  | 875 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 34 | 30 | 40 | 87 | 23 | 32 | 0 | 0 | 0 | 9 | 29 | 42 | 0 | 34 | 25 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 153 | 0 | 0 | 212 | 0 | 0 | 146 | 0 | 414 | 93 | 145 | 113 | 50 | 94 | 0 | 2 | 95 | 940 | 222 | 0 | 17 | 2 | 12 | 34 | 0 | 0 |  | 7915 | 4504 | 12419 | 3839 | 875 | 1673 | 737 | 3412 | 1140 | 75 | 212 | 554 | 72 | 42 | 0 | 91.4
18:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 257 | 153 |  | 0 | 190 | 0 | 48 | 0 | 55 | 0 | 0 | 0 | 30 | 93 | 125 | 0 | 0 | 0 | 0 | 35 | 53 | 0 | 19 | 25 | 21 | 25 | 30 | 48 | 0 | 40 | 35 | 100 | 0 | 1 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 31 | 81 | 38 | 19 | 10 | 0 | 0 | 0 | 290 | 290 | 211 | 108 | 0 | 37 | 45 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 23 | 20 | 64 | 81 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 61 | 20 | 0 | 220 | 0 | 0 | 10 | 275 | 8 | 0 | 0 | 273 | 0 | 0 | 160 | 0 | 149 | 1 | 90 | 183 | 125 | 381 | 95 | 105 | 105 | 0 | 278 | 36 | 92 | 0 | 113 | 76 | 390 | 104 | 4 | 147 | 108 | 0 | 35 | 2 | 72 | 55 | 0 |  | 874 | 0 | 250 | 0 | 17 | 0 | 0 | 0 | 34 | 25 | 40 | 87 | 22 | 32 | 0 | 0 | 0 | 19 | 28 | 84 | 0 | 34 | 32 | 8 | 15 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 0 | 206 | 0 | 0 | 143 | 0 | 355 | 93 | 0 | 113 | 32 | 94 | 0 | 0 | 95 | 880 | 165 | 0 | 17 | 0 | 9 | 34 | 0 | 0 |  | 7315 | 4213 | 11528 | 3747 | 874 | 1506 | 0 | 3551 | 1079 | 75 | 206 | 616 | 64 | 16 | 0 | 91.4
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 254 | 154 |  | 0 | 180 | 0 | 48 | 0 | 55 | 0 | 0 | 0 | 30 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 53 | 0 | 19 | 25 | 21 | 25 | 30 | 48 | 0 | 40 | 35 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 22 | 10 | 51 | 31 | 81 | 38 | 19 | 20 | 0 | 0 | 0 | 325 | 315 | 192 | 108 | 0 | 37 | 46 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 25 | 20 | 82 | 104 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 102 | 273 | 192 | 93 | 170 | 97 | 149 | 0 | 90 | 200 | 125 | 402 | 105 | 105 | 105 | 0 | 278 | 36 | 92 | 0 | 114 | 76 | 395 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 858 | 0 | 245 | 0 | 20 | 0 | 0 | 0 | 37 | 40 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 30 | 84 | 0 | 34 | 32 | 34 | 28 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 146 | 0 | 0 | 147 | 0 | 0 | 143 | 0 | 414 | 93 | 11 | 113 | 60 | 94 | 0 | 0 | 95 | 880 | 218 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8062 | 4435 | 12497 | 3830 | 858 | 1634 | 495 | 3777 | 1080 | 75 | 147 | 666 | 82 | 0 | 0 | 91.41
19:30 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 249 | 152 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 17 | 25 | 29 | 49 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 23 | 61 | 31 | 81 | 38 | 19 | 16 | 0 | 0 | 0 | 285 | 275 | 138 | 108 | 0 | 38 | 46 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 25 | 20 | 80 | 105 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 63 | 81 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 200 | 273 | 301 | 98 | 170 | 101 | 149 | 0 | 90 | 200 | 132 | 402 | 105 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 114 | 76 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 858 | 0 | 245 | 0 | 22 | 0 | 0 | 0 | 51 | 40 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 30 | 84 | 0 | 34 | 32 | 43 | 28 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 145 | 0 | 0 | 204 | 0 | 88 | 139 | 0 | 414 | 93 | 172 | 113 | 105 | 94 | 0 | 0 | 95 | 1000 | 224 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8267 | 4931 | 13198 | 3691 | 858 | 1715 | 960 | 3859 | 1199 | 75 | 204 | 761 | 80 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 250 | 152 |  | 0 | 180 | 0 | 41 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 21 | 25 | 30 | 48 | 0 | 42 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 31 | 85 | 37 | 19 | 16 | 0 | 0 | 0 | 315 | 315 | 125 | 16 | 0 | 39 | 46 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 25 | 20 | 80 | 105 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 200 | 273 | 302 | 98 | 170 | 100 | 149 | 0 | 90 | 200 | 128 | 403 | 105 | 105 | 105 | 0 | 278 | 36 | 106 | 0 | 115 | 76 | 393 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 72 | 55 | 0 |  | 857 | 0 | 240 | 0 | 23 | 0 | 0 | 0 | 39 | 70 | 40 | 84 | 31 | 32 | 0 | 0 | 0 | 34 | 30 | 87 | 0 | 34 | 32 | 43 | 28 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 208 | 0 | 60 | 139 | 0 | 414 | 93 | 155 | 113 | 105 | 94 | 0 | 0 | 95 | 1000 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8254 | 4900 | 13154 | 3739 | 857 | 1626 | 915 | 3856 | 1200 | 77 | 208 | 804 | 80 | 0 | 0 | 91.4
21:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 249 | 152 |  | 0 | 180 | 0 | 36 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 23 | 25 | 31 | 50 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 31 | 82 | 38 | 19 | 8 | 0 | 0 | 0 | 280 | 280 | 124 | 8 | 0 | 40 | 47 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 32 | 20 | 82 | 105 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 0 | 10 | 295 | 8 | 0 | 200 | 273 | 301 | 97 | 170 | 101 | 149 | 0 | 90 | 200 | 132 | 402 | 105 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 115 | 76 | 400 | 104 | 0 | 162 | 96 | 0 | 35 | 0 | 71 | 55 | 0 |  | 858 | 0 | 240 | 0 | 20 | 0 | 0 | 0 | 39 | 70 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 31 | 87 | 0 | 34 | 32 | 43 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 211 | 0 | 94 | 139 | 0 | 414 | 93 | 178 | 107 | 105 | 94 | 0 | 0 | 95 | 1050 | 226 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8212 | 5009 | 13221 | 3683 | 858 | 1613 | 971 | 3837 | 1250 | 119 | 211 | 808 | 82 | 0 | 0 | 91.41
22:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 249 | 152 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 23 | 25 | 32 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 31 | 82 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 260 | 126 | 8 | 0 | 40 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 82 | 105 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 200 | 273 | 302 | 97 | 179 | 101 | 149 | 0 | 90 | 200 | 138 | 403 | 105 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 115 | 76 | 397 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 858 | 0 | 240 | 0 | 30 | 0 | 0 | 0 | 35 | 63 | 40 | 86 | 34 | 32 | 0 | 0 | 0 | 34 | 30 | 87 | 0 | 34 | 32 | 43 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 136 | 0 | 0 | 212 | 0 | 94 | 137 | 0 | 414 | 93 | 171 | 107 | 105 | 95 | 0 | 0 | 95 | 1090 | 222 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 8246 | 5035 | 13281 | 3658 | 858 | 1619 | 965 | 3882 | 1290 | 125 | 212 | 802 | 82 | 0 | 0 | 91.41
23:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 255 | 155 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 8 | 25 | 32 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 31 | 82 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 260 | 126 | 8 | 0 | 40 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 86 | 106 | 0 | 13 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 0 | 10 | 315 | 8 | 0 | 200 | 273 | 302 | 96 | 180 | 100 | 149 | 0 | 90 | 200 | 140 | 401 | 106 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 113 | 76 | 388 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 96 | 55 | 0 |  | 858 | 0 | 235 | 0 | 16 | 0 | 0 | 0 | 32 | 62 | 40 | 85 | 35 | 32 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 43 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 210 | 0 | 94 | 129 | 0 | 414 | 93 | 169 | 107 | 105 | 95 | 0 | 0 | 95 | 1100 | 222 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 8259 | 5009 | 13268 | 3614 | 858 | 1635 | 961 | 3892 | 1299 | 126 | 210 | 797 | 86 | 0 | 0 | 91.41
24:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 268 | 155 |  | 0 | 180 | 0 | 41 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 31 | 83 | 0 | 19 | 28 | 0 | 0 | 0 | 280 | 260 | 127 | 8 | 0 | 40 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 84 | 107 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 64 | 81 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 160 | 273 | 192 | 97 | 117 | 61 | 149 | 0 | 90 | 200 | 140 | 402 | 59 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 50 | 76 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 857 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 88 | 35 | 32 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 210 | 0 | 60 | 129 | 0 | 420 | 93 | 166 | 70 | 105 | 96 | 0 | 0 | 55 | 1100 | 221 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7824 | 4885 | 12709 | 3677 | 857 | 1617 | 736 | 3516 | 1300 | 127 | 210 | 795 | 84 | 0 | 0 | 91.41
KWH | 0 | 0 | 0 | 4378500 | 7183645 | 2083590 | 0 | 7856130 | 5128000 |  | 0 | 4540000 | 0 | 1609920 | 0 | 1287155 | 0 | 0 | 0 | 1756666 | 2197584 | 2689440 | 0 | 0 | 0 | 0 | 868320 | 330756 | 300289 | 413925 | 600000 | 485460 | 600480 | 757400 | 1066560 | 0 | 1918238 | 844000 | 2300000 | 0 | 528984 | 0 | 0 | 0 | 0 |  | 508320 | 470592 | 547918 | 971400 | 1666560 | 892320 | 448560 | 441600 | 0 | 0 | 0 | 7895500 | 7441000 | 4670000 | 3027636 | 0 | 894096 | 1068960 | 0 | 1184023 | 0 | 847032 | 200501 | 478008 | 238680 | 697300 | 521630 | 1780800 | 2213760 | 0 | 392040 | 13650 | 946000 | 959192 | 0 | 0 | 0 | 0 | 1423776 | 1177920 | 0 | 5274280 | 0 | 0 | 237780 | 7371000 | 137424 | 0 | 2359104 | 6546216 | 3551784 | 1462706 | 3081600 | 1286484 | 3582430 | 118395 | 2038080 | 3475680 | 2206327 | 9602000 | 1669200 | 2464800 | 2320072 | 28561 | 5414618 | 903661 | 2399517 | 285000 | 979440 | 2167680 | 9469400 | 2575680 | 314880 | 3402720 | 2569309 | 0 | 885600 | 193013 | 2108160 | 1239840 | 0 |  | 21377454 | 0 | 6988032 | 0 | 395520 | 0 | 0 | 0 | 3084 | 454656 | 675000 | 2063707 | 618776 | 706560 | 0 | 0 | 0 | 353328 | 299203 | 1254240 | 0 | 691952 | 434420 | 350606 | 342036 | 447840 | 0 | 264276 | 0 | 0 | 4883900 | 0 | 0 | 4405991 | 0 | 0 | 4781509 | 0 | 449280 | 4338882 | 0 | 9880800 | 1387200 | 1403146 | 2068896 | 2340288 | 2085139 | 0 | 34959 | 1607040 | 24914300 | 5268464 | 0 | 445200 | 33360 | 651600 | 1808256 | 0 | 0 |  | 189466257 | 110508900 | 299975157 | 96339074 | 21377454 | 42476389 | 10512504 | 81062622 | 29798200 | 2762238 | 4781509 | 7695949 | 1780800 | 1388418 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 8045682.4 | 2771174.7 | 0 | 8248936.5 | 5538240 |  | 0 | 4948600 | 0 | 17998905.6 | 0 | 17054803.75 | 0 | 0 | 0 | 25682456.92 | 30920006.88 | 43595822.4 | 0 | 0 | 0 | 0 | 11045030.4 | 4465206 | 4026875.49 | 310443.75 | 450000 | 0 | 0 | 0 | 18142185.6 | 0 | 517924.26 | 227880 | 4347000 | 0 | 8648888.4 | 0 | 0 | 0 | 0 |  | 6633576 | 7849474.56 | 9325564.36 | 13123614 | 21131980.8 | 10324142.4 | 569671.2 | 1470528 | 0 | 0 | 0 | 8764005 | 8110690 | 5417200 | 3905650.44 | 0 | 1010328.48 | 1592750.4 | 0 | 1977318.41 | 0 | 14628242.64 | 2696738.45 | 654870.96 | 179010 | 1220275 | 391222.5 | 12786144 | 2412998.4 | 0 | 533174.4 | 217581 | 1296020 | 1266133.44 | 0 | 0 | 0 | 0 | 2762125.44 | 2685657.6 | 0 | 5327022.8 | 0 | 0 | 470804.4 | 7371000 | 103068 | 0 | 49446819.84 | 89355848.4 | 74445392.64 | 30234133.02 | 41539968 | 26591624.28 | 49616655.5 | 1384037.55 | 21032985.6 | 47477788.8 | 29277959.29 | 8833840 | 20297472 | 35641008 | 29348910.8 | 0 | 63567615.32 | 9840868.29 | 25506865.71 | 3867450 | 12624981.6 | 25535270.4 | 8711848 | 33355056 | 4550016 | 43180516.8 | 29238736.42 | 0 | 11565936 | 2306505.35 | 31559155.2 | 16328692.8 | 0 |  | 64132362 | 0 | 7826595.84 | 0 | 4117363.2 | 0 | 0 | 0 | 55542.84 | 8183808 | 9699750 | 2311351.84 | 1200425.44 | 7701504 | 0 | 0 | 0 | 5925310.56 | 5233060.47 | 19616313.6 | 0 | 11458725.12 | 7346042.2 | 4778759.78 | 5770147.32 | 927028.8 | 0 | 200056.932 | 0 | 0 | 25835831 | 0 | 0 | 5110949.56 | 0 | 0 | 83485147.14 | 0 | 9425894.4 | 5033103.12 | 0 | 9781992 | 18643968 | 29423971.62 | 24475039.68 | 33817161.6 | 26481265.3 | 0 | 386296.95 | 19509465.6 | 224477843 | 5373833.28 | 0 | 3294480 | 377301.6 | 7643268 | 27720564.48 | 0 | 0 |  | 1257982568.74 | 726781524.272 | 1984764093.012 | 105971588.562 | 64132362 | 50015003.47 | 219567835.8 | 1053352198.38 | 250313674 | 745804.26 | 83485147.14 | 127529328.95 | 12786144 | 16865006.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 358 | 238 |  | 0 | 225 | 0 | 71 | 0 | 55 | 0 | 0 | 0 | 94 | 93 | 114 | 0 | 0 | 0 | 0 | 17 | 0 | 3 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 55 | 68 | 38 | 19 | 2 | 0 | 0 | 0 | 320 | 315 | 208 | 158 | 0 | 37 | 47 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 27 | 20 | 66 | 92 | 0 | 21 | 2 | 44 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 8 | 300 | 8 | 0 | 50 | 274 | 300 | 96 | 115 | 93 | 148 | 20 | 76 | 120 | 103 | 403 | 59 | 105 | 105 | 4 | 278 | 36 | 92 | 17 | 8 | 100 | 400 | 104 | 54 | 144 | 108 | 0 | 35 | 22 | 95 | 0 | 0 |  | 876 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 207 | 0 | 0 | 188 | 0 | 418 | 0 | 1 | 70 | 105 | 82 | 0 | 3 | 55 | 840 | 222 | 0 | 17 | 4 | 95 | 72 | 0 | 0 |  | 12258 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 249 | 152 | 0 | 0 | 180 | 0 | 36 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 23 | 25 | 31 | 50 | 0 | 84 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 23 | 51 | 51 | 31 | 82 | 38 | 19 | 8 | 0 | 0 | 0 | 280 | 280 | 124 | 8 | 0 | 40 | 47 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 32 | 20 | 82 | 105 | 0 | 21 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 0 | 10 | 295 | 8 | 0 | 200 | 273 | 301 | 97 | 170 | 101 | 149 | 0 | 90 | 200 | 132 | 402 | 105 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 115 | 76 | 400 | 104 | 0 | 162 | 96 | 0 | 35 | 0 | 71 | 55 | 0 |  | 858 | 0 | 240 | 0 | 20 | 0 | 0 | 0 | 39 | 70 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 31 | 87 | 0 | 34 | 32 | 43 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 211 | 0 | 94 | 139 | 0 | 414 | 93 | 178 | 107 | 105 | 94 | 0 | 0 | 95 | 1050 | 226 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 13221 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 270 | 180 | 0 | 0 | 180 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 51 | 31 | 82 | 38 | 19 | 10 | 0 | 0 | 0 | 280 | 280 | 154 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 79 | 105 | 0 | 22 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 280 | 0 | 0 | 200 | 0 | 149 | 0 | 90 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 285 | 36 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 95 | 55 |  |  | 875 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 42 | 70 | 40 | 87 | 30 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 414 | 93 | 0 | 113 | 105 | 94 | 0 | 0 | 95 | 1100 | 220 |  | 35 |  |  | 109
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 270 | 180 | 0 | 0 | 180 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 32 | 88 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  |  | 31 | 82 | 38 | 19 | 5 | 0 | 0 | 0 | 280 | 280 | 154 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 60 | 105 | 0 | 22 | 1.6 | 30 | 42 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 280 | 0 | 0 | 116 | 0 | 149 | 20 | 90 | 120 | 140 | 400 | 60 | 105 | 105 | 5 | 278 | 36 | 110 | 0 | 9 | 100 | 400 | 104 | 50 | 162 | 108 | 0 | 35 | 30 | 95 | 55 |  |  | 890 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 26 | 16 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 93 | 0 | 94 | 105 | 68 | 0 | 8 | 75 | 1100 | 220 |  | 17 | 6 | 100 | 109
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 260 | 89 | 0 | 303 | 187 | 0 | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 88 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 23 | 25 | 32 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 31 | 82 | 38 | 0 | 4 | 0 | 0 | 0 | 280 | 260 | 154 | 8 | 0 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 29 | 20 | 62 | 106 | 0 | 22 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 219 | 0 | 0 | 10 | 255 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 8 | 76 | 120 | 128 | 361 | 59 | 105 | 87 | 3 | 278 | 36 | 110 | 0 | 8 | 64 | 350 | 104 | 21 | 162 | 108 | 0 | 35 | 15 | 95 | 55 | 0 | 0 | 909 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 330 | 93 | 0 | 70 | 105 | 82 | 0 | 1 | 55 | 850 | 183 | 0 | 17 | 2 | 50 | 109 | 0 | 0 | 0 |  |  |  |  | 104052584 |  | 0
104052584
| Minimum Generation |  | 11150 | 8:00
| Highest Generation |  | 13281 | 22:00
| Day Peak Generation |  | 12258 | 10:00
| Evening Peak Generation |  | 13221 | 21:00
| HVDC Max Flow |  | 911 | 2:00
| HVDC EvPeak Flow |  | 858 | 21:00
| Load factor L.F |  | 94.11% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-19
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12258 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 10633 | MW
Evening Peak Generation : |  | 13221 | MW Hour : | 21:00 | Available Max Generation : |  | 12482 | MW
E.P. Demand (at gen end) : |  | 14006 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14400 | MW
Maximum Generation : |  | 13281 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 299.9752 | System Load Factor : | 94.11% | Load Shed : |  | 2556.1938 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 212 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-19
Actual : | 91.93 | Ft.(MSL) , | Rule curve : | 86.88 | Ft.( MSL )
Gas Consumed : | Total = | 981.81 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155986592.032
: |  | Coal : | 250313674 | Oil : | 1483934510.27 | Total : | 1890234776.302
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 98 | 2352:00 | 5249.7833 |  |  | 831 | 7.09%
Chittagong Area | 100 | 2400:00 | 1461.5403 |  |  | 264 | 19.8%
Khulna Area | 0 | 0:00 | 1922.5405 |  |  | 356 | 24.03%
Rajshahi Area | 0 | 0:00 | 1697.4071 |  |  | 324 | 12.71%
Cumilla Area | 90 | 2160:00 | 1449.1499 |  |  | 272 | 10.45%
Mymensingh Area | 293 | 7032:00 | 1191.8926 |  |  | 230 | 13.51%
Sylhet Area | 20 | 480:00 | 538.2479 |  |  | 98 | 9.847%
Barisal Area | 0 | 0:00 | 435.1938 |  |  | 0.19385 | 0.04456%
Rangpur Area | 184 | 4416:00 | 940.6353 |  |  | 181 | 4.515%
Total | 785 |  | 14886.3908 |  |  | 2556.1938
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chandpur-Chandpur P/P 132 kV Ckt was under shut down from 10:02 to 15:32 for C/M.
b) Amnura 132/33 kV T-1 transformer was switched on at 09:52.
c) Bheramara-Bheramara 400 kV Ckt-3 was under shut down from 10:57 to 20:19 for C/M.
d) Bheramara-Bheramara 400 kV Ckt-4 was under shut down from 10:58 to 21:30 for C/M.
e) Netrokona 132/33 kV T-2 transformer was switched on at 11:16.
f) Ghorasal GIS unit-4 was under shut down from 11:30 to 14:30 for C/M.
g) Gopalganj 132/33 kV T-1 transformer was under shut down from 09:14 to 17:08 for C/M.
h) Fenchuganj STG with GT-2 tripped at
i) Ghorasal 132 kV Bus-2 was under shut down from 00:25(19-07-2022) to 00:40(19-07-2022) due to
breaker of Norsingdi Ckt-2 got locked.
j) Ghorasal-Norsingdi 132 kV Ckt-2 was under shut down from 00:25(19-07-2022) to 00:51(19-07-2022)
from Ghorasal end as breaker at Ghorasal end got locked.
k) Sirajganj unit-2 ST was shut down at 04:11(19-07-2022) due to fuel shortage.
l) Sirajganj unit-2 GT was shut down at 04:34(19-07-2022) due to fuel shortage.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7183645 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 89 | 2083590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 249 | 7856130 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 152 | 5128000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4540000 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 36 | 1609920 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1287155
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 413925 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 32 | 1756666 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2197584 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 868320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 2689440 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 330756
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 300289 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1085460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 600480 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 757400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1066560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 273 | 6546216 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 301 | 3551784
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 97 | 1462706
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 101 | 1286484
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3582430
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2464800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2575680
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3402720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 193013
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1239840
| Dhaka area Total |  |  |  | 5847 | 3120 | 72439493
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 528984
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 118395
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 892320 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 119 | 2762238 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2320072
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 470592 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 547918 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 31 | 971400 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2038080 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448560
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 441600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 1666560 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28561
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 278 | 5414618 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 903661 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2399517 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 76 | 2167680 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 96 | 2569309 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1315 | 28990065
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 124 | 4670000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7895500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7441000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 894096 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1068960 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 3027636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1184023
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 2206327 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 847032
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3475680
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 478008
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 238680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 1780800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 697300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 200501 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 521630 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2359104
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 285000 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 979440
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 885600 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 71 | 2108160 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 1803 | 43244477
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2213760 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 392040
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 3081600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1669200
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 314880
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 508320
| Mymensingh Area Total |  |  |  | 614 | 424 | 8193450
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 946000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 959192 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1423776 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1177920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5274280
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 137424 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7371000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9602000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237780
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9469400
| Sylhet Area Total |  |  |  | 2477 | 1550 | 36598772
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 858 | 21377454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 20 | 395520 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 3084 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 454656 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 240 | 6988032 | FGMO & gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 675000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 94 | 449280 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1387200 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2340288
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 651600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1559 | 34722114
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 706560 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 618776 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2063707 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 24914300 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 226 | 5268464
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 445200 | Transformer O/L
| Barisal Area Total |  |  |  | 1958 | 1442 | 34017007
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 353328 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 299203 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 691952 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 434420 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 140 | 4405991 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 211 | 4781509
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 139 | 4338882 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9880800 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 342036 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 447840
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 264276
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 350606 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1254240 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 178 | 1403146 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 107 | 2068896
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1607040 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33360
| Rajshahi Area Total |  |  |  | 2129 | 1606 | 32957525
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4883900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 94 | 2085139 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34959
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1808256
| Rangpur Area Total |  |  |  | 720 | 402 | 8812254
| Total |  |  |  | 21396 | 13221 | 299975157
| Eastern Grid Total |  |  |  | 14205 | 8212 | 189466257
| Western Grid Total |  |  |  | 7191 | 5009 | 110508900
| National Grid Total |  |  |  | 21396 | 13221 | 299975157
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-18
(a) ENTIRE EASTERN GRID : |  | 8518.21 | MW | (b) ENTIRE WESTERN GRID : |  | 4370.88 | MW
i) Dhaka area |  | 4804.21 | MW | i) Khulna area |  | 1660 | MW
ii) Chittagong area |  | 1120 | MW | ii) Rajshahi area |  | 1506 | MW
iii) Comilla area |  | 1222 | MW | iii) Barisal area |  | 386.88 | MW
iv) Mymensingh area |  | 902 | MW | iv) Rangpur area |  | 818 | MW
v) Sylhet area |  | 470 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12889.09 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 13 | 12:00 | Chowmuhani | 225 | 20:00 | Kaptai | 5 | 19:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 128 | 10:00 | Chuadanga | 111 | 22:00 | Kazla | 82 | 18:30 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 15:00 | Coxsbazar | 114 | 20:00 | Keranigonj | 58 | 21:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 95 | 12:00 | Cumilla(N) | 155 | 22:00 | Khagrachori | 28 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 84 | 15:00 | Cumilla(S) | 174 | 19:00 | Khulna | 92 | 00:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 68 | 21:00 | Daudkandi | 142 | 00:00 | Khulshi | 175 | 14:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 34 | 00:00 | Dhaka | 44 | 11:00 | Kishoreganj | 144 | 06:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 154 | 00:00 | Dhamrai | 120 | 21:00 | Kodda | 294 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 104 | 00:00 | Dhanmondi | 132 | 13:00 | Kulaura | 48 | 00:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 126 | 19:00 | Dohazari | 102 | 22:00 | Kurigram | 66 | 01:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 64 | 15:00 | Faridpur | 152 | 00:00 | Kushtia | 145 | 20:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 24 | 10:00 | Fatullah | 61 | 12:00 | Lalbag | 94 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 59 | 21:00 | Fenchuganj | 49 | 00:00 | Lalmonirhat | 50 | 01:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 125 | 20:00 | Madanganj | 88 | 11:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 116 | 00:00 | GPH | 84 | 15:00 | Madaripur | 109 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 74 | 19:30 | Ghorashal | 67 | 23:00 | Madartek | 82 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 62 | 01:00 | Goalpara | 29 | 21:00 | Madunaghat | 61 | 18:30 | Rajshahi | 132 | 22:00
Baroirhat | 56 | 22:00 | Gollamari | 56 | 21:00 | Magura | 64 | 19:30 | Rajshahi-230 | 26 | 02:00
Bashundhara | 169 | 15:00 | Gopalganj | 98 | 00:00 | Mahasthangarh | 78 | 20:00 | Ramganj | 88 | 19:00
BashundharaCement | 12 | 00:00 | Gulshan | 132 | 12:00 | Manikganj | 88 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 67 | 00:00 | Halishahar | 96 | 11:00 | Maniknagar | 81 | 12:00 | Rangamati | 14 | 19:00
Benapole | 60 | 21:00 | HaripurSBU | 113 | 12:00 | Matarbari | 44 | 19:30 | Rangpur | 105 | 08:00
Bhaluka | 138 | 09:00 | Hasnabad | 81 | 00:00 | Matuail | 54 | 12:00 | Ruppur | 5 | 09:00
Bhandaria | 53 | 23:00 | Hathazari | 98 | 19:00 | Millgate | 58 | 12:00 | SSM | 3 | 05:00
Bhangura | 36 | 19:30 | Ishurdi | 78 | 20:00 | Mirpur | 134.5 | 15:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 63 | 21:00 | Jaldhaka | 68 | 03:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 198 | 17:00 | Jamalpur | 142 | 06:00 | Mithapukur | 34 | 02:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 00:00 | Jashore | 134 | 19:30 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 178 | 22:00 | Jhenaidah | 120 | 00:00 | Mogbazar | 135 | 12:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 01:00 | Joydebpur | 185 | 20:00 | Mongla | 34 | 12:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 170 | 04:00 | Joypurhat | 66 | 22:00 | Motijheel | 40 | 12:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 154 | 15:00 | Juldah | 27 | 00:00 | Munshiganj | 106 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 73 | 00:00 | KSRM | 45.76 | 23:00 | Mymensingh | 209 | 00:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:30 | Kabirpur | 284 | 15:00 | Naogaon | 137 | 20:00 | Shikalbaha | 28 | 19:00
Chapai | 85 | 03:00 | Kachua | 80 | 00:00 | Narail | 47 | 21:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 29 | 16:00 | Kallyanpur | 99 | 00:00 | Narinda | 64 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 45 | 19:00 | Kalurghat | 5 | 09:00 | Narshingdi | 175 | 00:00 | Sholosohor | N/A | N/A
Chhatak | 30 | 23:00 | Kamrangirchar | 51 | 13:00 | Natore | 158 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 403 | 04:00 | 389 | 15:00 | Kaliakoir | 397 | 15:00 | 386 | 11:00
| Bibiana | 407 | 21:00 | 401 | 09:00 | Payra | 421 | 18:00 | 409 | 22:00
| BIPTC | 397 | 04:00 | 385 | 11:00
| Gopalganj_I | 413 | 18:00 | 393 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 04:00 | 218 | 12:00 | Hasnabad | 228 | 00:00 | 220 | 12:00
| AKSML | 239 | 21:00 | 223 | 06:00 | Hathazari | 238 | 21:00 | 226 | 06:00
| Aminbazar | 228 | 04:00 | 219 | 11:00 | Ishurdi | 236 | 18:00 | 224 | 02:00
| Ashuganj | 240 | 00:00 | 235 | 07:00 | Jhenaidah | 232 | 18:00 | 216 | 22:00
| Baghabari | 234 | 18:30 | 225 | 00:00 | Kaliakoir | 228 | 21:00 | 221 | 11:00
| Barapukuria | 222 | 18:00 | 205 | 00:00 | Keranigonj | 227 | 21:00 | 218 | 12:00
| Barishal | 245 | 18:00 | 235 | 23:00 | Khulna(S) | 242 | 18:00 | 223 | 23:00
| Bheramara | 232 | 18:00 | 221 | 02:00 | Maniknagar | 229 | 05:00 | 221 | 12:00
| Bhulta | 233 | 05:00 | 224 | 15:00 | Meghnaghat | 231 | 19:30 | 227 | 03:00
| Bibiana | 236 | 21:00 | 232 | 02:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 18:00 | 222 | 00:00 | Rajshahi | 234 | 18:30 | 218 | 00:00
| Bogura | 227 | 18:30 | 210 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 18:30 | 241 | 23:00 | Rampura | 231 | 00:00 | 222 | 15:00
| BSRM | 236 | 21:00 | 224 | 06:00 | Shikalbaha | 239 | 21:00 | 222 | 07:00
| Cumilla(N) | 230 | 09:00 | 225 | 07:00 | Shyampur | 228 | 21:00 | 219 | 12:00
| Fenchuganj | 237 | 18:30 | 234 | 01:00 | Siddhirganj | 231 | 04:00 | 223 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:30 | 225 | 00:00
| GPH | 238 | 21:00 | 226 | 05:00 | Tongi | 232 | 01:00 | 221 | 15:00
| Haripur | 228 | 00:00 | 222 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 05:00 | 126 | 11:00 | Lalbag | 138 | 01:00 | 130 | 12:00
| Agargaon | 135 | 04:00 | 128 | 12:00 | Lalmonirhat | 127 | 18:30 | 113 | 21:00
| Agrabad | 141 | 21:00 | 131 | 06:00 | Madanganj | 136 | 21:00 | 130 | 11:00
| AKS | 138 | 08:00 | 128 | 05:00 | Madaripur | 138 | 07:00 | 130 | 00:00
| Aminbazar | 133 | 04:00 | 128 | 11:00 | Madartek | 134 | 04:00 | 125 | 12:00
| Amnura | 132 | 18:00 | 119 | 07:00 | Madunaghat | 140 | 21:00 | 132 | 07:00
| Ashuganj | 136 | 09:00 | 135 | 00:00 | Magura | 140 | 18:00 | 127 | 00:00
| Bagerhat | 136 | 18:00 | 122 | 22:00 | Mahasthangarh | 134 | 18:30 | 120 | 00:00
| Bakulia | 141 | 21:00 | 133 | 08:00 | Manikganj | 134 | 04:00 | 130 | 10:00
| Banani | 135 | 03:00 | 125 | 15:00 | Maniknagar | 132 | 03:00 | 124 | 12:00
| Bangabhaban | 132 | 03:00 | 125 | 12:00 | Matarbari | 131 | 11:00 | 118 | 06:00
| Barapukuria | 136 | 18:00 | 123 | 00:00 | Matuail | 134.7 | 02:00 | 128 | 00:00
| Barguna | 138 | 17:00 | 127 | 22:00 | Millgate | 136 | 05:00 | 127 | 12:00
| Barishal | 139 | 18:00 | 126 | 22:00 | Mirpur | 132 | 03:00 | 125 | 11:00
| Barishal-230 | 139 | 18:00 | 131 | 23:00 | Mithapukur | 132 | 18:30 | 114 | 03:00
| Baroaulia | 140 | 21:00 | 131 | 06:00 | Modern | 139 | 18:00 | 132 | 06:00
| Baroirhat | 133 | 12:00 | 122 | 01:00 | Mogbazar | 135 | 01:00 | 125 | 15:00
| Bashundhara | 135 | 03:00 | 125 | 15:00 | Mongla | 136 | 18:00 | 123 | 12:00
| BashundharaCement | 136 | 21:00 | 130 | 11:00 | Motijheel | 132 | 03:00 | 125 | 12:00
| Beanibazar | 129 | 21:00 | 124 | 01:00 | Munshiganj | 137 | 21:00 | 132 | 11:00
| Benapole | 138 | 18:00 | 124 | 23:00 | Mymensingh | 129 | 17:00 | 116 | 07:00
| Bhaluka | 129 | 23:00 | 113 | 08:00 | Naogaon | 129 | 18:30 | 114 | 00:00
| Bhandaria | 138 | 18:00 | 126 | 23:00 | Narail | 139 | 18:00 | 126 | 22:00
| Bhangura | 138 | 18:00 | 131 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:00 | 131 | 02:00 | Narshingdi | 132 | 18:30 | 127 | 10:00
| Bheramara(GK) | 139 | 18:30 | 132 | 00:00 | Natore | 134 | 18:00 | 123 | 02:00
| Bhulta | 130 | 05:00 | 123 | 11:00 | Nawabganj | 138 | 01:00 | 130 | 12:00
| Bog-Sherpur | 135 | 18:30 | 123 | 00:00 | Netrakona | 130 | 18:00 | 115 | 08:00
| Bogura | 136 | 19:00 | 123 | 00:00 | New | 134 | 00:00 | 126 | 11:00
| Bogura-230 | 137 | 18:30 | 124 | 00:00 | Niamatpur | 124 | 14:00 | 102 | 00:00
| Brahmanbaria | 132 | 07:00 | 130 | 00:00 | Noapara | 138 | 18:00 | 127 | 12:00
| Cantonment | 134 | 04:00 | 126 | 12:00 | Pabna | 136 | 18:00 | 128 | 01:00
| Chandpur | 139 | 16:00 | 123 | 01:00 | Palashbari | 130 | 19:00 | 114 | 00:00
| Chandraghona | 141 | 21:00 | 133 | 06:00 | Panchagarh | 134 | 18:30 | 116 | 01:00
| Chapai | 132 | 18:00 | 119 | 07:00 | Patuakhali | 137 | 17:00 | 129 | 22:00
| Charsaidpur | 137 | 20:00 | 131 | 12:00 | Payra | 138 | 17:00 | 133 | 22:00
| Chauddagram | 132 | 12:00 | 124 | 01:00 | PHP | 132 | 12:00 | 122 | 01:00
| Chhatak | 130 | 19:00 | 125 | 03:00 | Purbachal | 136 | 06:00 | 124 | 16:00
| Chowmuhani | 132 | 16:00 | 114 | 01:00 | Purbasadipur | 133 | 19:00 | 115 | 00:00
| Chuadanga | 136 | 18:00 | 120 | 22:00 | Rahim | 136 | 00:00 | 132 | 11:00
| Coxsbazar | 130 | 11:00 | 116 | 06:00 | Rajbari | 137 | 18:00 | 126 | 22:00
| Cumilla(N) | 136 | 21:00 | 129 | 06:00 | Rajendrapur | 135 | 06:00 | 129 | 11:00
| Cumilla(S) | 137 | 23:00 | 126 | 06:00 | Rajshahi | 134 | 18:00 | 123 | 00:00
| Daudkandi | 137 | 21:00 | 128 | 07:00 | Rajshahi-230 | 133 | 18:00 | 123 | 07:00
| Dhaka | 135 | 05:00 | 126 | 11:00 | Ramganj | 133 | 12:00 | 119 | 02:00
| Dhamrai | 132 | 01:00 | 125 | 12:00 | Rampur | 140 | 21:00 | 132 | 09:00
| Dhanmondi | 136 | 01:00 | 131 | 11:00 | Rampura | 134 | 01:00 | 125 | 15:00
| Dohazari | 141 | 23:00 | 126 | 06:00 | Rangamati | 139 | 12:00 | 132 | 07:00
| Faridpur | 136 | 18:30 | 127 | 00:00 | Rangpur | 130 | 18:30 | 115 | 00:00
| Fatullah | 137 | 21:00 | 132 | 11:00 | Ruppur | 137 | 18:00 | 130 | 01:00
| Fenchuganj | 133 | 05:00 | 131 | 02:00 | Saidpur | 132 | 19:00 | 115 | 01:00
| Feni | 134 | 12:00 | 124 | 01:00 | Satkhira | 135 | 18:00 | 120 | 23:00
| Ghorashal | 143 | 21:00 | 137 | 13:00 | Satmasjid | 134 | 01:00 | 128 | 12:00
| Goalpara | 137 | 18:00 | 127 | 02:00 | Savar | 133 | 21:00 | 125 | 16:00
| Gollamari | 138 | 18:00 | 127 | 02:00 | Shahjadpur | 142 | 18:00 | 136 | 01:00
| Gopalganj | 139 | 18:00 | 130 | 02:00 | Shahjibazar | 135 | 20:00 | 132 | 10:00
| Gopalganj_I | 141 | 18:00 | 133 | 21:00 | Shahmirpur | 140 | 23:00 | 135 | 15:00
| Gulshan | 134 | 05:00 | 125 | 15:00 | Shariatpur | 137 | 18:30 | 127 | 00:00
| Halishahar | 141 | 21:00 | 130 | 06:00 | Sherpur | 134 | 18:00 | 112 | 07:00
| Haripur | 136 | 00:00 | 132 | 11:00 | Shikalbaha | 143 | 21:00 | 131 | 06:00
| HaripurSBU | 136 | 00:00 | 132 | 11:00 | Shikalbaha-230 | 140 | 12:00 | 131 | 07:00
| Hasnabad | 137 | 00:00 | 132 | 11:00 | Shitalakhya | 138 | 01:00 | 132 | 12:00
| Hathazari | 140 | 21:00 | 133 | 06:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 137 | 18:00 | 130 | 22:00 | Shyampur | 134 | 01:00 | 129 | 11:00
| Jaldhaka | 129 | 19:00 | 112 | 01:00 | Shyampur-230 | 136 | 01:00 | 131 | 12:00
| Jamalpur | 135 | 22:00 | 117 | 07:00 | Siddhirganj | 136 | 04:00 | 131 | 11:00
| Jashore | 138 | 18:00 | 125 | 23:00 | Sirajganj | 136 | 18:30 | 126 | 00:00
| Jhenaidah | 139 | 17:00 | 130 | 22:00 | Sonargaon | 136 | 01:00 | 130 | 17:00
| Jhenaidah-230 | 141 | 18:00 | 130 | 22:00 | Sreemongol | 135 | 09:00 | 132 | 11:00
| Joydebpur | 141 | 22:00 | 137 | 07:00 | Srinagar | 137 | 00:00 | 130 | 12:00
| Joypurhat | 126 | 18:30 | 108 | 00:00 | SSM | 140 | 07:00 | 134 | 05:00
| Juldah | 142 | 21:00 | 133 | 05:00 | Sunamganj | 127 | 07:00 | 123 | 03:00
| Kabirpur | 136 | 06:00 | 123 | 15:00 | Sylhet | 130 | 06:00 | 128 | 02:00
| Kachua | 136 | 18:00 | 124 | 01:00 | Tangail | 136 | 17:00 | 129 | 00:00
| Kaliakoir | 138 | 22:00 | 132 | 19:00 | Thakurgaon | 133 | 18:30 | 115 | 01:00
| Kallyanpur | 133 | 21:00 | 127 | 11:00 | TK | 142 | 21:00 | 132 | 06:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 572 | 7824 | 4885 | 12709 |  |  |  | QF-LDC-11
0:30 | 392 | 8100.5 | 4871 | 12971.5 | Date: | 2022-07-18
1:00 | 212 | 8377 | 4857 | 13234
1:30 | 252 | 8229 | 4821 | 13050
2:00 | 292 | 8081 | 4785 | 12866
2:30 | 285 | 7982 | 4741.5 | 12723.5 | [5 empty] | Gen. at Eve. Peak | 13221 | 13221 MW (21:00 )
3:00 | 278 | 7883 | 4698 | 12581 | [6 empty] | 21:00
3:30 | 295 | 7843 | 4667.5 | 12510.5 | [5 empty] | Gen. at Day Peak | 12258 | 12258 MW (10:00 )
4:00 | 312 | 7803 | 4637 | 12440 | [6 empty] | 10:00
4:30 | 332 | 7707 | 4595.5 | 12302.5 | [5 empty] | Highest Generation | 13281
5:00 | 352 | 7611 | 4554 | 12165 | [6 empty] | 22:00
5:30 | 378 | 7276.5 | 4390 | 11666.5
6:00 | 404 | 6942 | 4226 | 11168
6:30 | 410 | 6982.5 | 4203.5 | 11186
7:00 | 416 | 7023 | 4181 | 11204
7:30 | 426 | 7062.5 | 4114.5 | 11177
8:00 | 436 | 7102 | 4048 | 11150
8:30 | 449 | 7311 | 4055.5 | 11366.5
9:00 | 462 | 7520 | 4063 | 11583
9:30 | 476 | 7823 | 4097.5 | 11920.5
10:00 | 490 | 8126 | 4132 | 12258
10:30 | 492 | 8061 | 4091.5 | 12152.5
11:00 | 494 | 7996 | 4051 | 12047
11:30 | 515 | 7910.5 | 4061 | 11971.5
12:00 | 536 | 7825 | 4071 | 11896
12:30 | 489 | 7925.5 | 4085.5 | 12011
13:00 | 442 | 8026 | 4100 | 12126
13:30 | 522 | 8003 | 4185 | 12188
14:00 | 602 | 7980 | 4270 | 12250
14:30 | 649 | 8021.5 | 4308.5 | 12330
15:00 | 696 | 8063 | 4347 | 12410
15:30 | 720 | 7992 | 4384.5 | 12376.5
16:00 | 744 | 7921 | 4422 | 12343
16:30 | 741 | 7918 | 4463 | 12381
17:00 | 738 | 7915 | 4504 | 12419
17:30 | 702 | 7615 | 4358.5 | 11973.5
18:00 | 666 | 7315 | 4213 | 11528
18:30 | 693 | 7688.5 | 4324 | 12012.5
19:00 | 720 | 8062 | 4435 | 12497
19:30 | 642 | 8267 | 4931 | 13198
20:00 | 414 | 8254 | 4900 | 13154 |  |  |  | Executive Engineer
20:30 | 398 | 8233 | 4954.5 | 13187.5 |  |  |  | Network Operation Division
21:00 | 382 | 8212 | 5009 | 13221
21:30 | 371 | 8229 | 5022 | 13251
22:00 | 360 | 8246 | 5035 | 13281 |  |  |  |  | Page 6 of 7
22:30 | 393 | 8252.5 | 5022 | 13274.5
23:00 | 426 | 8259 | 5009 | 13268
23:30 | 499 | 8041.5 | 4947 | 12988.5
24:00 | 572 | 7824 | 4885 | 12709
13221 MW (21:00 )
12258 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-18 |  | Energy |  | 299975157
[13 empty] | 2022-07-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3677 | 857 | 1617 | 736 | 3516 | 1300 | 127 | 210 | 795 | 84 | 0 | 0
0:30 | 3925.5 | 883 | 1782.5 | 593 | 3503 | 1278.5 | 127.5 | 213 | 794.5 | 84 | 0 | 0 | Date: | 2022-07-18
1:00 | 4174 | 909 | 1948 | 450 | 3490 | 1257 | 128 | 216 | 794 | 84 | 0 | 0
1:30 | 4200.5 | 910 | 1943 | 335 | 3456 | 1257 | 128 | 216 | 738.5 | 82 | 0 | 0 | [8 empty] | Total Energy | 299.9752 | Total Energy Gen 299.975 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 299.975 MKWHr
2:00 | 4227 | 911 | 1938 | 220 | 3422 | 1257 | 128 | 216 | 683 | 80 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4222 | 910.5 | 1936 | 180 | 3338.5 | 1247 | 128 | 213.5 | 682.5 | 79 | 0 | 0 | [8 empty] | Energy Requirement | 299.9752
3:00 | 4217 | 910 | 1934 | 140 | 3255 | 1237 | 128 | 211 | 682 | 78 | 0 | 0
3:30 | 4219.5 | 910 | 1934.5 | 140 | 3224.5 | 1222.5 | 128 | 189.5 | 654.5 | 77 | 0 | 0 | [6 empty] | Shortage
4:00 | 4222 | 910 | 1935 | 140 | 3194 | 1208 | 128 | 168 | 627 | 76 | 0 | 0
4:30 | 4225.5 | 910.5 | 1934.5 | 80 | 3165.5 | 1203 | 126.5 | 149 | 581 | 76 | 0 | 0
5:00 | 4229 | 911 | 1934 | 20 | 3137 | 1198 | 125 | 130 | 535 | 76 | 0 | 0
5:30 | 4234.5 | 910.5 | 1930.5 | 10 | 2858.5 | 1173 | 124.5 | 130 | 348 | 74 | 3 | 0
6:00 | 4240 | 910 | 1927 | 0 | 2580 | 1148 | 124 | 130 | 161 | 72 | 6 | 0
6:30 | 4260.5 | 910 | 1943 | 0 | 2565 | 1133 | 124 | 130 | 153.5 | 69 | 28 | 0 |  |  |  |  | Coal
7:00 | 4281 | 910 | 1959 | 0 | 2550 | 1118 | 124 | 130 | 146 | 66 | 50 | 0
7:30 | 4225 | 910 | 1922.5 | 0 | 2599.5 | 1088 | 124 | 130 | 163 | 65 | 80 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4169 | 910 | 1886 | 0 | 2649 | 1058 | 124 | 130 | 180 | 64 | 110 | 0
8:30 | 4122.5 | 910.5 | 1870 | 48.5 | 2839.5 | 1048.5 | 125 | 140 | 222 | 64 | 116 | 0
9:00 | 4076 | 911 | 1854 | 97 | 3030 | 1039 | 126 | 150 | 264 | 64 | 122 | 0
9:30 | 4078 | 893.5 | 1834.5 | 318.5 | 3110 | 1039.5 | 126 | 178.5 | 292.5 | 65 | 163 | 0
10:00 | 4080 | 876 | 1815 | 540 | 3190 | 1040 | 126 | 207 | 321 | 66 | 204 | 0
10:30 | 4087.5 | 876.5 | 1818 | 494 | 3138.5 | 1039.5 | 126.5 | 210 | 329.5 | 66 | 176.5 | 0
11:00 | 4095 | 877 | 1821 | 448 | 3087 | 1039 | 127 | 213 | 338 | 66 | 149 | 0
11:30 | 4051.5 | 876.5 | 1803.5 | 345 | 3114 | 1054 | 127.5 | 211.5 | 358 | 68 | 173.5 | 0
12:00 | 4008 | 876 | 1786 | 242 | 3141 | 1069 | 128 | 210 | 378 | 70 | 198 | 0
12:30 | 3933.5 | 875 | 1778.5 | 343 | 3204 | 1094 | 128 | 209.5 | 383.5 | 73 | 198.5 | 0
13:00 | 3859 | 874 | 1771 | 444 | 3267 | 1119 | 128 | 209 | 389 | 76 | 199 | 0
13:30 | 3859 | 874 | 1771 | 444 | 3267 | 1119 | 128 | 209 | 389 | 76 | 199 | 0
14:00 | 3859 | 874 | 1771 | 444 | 3267 | 1119 | 128 | 209 | 389 | 76 | 199 | 0
14:30 | 3853.5 | 874.5 | 1731.5 | 592.5 | 3305.5 | 1139.5 | 128 | 209 | 415 | 77 | 151 | 0
15:00 | 3848 | 875 | 1692 | 741 | 3344 | 1160 | 128 | 209 | 441 | 78 | 103 | 0
15:30 | 3854 | 875 | 1691 | 790.5 | 3301.5 | 1160 | 98 | 210 | 459 | 76 | 71.5 | 0
16:00 | 3860 | 875 | 1690 | 840 | 3259 | 1160 | 68 | 211 | 477 | 74 | 40 | 0
16:30 | 3839 | 875 | 1681.5 | 788.5 | 3335.5 | 1150 | 71.5 | 211.5 | 515.5 | 73 | 41 | 0
17:00 | 3839 | 875 | 1673 | 737 | 3412 | 1140 | 75 | 212 | 554 | 72 | 42 | 0
17:30 | 3793 | 874.5 | 1589.5 | 368.5 | 3481.5 | 1109.5 | 75 | 209 | 585 | 68 | 29 | 0
18:00 | 3747 | 874 | 1506 | 0 | 3551 | 1079 | 75 | 206 | 616 | 64 | 16 | 0
18:30 | 3788.5 | 866 | 1570 | 247.5 | 3664 | 1079.5 | 75 | 176.5 | 641 | 73 | 8 | 0
19:00 | 3830 | 858 | 1634 | 495 | 3777 | 1080 | 75 | 147 | 666 | 82 | 0 | 0
19:30 | 3691 | 858 | 1715 | 960 | 3859 | 1199 | 75 | 204 | 761 | 80 | 0 | 0
20:00 | 3739 | 857 | 1626 | 915 | 3856 | 1200 | 77 | 208 | 804 | 80 | 0 | 0
20:30 | 3711 | 857.5 | 1619.5 | 943 | 3846.5 | 1225 | 98 | 209.5 | 806 | 81 | 0 | 0
21:00 | 3683 | 858 | 1613 | 971 | 3837 | 1250 | 119 | 211 | 808 | 82 | 0 | 0
21:30 | 3670.5 | 858 | 1616 | 968 | 3859.5 | 1270 | 122 | 211.5 | 805 | 82 | 0 | 0
22:00 | 3658 | 858 | 1619 | 965 | 3882 | 1290 | 125 | 212 | 802 | 82 | 0 | 0
22:30 | 3636 | 858 | 1627 | 963 | 3887 | 1294.5 | 125.5 | 211 | 799.5 | 84 | 0 | 0
23:00 | 3614 | 858 | 1635 | 961 | 3892 | 1299 | 126 | 210 | 797 | 86 | 0 | 0
23:30 | 3645.5 | 857.5 | 1626 | 848.5 | 3704 | 1299.5 | 126.5 | 210 | 796 | 85 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.8° C
24:00 | 3677 | 857 | 1617 | 736 | 3516 | 1300 | 127 | 210 | 795 | 84 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 299.975 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 299.975 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 93 | 93 | 93 | 93 | 90 | 89 | 89 | 89 | 91 | 91 | 92 | 93 | 93 | 93 | 93 | 33 | 40 | 40 |  | 40 | 40 | 42 | 84 | 90 | 91 | 92 | 1918238
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 |  | 0 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1 |  | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 528984
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 15 | 20 | 19 | 18 | 18 | 14 | 9 | 8 | 4 | 1 | [8 empty] | 118395
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 0 | [13 empty] | 51 | 61 | 51 | 51 | 51 | 51 | 51 | 547918
12 | Hathazari 100 MW peaking PP | 51 | 42 | 42 | 42 | 42 | 0 | [13 empty] | 10 | 23 | 51 | 51 | 51 | 51 | 51 | 470592
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 17 | 17 | 20 | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 81 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2320072
| Daudkandi 200 MW PP (B.Trac) | 200 | 200 | 140 | 140 | 20 |  |  |  | 0 | 50 | 50 | 0 |  |  | 200 | 200 | 150 |  |  | 102 | 200 | 200 | 200 | 200 | 200 | 160 | 2359104
14 | Titas 50 MW Peaking PP | 47 | 47 | 47 | 47 | 47 | [6 empty] | 43 | 47 | 49 | 49 | 49 | 48 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 847032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 264 | 262 | 274 | 273 | 273 | 270 | 273 | 273 | 273 | 273 | 273 |  | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 6546216
19 | Ashuganj 195MW PP (APSCL-United) | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 158 | 158 | 158 | 158 | 128 | 124 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 16 | 8 | 8 | 8 | 8 | 3027636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7183645
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 39 | 38 | 38 | 38 | 39 | 39 | 39 | 36 | 37 | 38 | 37 | 37 | 37 | 34 | 36 | 36 | 37 |  | 37 | 38 | 39 | 40 | 40 | 40 | 40 | 894096
33 | Ashuganj 225 MW CCPP | 212 | 210 | 211 | 212 | 211 | 212 | 210 | 210 | 211 | 208 | 206 | 206 | 204 | 206 | 207 | 207 | 210 | 211 |  | 192 | 138 | 125 | 124 | 126 | 126 | 127 | 4670000
34 | Ashuganj 450 MW CCPP(South) | 305 | 330 | 320 | 305 | 305 | 305 | 335 | 340 | 305 | 315 | 330 | 330 | 305 | 305 | 310 | 310 | 305 | 290 |  | 315 | 275 | 315 | 280 | 260 | 260 | 260 | 7441000
| Ashuganj 450 MW CCPP(North) | 310 | 335 | 325 | 310 | 310 | 310 | 345 | 325 | 310 | 320 | 345 | 345 | 310 | 310 | 315 | 320 | 310 | 290 |  | 325 | 285 | 315 | 280 | 280 | 280 | 280 | 7895500
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 48 | 48 | 48 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 45 | 45 | 45 | 44 | 43 | 43 | 45 |  | 46 | 46 | 46 | 47 | 30 | 30 | 30 | 1068960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 367 | 375 | 383 | 393 | 394 | 395 | 396 | 380 | 369 | 358 | 370 | 330 | 309 | 297 | 286 | 276 | 265 | 257 |  | 254 | 249 | 250 | 249 | 249 | 255 | 268 | 7856130
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 215 | 210 | 205 | 200 | 190 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4540000
41 | Haripur 360MW CCPP(HPL) | 240 | 252 | 262 | 266 | 267 | 267 | 267 | 260 | 243 | 238 | 248 | 239 | 217 | 207 | 192 | 177 | 169 | 153 |  | 154 | 152 | 152 | 152 | 152 | 155 | 155 | 5128000
42 | RPCL 210MW CCPP | 106 | 106 | 107 | 107 | 107 | 107 | 106 | 106 | 97 | 92 | 80 | 80 | 68 | 68 | 70 | 70 | 81 | 81 |  | 104 | 105 | 105 | 105 | 105 | 106 | 107 | 2213760
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 29 | 24 | 54 | 35 | 39 | 50 | 24 | 30 | 3 | 15 | 4 |  | 0 | [6 empty] | 314880
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 42 | 42 | 42 | 42 | 42 | 43 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 946000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 959192
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 59 | 59 | 59 | 59 | 58 | 58 | 62 | 58 | 54 | 57 | 58 | 58 | 55 | 55 | 55 | 61 |  | 60 | 63 | 62 | 62 | 62 | 61 | 64 | 1423776
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 81 | 81 | 81 | 81 | 81 | 81 | 1177920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5274280
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237780
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 8 | [7 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 137424
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 290 | 290 | 285 | 280 | 320 | 310 | 300 | 300 | 300 | 305 | 310 | 290 | 295 | 305 | 300 | 275 |  | 280 | 300 | 300 | 295 | 300 | 315 | 290 | 7371000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 388 | 386 | 394 | 388 | 397 | 395 | 400 | 390 |  | 395 | 400 | 393 | 400 | 397 | 388 | 400 | 9469400
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 0 | 3 | 55 | 55 | 55 | 55 | 55 | [11 empty] | 300289
59 | Tangail Palli Power Gen 22 MW | 22 | 23 | 22 | 22 | 18 | 19 | 21 | 19 | 23 | 24 | 23 | 23 | 22 | 20 | 13 | 14 | 20 | 20 |  | 22 | 23 | 23 | 23 | 23 | 22 | 22 | 508320
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448560
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 413925
62 | Tangail 22 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 13 | 8 | 392040
63 | Impoprt (Tripura) | 84 | 80 | 78 | 76 | 76 | 72 | 66 | 64 | 64 | 66 | 66 | 70 | 76 | 80 | 78 | 74 | 72 | 64 |  | 82 | 80 | 80 | 82 | 82 | 86 | 84 | 1780800
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 31 | 31 | 40 | 40 | 35 | 10 | 2 | 2 | 2 | 2 | 7 | 2 | 3 | 4 | 12 | 10 |  | 20 | 16 | 16 | 8 | 30 | 30 | 28 | 441600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 478008
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238680
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 27 | 23 | 21 | 25 | 23 | 25 | 30 | 30 | 23 |  | 25 | 25 | 25 | 32 | 33 | 33 | 33 | 697300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 521630
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 17 | 21 | 23 | 23 | 8 | 23 | 485460
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600480
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 29 | 30 | 31 | 32 | 32 | 33 | 757400
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 89 | 89 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 81 | 82 |  | 83 | 83 | 89 | 89 | 85 | 82 | 86 | 2083590
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [9 empty] | 285000
| Chowmuhani 113 MW | 12 |  |  |  | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 30 | 107 | 113 |  | 114 | 114 | 115 | 115 | 115 | 113 | 50 | 979440
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 35 | 35 | 50 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 147 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3402720
77 | Siddhirganj 100 PP(Dutch Bangla) | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 94 | 94 | 94 | 87 | 88 | 88 | 88 | 87 | 80 | 39 | 30 |  | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 1756666
78 | Gazipur 52 MW PP | 42 | 42 | 42 | 42 | 42 | 24 | 24 | 32 | 42 | 42 | 41 | 43 | 49 | 49 | 49 | 48 | 48 | 48 |  | 48 | 49 | 48 | 50 | 50 | 50 | 50 | 1066560
79 | Kodda 150MW PP | 128 | 128 | 132 | 132 | 115 | 16 | 16 | 50 | 114 | 114 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 130 | 130 | 130 | 2689440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200501
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 105 | 98 | 90 | 90 | 96 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2464800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 6 | 4 | 4 | 0 | 0 | 0 | 0 | [8 empty] | 28561
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 903661
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 92 | 92 | 92 | 72 | 72 | 72 | 75 | 92 | 92 | 92 | 92 |  | 92 | 110 | 106 | 110 | 110 | 110 | 110 | 2399517
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 86 | 86 | 86 | 85 | 85 | 80 | 79 | 79 | 73 | 71 | 66 | 72 | 72 | 72 | 72 | 72 | 71 | 48 |  | 48 | 40 | 41 | 36 | 40 | 40 | 41 | 1609920
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2575680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | 30 | 40 | 55 | 55 | 55 | 33 | 33 | 31 | 32 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 971400
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1184023
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 84 | 93 | 84 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2197584
95 | Patenga 50MW PP (Baraka) | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 38 | 38 |  | 38 | 38 | 37 | 38 | 38 | 38 | 0 | 892320
96 | Chattogram 108 MW PP (ECPV) | 74 | 74 | 74 | 74 | 74 | 35 | 11 | 24 | 66 | 68 | 64 | 64 | 72 | 73 | 73 | 76 | 76 | 81 |  | 81 | 81 | 85 | 82 | 82 | 82 | 83 | 1666560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1287155
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 9 | 53 |  | 53 | 55 | 55 | 55 | 55 | 55 | 0 | 330756
101 | Kushiara 163 MW CCPP (KP) | [26 empty] | 0
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 3 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 13650
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 35 | 35 | 35 | 17 |  | 17 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 868320
104 | Keranigonj 300 MW PP (APR) | 50 | 20 | [6 empty] | 0 | 300 | 298 | 150 | 250 | 305 | 270 | 271 | 250 |  |  | 192 | 301 | 302 | 301 | 302 | 302 | 192 | 3551784
105 | Bramhangoan 100 MW PP (Aggreko) | 98 | [6 empty] | 0 | 97 | 96 | 50 | 92 | 94 | 92 | 92 | 96 | 93 |  |  | 93 | 98 | 98 | 97 | 97 | 96 | 97 | 1462706
106 | Mymensingh 200 MW PP (United) | 116 | 117 | 117 | 117 | 117 | 117 | 117 | 116 | 116 | 115 | 115 | 114 | 115 | 115 | 114 | 114 | 114 | 160 |  | 170 | 170 | 170 | 170 | 179 | 180 | 117 | 3081600
112 | Aurahati 100MW PP (Aggreko) | 102 | [7 empty] | 0 | 93 | 50 | 0 | 100 | 101 | 100 | 100 | 99 |  |  | 97 | 101 | 100 | 101 | 101 | 100 | 61 | 1286484
114 | Kodda 149 MW PP Unit-1 (Summit) | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 146 | 139 | 148 | 135 | 135 | 135 | 143 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3582430
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 76 | 90 | 63 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2038080
116 | Chandpur 200MW (Desh energy) | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 148 | 183 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3475680
117 | Ashuganj 150MW PP (Midland) | 80 | 10 | 10 | 10 | 10 | 10 | 18 | 36 | 76 | 103 | 107 | 110 | 112 | 115 | 113 | 118 | 122 | 125 |  | 125 | 132 | 128 | 132 | 138 | 140 | 140 | 2206327
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 402 | 401 | 401 | 403 | 404 | 403 | 403 | 400 | 402 | 403 | 404 | 404 | 404 | 403 | 381 |  | 402 | 402 | 403 | 402 | 403 | 401 | 402 | 9602000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 59 | 59 | 58 | 58 | 58 | 95 |  | 105 | 105 | 105 | 105 | 105 | 106 | 59 | 1669200
| Anwara 300 MW PP (United) | 278 | 278 | 190 | 130 | 100 | 0 |  | 30 | 110 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 |  | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 5414618
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 83 | 70 | 77 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 2167680
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 90 | 106 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 96 | 108 | 108 | 108 | 2569309
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885600
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 2 | 14 | 27 | 22 | 32 | 17 | 35 | 5 | 14 | 6 | 7 | 2 | [8 empty] | 193013
| Chandpur 115(Doreen) | 95 | 95 | 95 | 95 | 96 | 95 | 95 | 95 | 95 | 95 | 94 | 94 | 94 | 94 | 81 | 72 | 72 | 72 |  | 72 | 72 | 72 | 71 | 74 | 96 | 95 | 2108160
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 |  | 32 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1239840
120 | Eastern Zone Total | 8377 | 8081 | 7883 | 7803 | 7611 | 6942 | 7023 | 7102 | 7520 | 8126 | 7996 | 7825 | 8026 | 7980 | 8063 | 7921 | 7915 | 7315 |  | 8062 | 8267 | 8254 | 8212 | 8246 | 8259 | 7824 | 189466257
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 17 |  | 20 | 22 | 23 | 20 | 30 | 16 | 16 | 395520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 38 | [14 empty] | 9 | 34 | 34 |  | 37 | 51 | 39 | 39 | 35 | 32 | 30 | 3084
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 35 | 35 | 35 | [7 empty] | 17 | 84 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1387200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 36 | 52 | 49 | 95 | 51 | 105 | 79 | 101 | 40 | 17 | 12 | 9 | [8 empty] | 651600
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445200
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 223 | 223 | 223 | 221 | 220 | 223 | 223 | 222 | 222 | 220 | 218 | 218 | 218 | 220 | 225 | 222 | 165 |  | 218 | 224 | 220 | 226 | 222 | 222 | 221 | 5268464
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 706560
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 87 | 84 | 84 | 86 | 88 | 85 | 87 | 87 | 87 |  | 87 | 87 | 84 | 87 | 86 | 85 | 88 | 2063707
140 | Bhola 33 MW PP (Venture) | 35 | 34 | 29 | 28 | 26 | 25 | 19 | 20 | 22 | 21 | 20 | 23 | 24 | 21 | 22 | 23 | 23 | 22 |  | 30 | 30 | 31 | 30 | 34 | 35 | 35 | 618776
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 88 | 60 | 94 | 94 | 94 | 60 | 449280
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 8 | [6 empty] | 16 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 675000
143 | Gopalganj 100 MW Peaking PP | 60 | [14 empty] | 20 | 30 | 25 |  | 40 | 40 | 70 | 70 | 63 | 62 | 62 | 454656
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 67 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | 50 | 32 |  | 60 | 105 | 105 | 105 | 105 | 105 | 105 | 2340288
146 | Bheramara HVDC | 909 | 911 | 910 | 910 | 911 | 910 | 910 | 910 | 911 | 876 | 877 | 876 | 874 | 875 | 875 | 875 | 875 | 874 |  | 858 | 858 | 857 | 858 | 858 | 858 | 857 | 21377454
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 370 | 375 | 365 | 350 | 290 | 280 | 280 | 280 | 245 | 205 | 205 | 255 | 250 | 245 | 250 |  | 245 | 245 | 240 | 240 | 240 | 235 | 245 | 6988032
148 | Payra 1320 MW | 1060 | 1060 | 1040 | 1010 | 1000 | 950 | 920 | 860 | 840 | 840 | 840 | 870 | 920 | 940 | 960 | 960 | 940 | 880 |  | 880 | 1000 | 1000 | 1050 | 1090 | 1100 | 1100 | 24914300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 197 | 197 | 197 | 198 | 198 | 198 | 198 | 198 | 199 | 200 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 199 |  | 200 | 199 | 200 | 200 | 200 | 199 | 200 | 4883900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 25 | 0 | [11 empty] | 9 | 19 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 353328
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 3 | 5 | 3 | 5 | 2 | 1 | 2 | 0 | [8 empty] | 33360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 192 | 196 | 200 | 205 | 208 | 208 | 205 | 196 | 186 | 187 | 198 | 185 | 175 | 169 | 160 | 159 | 153 | 146 |  | 146 | 145 | 144 | 140 | 136 | 134 | 142 | 4405991
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 216 | 216 | 211 | 168 | 130 | 130 | 130 | 130 | 150 | 207 | 213 | 210 | 209 | 211 | 209 | 211 | 212 | 206 |  | 147 | 204 | 208 | 211 | 212 | 210 | 210 | 4781509
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 203 | 203 | 203 | 203 | 203 | 207 | 202 | 196 | 191 | 188 | 183 | 182 | 165 | 154 | 149 | 149 | 146 | 143 |  | 143 | 139 | 139 | 139 | 137 | 129 | 129 | 4338882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 418 | 418 | 416 | 414 | 414 | 415 | 414 | 414 | 414 | 355 |  | 414 | 414 | 414 | 414 | 414 | 414 | 420 | 9880800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 19 | 15 | 15 | 12 | 0 | [10 empty] | 5 | 29 | 28 |  | 30 | 30 | 30 | 31 | 30 | 30 | 30 | 299203
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 447840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264276
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 0 |  | 0 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 691952
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 0 | [7 empty] | 16 | 16 | 16 | 25 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 434420
168 | Santahar 50 MW Peaking PP | 29 | 29 | 29 | 29 | 29 | 0 | [11 empty] | 15 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 342036
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 43 | 43 | 43 | 43 | 43 | 8 | 350606
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 89 | 15 | 0 | [5 empty] | 8 | 42 | 42 | 42 | 42 | 84 |  | 84 | 84 | 87 | 87 | 87 | 88 | 88 | 1254240
171 | Baghabari 200 MW PP (Paramount) | 0 | [7 empty] | 0 | 1 | 0 |  |  |  | 79 | 173 | 145 |  |  | 11 | 172 | 155 | 178 | 171 | 169 | 166 | 1403146
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 113 | 113 |  | 113 | 113 | 113 | 107 | 107 | 107 | 70 | 2068896
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1607040
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 96 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 78 | 81 | 81 | 80 | 80 | 81 | 94 | 94 |  | 94 | 94 | 94 | 94 | 95 | 95 | 96 | 2085139
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 6 | 7 | 7 | 6 | 4 | 2 | 0 | [8 empty] | 34959
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 72 | 72 | 72 | 72 | 72 | 52 | 34 | 34 | 34 | 34 | 0 | 34 | 34 |  | 108 | 108 | 108 | 108 | 108 | 109 | 109 | 1808256
178