## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-20 | Wednesday
|  |  | Date (day): | 2022-07-20 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11519.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12051 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-19 | 2022-07-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 89 | 89 | 89 |  | 19 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 283 | 288 | 280 | 280 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 176 | 198 | 200 | 200 |  | 30 | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 190 | 170 | 170 | 170 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 40 | 40 | 40 |  | 60 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 32 | 32 | 32 |  | 68 | Engine problem
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 88 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 17 |  |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 125 | 115 | 130 |  | 19 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 50 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 28 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 50 | 50 | 50 |  | 2
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 258 | 255 | 255 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 148 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 17 | 35 | 144 |  |  | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2579 | 2522 | 2479 | 2718 | 1656 | 1107
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 3 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 38 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 126 | 123 | 127 | 127 |  | 103 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 61 | 51 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 31 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 76 | 85 | 89 | 89 |  | 19 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 265 | 285 | 278 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  |  | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 92 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 77 | 77 | 50 | 50
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1213 | 1349 | 1322 | 1337 | 378 | 589
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 150 | 208 | 210 | 210 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 300 | 300 |  |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 290 | 290 | 290 |  |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 10 | 10 | 10 |  | 35 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 |  | 50 | Engine problem
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 130 | 135 | 130 |  | 20 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 45 | 41 | 45
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Grid problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 120 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 66 | 128 | 60 | 79
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 22 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 18 | 8 | 8
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 76 | 35 | 54 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1306 | 1545 | 1409 | 1528 | 675 | 336
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 106 | 105 | 105 |  | 97 | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 180 | 116 | 180 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 104 | 60 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 14 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 16 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 335 | 428 | 376.6 | 434 | 0 | 115
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 62 | 64 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 25 | 25 | 25
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 290 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 398 | 396 | 360 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1518 | 1520 | 1462 | 1510 | 275 | 505
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 908 | 857 | 890 | 875
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 32 | 32 | 83 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42 |  | 12 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 55 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 245 | 200 | 225 | 225 | 185 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40 | 32
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 40 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1447 | 1429 | 1540 | 1472 | 646 | 73
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 16 | 48
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 31 | 26 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 82 | 82 | 82 | 112 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1060 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1221 | 1458 | 1461 | 1497 | 112 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 22 | 16 | 22 |  | 49 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 154 | 127 | 154 | 154 | 56 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 147 | 142 | 142 | 145 | 75 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 325 | 360 | 360 |  |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 22 | 28 |  | 22 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 85 | 85 |  | 19 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 94 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 75 | 95
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 914 | 1078 | 1085 | 1143 | 766 | 142
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 79 | 103 | 68 | 103 |  | 10 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 109 | 108 | 109 | 109 |  | 6 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 390 | 410 | 385 | 412 | 199 | 101
|  | Total |  |  |  |  | 22678 | 21396 | 10923 | 11739 | 11519.6 | 12051 | 4707 | 2978
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 12547.7625 | 13485.14 | 13233.1049 | 13843.549
| A. |  | 2022-07-19 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12616 | MW at | 2:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10633 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14124 | MW
| 3 | Day peak Generation : |  |  | 10923 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13485.14 | MW
| 4 | Evening peak Generation : |  |  | 11739 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 2385 | MW
| 5 | Total Energy Generation : |  | 275.2303 | MKWHr | By Solar | 1.0733 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 124.7263 | MKWHr |  | By Oil: | 92.8047 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.1444 | MKWHr |  | By Hydro: | 2.9689 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4707 | MW | Dhaka | 4800.84 | 4037.84 |  | 763
|  |  |  | For Plants S/D or M/C prob = |  |  | 2978 | MW | Chittagong | 1289.1 | 1044.1 |  | 245 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7685 | MW | Khulna | 1759.4 | 1429.4 |  | 330 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 928.35 | MMCFD |  |  | Rajshahi | 1480 | 1177 |  | 303 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 139384678.95 | ii) Oil : | Taka | 1270375125.69 | Comilla | 1322 | 1069 |  | 253 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 253560532 | Total | Taka | 1663320336.64 | Mymensingh | 1082 | 862 |  | 220 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 511 | 420 |  | 91 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 458 | MW (E to W) at | 21:00 | hrs | Barisal | 383.8 | 383.8 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 386 | MW at | 5:00 | hrs | Rangpur | 857 | 677 |  | 180 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 13485.14 | 11100.14 |  | 2385
| B. |  | 2022-07-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 2085 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12051 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12150 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 309.7868 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11182 | MW at | 8:00 | 655 | 220 | 290 | 265 | 220 | 190 | 80 | 0 | 165
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2655 | MKWHr. | ii) HVDC Flow at Peak Time |  | 857 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2474 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.93 |  | (b) Today: | 91.31 |  | (c) Rule Curve: |  | 87.04
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 268 | 156 |  | 0 | 180 | 0 | 41 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 51 | 51 | 31 | 82 | 8 | 19 | 31 | 0 | 0 | 0 | 280 | 260 | 127 | 8 | 0 | 40 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 80 | 107 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 64 | 40 | 0 | 220 | 0 | 0 | 10 | 275 | 8 | 0 | 160 | 273 | 192 | 96 | 117 | 60 | 140 | 0 | 90 | 137 | 138 | 401 | 59 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 24 | 71 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 908 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 87 | 34 | 32 | 0 | 0 | 0 | 34 | 29 | 88 | 0 | 34 | 32 | 0 | 29 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 150 | 0 | 0 | 213 | 0 | 60 | 139 | 0 | 422 | 94 | 168 | 70 | 105 | 82 | 0 | 0 | 55 | 1090 | 222 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7640 | 4918 | 12558 | 3703 | 908 | 1570 | 736 | 3348 | 1288 | 127 | 213 | 798 | 80 | 0 | 0 | 91.4
2:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 277 | 161 |  | 0 | 180 | 0 | 41 | 0 | 50 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 51 | 51 | 31 | 82 | 35 | 19 | 31 | 0 | 0 | 0 | 280 | 260 | 129 | 8 | 0 | 40 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 78 | 108 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 65 | 40 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 160 | 268 | 192 | 96 | 117 | 60 | 149 | 0 | 90 | 120 | 135 | 401 | 60 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 9 | 64 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 908 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 87 | 33 | 32 | 0 | 0 | 0 | 34 | 29 | 88 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 156 | 0 | 0 | 213 | 0 | 60 | 144 | 0 | 423 | 94 | 166 | 70 | 105 | 81 | 0 | 0 | 55 | 1100 | 220 | 0 | 17 | 0 | 0 | 104 | 0 | 0 |  | 7656 | 4960 | 12616 | 3737 | 908 | 1578 | 734 | 3364 | 1299 | 127 | 213 | 791 | 78 | 0 | 0 | 91.4
3:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 290 | 174 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 51 | 51 | 31 | 82 | 38 | 19 | 31 | 0 | 0 | 0 | 280 | 260 | 138 | 8 | 0 | 37 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 76 | 108 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 63 | 40 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 0 | 120 | 268 | 120 | 96 | 116 | 31 | 149 | 0 | 88 | 120 | 129 | 400 | 59 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 9 | 64 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 909 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 86 | 32 | 32 | 0 | 0 | 0 | 34 | 28 | 88 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 161 | 0 | 0 | 130 | 0 | 30 | 149 | 0 | 423 | 94 | 168 | 70 | 105 | 82 | 0 | 0 | 55 | 1100 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7530 | 4877 | 12407 | 3777 | 909 | 1580 | 565 | 3368 | 1298 | 127 | 130 | 707 | 76 | 0 | 0 | 91.4
4:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 299 | 187 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 31 | 82 | 38 | 19 | 31 | 0 | 0 | 0 | 280 | 260 | 141 | 8 | 0 | 37 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 74 | 107 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 64 | 40 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 60 | 273 | 61 | 96 | 116 | 30 | 149 | 0 | 88 | 120 | 130 | 402 | 60 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 9 | 64 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 908 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 87 | 31 | 16 | 0 | 0 | 0 | 34 | 28 | 88 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 164 | 0 | 0 | 85 | 0 | 30 | 160 | 0 | 415 | 94 | 90 | 70 | 105 | 82 | 0 | 0 | 55 | 1080 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7472 | 4734 | 12206 | 3816 | 908 | 1604 | 367 | 3369 | 1279 | 127 | 85 | 662 | 74 | 0 | 0 | 91.93
5:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 308 | 188 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 23 | 25 | 33 | 41 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 31 | 82 | 0 | 19 | 31 | 0 | 0 | 0 | 280 | 260 | 138 | 8 | 0 | 37 | 30 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 72 | 107 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 64 | 40 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 60 | 273 | 61 | 96 | 116 | 30 | 149 | 0 | 88 | 120 | 129 | 402 | 60 | 105 | 105 | 0 | 278 | 36 | 110 | 0 | 9 | 64 | 400 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 95 | 55 | 0 |  | 909 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 30 | 62 | 40 | 87 | 27 | 16 | 0 | 0 | 0 | 34 | 28 | 88 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 198 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 417 | 94 | 70 | 70 | 105 | 82 | 0 | 0 | 55 | 1050 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7399 | 4580 | 11979 | 3816 | 909 | 1603 | 317 | 3311 | 1248 | 126 | 0 | 577 | 72 | 0 | 0 | 91.93
6:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 312 | 192 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 31 | 82 | 22 | 19 | 40 | 0 | 0 | 0 | 280 | 260 | 135 | 8 | 0 | 35 | 30 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 33 | 20 | 66 | 104 | 0 | 8 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 62 | 40 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 260 | 0 | 0 | 117 | 0 | 149 | 0 | 86 | 120 | 130 | 403 | 60 | 105 | 105 | 0 | 278 | 36 | 103 | 0 | 9 | 64 | 396 | 104 | 1 | 162 | 108 | 0 | 35 | 1 | 95 | 55 | 0 |  | 909 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 93 | 0 | 70 | 105 | 82 | 0 | 0 | 55 | 1030 | 220 | 0 | 17 | 0 | 4 | 109 | 0 | 0 |  | 7010 | 4248 | 11258 | 3808 | 909 | 1623 | 0 | 3312 | 1229 | 125 | 0 | 180 | 66 | 6 | 0 | 91.93
7:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 310 | 192 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 23 | 25 | 33 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 31 | 82 | 38 | 19 | 35 | 0 | 0 | 0 | 280 | 260 | 132 | 8 | 0 | 35 | 30 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 31 | 20 | 66 | 106 | 0 | 14 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 61 | 40 | 0 | 220 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 1 | 76 | 120 | 128 | 394 | 56 | 105 | 92 | 1 | 278 | 36 | 110 | 0 | 8 | 64 | 394 | 104 | 7 | 162 | 108 | 0 | 35 | 7 | 95 | 55 | 0 |  | 909 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 416 | 93 | 0 | 70 | 105 | 82 | 0 | 1 | 55 | 950 | 220 | 0 | 17 | 0 | 22 | 109 | 0 | 0 |  | 7013 | 4161 | 11174 | 3824 | 909 | 1647 | 0 | 3301 | 1149 | 124 | 0 | 115 | 66 | 39 | 0 | 91.38
8:00 | 0 | 0 | 0 | 180 | 260 | 89 | 0 | 303 | 187 |  | 0 | 180 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 88 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 23 | 25 | 32 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 31 | 82 | 38 | 0 | 4 | 0 | 0 | 0 | 280 | 260 | 154 | 8 | 0 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 29 | 20 | 62 | 106 | 0 | 22 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 219 | 0 | 0 | 10 | 255 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 8 | 76 | 120 | 128 | 361 | 59 | 105 | 87 | 3 | 278 | 36 | 110 | 0 | 8 | 64 | 350 | 104 | 21 | 162 | 108 | 0 | 35 | 15 | 95 | 55 | 0 |  | 909 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 330 | 93 | 0 | 70 | 105 | 82 | 0 | 1 | 55 | 850 | 183 | 0 | 17 | 2 | 50 | 109 | 0 | 0 |  | 6740 | 3893 | 10633 | 3613 | 909 | 1385 | 0 | 3276 | 1049 | 124 | 0 | 115 | 62 | 100 | 0 | 91.38
9:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 292 | 181 |  | 0 | 190 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 25 | 32 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 31 | 80 | 38 | 19 | 2 | 0 | 0 | 0 | 280 | 260 | 162 | 8 | 0 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 22 | 20 | 64 | 105 | 0 | 22 | 2 | 30 | 42 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 12 | 63 | 120 | 127 | 375 | 58 | 105 | 93 | 4 | 278 | 36 | 110 | 0 | 8 | 76 | 390 | 104 | 20 | 162 | 108 | 0 | 35 | 23 | 77 | 55 | 0 |  | 908 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 335 | 93 | 0 | 70 | 105 | 80 | 0 | 1 | 55 | 820 | 184 | 0 | 17 | 1 | 84 | 109 | 0 | 0 |  | 6857 | 3876 | 10733 | 3681 | 908 | 1416 | 0 | 3258 | 1020 | 124 | 0 | 115 | 64 | 147 | 0 | 91.38
10:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 283 | 176 |  | 0 | 190 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 21 | 25 | 32 | 41 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 31 | 76 | 37 | 19 | 2 | 0 | 0 | 0 | 300 | 250 | 150 | 8 | 0 | 36 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 22 | 20 | 66 | 105 | 0 | 22 | 2 | 30 | 42 | 0 | 0 | 0 | 0 | 58 | 40 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 148 | 3 | 90 | 120 | 122 | 402 | 58 | 105 | 105 | 3 | 265 | 36 | 110 | 0 | 8 | 77 | 398 | 104 | 14 | 162 | 108 | 0 | 35 | 33 | 76 | 55 | 0 |  | 908 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 93 | 0 | 70 | 105 | 79 | 0 | 2 | 55 | 860 | 221 | 0 | 17 | 2 | 40 | 109 | 0 | 0 |  | 6951 | 3972 | 10923 | 3720 | 908 | 1556 | 0 | 3273 | 1060 | 126 | 0 | 115 | 66 | 99 | 0 | 91.37
11:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 276 | 172 |  | 0 | 190 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 26 | 25 | 32 | 41 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 33 | 77 | 0 | 19 | 2 | 0 | 0 | 0 | 300 | 250 | 150 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 16 | 20 | 70 | 101 | 0 | 22 | 2 | 30 | 42 | 0 | 0 | 0 | 0 | 58 | 40 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 9 | 90 | 120 | 120 | 381 | 57 | 90 | 105 | 3 | 265 | 36 | 110 | 0 | 8 | 77 | 386 | 104 | 54 | 17 | 108 | 0 | 35 | 12 | 76 | 55 | 0 |  | 874 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 372 | 93 | 0 | 70 | 105 | 78 | 0 | 3 | 55 | 880 | 214 | 0 | 17 | 5 | 40 | 109 | 0 | 0 |  | 6710 | 3878 | 10588 | 3642 | 874 | 1492 | 0 | 3064 | 1079 | 124 | 0 | 115 | 70 | 128 | 0 | 91.37
12:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 272 | 153 |  | 0 | 185 | 0 | 41 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 128 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 25 | 30 | 41 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 33 | 80 | 0 | 19 | 2 | 0 | 0 | 0 | 300 | 250 | 147 | 8 | 0 | 34 | 5 | 0 | 51 | 0 | 14 | 8 | 19 | 10 | 16 | 20 | 70 | 106 | 0 | 22 | 2 | 30 | 42 | 0 | 0 | 0 | 0 | 53 | 20 | 0 | 220 | 0 | 0 | 10 | 320 | 8 | 0 | 0 | 258 | 0 | 0 | 114 | 0 | 149 | 0 | 90 | 120 | 122 | 404 | 58 | 105 | 105 | 2 | 278 | 36 | 110 | 0 | 8 | 77 | 372 | 95 | 8 | 17 | 108 | 0 | 35 | 33 | 76 | 55 | 0 |  | 874 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 355 | 93 | 0 | 70 | 105 | 82 | 0 | 4 | 55 | 950 | 214 | 0 | 17 | 2 | 42 | 109 | 0 | 0 |  | 6699 | 3906 | 10605 | 3597 | 874 | 1451 | 0 | 3094 | 1150 | 126 | 0 | 150 | 70 | 93 | 0 | 91.37
13:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 265 | 135 |  | 0 | 185 | 0 | 36 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 27 | 25 | 24 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 33 | 81 | 0 | 19 | 4 | 0 | 0 | 0 | 300 | 270 | 165 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 36 | 8 | 19 | 10 | 15 | 20 | 66 | 105 | 0 | 22 | 1 | 30 | 42 | 0 | 0 | 0 | 0 | 53 | 20 | 0 | 220 | 0 | 0 | 10 | 320 | 0 | 0 | 0 | 258 | 0 | 0 | 114 | 0 | 149 | 14 | 90 | 120 | 122 | 380 | 57 | 105 | 105 | 2 | 278 | 36 | 110 | 0 | 8 | 77 | 373 | 88 | 22 | 17 | 90 | 0 | 8 | 31 | 79 | 55 | 0 |  | 874 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 21 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 34 | 16 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 322 | 93 | 0 | 70 | 105 | 82 | 0 | 4 | 55 | 940 | 210 | 0 | 17 | 5 | 89 | 109 | 0 | 0 |  | 6644 | 3899 | 10543 | 3551 | 874 | 1397 | 0 | 3039 | 1139 | 127 | 0 | 182 | 66 | 168 | 0 | 91.36
14:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 246 | 121 |  | 0 | 180 | 0 | 32 | 0 | 40 | 0 | 0 | 0 | 28 | 93 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 25 | 25 | 24 | 46 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 80 | 31 | 19 | 6 | 0 | 0 | 0 | 300 | 290 | 164 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 42 | 12 | 19 | 10 | 0 | 20 | 108 | 96 | 0 | 22 | 2 | 29 | 42 | 0 | 0 | 0 | 0 | 57 | 20 | 0 | 220 | 0 | 0 | 10 | 310 | 0 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 149 | 19 | 90 | 120 | 118 | 401 | 57 | 105 | 105 | 5 | 280 | 36 | 110 | 0 | 8 | 77 | 382 | 95 | 28 | 17 | 72 | 0 | 35 | 7 | 40 | 55 | 0 |  | 874 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 0 | 16 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 34 | 16 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 315 | 80 | 0 | 70 | 105 | 86 | 0 | 4 | 55 | 940 | 216 | 0 | 17 | 5 | 24 | 108 | 0 | 0 |  | 6672 | 3788 | 10460 | 3559 | 874 | 1348 | 0 | 3032 | 1139 | 127 | 0 | 179 | 108 | 94 | 0 | 91.36
15:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 237 | 132 |  | 0 | 170 | 0 | 37 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 25 | 25 | 24 | 48 | 0 | 40 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 14 | 0 | 33 | 80 | 27 | 19 | 7 | 0 | 0 | 0 | 300 | 290 | 163 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 47 | 11 | 19 | 10 | 16 | 20 | 122 | 102 | 0 | 22 | 1 | 30 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 10 | 325 | 0 | 0 | 0 | 258 | 0 | 0 | 113 | 0 | 147 | 16 | 90 | 120 | 118 | 375 | 53 | 99 | 105 | 1 | 283 | 36 | 110 | 0 | 8 | 52 | 393 | 104 | 22 | 17 | 81 | 0 | 35 | 9 | 35 | 55 | 0 |  | 873 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 14 | 16 | 0 | 0 | 0 | 34 | 5 | 55 | 0 | 34 | 16 | 8 | 25 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 279 | 74 | 0 | 70 | 105 | 83 | 0 | 4 | 55 | 950 | 219 | 0 | 17 | 0 | 22 | 108 | 0 | 0 |  | 6636 | 3893 | 10529 | 3579 | 873 | 1342 | 0 | 3006 | 1149 | 75 | 0 | 308 | 122 | 75 | 0 | 91.36
16:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 224 | 132 |  | 0 | 150 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 25 | 24 | 49 | 0 | 86 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 43 | 14 | 33 | 68 | 31 | 19 | 9 | 0 | 0 | 0 | 300 | 290 | 167 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 16 | 20 | 112 | 103 | 0 | 22 | 1 | 5 | 42 | 0 | 0 | 0 | 0 | 59 | 20 | 0 | 220 | 0 | 0 | 10 | 320 | 8 | 0 | 0 | 245 | 0 | 0 | 114 | 0 | 149 | 0 | 90 | 120 | 118 | 402 | 53 | 91 | 105 | 3 | 285 | 36 | 110 | 0 | 8 | 50 | 382 | 104 | 28 | 17 | 108 | 0 | 35 | 8 | 35 | 55 | 0 |  | 872 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 19 | 16 | 0 | 0 | 0 | 34 | 5 | 55 | 0 | 34 | 16 | 8 | 28 | 12 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 285 | 73 | 0 | 70 | 105 | 82 | 0 | 3 | 55 | 940 | 219 | 0 | 17 | 2 | 11 | 107 | 0 | 0 |  | 6662 | 3872 | 10534 | 3546 | 872 | 1325 | 0 | 3009 | 1139 | 121 | 0 | 354 | 112 | 56 | 0 | 91.35
17:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 224 | 151 |  | 0 | 150 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 25 | 25 | 24 | 49 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 43 | 48 | 33 | 74 | 34 | 19 | 15 | 0 | 0 | 0 | 300 | 290 | 164 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 16 | 20 | 116 | 103 | 0 | 22 | 1 | 12 | 42 | 0 | 0 | 0 | 0 | 59 | 20 | 0 | 220 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 245 | 0 | 0 | 115 | 0 | 138 | 1 | 90 | 126 | 132 | 402 | 53 | 105 | 105 | 1 | 260 | 36 | 110 | 0 | 12 | 50 | 400 | 96 | 9 | 17 | 108 | 0 | 35 | 7 | 35 | 55 | 0 |  | 872 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 10 | 5 | 40 | 81 | 17 | 16 | 0 | 0 | 0 | 34 | 6 | 55 | 0 | 34 | 16 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 285 | 64 | 0 | 90 | 105 | 83 | 0 | 2 | 90 | 910 | 223 | 0 | 17 | 0 | 19 | 107 | 0 | 0 |  | 6778 | 3914 | 10692 | 3587 | 872 | 1346 | 0 | 3090 | 1109 | 115 | 0 | 417 | 116 | 40 | 0 | 91.35
18:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 262 | 171 |  | 0 | 170 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 98 | 0 | 0 | 0 | 0 | 17 | 36 | 55 | 22 | 25 | 25 | 0 | 24 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 33 | 81 | 38 | 19 | 9 | 0 | 0 | 0 | 300 | 290 | 168 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 16 | 20 | 110 | 105 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 20 | 0 | 220 | 0 | 0 | 10 | 260 | 8 | 0 | 0 | 252 | 0 | 0 | 85 | 0 | 129 | 0 | 90 | 186 | 133 | 377 | 53 | 105 | 105 | 0 | 190 | 36 | 95 | 0 | 13 | 50 | 380 | 96 | 8 | 17 | 108 | 0 | 35 | 2 | 35 | 55 | 0 |  | 871 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 40 | 5 | 40 | 82 | 22 | 16 | 0 | 0 | 0 | 34 | 7 | 55 | 0 | 34 | 24 | 16 | 28 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 287 | 53 | 0 | 110 | 105 | 87 | 0 | 0 | 95 | 810 | 191 | 0 | 17 | 0 | 3 | 107 | 0 | 0 |  | 6750 | 3835 | 10585 | 3593 | 871 | 1311 | 0 | 3123 | 1009 | 123 | 0 | 432 | 110 | 13 | 0 | 91.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 275 | 181 |  | 0 | 170 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 25 | 24 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 44 | 51 | 33 | 81 | 37 | 19 | 18 | 0 | 0 | 0 | 300 | 290 | 170 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 17 | 20 | 130 | 105 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 255 | 0 | 0 | 100 | 0 | 126 | 0 | 90 | 200 | 132 | 403 | 70 | 105 | 105 | 0 | 250 | 36 | 92 | 0 | 18 | 60 | 380 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 872 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 47 | 33 | 40 | 82 | 29 | 16 | 0 | 0 | 0 | 34 | 7 | 85 | 0 | 34 | 32 | 48 | 28 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 286 | 69 | 0 | 113 | 105 | 92 | 0 | 0 | 95 | 960 | 217 | 0 | 17 | 0 | 0 | 107 | 0 | 0 |  | 7069 | 4147 | 11216 | 3658 | 872 | 1409 | 0 | 3332 | 1159 | 123 | 0 | 533 | 130 | 0 | 0 | 91.34
19:30 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 287 | 191 |  | 0 | 170 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 10 | 25 | 28 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 33 | 81 | 38 | 19 | 11 | 0 | 0 | 0 | 300 | 290 | 167 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 20 | 20 | 128 | 105 | 0 | 22 | 0 | 44 | 42 | 0 | 0 | 0 | 0 | 58 | 50 | 0 | 220 | 0 | 0 | 10 | 325 | 8 | 0 | 0 | 255 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 130 | 403 | 102 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 18 | 65 | 397 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 871 | 0 | 190 | 0 | 21 | 0 | 0 | 0 | 42 | 58 | 40 | 86 | 29 | 48 | 0 | 0 | 0 | 34 | 11 | 85 | 0 | 34 | 32 | 0 | 28 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 286 | 80 | 0 | 113 | 105 | 102 | 0 | 0 | 95 | 1070 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7320 | 4299 | 11619 | 3682 | 871 | 1465 | 0 | 3516 | 1269 | 123 | 0 | 565 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 285 | 192 |  | 0 | 170 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 25 | 28 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 61 | 33 | 82 | 38 | 19 | 12 | 0 | 0 | 0 | 280 | 290 | 177 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 23 | 20 | 124 | 106 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 65 | 50 | 0 | 220 | 0 | 0 | 10 | 320 | 8 | 0 | 0 | 255 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 132 | 365 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 18 | 72 | 370 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 872 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 42 | 60 | 40 | 79 | 29 | 48 | 0 | 0 | 0 | 34 | 21 | 85 | 0 | 34 | 32 | 1 | 28 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 317 | 80 | 0 | 113 | 105 | 102 | 0 | 0 | 95 | 1080 | 167 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7284 | 4316 | 11600 | 3633 | 872 | 1441 | 0 | 3541 | 1279 | 123 | 0 | 587 | 124 | 0 | 0 | 91.34
21:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 288 | 198 |  | 0 | 170 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 25 | 25 | 28 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 42 | 61 | 33 | 85 | 38 | 19 | 30 | 0 | 0 | 0 | 300 | 290 | 208 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 45 | 8 | 19 | 10 | 25 | 20 | 128 | 106 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 255 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 130 | 404 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 18 | 77 | 396 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 857 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 42 | 60 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 34 | 22 | 85 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 127 | 0 | 0 | 3 | 0 | 0 | 142 | 0 | 325 | 93 | 0 | 113 | 105 | 103 | 0 | 0 | 95 | 1060 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7364 | 4378 | 11742 | 3759 | 857 | 1494 | 0 | 3543 | 1259 | 123 | 3 | 579 | 128 | 0 | 0 | 91.34
22:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 291 | 198 |  | 0 | 180 | 0 | 42 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 24 | 25 | 28 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 61 | 33 | 87 | 38 | 19 | 35 | 0 | 0 | 0 | 300 | 290 | 208 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 48 | 8 | 21 | 10 | 30 | 20 | 136 | 105 | 0 | 19 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 220 | 0 | 0 | 10 | 315 | 8 | 0 | 0 | 255 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 200 | 128 | 404 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 19 | 77 | 392 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 857 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 40 | 57 | 40 | 84 | 29 | 48 | 0 | 0 | 0 | 34 | 22 | 87 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 133 | 0 | 0 | 16 | 0 | 0 | 143 | 0 | 350 | 93 | 0 | 113 | 105 | 104 | 0 | 0 | 95 | 1060 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7419 | 4421 | 11840 | 3767 | 857 | 1537 | 0 | 3555 | 1259 | 123 | 16 | 606 | 136 | 0 | 0 | 91.33
23:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 298 | 199 |  | 0 | 190 | 0 | 38 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 61 | 33 | 87 | 38 | 19 | 36 | 0 | 0 | 0 | 300 | 290 | 209 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 21 | 10 | 0 | 20 | 136 | 103 | 0 | 13 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 325 | 8 | 0 | 0 | 253 | 0 | 0 | 171 | 0 | 135 | 0 | 90 | 200 | 132 | 393 | 105 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 396 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 766 | 0 | 210 | 0 | 32 | 0 | 0 | 0 | 40 | 57 | 40 | 82 | 29 | 48 | 0 | 0 | 0 | 34 | 25 | 89 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 0 | 66 | 0 | 0 | 144 | 0 | 350 | 87 | 0 | 113 | 88 | 105 | 0 | 0 | 95 | 1070 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7346 | 4390 | 11736 | 3754 | 766 | 1559 | 0 | 3465 | 1269 | 125 | 66 | 662 | 136 | 0 | 0 | 91.33
24:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 301 | 207 |  | 0 | 190 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 61 | 33 | 87 | 38 | 19 | 36 | 0 | 0 | 0 | 300 | 290 | 211 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 21 | 138 | 106 | 0 | 11 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 315 | 8 | 0 | 0 | 263 | 0 | 0 | 117 | 0 | 134 | 0 | 90 | 200 | 140 | 403 | 59 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 9 | 50 | 394 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 765 | 0 | 205 | 0 | 32 | 0 | 0 | 0 | 40 | 57 | 40 | 82 | 35 | 48 | 0 | 0 | 0 | 34 | 24 | 89 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 361 | 75 | 0 | 70 | 88 | 105 | 0 | 0 | 55 | 1070 | 221 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7274 | 4441 | 11715 | 3795 | 765 | 1575 | 0 | 3257 | 1270 | 126 | 199 | 789 | 138 | 0 | 0 | 91.33
KWH | 0 | 0 | 0 | 4315500 | 7033045 | 2083590 | 0 | 6815740 | 4120000 |  | 0 | 3658500 | 0 | 956160 | 0 | 1175085 | 0 | 0 | 0 | 771283 | 2211264 | 2870400 | 0 | 0 | 0 | 0 | 634320 | 272699 | 325044 | 348192 | 600000 | 521460 | 541500 | 709800 | 1087200 | 0 | 2124851 | 844000 | 2400000 | 0 | 605914 | 0 | 0 | 0 | 0 |  | 470400 | 685920 | 704498 | 771000 | 1954560 | 715200 | 440448 | 446400 | 0 | 0 | 0 | 7323400 | 6701000 | 3885000 | 200727 | 0 | 568872 | 324480 | 0 | 1135588 | 0 | 801808 | 209083 | 448740 | 238320 | 586400 | 530960 | 2247360 | 2447040 | 0 | 357048 | 15550 | 748000 | 958080 | 0 | 0 | 0 | 0 | 1411776 | 888960 | 0 | 5246730 | 0 | 0 | 237060 | 7483000 | 162576 | 0 | 655296 | 6220034 | 755974 | 542709 | 3012000 | 259966 | 3561552 | 91935 | 2035200 | 3965760 | 3082836 | 9466000 | 1578000 | 2467200 | 2507418 | 29279 | 6531164 | 907910 | 2546716 | 0 | 281400 | 1610880 | 9274200 | 2480640 | 264800 | 1956960 | 2527909 | 0 | 855720 | 152779 | 1549440 | 1341000 | 0 |  | 21265454 | 0 | 5668992 | 0 | 453120 | 0 | 0 | 0 | 421920 | 644992 | 946125 | 2048998 | 572566 | 615072 | 0 | 0 | 0 | 523504 | 297254 | 1214712 | 0 | 771072 | 415500 | 200160 | 389770 | 446640 | 0 | 254370 | 0 | 0 | 4849600 | 0 | 0 | 3720691 | 0 | 0 | 1077382 | 0 | 240000 | 3728000 | 0 | 8507491 | 2069760 | 725253 | 2045856 | 2549376 | 2094998 | 0 | 31830 | 1607520 | 25294800 | 5120427 | 0 | 468000 | 26340 | 460800 | 2577792 | 0 | 0 |  | 170884208 | 104346137 | 275230345 | 89500878 | 21265454 | 35225429 | 3179198 | 79577802 | 30144400 | 2968851 | 1077382 | 8970278 | 2247360 | 1073313 | 0
Fuel Cost | 0 | 0 | 0 | 6430095 | 7877010.4 | 2771174.7 | 0 | 7156527 | 4449600 |  | 0 | 3987765 | 0 | 10689868.8 | 0 | 15569876.25 | 0 | 0 | 0 | 11276157.46 | 31112484.48 | 46529184 | 0 | 0 | 0 | 0 | 8068550.4 | 3681436.5 | 4358840.04 | 261144 | 450000 | 0 | 0 | 0 | 18493272 | 0 | 573709.77 | 227880 | 4536000 | 0 | 9906693.9 | 0 | 0 | 0 | 0 |  | 6138720 | 11441145.6 | 11990555.96 | 10416210 | 24783820.8 | 8274864 | 559368.96 | 1486512 | 0 | 0 | 0 | 8128974 | 7304090 | 4506600 | 258937.83 | 0 | 642825.36 | 483475.2 | 0 | 1896431.96 | 0 | 13847224.16 | 2812166.35 | 614773.8 | 178740 | 1026200 | 398220 | 16136044.8 | 2667273.6 | 0 | 485585.28 | 247867 | 1024760 | 1264665.6 | 0 | 0 | 0 | 0 | 2738845.44 | 2026828.8 | 0 | 5299197.3 | 0 | 0 | 469378.8 | 7483000 | 121932 | 0 | 13735004.16 | 84903464.1 | 15845215.04 | 11217795.03 | 40601760 | 5373497.22 | 49327495.2 | 1074720.15 | 21003264 | 54172281.6 | 40909233.72 | 8708720 | 19188480 | 35675712 | 31718837.7 | 0 | 76675865.36 | 9887139.9 | 27071591.08 | 0 | 3627246 | 18976166.4 | 8532264 | 32124288 | 3826360 | 24833822.4 | 28767604.42 | 0 | 11175703.2 | 1825709.05 | 23195116.8 | 17660970 | 0 |  | 63796362 | 0 | 6349271.04 | 0 | 4716979.2 | 0 | 0 | 0 | 7598779.2 | 11609856 | 13595816.25 | 2294877.76 | 1110778.04 | 6704284.8 | 0 | 0 | 0 | 8779162.08 | 5198972.46 | 18998095.68 | 0 | 12768952.32 | 7026105 | 2728180.8 | 6575419.9 | 924544.8 | 0 | 192558.09 | 0 | 0 | 25654384 | 0 | 0 | 4316001.56 | 0 | 0 | 18811089.72 | 0 | 5035200 | 4324480 | 0 | 8422416.09 | 27817574.4 | 15208555.41 | 24202476.48 | 36838483.2 | 26606474.6 | 0 | 351721.5 | 19515292.8 | 227906148 | 5222835.54 | 0 | 3463200 | 297905.4 | 5405184 | 39517551.36 | 0 | 0 |  | 1077197830.83 | 679885969.48 | 1757083800.31 | 98391000.19 | 63796362 | 40993678.76 | 66415266.86 | 1035554269.07 | 253560532 | 801589.77 | 18811089.72 | 149594500.04 | 16136044.8 | 13029467.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 283 | 176 |  | 0 | 190 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 21 | 25 | 32 | 41 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 31 | 76 | 37 | 19 | 2 | 0 | 0 | 0 | 300 | 250 | 150 | 8 | 0 | 36 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 22 | 20 | 66 | 105 | 0 | 22 | 2 | 30 | 42 | 0 | 0 | 0 | 0 | 58 | 40 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 148 | 3 | 90 | 120 | 122 | 402 | 58 | 105 | 105 | 3 | 265 | 36 | 110 | 0 | 8 | 77 | 398 | 104 | 14 | 162 | 108 | 0 | 35 | 33 | 76 | 55 | 0 |  | 908 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 93 | 0 | 70 | 105 | 79 | 0 | 2 | 55 | 860 | 221 | 0 | 17 | 2 | 40 | 109 | 0 | 0 |  | 10923 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 288 | 198 | 0 | 0 | 170 | 0 | 40 | 0 | 40 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 25 | 25 | 28 | 50 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 61 | 33 | 85 | 38 | 19 | 30 | 0 | 0 | 0 | 300 | 290 | 208 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 45 | 8 | 19 | 10 | 25 | 20 | 128 | 106 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 255 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 130 | 404 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 18 | 77 | 396 | 104 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 857 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 42 | 60 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 34 | 22 | 85 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 325 | 93 | 0 | 113 | 105 | 103 | 0 | 0 | 95 | 1060 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 11742 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 280 | 200 | 0 | 0 | 170 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 33 | 89 | 38 | 19 | 20 | 0 | 0 | 0 | 300 | 290 | 210 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 45 | 8 | 19 | 10 | 25 | 20 | 79 | 105 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 285 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 130 | 400 | 105 | 105 | 105 | 0 | 285 | 36 | 110 | 0 | 8 | 50 | 400 | 104 | 0 | 144 | 108 | 0 | 35 |  | 75 | 55 |  |  | 875 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 42 | 60 | 40 | 82 | 30 | 48 | 0 | 0 | 0 | 34 | 22 | 85 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 360 | 93 | 0 | 113 | 105 | 103 | 0 | 0 | 95 | 1100 | 220 |  | 17 |  |  | 109
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 280 | 200 | 0 | 0 | 170 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 88 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 33 | 89 | 38 | 19 | 5 | 0 | 0 | 0 | 300 | 290 | 210 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 25 | 20 | 60 | 105 | 0 | 22 | 1.6 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 255 | 0 | 0 | 116 | 0 | 149 | 20 | 90 | 120 | 135 | 400 | 60 | 105 | 105 | 5 | 278 | 36 | 92 | 0 | 8 | 50 | 360 | 104 | 50 | 35 | 108 | 0 | 35 | 30 | 54 | 55 |  |  | 890 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 26 | 16 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 360 | 93 | 0 | 94 | 105 | 68 | 0 | 8 | 75 | 1100 | 220 |  | 17 | 6 | 100 | 109
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 349 | 274 | 0 | 0 | 210 | 0 | 39 | 0 | 55 | 0 | 0 | 0 | 32 | 86 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 51 | 51 | 33 | 89 | 38 | 19 | 8 | 0 | 0 | 0 | 300 | 290 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 14 | 12 | 100 | 100 | 0 | 19 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 285 | 0 | 0 | 0 | 257 | 0 | 0 | 116 | 0 | 149 | 12 | 90 | 120 | 137 | 375 | 58 | 105 | 105 | 1 | 267 | 36 | 92 | 0 | 8 | 50 | 360 | 89 | 5 | 35 | 108 | 0 | 17 | 12 | 54 | 55 | 0 | 0 | 912 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 23 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 22 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 302 | 93 | 0 | 0 | 88 | 83 | 0 | 1 | 55 | 950 | 154 | 0 | 0 | 1 | 20 | 109 | 0 | 0 | 0 |  |  |  |  | 92804660 |  | 0
92804660
| Minimum Generation |  | 10633 | 8:00
| Highest Generation |  | 12616 | 2:00
| Day Peak Generation |  | 10923 | 10:00
| Evening Peak Generation |  | 11739 | 21:00
| HVDC Max Flow |  | 909 | 3:00
| HVDC EvPeak Flow |  | 857 | 21:00
| Load factor L.F |  | 90.9% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-20
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10923 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 11182 | MW
Evening Peak Generation : |  | 11739 | MW Hour : | 21:00 | Available Max Generation : |  | 12051 | MW
E.P. Demand (at gen end) : |  | 14124 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 12616 | MW Hour : | 2:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 275.2303 | System Load Factor : | 90.9% | Load Shed : |  | 2085 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 386 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-20
Actual : | 91.31 | Ft.(MSL) , | Rule curve : | 87.04 | Ft.( MSL )
Gas Consumed : | Total = | 928.35 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 139384678.95
: |  | Coal : | 253560532 | Oil : | 1270375125.69 | Total : | 1663320336.64
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 763 | 18312:00 | 5732.2842 |  |  | 655 | 18.02%
Chittagong Area | 245 | 5880:00 | 1598.4644 |  |  | 220 | 31.02%
Khulna Area | 330 | 7920:00 | 2103.2525 |  |  | 290 | 35.69%
Rajshahi Area | 303 | 7272:00 | 1857.6847 |  |  | 265 | 23.35%
Cumilla Area | 253 | 6072:00 | 1585.6569 |  |  | 220 | 20.86%
Mymensingh Area | 220 | 5280:00 | 1304.6291 |  |  | 190 | 24.25%
Sylhet Area | 91 | 2184:00 | 588.7082 |  |  | 80 | 20.14%
Barisal Area | 0 | 0:00 | 476.3406 |  |  | 0 | 9.504%
Rangpur Area | 180 | 4320:00 | 1029.6012 |  |  | 165 | 14.4%
Total | 2385 |  | 16276.6219 |  |  | 2085
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rajshahi 132/33 kV T-2 & T3 transformers tripped at 10:24 from both end showing O/C, E/F relays & | [5 empty] | About 75 MW power interruption occurred under
33 kV PBS feeder fault and was switched on at 10:38. | [5 empty] | Rajshahi S/S area from 10:24 to 10:38.
b) B.Baria 132/33 kV T-1 & T-2 transformers tripped at 10:10 from both end showing O/C, E/F relays & | [5 empty] | About 10 MW power interruption occurred under
33 kV PBS feeder fault and was switched on at 10:54. | [5 empty] | B.Baria S/S area from 10:10 to 10:54.
c) Sitalakha 132/33 kV T-1 transformer was under shut down from 11:00 to 11:47 for C/M.
d) Rampura-Bashundhara 132 kV Ckt-1 tripped at 11:28 from both end showing Dist. Z1, B-phase relays
and was switched on at 11:54.
e) Chaddogram 132/33 kV T-1 transformer was under shut down from 13:31 to 14:46 for red hot maint.
f) Kurigram 132/33 kV T-1 transformer was under shut down from 11:37 to 13:17 for C/M.
g) Madanganj-Haripur 132 kV Ckt was under shut down from 19:51 to 21:41 due to red hot maintenance
at 33 kV DS.
h) Sirajganj unit-2 GT was synchronized at 20:20.
i) Bheramara HVDC-Bheramara 400 kV Ckt-3 was switched on at 20:47.
j) Thakurgaon P/P-Thakurgaon S/S 132 kV Ckt tripped at 03:36(20-07-2022) from Thakurgaon S/S end
showing Dist. C-phase relays and was switched on at 03:44(20-07-2022).
k) Bogura Confidence unit-2 was shut down at 06:43(20-07-2022) due to work on L/A at Bogura New S/S
end and was synchronized at 08:35(20-07-2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7033045 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 89 | 2083590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 288 | 6815740 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 198 | 4120000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 170 | 3658500 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 40 | 956160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 1175085 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 348192
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 32 | 771283 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2211264 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 634320 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 2870400 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 272699
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 325044
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1121460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 541500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 709800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1087200 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 255 | 6220034 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 755974
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 542709
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 259966
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3561552
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2467200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2480640
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 1956960 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 152779
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1341000
| Dhaka area Total |  |  |  | 5847 | 2522 | 60789596
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 605914
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 91935
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 715200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 123 | 2968851 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2507418
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 685920 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 61 | 704498 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 771000 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2035200 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440448
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 446400
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1954560 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29279
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 6531164 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 907910 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2546716 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 77 | 1610880
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2527909 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1349 | 30481202
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 3885000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7323400 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6701000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 568872 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 324480 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1135588
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 3082836 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 45 | 801808
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3965760
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448740
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 238320
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2247360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 586400 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 209083 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 530960 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 655296
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 281400 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 855720 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 35 | 1549440 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 1545 | 35592190
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2447040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 357048
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3012000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1578000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 264800
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 16 | 470400
| Mymensingh Area Total |  |  |  | 614 | 428 | 8144838
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 748000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 958080 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1411776 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 25 | 888960 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5246730
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 162576 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7483000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9466000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237060
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 9274200
| Sylhet Area Total |  |  |  | 2477 | 1520 | 35876382
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 857 | 21265454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 453120 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 421920 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 644992 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5668992 | FGMO & gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 946125
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 240000 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 2069760 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2549376
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 460800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1429 | 34720539
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 615072 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 572566 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 2048998 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 25294800 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5120427
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 468000 | Transformer O/L
| Barisal Area Total |  |  |  | 1958 | 1458 | 34119863
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 523504 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 22 | 297254 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 771072 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 415500 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 127 | 3720691 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 1077382
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 142 | 3728000 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 325 | 8507491 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 389770 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 446640
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 254370
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 200160 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 1214712 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 725253 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2045856
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1607520 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26340
| Rajshahi Area Total |  |  |  | 2129 | 1078 | 25951515
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4849600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 103 | 2094998 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31830
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 2577792
| Rangpur Area Total |  |  |  | 720 | 410 | 9554220
| Total |  |  |  | 21396 | 11739 | 275230345
| Eastern Grid Total |  |  |  | 14205 | 7364 | 170884208
| Western Grid Total |  |  |  | 7191 | 4375 | 104346137
| National Grid Total |  |  |  | 21396 | 11739 | 275230345
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-19
(a) ENTIRE EASTERN GRID : |  | 7432.94 | MW | (b) ENTIRE WESTERN GRID : |  | 3667.2 | MW
i) Dhaka area |  | 4037.84 | MW | i) Khulna area |  | 1429.4 | MW
ii) Chittagong area |  | 1044.1 | MW | ii) Rajshahi area |  | 1177 | MW
iii) Comilla area |  | 1069 | MW | iii) Barisal area |  | 383.8 | MW
iv) Mymensingh area |  | 862 | MW | iv) Rangpur area |  | 677 | MW
v) Sylhet area |  | 420 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11100.14 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 15 | 14:00 | Chowmuhani | 198 | 05:00 | Kaptai | 4.2 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 138 | 04:00 | Chuadanga | 106 | 01:00 | Kazla | 81 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 16:00 | Coxsbazar | 102 | 02:00 | Keranigonj | 56 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 94 | 10:00 | Cumilla(N) | 132 | 01:00 | Khagrachori | 30 | 20:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 80 | 15:00 | Cumilla(S) | 182 | 23:00 | Khulna | 87 | 23:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 63 | 03:00 | Daudkandi | 126 | 02:00 | Khulshi | 176 | 10:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 28 | 12:00 | Dhaka | 44 | 13:00 | Kishoreganj | 136 | 06:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 167 | 01:00 | Dhamrai | 108 | 00:00 | Kodda | 287 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 98 | 02:00 | Dhanmondi | 111 | 14:00 | Kulaura | 34 | 02:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 115 | 19:00 | Dohazari | 82 | 21:00 | Kurigram | 67 | 02:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 61 | 15:00 | Faridpur | 142 | 01:00 | Kushtia | 132 | 02:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 10:00 | Fatullah | 64 | 10:00 | Lalbag | 89 | 18:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 55 | 00:00 | Fenchuganj | 41 | 04:00 | Lalmonirhat | 50 | 02:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 22 | 22:00 | Feni | 100 | 22:00 | Madanganj | 92 | 23:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 103 | 23:00 | GPH | 75 | 03:00 | Madaripur | 110 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 74 | 01:00 | Ghorashal | 66 | 00:00 | Madartek | 83 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 62 | 15:00 | Goalpara | 29 | 12:00 | Madunaghat | 57 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 54 | 19:00 | Gollamari | 56 | 00:00 | Magura | 52 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 155 | 14:00 | Gopalganj | 100 | 19:30 | Mahasthangarh | 68 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 7 | 04:00 | Gulshan | 124 | 13:00 | Manikganj | 86 | 00:00 | Rampur | 16 | 00:00
Beanibazar | 50 | 04:00 | Halishahar | 93 | 11:00 | Maniknagar | 77 | 10:00 | Rangamati | 14 | 19:00
Benapole | 58 | 00:00 | HaripurSBU | 121 | 15:00 | Matarbari | 39 | 02:00 | Rangpur | 105 | 08:00
Bhaluka | 134 | 08:00 | Hasnabad | 92 | 23:00 | Matuail | 56 | 12:00 | Ruppur | 5 | 09:00
Bhandaria | 53 | 00:00 | Hathazari | 84 | 00:00 | Millgate | 58 | 15:00 | SSM | 3 | 05:00
Bhangura | 30 | 02:00 | Ishurdi | 71 | 19:30 | Mirpur | 131 | 17:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 55 | 00:00 | Jaldhaka | 60 | 03:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 204 | 23:00 | Jamalpur | 146 | 06:00 | Mithapukur | 34 | 02:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 60 | 03:00 | Jashore | 123 | 01:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 154 | 02:00 | Jhenaidah | 107 | 00:00 | Mogbazar | 130 | 14:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 23:00 | Joydebpur | 165 | 00:00 | Mongla | 30 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 146 | 00:00 | Joypurhat | 65 | 01:00 | Motijheel | 39 | 16:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 147 | 17:00 | Juldah | 21 | 04:00 | Munshiganj | 104 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 69 | 02:00 | KSRM | 29.8 | 21:00 | Mymensingh | 199 | 05:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 04:00 | Kabirpur | 266 | 17:00 | Naogaon | 122 | 03:00 | Shikalbaha | 28 | 19:00
Chapai | 66 | 05:00 | Kachua | 68 | 02:00 | Narail | 46 | 23:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 31 | 19:00 | Kallyanpur | 96 | 00:00 | Narinda | 64 | 16:00 | Shitalakhya | 114 | 12:00
Chauddagram | 47 | 01:00 | Kalurghat | 6 | 15:00 | Narshingdi | 159 | 03:00 | Sholosohor | N/A | N/A
Chhatak | 29 | 03:00 | Kamrangirchar | 47 | 10:00 | Natore | 133 | 03:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 402 | 03:00 | 379 | 11:00 | Kaliakoir | 395 | 11:00 | 381 | 14:00
| Bibiana | 407 | 00:00 | 400 | 12:00 | Payra | 421 | 08:00 | 409 | 01:00
| BIPTC | 402 | 23:00 | 392 | 12:00
| Gopalganj_I | 415 | 08:00 | 393 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 02:00 | 213 | 13:00 | Hasnabad | 227 | 00:00 | 215 | 12:00
| AKSML | 241 | 08:00 | 222 | 14:00 | Hathazari | 240 | 08:00 | 230 | 18:00
| Aminbazar | 228 | 02:00 | 212 | 03:00 | Ishurdi | 237 | 23:00 | 226 | 03:00
| Ashuganj | 240 | 00:00 | 230 | 12:00 | Jhenaidah | 231 | 08:00 | 219 | 01:00
| Baghabari | 235 | 23:00 | 227 | 03:00 | Kaliakoir | 229 | 04:00 | 217 | 14:00
| Barapukuria | 225 | 17:00 | 214 | 02:00 | Keranigonj | 228 | 03:00 | 213 | 13:00
| Barishal | 244 | 08:00 | 237 | 23:00 | Khulna(S) | 241 | 18:00 | 225 | 02:00
| Bheramara | 234 | 23:00 | 222 | 03:00 | Maniknagar | 229 | 02:00 | 216 | 14:00
| Bhulta | 231 | 02:00 | 218 | 11:00 | Meghnaghat | 231 | 01:00 | 220 | 14:00
| Bibiana | 238 | 08:00 | 230 | 14:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 23:00 | 224 | 03:00 | Rajshahi | 234 | 16:00 | 222 | 03:00
| Bogura | 229 | 17:00 | 217 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 08:00 | 239 | 00:00 | Rampura | 230 | 02:00 | 216 | 16:00
| BSRM | 235 | 17:00 | 225 | 13:00 | Shikalbaha | 239 | 19:30 | 233 | 02:00
| Cumilla(N) | 231 | 08:00 | 222 | 11:00 | Shyampur | 228 | 02:00 | 215 | 12:00
| Fenchuganj | 238 | 02:00 | 233 | 15:00 | Siddhirganj | 231 | 02:00 | 218 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 23:00 | 225 | 04:00
| GPH | 237 | 17:00 | 225 | 18:30 | Tongi | 229 | 04:00 | 217 | 13:00
| Haripur | 228 | 00:00 | 216 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 21:00 | 123 | 11:00 | Lalbag | 138 | 02:00 | 128 | 12:00
| Agargaon | 136 | 02:00 | 125 | 13:00 | Lalmonirhat | 133 | 17:00 | 119 | 02:00
| Agrabad | 140 | 17:00 | 134 | 09:00 | Madanganj | 135 | 00:00 | 126 | 15:00
| AKS | 139 | 18:30 | 132 | 02:00 | Madaripur | 138 | 07:00 | 130 | 00:00
| Aminbazar | 134 | 04:00 | 121 | 14:00 | Madartek | 135 | 20:00 | 122 | 12:00
| Amnura | 134 | 20:00 | 122 | 07:00 | Madunaghat | 140 | 17:00 | 135 | 14:00
| Ashuganj | 137 | 00:00 | 135 | 01:00 | Magura | 140 | 17:00 | 130 | 02:00
| Bagerhat | 136 | 08:00 | 125 | 01:00 | Mahasthangarh | 137 | 17:00 | 122 | 03:00
| Bakulia | 142 | 19:30 | 134 | 09:00 | Manikganj | 136 | 07:00 | 130 | 18:00
| Banani | 135 | 04:00 | 126 | 11:00 | Maniknagar | 131 | 03:00 | 122 | 12:00
| Bangabhaban | 132 | 03:00 | 122 | 12:00 | Matarbari | 134 | 12:00 | 119 | 04:00
| Barapukuria | 138 | 08:00 | 131 | 01:00 | Matuail | 135 | 01:00 | 127 | 15:00
| Barguna | 134 | 08:00 | 128 | 00:00 | Millgate | 135 | 02:00 | 126 | 14:00
| Barishal | 139 | 07:00 | 126 | 19:00 | Mirpur | 134 | 05:00 | 120 | 14:00
| Barishal-230 | 139 | 08:00 | 133 | 00:00 | Mithapukur | 137 | 17:00 | 120 | 03:00
| Baroaulia | 141 | 17:00 | 137 | 05:00 | Modern | 140 | 19:30 | 135 | 02:00
| Baroirhat | 133 | 08:00 | 125 | 21:00 | Mogbazar | 135 | 20:00 | 122 | 12:00
| Bashundhara | 135 | 02:00 | 125 | 14:00 | Mongla | 135 | 08:00 | 128 | 06:00
| BashundharaCement | 135 | 00:00 | 126 | 15:00 | Motijheel | 132 | 03:00 | 122 | 12:00
| Beanibazar | 132 | 08:00 | 126 | 04:00 | Munshiganj | 136 | 00:00 | 128 | 12:00
| Benapole | 137 | 20:00 | 126 | 01:00 | Mymensingh | 132 | 10:00 | 117 | 06:00
| Bhaluka | 133 | 10:00 | 115 | 06:00 | Naogaon | 131 | 17:00 | 116 | 02:00
| Bhandaria | 137 | 08:00 | 127 | 00:00 | Narail | 139 | 08:00 | 128 | 03:00
| Bhangura | 139 | 17:00 | 133 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 23:00 | 132 | 03:00 | Narshingdi | 137 | 16:00 | 126 | 11:00
| Bheramara(GK) | 138 | 12:00 | 135 | 03:00 | Natore | 136 | 23:00 | 125 | 03:00
| Bhulta | 129 | 00:00 | 121 | 12:00 | Nawabganj | 138 | 03:00 | 127 | 13:00
| Bog-Sherpur | 138 | 17:00 | 126 | 03:00 | Netrakona | 131 | 13:00 | 114 | 06:00
| Bogura | 139 | 23:00 | 127 | 03:00 | New | 135 | 01:00 | 126 | 14:00
| Bogura-230 | 139 | 17:00 | 129 | 07:00 | Niamatpur | 130 | 23:00 | 112 | 07:00
| Brahmanbaria | 132 | 10:00 | 129 | 18:00 | Noapara | 138 | 20:00 | 128 | 01:00
| Cantonment | 135 | 03:00 | 123 | 13:00 | Pabna | 136 | 17:00 | 130 | 03:00
| Chandpur | 135 | 00:00 | 127 | 21:00 | Palashbari | 134 | 17:00 | 119 | 02:00
| Chandraghona | 140 | 19:00 | 134 | 11:00 | Panchagarh | 142 | 17:00 | 125 | 04:00
| Chapai | 133 | 20:00 | 121 | 07:00 | Patuakhali | 135 | 07:00 | 130 | 00:00
| Charsaidpur | 138 | 04:00 | 128 | 12:00 | Payra | 138 | 08:00 | 134 | 00:00
| Chauddagram | 132 | 08:00 | 124 | 19:30 | PHP | 133 | 08:00 | 124 | 02:00
| Chhatak | 131 | 16:00 | 126 | 00:00 | Purbachal | 135 | 02:00 | 125 | 14:00
| Chowmuhani | 130 | 17:00 | 119 | 02:00 | Purbasadipur | 136 | 09:00 | 123 | 03:00
| Chuadanga | 137 | 08:00 | 123 | 01:00 | Rahim | 136 | 00:00 | 128 | 12:00
| Coxsbazar | 133 | 12:00 | 118 | 02:00 | Rajbari | 136 | 08:00 | 128 | 01:00
| Cumilla(N) | 135 | 00:00 | 128 | 21:00 | Rajendrapur | 137 | 08:00 | 129 | 18:30
| Cumilla(S) | 135 | 08:00 | 127 | 16:00 | Rajshahi | 133 | 16:00 | 125 | 07:00
| Daudkandi | 137 | 00:00 | 121 | 19:00 | Rajshahi-230 | 134 | 16:00 | 125 | 07:00
| Dhaka | 135 | 20:00 | 123 | 11:00 | Ramganj | 131 | 18:00 | 120 | 02:00
| Dhamrai | 133 | 08:00 | 127 | 11:00 | Rampur | 139 | 20:00 | 134 | 11:00
| Dhanmondi | 136 | 01:00 | 128 | 12:00 | Rampura | 135 | 20:00 | 124 | 12:00
| Dohazari | 140 | 19:30 | 131 | 07:00 | Rangamati | 140 | 17:00 | 130 | 23:00
| Faridpur | 135 | 18:00 | 128 | 01:00 | Rangpur | 136 | 17:00 | 124 | 06:00
| Fatullah | 136 | 00:00 | 127 | 12:00 | Ruppur | 138 | 23:00 | 131 | 03:00
| Fenchuganj | 135 | 10:00 | 132 | 00:00 | Saidpur | 136 | 08:00 | 120 | 02:00
| Feni | 134 | 08:00 | 125 | 02:00 | Satkhira | 135 | 18:00 | 122 | 01:00
| Ghorashal | 139 | 00:00 | 136 | 01:00 | Satmasjid | 135 | 02:00 | 124 | 13:00
| Goalpara | 138 | 08:00 | 129 | 02:00 | Savar | 134 | 08:00 | 120 | 12:00
| Gollamari | 138 | 08:00 | 128 | 01:00 | Shahjadpur | 143 | 18:00 | 137 | 12:00
| Gopalganj | 140 | 08:00 | 133 | 01:00 | Shahjibazar | 135 | 20:00 | 131 | 22:00
| Gopalganj_I | 140 | 08:00 | 134 | 04:00 | Shahmirpur | 141 | 08:00 | 134 | 09:00
| Gulshan | 135 | 20:00 | 122 | 12:00 | Shariatpur | 137 | 18:00 | 129 | 01:00
| Halishahar | 140 | 19:30 | 134 | 09:00 | Sherpur | 135 | 17:00 | 113 | 06:00
| Haripur | 136 | 00:00 | 128 | 12:00 | Shikalbaha | 142 | 19:30 | 135 | 11:00
| HaripurSBU | 136 | 00:00 | 128 | 12:00 | Shikalbaha-230 | 141 | 19:30 | 136 | 10:00
| Hasnabad | 137 | 00:00 | 128 | 15:00 | Shitalakhya | 139 | 03:00 | 127 | 16:00
| Hathazari | 140 | 08:00 | 135 | 13:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 18:00 | 133 | 05:00 | Shyampur | 133 | 00:00 | 126 | 12:00
| Jaldhaka | 135 | 16:00 | 120 | 03:00 | Shyampur-230 | 136 | 02:00 | 127 | 12:00
| Jamalpur | 137 | 10:00 | 118 | 06:00 | Siddhirganj | 135 | 00:00 | 127 | 12:00
| Jashore | 139 | 20:00 | 128 | 01:00 | Sirajganj | 137 | 17:00 | 128 | 02:00
| Jhenaidah | 141 | 08:00 | 132 | 01:00 | Sonargaon | 135 | 00:00 | 118 | 21:00
| Jhenaidah-230 | 141 | 08:00 | 132 | 01:00 | Sreemongol | 135 | 00:00 | 133 | 23:00
| Joydebpur | 141 | 00:00 | 135 | 09:00 | Srinagar | 138 | 03:00 | 127 | 12:00
| Joypurhat | 132 | 23:00 | 116 | 02:00 | SSM | 142 | 15:00 | 138 | 03:00
| Juldah | 141 | 19:30 | 135 | 07:00 | Sunamganj | 130 | 08:00 | 125 | 03:00
| Kabirpur | 139 | 08:00 | 123 | 14:00 | Sylhet | 133 | 08:00 | 130 | 12:00
| Kachua | 135 | 08:00 | 126 | 21:00 | Tangail | 136 | 08:00 | 132 | 14:00
| Kaliakoir | 139 | 05:00 | 128 | 12:00 | Thakurgaon | 140 | 17:00 | 122 | 03:00
| Kallyanpur | 132 | 00:00 | 123 | 12:00 | TK | 142 | 19:30 | 135 | 18:30
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 726 | 7274 | 4441 | 11715 |  |  |  | QF-LDC-11
0:30 | 660 | 7457 | 4679.5 | 12136.5 | Date: | 2022-07-19
1:00 | 594 | 7640 | 4918 | 12558
1:30 | 541 | 7648 | 4939 | 12587
2:00 | 488 | 7656 | 4960 | 12616
2:30 | 473 | 7593 | 4918.5 | 12511.5 | [5 empty] | Gen. at Eve. Peak | 11739 | 11739 MW (21:00 )
3:00 | 458 | 7530 | 4877 | 12407 | [6 empty] | 21:00
3:30 | 447 | 7501 | 4805.5 | 12306.5 | [5 empty] | Gen. at Day Peak | 10923 | 10923 MW (10:00 )
4:00 | 436 | 7472 | 4734 | 12206 | [6 empty] | 10:00
4:30 | 411 | 7435.5 | 4657 | 12092.5 | [5 empty] | Highest Generation | 12616
5:00 | 386 | 7399 | 4580 | 11979 | [6 empty] | 2:00
5:30 | 422 | 7204.5 | 4414 | 11618.5
6:00 | 458 | 7010 | 4248 | 11258
6:30 | 471 | 7011.5 | 4204.5 | 11216
7:00 | 484 | 7013 | 4161 | 11174
7:30 | 551 | 6876.5 | 4027 | 10903.5
8:00 | 618 | 6740 | 3893 | 10633
8:30 | 690 | 6798.5 | 3884.5 | 10683
9:00 | 762 | 6857 | 3876 | 10733
9:30 | 800 | 6904 | 3924 | 10828
10:00 | 838 | 6951 | 3972 | 10923
10:30 | 805 | 6830.5 | 3925 | 10755.5
11:00 | 772 | 6710 | 3878 | 10588
11:30 | 762 | 6704.5 | 3892 | 10596.5
12:00 | 752 | 6699 | 3906 | 10605
12:30 | 768 | 6671.5 | 3902.5 | 10574
13:00 | 784 | 6644 | 3899 | 10543
13:30 | 816 | 6658 | 3843.5 | 10501.5
14:00 | 848 | 6672 | 3788 | 10460
14:30 | 837 | 6654 | 3840.5 | 10494.5
15:00 | 826 | 6636 | 3893 | 10529
15:30 | 855 | 6649 | 3882.5 | 10531.5
16:00 | 884 | 6662 | 3872 | 10534
16:30 | 870 | 6720 | 3893 | 10613
17:00 | 856 | 6778 | 3914 | 10692
17:30 | 812 | 6764 | 3874.5 | 10638.5
18:00 | 768 | 6750 | 3835 | 10585
18:30 | 679 | 6909.5 | 3991 | 10900.5
19:00 | 590 | 7069 | 4147 | 11216
19:30 | 430 | 7320 | 4299 | 11619
20:00 | 508 | 7284 | 4316 | 11600 |  |  |  | Executive Engineer
20:30 | 483 | 7324 | 4347 | 11671 |  |  |  | Network Operation Division
21:00 | 458 | 7364 | 4378 | 11742
21:30 | 488 | 7391.5 | 4399.5 | 11791
22:00 | 518 | 7419 | 4421 | 11840 |  |  |  |  | Page 6 of 7
22:30 | 623 | 7382.5 | 4405.5 | 11788
23:00 | 728 | 7346 | 4390 | 11736
23:30 | 727 | 7310 | 4415.5 | 11725.5
24:00 | 726 | 7274 | 4441 | 11715
11739 MW (21:00 )
10923 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-19 |  | Energy |  | 275230345
[13 empty] | 2022-07-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3795 | 765 | 1575 | 0 | 3257 | 1270 | 126 | 199 | 789 | 138 | 0 | 1538
0:30 | 3749 | 836.5 | 1572.5 | 368 | 3302.5 | 1279 | 126.5 | 206 | 793.5 | 109 | 0 | 769 | Date: | 2022-07-19
1:00 | 3703 | 908 | 1570 | 736 | 3348 | 1288 | 127 | 213 | 798 | 80 | 0 | 0
1:30 | 3720 | 908 | 1574 | 735 | 3356 | 1293.5 | 127 | 213 | 794.5 | 79 | 0 | 0 | [8 empty] | Total Energy | 275.2303 | Total Energy Gen 275.230 MKWHr Energy Not Served 32.403 MKWHr Energy Requirement 307.633 MKWHr
2:00 | 3737 | 908 | 1578 | 734 | 3364 | 1299 | 127 | 213 | 791 | 78 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3757 | 908.5 | 1579 | 649.5 | 3366 | 1298.5 | 127 | 171.5 | 749 | 77 | 0 | 0 | [8 empty] | Energy Requirement | 275.2303
3:00 | 3777 | 909 | 1580 | 565 | 3368 | 1298 | 127 | 130 | 707 | 76 | 0 | 0
3:30 | 3796.5 | 908.5 | 1592 | 466 | 3368.5 | 1288.5 | 127 | 107.5 | 684.5 | 75 | 0 | 0 | [6 empty] | Shortage
4:00 | 3816 | 908 | 1604 | 367 | 3369 | 1279 | 127 | 85 | 662 | 74 | 0 | 0
4:30 | 3816 | 908.5 | 1603.5 | 342 | 3340 | 1263.5 | 126.5 | 42.5 | 619.5 | 73 | 0 | 0
5:00 | 3816 | 909 | 1603 | 317 | 3311 | 1248 | 126 | 0 | 577 | 72 | 0 | 0
5:30 | 3812 | 909 | 1613 | 158.5 | 3311.5 | 1238.5 | 125.5 | 0 | 378.5 | 69 | 3 | 0
6:00 | 3808 | 909 | 1623 | 0 | 3312 | 1229 | 125 | 0 | 180 | 66 | 6 | 0
6:30 | 3816 | 909 | 1635 | 0 | 3306.5 | 1189 | 124.5 | 0 | 147.5 | 66 | 22.5 | 0 |  |  |  |  | Coal
7:00 | 3824 | 909 | 1647 | 0 | 3301 | 1149 | 124 | 0 | 115 | 66 | 39 | 0
7:30 | 3718.5 | 909 | 1516 | 0 | 3288.5 | 1099 | 124 | 0 | 115 | 64 | 69.5 | 153.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3613 | 909 | 1385 | 0 | 3276 | 1049 | 124 | 0 | 115 | 62 | 100 | 307
8:30 | 3647 | 908.5 | 1400.5 | 0 | 3267 | 1034.5 | 124 | 0 | 115 | 63 | 123.5 | 766
9:00 | 3681 | 908 | 1416 | 0 | 3258 | 1020 | 124 | 0 | 115 | 64 | 147 | 1225
9:30 | 3700.5 | 908 | 1486 | 0 | 3265.5 | 1040 | 125 | 0 | 115 | 65 | 123 | 1366.5
10:00 | 3720 | 908 | 1556 | 0 | 3273 | 1060 | 126 | 0 | 115 | 66 | 99 | 1508
10:30 | 3681 | 891 | 1524 | 0 | 3168.5 | 1069.5 | 125 | 0 | 115 | 68 | 113.5 | 1722
11:00 | 3642 | 874 | 1492 | 0 | 3064 | 1079 | 124 | 0 | 115 | 70 | 128 | 1936
11:30 | 3619.5 | 874 | 1471.5 | 0 | 3079 | 1114.5 | 125 | 0 | 132.5 | 70 | 110.5 | 1951
12:00 | 3597 | 874 | 1451 | 0 | 3094 | 1150 | 126 | 0 | 150 | 70 | 93 | 1966
12:30 | 3574 | 874 | 1424 | 0 | 3066.5 | 1144.5 | 126.5 | 0 | 166 | 68 | 130.5 | 2105.5
13:00 | 3551 | 874 | 1397 | 0 | 3039 | 1139 | 127 | 0 | 182 | 66 | 168 | 2245
13:30 | 3551 | 874 | 1397 | 0 | 3039 | 1139 | 127 | 0 | 182 | 66 | 168 | 2245
14:00 | 3551 | 874 | 1397 | 0 | 3039 | 1139 | 127 | 0 | 182 | 66 | 168 | 2245
14:30 | 3565 | 873.5 | 1369.5 | 0 | 3022.5 | 1144 | 101 | 0 | 245 | 94 | 121.5 | 2228.5
15:00 | 3579 | 873 | 1342 | 0 | 3006 | 1149 | 75 | 0 | 308 | 122 | 75 | 2212
15:30 | 3562.5 | 872.5 | 1333.5 | 0 | 3007.5 | 1144 | 98 | 0 | 331 | 117 | 65.5 | 2303.5
16:00 | 3546 | 872 | 1325 | 0 | 3009 | 1139 | 121 | 0 | 354 | 112 | 56 | 2395
16:30 | 3587 | 872 | 1335.5 | 0 | 3049.5 | 1124 | 118 | 0 | 385.5 | 114 | 48 | 2221
17:00 | 3587 | 872 | 1346 | 0 | 3090 | 1109 | 115 | 0 | 417 | 116 | 40 | 2047
17:30 | 3590 | 871.5 | 1328.5 | 0 | 3106.5 | 1059 | 119 | 0 | 424.5 | 113 | 26.5 | 2099
18:00 | 3593 | 871 | 1311 | 0 | 3123 | 1009 | 123 | 0 | 432 | 110 | 13 | 2151
18:30 | 3625.5 | 871.5 | 1360 | 0 | 3227.5 | 1084 | 123 | 0 | 482.5 | 120 | 6.5 | 2175.5
19:00 | 3658 | 872 | 1409 | 0 | 3332 | 1159 | 123 | 0 | 533 | 130 | 0 | 2200
19:30 | 3682 | 871 | 1465 | 0 | 3516 | 1269 | 123 | 0 | 565 | 128 | 0 | 2317
20:00 | 3633 | 872 | 1441 | 0 | 3541 | 1279 | 123 | 0 | 587 | 124 | 0 | 2426
20:30 | 3696 | 864.5 | 1467.5 | 0 | 3542 | 1269 | 123 | 1.5 | 583 | 126 | 0 | 2405.5
21:00 | 3759 | 857 | 1494 | 0 | 3543 | 1259 | 123 | 3 | 579 | 128 | 0 | 2385
21:30 | 3763 | 857 | 1515.5 | 0 | 3549 | 1259 | 123 | 9.5 | 592.5 | 132 | 0 | 2289
22:00 | 3767 | 857 | 1537 | 0 | 3555 | 1259 | 123 | 16 | 606 | 136 | 0 | 2193
22:30 | 3760.5 | 811.5 | 1548 | 0 | 3510 | 1264 | 124 | 41 | 634 | 136 | 0 | 2098
23:00 | 3754 | 766 | 1559 | 0 | 3465 | 1269 | 125 | 66 | 662 | 136 | 0 | 2003
23:30 | 3774.5 | 765.5 | 1567 | 0 | 3361 | 1269.5 | 125.5 | 132.5 | 725.5 | 137 | 0 | 1770.5 | Max Temp. in Dhaka |  | 24.7° C | 34.4° C
24:00 | 3795 | 765 | 1575 | 0 | 3257 | 1270 | 126 | 199 | 789 | 138 | 0 | 1538
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 275.230 MKWHr Energy Not Served 32.403 MKWHr Energy Requirement 307.633 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-07-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 92 | 91 | 90 | 89 | 89 | 89 | 91 | 89 | 91 | 92 | 92 | 40 | 86 | 80 | 88 |  | 88 | 88 | 88 | 88 | 88 | 90 | 91 | 2124851
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 605914
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 | 12 | 3 | 9 | 0 | 14 | 19 | 16 |  | 1 | 0 | [8 empty] | 91935
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | [10 empty] | 14 | 48 | 51 |  | 51 | 51 | 61 | 61 | 61 | 61 | 61 | 704498
12 | Hathazari 100 MW peaking PP | 51 | 51 | 51 | 51 | 51 | [9 empty] | 14 | 43 | 43 | 43 |  | 44 | 51 | 51 | 42 | 51 | 51 | 51 | 685920
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 92 | 87 | 93 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2507418
| Daudkandi 200 MW PP (B.Trac) | 160 | 160 | 120 | 60 | 60 | [21 empty] | 655296
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | 49 |  |  |  |  | 0 |  | 14 | 36 | 42 | 47 | 47 | 47 | 47 |  | 47 | 48 | 48 | 45 | 48 | 49 | 49 | 801808
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 273 | 268 | 268 | 273 | 273 | 260 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 245 | 245 | 252 |  | 255 | 255 | 255 | 255 | 255 | 253 | 263 | 6220034
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7033045
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 37 | 37 | 37 | 35 | 35 | 34 | 34 | 36 | 35 | 34 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 568872
33 | Ashuganj 225 MW CCPP | 127 | 129 | 138 | 141 | 138 | 135 | 132 | 154 | 162 | 150 | 150 | 147 | 165 | 164 | 163 | 167 | 164 | 168 |  | 170 | 167 | 177 | 208 | 208 | 209 | 211 | 3885000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 250 | 270 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 6701000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 280 | 300 | 300 | 300 | 300 | 7323400
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 324480
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 268 | 277 | 290 | 299 | 308 | 312 | 310 | 303 | 292 | 283 | 276 | 272 | 265 | 246 | 237 | 224 | 224 | 262 |  | 275 | 287 | 285 | 288 | 291 | 298 | 301 | 6815740
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 190 | 190 | 190 | 185 | 185 | 180 | 170 | 150 | 150 | 170 |  | 170 | 170 | 170 | 170 | 180 | 190 | 190 | 3658500
41 | Haripur 360MW CCPP(HPL) | 156 | 161 | 174 | 187 | 188 | 192 | 192 | 187 | 181 | 176 | 172 | 153 | 135 | 121 | 132 | 132 | 151 | 171 |  | 181 | 191 | 192 | 198 | 198 | 199 | 207 | 4120000
42 | RPCL 210MW CCPP | 107 | 108 | 108 | 107 | 107 | 104 | 106 | 106 | 105 | 105 | 101 | 106 | 105 | 96 | 102 | 103 | 103 | 105 |  | 105 | 105 | 106 | 106 | 105 | 103 | 106 | 2447040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 21 | 20 | 14 | 54 | 8 | 22 | 28 | 22 | 28 | 9 | 8 | [8 empty] | 264800
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 30 | 5 | 12 | 43 |  | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 748000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 958080
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 65 | 63 | 64 | 64 | 62 | 61 | 40 | 40 | 58 | 58 | 53 | 53 | 57 | 58 | 59 | 59 | 61 |  | 58 | 58 | 65 | 62 | 60 | 62 | 62 | 1411776
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 50 | 50 | 25 | 25 | 25 | 25 | 888960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5246730
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237060
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 162576
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 270 | 290 | 290 | 300 | 330 | 255 | 280 | 310 | 300 | 320 | 320 | 310 | 325 | 320 | 305 | 260 |  | 305 | 325 | 320 | 310 | 315 | 325 | 315 | 7483000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 396 | 394 | 350 | 390 | 398 | 386 | 372 | 373 | 382 | 393 | 382 | 400 | 380 |  | 380 | 397 | 370 | 396 | 392 | 396 | 394 | 9274200
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 325044
59 | Tangail Palli Power Gen 22 MW | 16 | 11 | 12 | 22 | 22 | 22 | 22 | 22 | 18 | 19 | 22 | 23 | 22 | 18 | 18 | 22 | 18 | 12 |  | 22 | 22 | 22 | 16 | 18 | 23 | 23 | 470400
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440448
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | [9 empty] | 19 | 19 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 348192
62 | Tangail 22 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 19 | 13 | 11 | 357048
63 | Impoprt (Tripura) | 80 | 78 | 76 | 74 | 72 | 66 | 66 | 62 | 64 | 66 | 70 | 70 | 66 | 108 | 122 | 112 | 116 | 110 |  | 130 | 128 | 124 | 128 | 136 | 136 | 138 | 2247360
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 31 | 31 | 31 | 40 | 35 | 4 | 2 | 2 | 2 | 2 | 4 | 6 | 7 | 9 | 15 | 9 |  | 18 | 11 | 12 | 30 | 35 | 36 | 36 | 446400
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 21 | 21 | 19 | 448740
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238320
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 29 | 22 | 22 | 16 | 16 | 15 |  | 16 | 16 | 16 | 16 |  | 17 | 20 | 23 | 25 | 30 | 0 | 33 | 586400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 530960
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 21 | 23 | 23 | 10 | 21 | 26 | 20 | 27 | 25 | 25 | 25 | 25 | 25 |  | 25 | 10 | 25 | 25 | 24 | 27 | 27 | 521460
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 541500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 30 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 28 | 28 | 28 | 28 | 30 | 30 | 709800
73 | Ghorashal 108MW PP (Regent) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 85 | 85 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2083590
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 24 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 13 |  | 18 | 18 | 18 | 18 | 19 | 8 | 9 | 281400
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 1956960
77 | Siddhirganj 100 PP(Dutch Bangla) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 771283
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 46 | 48 | 49 | 49 | 49 |  | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 1087200
79 | Kodda 150MW PP | 130 | 130 | 130 | 130 | 130 | 130 | 115 | 115 | 115 | 115 | 115 | 128 | 125 | 112 | 112 | 112 | 125 | 98 |  | 125 | 125 | 125 | 125 | 130 | 130 | 125 | 2870400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 11 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 209083
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 105 | 105 | 99 | 91 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2467200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 3 | 3 | 2 | 2 | 5 | 1 | 3 | 1 | 0 | [8 empty] | 29279
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 907910
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 103 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 95 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2546716
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 41 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 36 | 32 | 37 | 40 | 39 | 40 |  | 40 | 39 | 39 | 40 | 42 | 38 | 40 | 956160
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 95 | 88 | 95 | 104 | 104 | 96 | 96 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2480640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 771000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1135588
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 88 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2211264
95 | Patenga 50MW PP (Baraka) | 8 | 35 | 38 | 38 |  | 22 | 38 | 38 | 38 | 37 | 0 |  |  | 31 | 27 | 31 | 34 | 38 |  | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 715200
96 | Chattogram 108 MW PP (ECPV) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 80 | 76 | 77 | 80 | 81 | 80 | 80 | 68 | 74 | 81 |  | 81 | 81 | 82 | 85 | 87 | 87 | 87 | 1954560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 55 | 55 | 55 | 1175085
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 36 |  | 55 | 55 | 55 | 55 | 55 | 35 | 0 | 272699
101 | Kushiara 163 MW CCPP (KP) | [26 empty] | 0
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 |  | 0 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 15550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 634320
104 | Keranigonj 300 MW PP (APR) | 192 | 192 | 120 | 61 | 61 | [21 empty] | 755974
105 | Bramhangoan 100 MW PP (Aggreko) | 96 | 96 | 96 | 96 | 96 | [21 empty] | 542709
106 | Mymensingh 200 MW PP (United) | 117 | 117 | 116 | 116 | 116 | 117 | 115 | 115 | 115 | 115 | 115 | 114 | 114 | 115 | 113 | 114 | 115 | 85 |  | 100 | 180 | 180 | 180 | 171 | 171 | 117 | 3012000
112 | Aurahati 100MW PP (Aggreko) | 60 | 60 | 31 | 30 | 30 | [21 empty] | 259966
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 148 | 149 | 149 | 149 | 149 | 147 | 149 | 138 | 129 |  | 126 | 149 | 149 | 149 | 149 | 135 | 134 | 3561552
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 88 | 88 | 88 | 86 | 76 | 76 | 63 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2035200
116 | Chandpur 200MW (Desh energy) | 137 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 126 | 186 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3965760
117 | Ashuganj 150MW PP (Midland) | 138 | 135 | 129 | 130 | 129 | 130 | 128 | 128 | 127 | 122 | 120 | 122 | 122 | 118 | 118 | 118 | 132 | 133 |  | 132 | 130 | 132 | 130 | 128 | 132 | 140 | 3082836
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 400 | 402 | 402 | 403 | 394 | 361 | 375 | 402 | 381 | 404 | 380 | 401 | 375 | 402 | 402 | 377 |  | 403 | 403 | 365 | 404 | 404 | 393 | 403 | 9466000
| Jamalpur 115 MW PP (United) | 59 | 60 | 59 | 60 | 60 | 60 | 56 | 59 | 58 | 58 | 57 | 58 | 57 | 57 | 53 | 53 | 53 | 53 |  | 70 | 102 | 104 | 104 | 104 | 105 | 59 | 1578000
| Anwara 300 MW PP (United) | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 265 | 265 | 278 | 278 | 280 | 283 | 285 | 260 | 190 |  | 250 | 285 | 285 | 285 | 285 | 285 | 285 | 6531164
| Juldah unit-2 (Acorn) | 71 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 76 | 77 | 77 | 77 | 77 | 77 | 52 | 50 | 50 | 50 |  | 60 | 65 | 72 | 77 | 77 | 50 | 50 | 1610880
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 90 | 72 | 81 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2527909
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 8 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 855720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 15 | 23 | 33 | 12 | 33 | 31 | 7 | 9 | 8 | 7 | 2 | [8 empty] | 152779
| Chandpur 115(Doreen) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 77 | 76 | 76 | 76 | 79 | 40 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 1549440
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1341000
120 | Eastern Zone Total | 7640 | 7656 | 7530 | 7472 | 7399 | 7010 | 7013 | 6740 | 6857 | 6951 | 6710 | 6699 | 6644 | 6672 | 6636 | 6662 | 6778 | 6750 |  | 7069 | 7320 | 7284 | 7364 | 7419 | 7346 | 7274 | 170884208
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 21 | 32 | 32 | 32 | 32 | 32 | 453120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | [11 empty] | 10 | 40 |  | 47 | 42 | 42 | 42 | 40 | 40 | 40 | 421920
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 94 | 94 | 94 | 94 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 80 | 74 | 73 | 64 | 53 |  | 69 | 80 | 80 | 93 | 93 | 87 | 75 | 2069760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 22 | 50 | 84 | 40 | 40 | 42 | 89 | 24 | 22 | 11 | 19 | 3 | [8 empty] | 460800
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 468000
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 220 | 220 | 220 | 220 | 220 | 220 | 183 | 184 | 221 | 214 | 214 | 210 | 216 | 219 | 219 | 223 | 191 |  | 217 | 220 | 167 | 220 | 220 | 220 | 221 | 5120427
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 615072
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 87 | 86 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 82 | 82 | 83 | 83 | 82 | 82 | 81 | 82 |  | 82 | 86 | 79 | 82 | 84 | 82 | 82 | 2048998
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 31 | 27 | 27 | 24 | 21 | 19 | 21 | 20 | 21 | 21 |  | 14 | 19 | 17 | 22 |  | 29 | 29 | 29 | 31 | 29 | 29 | 35 | 572566
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 60 | 30 | 30 | [22 empty] | 240000
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 946125
143 | Gopalganj 100 MW Peaking PP | 62 | 62 | 62 | 62 | 62 | [11 empty] | 5 | 5 |  | 33 | 58 | 60 | 60 | 57 | 57 | 57 | 644992
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 2549376
146 | Bheramara HVDC | 908 | 908 | 909 | 908 | 909 | 909 | 909 | 909 | 908 | 908 | 874 | 874 | 874 | 874 | 873 | 872 | 872 | 871 |  | 872 | 871 | 872 | 857 | 857 | 766 | 765 | 21265454
147 | Bheramara 410 MW CCPP | 255 | 265 | 280 | 290 | 290 | 285 | 305 | 240 | 240 | 245 | 230 | 210 | 200 | 195 | 200 | 190 | 190 | 190 |  | 190 | 190 | 200 | 200 | 200 | 210 | 205 | 5668992
148 | Payra 1320 MW | 1090 | 1100 | 1100 | 1080 | 1050 | 1030 | 950 | 850 | 820 | 860 | 880 | 950 | 940 | 940 | 950 | 940 | 910 | 810 |  | 960 | 1070 | 1080 | 1060 | 1060 | 1070 | 1070 | 25294800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 198 | 199 | 198 | 199 | 198 | 199 | 199 | 199 | 200 | 200 | 199 | 200 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 4849600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | [8 empty] | 4 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 523504
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 2 | 5 | 2 | 5 | 5 | 0 | 2 | 0 | 0 | [8 empty] | 26340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 156 | 161 | 164 | 174 | 182 | 187 | 183 | 169 | 154 | 147 | 137 | 127 | 113 | 121 | 125 | 124 | 124 |  | 125 | 125 | 125 | 127 | 133 | 141 | 141 | 3720691
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 213 | 213 | 130 | 85 | [18 empty] | 3 | 16 | 66 | 199 | 1077382
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 139 | 144 | 149 | 160 | 163 | 163 | 163 | 160 | 153 | 147 | 141 | 133 | 131 | 132 | 141 | 141 | 140 | 138 |  | 138 | 139 | 139 | 142 | 143 | 144 | 144 | 3728000
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 422 | 423 | 423 | 415 | 417 | 414 | 416 | 330 | 335 | 414 | 372 | 355 | 322 | 315 | 279 | 285 | 285 | 287 |  | 286 | 286 | 317 | 325 | 350 | 350 | 361 | 8507491
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 29 | 29 | 28 | 28 | 28 | [7 empty] | 5 | 5 | 5 | 5 | 6 | 7 |  | 7 | 11 | 21 | 22 | 22 | 25 | 24 | 297254
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 18 | 17 | 17 | 17 | 12 | 17 | 18 |  | 20 | 20 | 21 | 22 | 22 | 22 | 22 | 446640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 254370
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 771072
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | [6 empty] | 8 | 16 | 16 | 16 | 16 | 16 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 415500
168 | Santahar 50 MW Peaking PP | 29 | 22 | 22 | 22 | 22 | [9 empty] | 25 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 389770
169 | Natore 52 MW PP (Rajlanka) | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 48 |  | 1 | 8 | 8 | 8 | 8 | 200160
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 50 | [7 empty] | 0 | 55 | 55 | 55 | 55 |  | 85 | 85 | 85 | 85 | 87 | 89 | 89 | 1214712
171 | Baghabari 200 MW PP (Paramount) | 168 | 166 | 168 | 90 | 70 | [21 empty] | 725253
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 110 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2045856
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 90 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1607520
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 82 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 80 | 79 | 78 | 82 | 82 | 86 | 83 | 82 | 83 | 87 |  | 92 | 102 | 102 | 103 | 104 | 105 | 105 | 2094998
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [8 empty] | 31830
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 104 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 107 | 107 | 107 |  | 107 | 108 | 108 | 108 | 108 | 108 | 109 | 2577792
178