## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-21 | Thursday
|  |  | Date (day): | 2022-07-21 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11639.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12570 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-20 | 2022-07-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 88 | 89 | 89 |  | 19 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 361 | 334 | 300 | 330 | 82 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 278 | 243 | 200 | 250 | 110 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 30 | 40 | 40 |  | 60 | Engine problem
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 32 | 32 | 32 | 68 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 88 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54 |  |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 132 | 115 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 49 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 28 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 257 | 275 | 255 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 143 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 89 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 35 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 40 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2639 | 2859 | 2591 | 2882 | 1916 | 1053
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 38 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 125 | 125 | 125 |  | 105 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 41 | 51 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 51 | 68 | 34 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 30 | 30 | 30 | 70 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 30 | 5 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 90 | 90 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 177 | 285 | 278 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 92 | 92 | 92 |  | 18 | Engine problem
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 38 | 50 | 50
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1174 | 1273 | 1261 | 1285 | 431 | 616
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 209 | 208 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 280 | 290 | 300 | 60 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 41 | 20 | 40 |  | 5 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 133 | 140 | 135 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 49 | 41 | 49
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Grid problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 120 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 126 | 120 | 126
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 31 | 25 | 31
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 16 | 36 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 99 | 0 | 70 | 44 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 56 | 8 | 56 | 57 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 23 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 76 | 54 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1361 | 1750 | 1479 | 1761 | 868 | 202
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 83 | 106 | 105 | 110 |  | 92 | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 14 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 194 | 120 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 104 | 60 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 18 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 316 | 440 | 380.6 | 459 | 0 | 110
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 60 | 62 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 25 | 50 | 25 | 60 | 26 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 290 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 391 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 380 | 360 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1482 | 1504 | 1460 | 1545 | 388 | 505
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 878 | 854 | 890 | 875
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 65 | 94 | 32 | 100 | 15 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 44 |  | 10 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 55 | 63 | 55 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 205 | 225 | 225 | 185 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 88 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 36 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1470 | 1498 | 1540 | 1542 | 546 | 71
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 35 | 32 | 48
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 31 | 26 | 31 |  | 9 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 82 | 82 | 82 | 82 | 112 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 850 | 1010 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 182 | 217 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1150 | 1392 | 1477 | 1498 | 112 | 9
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 25 | 34 | 24 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 152 | 142 | 150 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 201 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 137 | 136 | 140 | 140 | 80 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 372 | 353 | 360 | 360 | 54 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 35 | 22 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 88 | 86 | 85 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 88 | 113 | 90 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 75 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1176 | 1366 | 1075 | 1185 | 794 | 144
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 79 | 105 | 68 | 105 |  | 8 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 109 | 108 | 100 | 108
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 387 | 412 | 376 | 413 | 199 | 93
|  | Total |  |  |  |  | 22678 | 21396 | 11155 | 12494 | 11639.6 | 12570 | 5254 | 2803
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11741.8116 | 13151.25 | 12251.9041 | 13231.248
| A. |  | 2022-07-20 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12567 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11054 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13664 | MW
| 3 | Day peak Generation : |  |  | 11155 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13151.25 | MW
| 4 | Evening peak Generation : |  |  | 12494 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1170 | MW
| 5 | Total Energy Generation : |  | 282.1154 | MKWHr | By Solar | 1.0311 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 129.0853 | MKWHr |  | By Oil: | 94.8851 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.0727 | MKWHr |  | By Hydro: | 3.0056 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5254 | MW | Dhaka | 4539.3 | 4339.3 |  | 200
|  |  |  | For Plants S/D or M/C prob = |  |  | 2803 | MW | Chittagong | 1234.1 | 1234.1 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 8057 | MW | Khulna | 1699.8 | 1549.8 |  | 150 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 954.1 | MMCFD |  |  | Rajshahi | 1496.2 | 1316.2 |  | 180 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 144291553.91 | ii) Oil : | Taka | 1299545734.34 | Comilla | 1230 | 1070 |  | 160 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 252865783 | Total | Taka | 1696703071.25 | Mymensingh | 1123 | 903 |  | 220 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 519 | 444 |  | 75 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 478 | MW (E to W) at | 21:00 | hrs | Barisal | 373.85 | 373.85 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 438 | MW at | 6:00 | hrs | Rangpur | 936 | 751 |  | 185 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 13151.25 | 11981.25 |  | 1170
| B. |  | 2022-07-21 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1365 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12570 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 318.7745 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10866 | MW at | 8:00 | 350 | 164 | 160 | 190 | 160 | 160 | 61 | 0 | 120
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2756 | MKWHr. | ii) HVDC Flow at Peak Time |  | 854 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.76 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.31 |  | (b) Today: | 91.2 |  | (c) Rule Curve: |  | 87.2
.

## YesterdayGen
2022-07-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 303 | 213 |  | 0 | 190 | 0 | 39 | 0 | 48 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 33 | 88 | 35 | 19 | 36 | 0 | 0 | 0 | 300 | 290 | 213 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 21 | 10 | 33 | 21 | 134 | 107 | 0 | 11 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 258 | 0 | 0 | 116 | 0 | 144 | 0 | 90 | 160 | 132 | 402 | 58 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 395 | 90 | 0 | 35 | 108 | 0 | 35 | 0 | 42 | 55 | 0 |  | 912 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 42 | 58 | 40 | 82 | 34 | 48 | 0 | 0 | 0 | 25 | 24 | 89 | 0 | 34 | 32 | 8 | 27 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 207 | 0 | 0 | 134 | 0 | 357 | 75 | 0 | 70 | 88 | 100 | 0 | 0 | 55 | 1070 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7188 | 4556 | 11744 | 3797 | 912 | 1570 | 0 | 3154 | 1270 | 127 | 207 | 780 | 134 | 0 | 0 | 91.32
2:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 311 | 233 |  | 0 | 190 | 0 | 39 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 33 | 89 | 38 | 19 | 36 | 0 | 0 | 0 | 300 | 290 | 211 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 21 | 10 | 33 | 21 | 128 | 106 | 0 | 13 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 258 | 0 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 135 | 400 | 59 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 400 | 89 | 0 | 35 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 912 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 40 | 58 | 40 | 82 | 33 | 48 | 0 | 0 | 0 | 25 | 24 | 89 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 212 | 0 | 0 | 124 | 0 | 365 | 93 | 0 | 70 | 85 | 104 | 0 | 0 | 55 | 1070 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7190 | 4570 | 11760 | 3796 | 912 | 1587 | 0 | 3164 | 1270 | 125 | 212 | 778 | 128 | 0 | 0 | 91.32
3:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 318 | 244 |  | 0 | 200 | 0 | 37 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 51 | 51 | 33 | 82 | 0 | 19 | 30 | 0 | 0 | 0 | 300 | 290 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 18 | 10 | 33 | 21 | 126 | 108 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 255 | 0 | 0 | 116 | 0 | 149 | 0 | 90 | 120 | 137 | 400 | 58 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 400 | 89 | 0 | 35 | 108 | 0 | 35 | 0 | 54 | 55 | 0 |  | 912 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 38 | 58 | 40 | 82 | 32 | 48 | 0 | 0 | 0 | 25 | 24 | 89 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 213 | 0 | 0 | 124 | 0 | 378 | 93 | 0 | 70 | 85 | 104 | 0 | 0 | 55 | 1070 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7162 | 4577 | 11739 | 3802 | 912 | 1614 | 0 | 3113 | 1270 | 125 | 213 | 777 | 126 | 0 | 0 | 91.32
4:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 328 | 243 |  | 0 | 200 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 32 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 51 | 51 | 33 | 87 | 31 | 19 | 38 | 0 | 0 | 0 | 300 | 290 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 18 | 10 | 33 | 21 | 126 | 108 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 255 | 0 | 0 | 116 | 0 | 149 | 0 | 90 | 120 | 132 | 399 | 58 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 400 | 89 | 0 | 35 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 912 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 28 | 58 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 25 | 24 | 89 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 214 | 0 | 0 | 124 | 0 | 386 | 93 | 0 | 70 | 88 | 104 | 0 | 0 | 55 | 1020 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7206 | 4529 | 11735 | 3817 | 912 | 1618 | 0 | 3149 | 1220 | 125 | 214 | 768 | 126 | 0 | 0 | 91.31
5:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 338 | 223 |  | 0 | 200 | 0 | 43 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 33 | 89 | 38 | 19 | 32 | 0 | 0 | 0 | 300 | 290 | 211 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 18 | 10 | 28 | 21 | 122 | 106 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 255 | 0 | 0 | 117 | 0 | 149 | 0 | 90 | 120 | 130 | 401 | 59 | 105 | 105 | 0 | 285 | 36 | 92 | 0 | 8 | 50 | 398 | 89 | 0 | 35 | 108 | 0 | 20 | 0 | 53 | 55 | 0 |  | 912 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 58 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 25 | 0 | 89 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 149 | 0 | 0 | 212 | 0 | 0 | 124 | 0 | 397 | 93 | 0 | 70 | 88 | 88 | 0 | 0 | 55 | 980 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7198 | 4436 | 11634 | 3825 | 912 | 1618 | 0 | 3132 | 1179 | 127 | 212 | 719 | 122 | 0 | 0 | 91.31
6:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 343 | 216 |  | 0 | 200 | 0 | 39 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 130 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 33 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 300 | 290 | 213 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 18 | 10 | 25 | 21 | 116 | 107 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 63 | 25 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 250 | 0 | 0 | 117 | 0 | 149 | 1 | 90 | 120 | 132 | 387 | 59 | 105 | 105 | 0 | 267 | 36 | 92 | 0 | 8 | 50 | 350 | 89 | 2 | 35 | 108 | 0 | 17 | 1 | 54 | 55 | 0 |  | 912 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 57 | 40 | 82 | 26 | 16 | 0 | 0 | 0 | 25 | 0 | 89 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 150 | 0 | 0 | 128 | 0 | 353 | 93 | 0 | 70 | 88 | 83 | 0 | 0 | 55 | 980 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7091 | 4294 | 11385 | 3776 | 912 | 1547 | 0 | 3068 | 1179 | 127 | 150 | 656 | 116 | 4 | 0 | 91.31
7:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 348 | 261 |  | 0 | 210 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 33 | 89 | 38 | 19 | 41 | 0 | 0 | 0 | 300 | 290 | 211 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 25 | 21 | 110 | 104 | 0 | 18 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 275 | 0 | 0 | 0 | 243 | 0 | 0 | 117 | 0 | 149 | 5 | 90 | 120 | 137 | 370 | 59 | 105 | 105 | 0 | 267 | 36 | 92 | 0 | 8 | 50 | 350 | 89 | 7 | 35 | 108 | 0 | 17 | 5 | 53 | 55 | 0 |  | 912 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 58 | 40 | 82 | 25 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 155 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 354 | 93 | 0 | 0 | 88 | 83 | 0 | 0 | 55 | 950 | 220 | 0 | 17 | 1 | 15 | 109 | 0 | 0 |  | 7106 | 4212 | 11318 | 3774 | 912 | 1596 | 0 | 2996 | 1149 | 127 | 130 | 621 | 110 | 33 | 0 | 91.31
8:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 349 | 274 |  | 0 | 210 | 0 | 39 | 0 | 55 | 0 | 0 | 0 | 32 | 86 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 51 | 51 | 33 | 89 | 38 | 19 | 8 | 0 | 0 | 0 | 300 | 290 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 14 | 12 | 100 | 100 | 0 | 19 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 285 | 0 | 0 | 0 | 257 | 0 | 0 | 116 | 0 | 149 | 12 | 90 | 120 | 137 | 375 | 58 | 105 | 105 | 1 | 267 | 36 | 92 | 0 | 8 | 50 | 360 | 89 | 5 | 35 | 108 | 0 | 17 | 12 | 54 | 55 | 0 |  | 912 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 23 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 22 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 154 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 302 | 93 | 0 | 0 | 88 | 83 | 0 | 1 | 55 | 950 | 154 | 0 | 0 | 1 | 20 | 109 | 0 | 0 |  | 7079 | 4103 | 11182 | 3776 | 912 | 1465 | 0 | 2990 | 1150 | 127 | 130 | 610 | 100 | 52 | 0 | 91.31
9:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 344 | 282 |  | 0 | 215 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 42 | 51 | 33 | 89 | 38 | 19 | 10 | 0 | 0 | 0 | 280 | 290 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 10 | 20 | 96 | 83 | 0 | 19 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 9 | 260 | 0 | 0 | 0 | 257 | 0 | 0 | 115 | 0 | 149 | 2 | 90 | 120 | 138 | 365 | 58 | 105 | 105 | 2 | 267 | 36 | 92 | 0 | 8 | 50 | 370 | 89 | 20 | 35 | 108 | 0 | 17 | 24 | 54 | 46 | 0 |  | 911 | 0 | 220 | 0 | 49 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 21 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 22 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 304 | 93 | 0 | 1 | 89 | 77 | 0 | 1 | 55 | 850 | 164 | 0 | 0 | 1 | 28 | 109 | 0 | 0 |  | 7031 | 4023 | 11054 | 3727 | 911 | 1460 | 0 | 3004 | 1050 | 126 | 130 | 601 | 96 | 79 | 0 | 91.3
10:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 361 | 278 |  | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 41 | 51 | 33 | 82 | 38 | 19 | 7 | 0 | 0 | 0 | 280 | 265 | 209 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 0 | 20 | 98 | 83 | 0 | 19 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 257 | 0 | 0 | 115 | 0 | 143 | 7 | 76 | 120 | 133 | 403 | 58 | 90 | 105 | 2 | 177 | 36 | 92 | 0 | 8 | 50 | 392 | 89 | 18 | 35 | 108 | 0 | 23 | 24 | 53 | 40 | 0 |  | 878 | 0 | 215 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 20 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 24 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 372 | 93 | 0 | 88 | 88 | 79 | 0 | 0 | 55 | 850 | 182 | 0 | 0 | 1 | 36 | 109 | 0 | 0 |  | 6972 | 4183 | 11155 | 3759 | 878 | 1577 | 0 | 2978 | 1049 | 125 | 130 | 602 | 98 | 89 | 0 | 91.3
11:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 356 | 255 |  | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 85 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 26 | 25 | 30 | 40 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 41 | 51 | 33 | 79 | 38 | 19 | 3 | 0 | 0 | 0 | 280 | 305 | 209 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 16 | 10 | 0 | 20 | 104 | 80 | 0 | 16 | 2 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 9 | 270 | 0 | 0 | 0 | 257 | 0 | 0 | 115 | 0 | 131 | 16 | 76 | 120 | 130 | 403 | 58 | 90 | 105 | 3 | 177 | 36 | 92 | 0 | 8 | 50 | 394 | 88 | 27 | 35 | 108 | 0 | 35 | 24 | 54 | 55 | 0 |  | 878 | 0 | 205 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 19 | 16 | 0 | 0 | 0 | 25 | 0 | 78 | 0 | 34 | 32 | 8 | 28 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 373 | 93 | 0 | 110 | 89 | 85 | 0 | 3 | 55 | 890 | 183 | 0 | 0 | 5 | 14 | 109 | 0 | 0 |  | 6947 | 4181 | 11128 | 3749 | 878 | 1531 | 0 | 3016 | 1090 | 125 | 130 | 541 | 104 | 94 | 0 | 91.3
12:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 352 | 257 |  | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 22 | 25 | 28 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 15 | 43 | 51 | 33 | 84 | 38 | 19 | 3 | 0 | 0 | 0 | 310 | 305 | 208 | 8 | 0 | 37 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 16 | 20 | 102 | 69 | 0 | 16 | 3 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 9 | 290 | 8 | 0 | 0 | 257 | 0 | 0 | 114 | 0 | 131 | 17 | 76 | 120 | 132 | 404 | 58 | 105 | 105 | 1 | 192 | 36 | 92 | 0 | 8 | 50 | 160 | 90 | 33 | 35 | 108 | 0 | 35 | 11 | 53 | 55 | 0 |  | 873 | 0 | 200 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 18 | 16 | 0 | 0 | 0 | 25 | 0 | 78 | 0 | 34 | 24 | 8 | 28 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 130 | 0 | 0 | 136 | 0 | 361 | 93 | 0 | 113 | 88 | 85 | 0 | 6 | 55 | 930 | 182 | 0 | 0 | 2 | 46 | 109 | 0 | 0 |  | 6842 | 4214 | 11056 | 3567 | 873 | 1539 | 0 | 3055 | 1130 | 126 | 130 | 545 | 102 | 119 | 0 | 91.29
13:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 357 | 268 |  | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 26 | 25 | 28 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 51 | 33 | 89 | 38 | 19 | 4 | 0 | 0 | 0 | 290 | 305 | 213 | 8 | 0 | 36 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 16 | 20 | 118 | 69 | 0 | 14 | 2 | 43 | 42 | 22 | 20 | 0 | 0 | 58 | 78 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 258 | 0 | 0 | 115 | 0 | 135 | 4 | 63 | 120 | 130 | 403 | 58 | 105 | 105 | 1 | 176 | 36 | 92 | 0 | 8 | 38 | 160 | 88 | 54 | 35 | 90 | 0 | 35 | 6 | 54 | 55 | 0 |  | 872 | 0 | 195 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 20 | 16 | 0 | 0 | 0 | 25 | 4 | 72 | 0 | 34 | 24 | 8 | 28 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 344 | 93 | 0 | 106 | 89 | 83 | 0 | 6 | 55 | 930 | 184 | 0 | 0 | 2 | 96 | 109 | 0 | 0 |  | 6921 | 4231 | 11152 | 3549 | 872 | 1641 | 0 | 3003 | 1130 | 127 | 130 | 541 | 118 | 171 | 0 | 91.29
14:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 363 | 272 |  | 0 | 225 | 0 | 36 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 23 | 25 | 26 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 28 | 51 | 33 | 89 | 38 | 19 | 2 | 0 | 0 | 0 | 285 | 265 | 209 | 8 | 0 | 37 | 5 | 0 | 51 | 0 | 42 | 8 | 19 | 10 | 16 | 17 | 120 | 68 | 0 | 14 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 250 | 0 | 0 | 115 | 0 | 149 | 7 | 30 | 120 | 140 | 366 | 58 | 105 | 105 | 6 | 175 | 36 | 92 | 0 | 8 | 38 | 391 | 89 | 32 | 44 | 102 | 0 | 35 | 15 | 53 | 55 | 0 |  | 869 | 0 | 195 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 82 | 22 | 16 | 0 | 0 | 0 | 25 | 5 | 72 | 0 | 34 | 24 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 137 | 0 | 0 | 130 | 0 | 0 | 133 | 0 | 341 | 74 | 0 | 113 | 104 | 83 | 0 | 5 | 55 | 930 | 218 | 0 | 0 | 3 | 62 | 109 | 0 | 0 |  | 6959 | 4224 | 11183 | 3709 | 869 | 1556 | 0 | 3005 | 1129 | 127 | 130 | 537 | 120 | 131 | 0 | 91.29
15:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 370 | 273 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 23 | 25 | 26 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 19 | 51 | 33 | 89 | 38 | 19 | 4 | 0 | 0 | 0 | 320 | 325 | 174 | 8 | 0 | 37 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 16 | 20 | 120 | 68 | 0 | 14 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 10 | 315 | 8 | 0 | 0 | 253 | 0 | 0 | 148 | 0 | 149 | 0 | 30 | 120 | 140 | 399 | 58 | 105 | 105 | 1 | 175 | 36 | 92 | 0 | 8 | 38 | 387 | 89 | 8 | 90 | 108 | 0 | 35 | 16 | 72 | 0 | 0 |  | 869 | 0 | 190 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 26 | 16 | 0 | 0 | 0 | 25 | 5 | 70 | 0 | 34 | 24 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 130 | 0 | 0 | 132 | 0 | 326 | 93 | 0 | 94 | 89 | 82 | 0 | 5 | 55 | 960 | 216 | 0 | 0 | 3 | 54 | 109 | 0 | 0 |  | 7100 | 4173 | 11273 | 3799 | 869 | 1583 | 0 | 3003 | 1159 | 127 | 130 | 525 | 120 | 88 | 0 | 91.28
16:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 369 | 265 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 23 | 25 | 26 | 41 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 28 | 51 | 33 | 69 | 38 | 19 | 10 | 0 | 0 | 0 | 285 | 270 | 167 | 8 | 0 | 37 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 25 | 20 | 120 | 69 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 263 | 0 | 0 | 174 | 0 | 149 | 0 | 30 | 120 | 140 | 366 | 58 | 90 | 105 | 1 | 175 | 36 | 92 | 0 | 15 | 38 | 380 | 89 | 14 | 120 | 90 | 0 | 35 | 3 | 76 | 15 | 0 |  | 869 | 0 | 200 | 0 | 61 | 0 | 0 | 0 | 14 | 0 | 8 | 82 | 24 | 16 | 0 | 0 | 0 | 25 | 19 | 70 | 0 | 34 | 24 | 8 | 29 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 136 | 0 | 0 | 130 | 0 | 0 | 133 | 0 | 324 | 75 | 0 | 94 | 89 | 82 | 0 | 3 | 55 | 960 | 220 | 0 | 0 | 2 | 39 | 108 | 0 | 0 |  | 6994 | 4161 | 11155 | 3685 | 869 | 1565 | 0 | 3005 | 1159 | 127 | 130 | 563 | 120 | 62 | 0 | 91.28
17:00 | 0 | 0 | 0 | 180 | 290 | 80 | 0 | 364 | 262 |  | 0 | 225 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 25 | 26 | 47 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 42 | 51 | 33 | 83 | 38 | 19 | 5 | 0 | 0 | 0 | 285 | 265 | 190 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 33 | 20 | 106 | 69 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 263 | 0 | 0 | 183 | 0 | 149 | 0 | 30 | 151 | 117 | 366 | 58 | 105 | 105 | 0 | 175 | 36 | 92 | 0 | 10 | 38 | 370 | 88 | 18 | 144 | 95 | 0 | 35 | 1 | 76 | 55 | 0 |  | 868 | 0 | 200 | 0 | 88 | 0 | 0 | 0 | 39 | 0 | 8 | 82 | 24 | 16 | 0 | 0 | 0 | 25 | 30 | 60 | 0 | 34 | 24 | 8 | 29 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 325 | 75 | 0 | 113 | 105 | 102 | 0 | 3 | 70 | 920 | 195 | 0 | 0 | 0 | 35 | 72 | 0 | 0 |  | 7114 | 4183 | 11297 | 3696 | 868 | 1514 | 0 | 3206 | 1120 | 127 | 130 | 603 | 106 | 57 | 0 | 91.28
18:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 354 | 262 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 12 | 25 | 26 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 42 | 51 | 33 | 77 | 38 | 19 | 9 | 0 | 0 | 0 | 285 | 265 | 204 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 30 | 20 | 98 | 69 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 63 | 25 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 273 | 0 | 0 | 183 | 0 | 149 | 0 | 30 | 200 | 130 | 365 | 104 | 90 | 105 | 0 | 175 | 36 | 92 | 0 | 9 | 38 | 340 | 88 | 4 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 869 | 0 | 200 | 0 | 92 | 0 | 0 | 0 | 39 | 0 | 8 | 78 | 24 | 16 | 0 | 0 | 0 | 25 | 30 | 70 | 0 | 34 | 24 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 325 | 93 | 0 | 113 | 105 | 105 | 0 | 1 | 95 | 930 | 150 | 0 | 0 | 0 | 5 | 72 | 0 | 0 |  | 7214 | 4176 | 11390 | 3658 | 869 | 1474 | 0 | 3400 | 1130 | 127 | 130 | 624 | 98 | 10 | 0 | 91.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 270 | 88 | 0 | 348 | 250 |  | 0 | 225 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 50 | 35 | 19 | 25 | 14 | 25 | 26 | 50 | 0 | 92 | 35 | 100 | 0 | 5 | 0 | 0 | 0 | 0 |  | 22 | 42 | 51 | 33 | 89 | 38 | 19 | 14 | 0 | 0 | 0 | 280 | 280 | 206 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 31 | 20 | 100 | 105 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 0 | 0 | 273 | 0 | 0 | 193 | 0 | 149 | 0 | 30 | 200 | 133 | 398 | 105 | 105 | 105 | 0 | 261 | 36 | 92 | 99 | 12 | 38 | 380 | 92 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 853 | 0 | 200 | 0 | 93 | 0 | 0 | 0 | 39 | 30 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 25 | 34 | 86 | 0 | 34 | 29 | 34 | 34 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 154 | 0 | 0 | 135 | 0 | 327 | 93 | 0 | 113 | 105 | 104 | 0 | 0 | 95 | 890 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 |  | 7564 | 4370 | 11934 | 3748 | 853 | 1545 | 0 | 3766 | 1090 | 127 | 154 | 705 | 100 | 0 | 0 | 91.26
19:30 | 0 | 0 | 0 | 180 | 290 | 92 | 0 | 341 | 250 |  | 0 | 225 | 0 | 35 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 14 | 25 | 27 | 49 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 42 | 51 | 33 | 90 | 38 | 19 | 10 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 31 | 20 | 108 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 50 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 273 | 0 | 0 | 193 | 0 | 149 | 0 | 30 | 200 | 137 | 377 | 105 | 105 | 105 | 0 | 272 | 36 | 92 | 99 | 56 | 38 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 854 | 0 | 200 | 0 | 94 | 0 | 0 | 0 | 39 | 55 | 40 | 82 | 33 | 48 | 0 | 0 | 0 | 25 | 34 | 86 | 0 | 34 | 32 | 43 | 34 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 205 | 0 | 0 | 135 | 0 | 327 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1000 | 225 | 0 | 2 | 0 | 0 | 108 | 0 | 0 |  | 7727 | 4618 | 12345 | 3769 | 854 | 1587 | 0 | 3916 | 1200 | 127 | 205 | 784 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 342 | 251 |  | 0 | 225 | 0 | 33 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 25 | 28 | 49 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 57 | 33 | 90 | 38 | 19 | 20 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 16 | 19 | 10 | 31 | 20 | 114 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 50 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 273 | 0 | 0 | 193 | 0 | 149 | 0 | 30 | 200 | 137 | 365 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 99 | 56 | 38 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 855 | 0 | 205 | 0 | 94 | 0 | 0 | 0 | 44 | 63 | 40 | 82 | 32 | 48 | 0 | 0 | 0 | 34 | 34 | 86 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 180 | 0 | 0 | 135 | 0 | 337 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1000 | 183 | 0 | 10 | 0 | 0 | 108 | 0 | 0 |  | 7789 | 4598 | 12387 | 3786 | 855 | 1568 | 0 | 3942 | 1200 | 125 | 180 | 797 | 114 | 0 | 0 | 91.26
21:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 334 | 243 |  | 0 | 225 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 68 | 33 | 90 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 0 | 41 | 5 | 0 | 51 | 0 | 49 | 16 | 19 | 10 | 31 | 20 | 126 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 194 | 0 | 149 | 0 | 30 | 200 | 140 | 391 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 99 | 56 | 38 | 380 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 854 | 0 | 205 | 0 | 94 | 0 | 0 | 0 | 44 | 63 | 40 | 82 | 31 | 35 | 0 | 0 | 0 | 34 | 30 | 86 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 0 | 201 | 0 | 0 | 136 | 0 | 353 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1010 | 217 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7826 | 4668 | 12494 | 3783 | 854 | 1632 | 0 | 3940 | 1209 | 125 | 201 | 825 | 126 | 0 | 0 | 91.26
22:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 327 | 235 |  | 0 | 225 | 0 | 28 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 25 | 28 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 68 | 33 | 88 | 38 | 19 | 36 | 0 | 0 | 0 | 280 | 280 | 206 | 8 | 0 | 41 | 5 | 0 | 51 | 0 | 49 | 16 | 19 | 10 | 33 | 20 | 128 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 320 | 8 | 0 | 0 | 275 | 0 | 0 | 184 | 0 | 149 | 0 | 30 | 200 | 142 | 404 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 99 | 58 | 38 | 390 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 855 | 0 | 205 | 0 | 111 | 0 | 0 | 0 | 44 | 62 | 40 | 82 | 37 | 32 | 0 | 0 | 0 | 34 | 21 | 88 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 214 | 0 | 0 | 136 | 0 | 359 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1020 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7851 | 4716 | 12567 | 3804 | 855 | 1665 | 0 | 3941 | 1219 | 125 | 214 | 830 | 128 | 0 | 0 | 91.25
23:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 328 | 235 |  | 0 | 225 | 0 | 22 | 0 | 55 | 0 | 0 | 0 | 32 | 86 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 51 | 68 | 33 | 89 | 38 | 19 | 39 | 0 | 0 | 0 | 280 | 280 | 205 | 8 | 0 | 41 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 124 | 105 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 220 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 275 | 0 | 0 | 184 | 0 | 149 | 0 | 30 | 200 | 132 | 404 | 103 | 105 | 105 | 0 | 177 | 36 | 92 | 99 | 58 | 38 | 392 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 854 | 0 | 205 | 0 | 110 | 0 | 0 | 0 | 44 | 62 | 8 | 82 | 36 | 32 | 0 | 0 | 0 | 34 | 28 | 88 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 0 | 210 | 0 | 0 | 137 | 0 | 360 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1050 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7704 | 4718 | 12422 | 3808 | 854 | 1678 | 0 | 3750 | 1249 | 126 | 210 | 833 | 124 | 0 | 0 | 91.25
24:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 350 | 252 |  | 0 | 225 | 0 | 31 | 0 | 48 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 27 | 25 | 32 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 68 | 33 | 90 | 38 | 19 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 126 | 108 | 0 | 8 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 260 | 0 | 0 | 184 | 0 | 149 | 0 | 30 | 200 | 132 | 402 | 58 | 105 | 105 | 0 | 177 | 36 | 92 | 23 | 58 | 38 | 398 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 55 | 55 | 0 |  | 854 | 0 | 205 | 0 | 110 | 0 | 0 | 0 | 44 | 62 | 8 | 82 | 37 | 32 | 0 | 0 | 0 | 34 | 29 | 89 | 0 | 34 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 147 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 359 | 93 | 0 | 70 | 105 | 105 | 0 | 0 | 55 | 1060 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7583 | 4617 | 12200 | 3892 | 854 | 1652 | 0 | 3453 | 1259 | 126 | 213 | 838 | 126 | 0 | 0 | 91.24
KWH | 0 | 0 | 0 | 4378500 | 7193764 | 2039681 | 0 | 8367280 | 6052000 |  | 0 | 4726000 | 0 | 864000 | 0 | 1331210 | 0 | 0 | 0 | 776141 | 2193696 | 2931840 | 0 | 0 | 0 | 0 | 641880 | 269921 | 286512 | 410184 | 600000 | 577440 | 620560 | 691800 | 1129440 | 0 | 2165591 | 840000 | 2400000 | 0 | 591057 | 0 | 0 | 0 | 0 |  | 486720 | 1053760 | 1292769 | 786360 | 2073600 | 892320 | 446208 | 490560 | 0 | 0 | 0 | 7406100 | 7059000 | 4985000 | 217454 | 0 | 584856 | 142560 | 0 | 1184321 | 0 | 1089056 | 234744 | 431208 | 231480 | 602500 | 507930 | 2760000 | 2125440 | 0 | 338292 | 9300 | 1024000 | 934804 | 21600 | 21672 | 0 | 0 | 1437560 | 816960 | 0 | 5376650 | 0 | 0 | 238500 | 7267500 | 151392 | 0 | 0 | 6242616 | 0 | 0 | 3388800 | 0 | 3557376 | 71280 | 1453440 | 3502080 | 3226690 | 9290000 | 1654800 | 2454000 | 2534181 | 19080 | 5565164 | 908592 | 2240608 | 458280 | 477960 | 1065600 | 8763200 | 2222400 | 240560 | 1892160 | 2553000 | 0 | 785880 | 147458 | 1488960 | 1258560 | 0 |  | 21275636 | 0 | 5086944 | 0 | 1456320 | 0 | 0 | 0 | 463680 | 912640 | 759750 | 1979944 | 639513 | 719712 | 0 | 0 | 0 | 634160 | 346232 | 1953056 | 0 | 776576 | 638500 | 355680 | 652520 | 459840 | 0 | 251010 | 0 | 0 | 4862700 | 0 | 0 | 3683000 | 0 | 0 | 4228636 | 0 | 0 | 3457855 | 0 | 8422182 | 2128320 | 0 | 2109600 | 2305152 | 2234313 | 0 | 32621 | 1606560 | 25210000 | 4951064 | 0 | 219600 | 24840 | 486000 | 2527872 | 0 | 0 |  | 174263398 | 107852028 | 282115426 | 91393901 | 21275636 | 37691407 | 0 | 78688203 | 30072700 | 3005591 | 4228636 | 11968213 | 2760000 | 1031139 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 8057015.68 | 2712775.73 | 0 | 8785644 | 6536160 |  | 0 | 5151340 | 0 | 9659520 | 0 | 17638532.5 | 0 | 0 | 0 | 11347181.42 | 30865302.72 | 47525126.4 | 0 | 0 | 0 | 0 | 8164713.6 | 3643933.5 | 3842125.92 | 307638 | 450000 | 0 | 0 | 0 | 19211774.4 | 0 | 584709.57 | 226800 | 4536000 | 0 | 9663781.95 | 0 | 0 | 0 | 0 |  | 6351696 | 17576716.8 | 22002928.38 | 10623723.6 | 26293248 | 10324142.4 | 566684.16 | 1633564.8 | 0 | 0 | 0 | 8220771 | 7694310 | 5782600 | 280515.66 | 0 | 660887.28 | 212414.4 | 0 | 1977816.07 | 0 | 18807997.12 | 3157306.8 | 590754.96 | 173610 | 1054375 | 380947.5 | 19816800 | 2316729.6 | 0 | 460077.12 | 148242 | 1402880 | 1233941.28 | 37584 | 37492.56 | 0 | 0 | 2788866.4 | 1862668.8 | 0 | 5430416.5 | 0 | 0 | 472230 | 7267500 | 113544 | 0 | 0 | 85211708.4 | 0 | 0 | 45681024 | 0 | 49269657.6 | 833263.2 | 14999500.8 | 47838412.8 | 42818176.3 | 8546800 | 20122368 | 35484840 | 32057389.65 | 0 | 65335025.36 | 9894566.88 | 23817663.04 | 6218859.6 | 6160904.4 | 12552768 | 8062144 | 28780080 | 3476092 | 24011510.4 | 29053140 | 0 | 10263592.8 | 1762123.1 | 22289731.2 | 16575235.2 | 0 |  | 63826908 | 0 | 5697377.28 | 0 | 15160291.2 | 0 | 0 | 0 | 8350876.8 | 16427520 | 10917607.5 | 2217537.28 | 1240655.22 | 7844860.8 | 0 | 0 | 0 | 10634863.2 | 6055597.68 | 30545795.84 | 0 | 12860098.56 | 10797035 | 4847918.4 | 11008012.4 | 951868.8 | 0 | 190014.57 | 0 | 0 | 25723683 | 0 | 0 | 4272280 | 0 | 0 | 73831984.56 | 0 | 0 | 4011111.8 | 0 | 8337960.18 | 28604620.8 | 0 | 24956568 | 33309446.4 | 28375775.1 | 0 | 360462.05 | 19503638.4 | 227142100 | 5050085.28 | 0 | 1625040 | 280940.4 | 5700780 | 38752277.76 | 0 | 0 |  | 1044306599.31 | 749413592.26 | 1793720191.57 | 100528922.41 | 63826908 | 43762631.5 | 0 | 1025981280.16 | 252865783 | 811509.57 | 73831984.56 | 199732469.62 | 19816800 | 12561902.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 361 | 278 |  | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 30 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 41 | 51 | 33 | 82 | 38 | 19 | 7 | 0 | 0 | 0 | 280 | 265 | 209 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 0 | 20 | 98 | 83 | 0 | 19 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 257 | 0 | 0 | 115 | 0 | 143 | 7 | 76 | 120 | 133 | 403 | 58 | 90 | 105 | 2 | 177 | 36 | 92 | 0 | 8 | 50 | 392 | 89 | 18 | 35 | 108 | 0 | 23 | 24 | 53 | 40 | 0 |  | 878 | 0 | 215 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 20 | 16 | 0 | 0 | 0 | 25 | 0 | 88 | 0 | 34 | 32 | 8 | 24 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 372 | 93 | 0 | 88 | 88 | 79 | 0 | 0 | 55 | 850 | 182 | 0 | 0 | 1 | 36 | 109 | 0 | 0 |  | 11155 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 334 | 243 | 0 | 0 | 225 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 68 | 33 | 90 | 38 | 19 | 30 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 0 | 41 | 5 | 0 | 51 | 0 | 49 | 16 | 19 | 10 | 31 | 20 | 126 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 194 | 0 | 149 | 0 | 30 | 200 | 140 | 391 | 104 | 105 | 105 | 0 | 285 | 36 | 92 | 99 | 56 | 38 | 380 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 854 | 0 | 205 | 0 | 94 | 0 | 0 | 0 | 44 | 63 | 40 | 82 | 31 | 35 | 0 | 0 | 0 | 34 | 30 | 86 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 0 | 201 | 0 | 0 | 136 | 0 | 353 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1010 | 217 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 12494 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 330 | 250 | 0 | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 68 | 33 | 90 | 38 | 19 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 16 | 19 | 10 | 31 | 20 | 126 | 110 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 60 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 200 | 0 | 149 | 0 | 30 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 285 | 36 | 92 | 70 | 56 | 50 | 400 | 104 | 0 | 144 | 108 | 0 | 35 |  | 75 | 55 |  |  | 875 | 0 | 225 | 0 | 100 | 0 | 0 | 0 | 44 | 60 | 40 | 82 | 31 | 48 | 0 | 0 | 0 | 34 | 30 | 86 | 0 | 34 | 32 | 43 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 360 | 93 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1100 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 300 | 200 | 0 | 0 | 225 | 0 | 40 | 0 | 55 | 0 | 0 | 0 | 32 | 88 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 33 | 90 | 38 | 19 | 5 | 0 | 0 | 0 | 300 | 290 | 210 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 25 | 20 | 120 | 105 | 0 | 22 | 1.6 | 43 | 42 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 255 | 0 | 0 | 120 | 0 | 149 | 20 | 30 | 120 | 135 | 400 | 60 | 105 | 105 | 5 | 278 | 36 | 92 | 0 | 8 | 50 | 360 | 104 | 50 | 35 | 108 | 0 | 35 | 30 | 54 | 55 |  |  | 890 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 40 | 82 | 26 | 32 | 0 | 0 | 0 | 24 | 16 | 85 | 0 | 34 | 32 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 360 | 93 | 0 | 90 | 105 | 68 | 0 | 8 | 75 | 1100 | 220 |  | 17 | 6 | 100 | 100
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 355 | 262 | 0 | 0 | 225 | 0 | 31 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 0 | 25 | 12 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 33 | 76 | 38 | 19 | 10 | 0 | 0 | 0 | 280 | 280 | 186 | 8 | 0 | 38 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 28 | 20 | 96 | 104 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 275 | 0 | 0 | 164 | 0 | 149 | 10 | 30 | 120 | 127 | 403 | 58 | 90 | 105 | 3 | 175 | 36 | 92 | 0 | 8 | 38 | 400 | 104 | 8 | 35 | 108 | 0 | 35 | 14 | 53 | 28 | 0 | 0 | 907 | 0 | 205 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 0 | 130 | 0 | 0 | 141 | 0 | 364 | 74 | 0 | 70 | 105 | 84 | 0 | 2 | 55 | 930 | 221 | 0 | 17 | 1 | 55 | 52 | 0 | 0 | 0 |  |  |  |  | 94885052 |  | 0
94885052
| Minimum Generation |  | 11054 | 9:00
| Highest Generation |  | 12567 | 22:00
| Day Peak Generation |  | 11155 | 10:00
| Evening Peak Generation |  | 12494 | 21:00
| HVDC Max Flow |  | 912 | 1:00
| HVDC EvPeak Flow |  | 854 | 21:00
| Load factor L.F |  | 93.54% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-21
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11155 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 10866 | MW
Evening Peak Generation : |  | 12494 | MW Hour : | 21:00 | Available Max Generation : |  | 12570 | MW
E.P. Demand (at gen end) : |  | 13664 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 12567 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 282.1154 | System Load Factor : | 93.54% | Load Shed : |  | 1365 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 438 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-21
Actual : | 91.2 | Ft.(MSL) , | Rule curve : | 87.2 | Ft.( MSL )
Gas Consumed : | Total = | 954.1 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144291553.91
: |  | Coal : | 252865783 | Oil : | 1299545734.34 | Total : | 1696703071.25
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 200 | 4800:00 | 5266.762 |  |  | 350 | 8.437%
Chittagong Area | 0 | 0:00 | 1466.3586 |  |  | 164 | 20.19%
Khulna Area | 150 | 3600:00 | 1928.8996 |  |  | 160 | 24.45%
Rajshahi Area | 180 | 4320:00 | 1703.0471 |  |  | 190 | 13.08%
Cumilla Area | 160 | 3840:00 | 1453.9534 |  |  | 160 | 10.82%
Mymensingh Area | 220 | 5280:00 | 1195.8597 |  |  | 160 | 13.89%
Sylhet Area | 75 | 1800:00 | 540.0235 |  |  | 61 | 10.21%
Barisal Area | 0 | 0:00 | 436.6418 |  |  | 0 | 0.3774%
Rangpur Area | 185 | 4440:00 | 943.766 |  |  | 120 | 4.863%
Total | 1170 |  | 14935.3116 |  |  | 1365
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bheramara-HVDC 400 kV Ckt-2 was under shut down from 08:46 to 19:16 for D/W.
b) Dohazari 132/33 kV T-1 transformer was under shut down from 08:15 for D/W.
c) Bibiyana(S) CCPP ST was forced shut down at 11:52 due to diverter damper problem an was synchronized at 12:54..
d) Tongi 132/33 kV T-1 transformer was under shut down from 10:54 to 17:32 for D/W.
e) Tongi 132/33 kV T-1 transformer tripped at 18:01 showing differential relay and was switched on at 18:50.
and again shut down at 20:22 due to maintenance work.
f) Khulna(S)-Rampal 230 kV Ckt is under shut down since 06:20(21/7/22) for C/M.
g) Noapara 132/33 kV T-2 transformer tripped from 07:16 to 07:52(21/7/22) showing PRD.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7193764 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 88 | 2039681 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 334 | 8367280 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 243 | 6052000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4726000 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 30 | 864000 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1331210
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 410184
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 32 | 776141 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2193696 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 641880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2931840 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 269921
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 286512 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1177440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 620560 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 691800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1129440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 6242616 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3557376
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2454000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2222400
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1892160 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 147458
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1258560
| Dhaka area Total |  |  |  | 5847 | 2859 | 63856419
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 591057
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 71280
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 892320 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 125 | 3005591 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2534181
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 1053760 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1292769 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 786360 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 30 | 1453440 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 446208
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 490560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 2073600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 5565164 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 908592 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2240608 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 1065600
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2553000 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1273 | 29443170
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4985000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7406100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7059000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 584856 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 142560 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1184321
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3226690 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 1089056
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3502080
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 431208
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 231480
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2760000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 31 | 602500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 234744 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 507930 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 458280
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 477960 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 785880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 1488960 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 1750 | 37376059
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 2125440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 338292
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 194 | 3388800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1654800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 240560
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 486720
| Mymensingh Area Total |  |  |  | 614 | 440 | 8243912
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 934804 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 21600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 21672 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1437560 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 816960 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5376650
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 151392 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7267500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 391 | 9290000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238500
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 8763200
| Sylhet Area Total |  |  |  | 2477 | 1504 | 35343838
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 854 | 21275636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 94 | 1456320 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 44 | 463680 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 912640 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 205 | 5086944 | FGMO & gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 759750
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 2128320 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2305152
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 486000
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1498 | 34874442
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 35 | 719712 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 639513 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 1979944 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1010 | 25210000 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 217 | 4951064
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 219600 | Transformer O/L
| Barisal Area Total |  |  |  | 1958 | 1392 | 33719833
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 634160 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 346232 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 776576 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 638500 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 142 | 3683000 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4228636
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 136 | 3457855 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 353 | 8422182 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 652520 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 459840
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251010
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 355680 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 1953056 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2109600
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1606560 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24840
| Rajshahi Area Total |  |  |  | 2129 | 1366 | 29600247
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4862700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 2234313 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32621
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 2527872
| Rangpur Area Total |  |  |  | 720 | 412 | 9657506
| Total |  |  |  | 21396 | 12494 | 282115426
| Eastern Grid Total |  |  |  | 14205 | 7826 | 174263398
| Western Grid Total |  |  |  | 7191 | 4668 | 107852028
| National Grid Total |  |  |  | 21396 | 12494 | 282115426
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-20
(a) ENTIRE EASTERN GRID : |  | 7990.4 | MW | (b) ENTIRE WESTERN GRID : |  | 3990.85 | MW
i) Dhaka area |  | 4339.3 | MW | i) Khulna area |  | 1549.8 | MW
ii) Chittagong area |  | 1234.1 | MW | ii) Rajshahi area |  | 1316.2 | MW
iii) Comilla area |  | 1070 | MW | iii) Barisal area |  | 373.85 | MW
iv) Mymensingh area |  | 903 | MW | iv) Rangpur area |  | 751 | MW
v) Sylhet area |  | 444 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11981.25 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 21 | 14:00 | Chowmuhani | 192 | 06:00 | Kaptai | 4.2 | 19:30 | Nawabganj | 40 | 21:00 | Siddhirganj | 110 | 10:00
AKSML | 128 | 07:00 | Chuadanga | 96 | 14:00 | Kazla | 82 | 10:00 | Netrakona | 101 | 19:00 | Sirajganj | 97 | 21:00
Aftabnagar | 31 | 00:00 | Coxsbazar | 124 | 22:00 | Keranigonj | 58 | 15:00 | New | 81.1 | 09:00 | Sonargaon | 88 | 03:00
Agargaon | 88 | 10:00 | Cumilla(N) | 140 | 20:00 | Khagrachori | 30 | 19:30 | Niamatpur | 96 | 05:00 | Sreemongol | 47 | 04:00
Agrabad | 76 | 15:00 | Cumilla(S) | 182 | 00:00 | Khulna | 90 | 21:00 | Noapara | 47 | 21:00 | Srinagar | 35.5 | 21:00
Amnura | 58 | 03:00 | Daudkandi | 130 | 02:00 | Khulshi | 170 | 20:00 | PHP | 9 | 05:00 | Sunamganj | 37 | 21:00
Ashuganj | 43 | 05:00 | Dhaka | 40 | 11:00 | Kishoreganj | 126 | 22:00 | Pabna | 107 | 18:30 | Sylhet | 140 | 19:00
BSRM | 160 | 05:00 | Dhamrai | 112 | 21:00 | Kodda | 286 | 08:00 | Palashbari | 112 | 06:00 | TK | 30.6 | 23:00
Bagerhat | 94 | 21:00 | Dhanmondi | 117 | 14:00 | Kulaura | 38 | 04:00 | Panchagarh | 49 | 18:00 | Tangail | 179 | 22:00
Bakulia | 119 | 19:00 | Dohazari | 84 | 00:00 | Kurigram | 56 | 06:00 | Patuakhali | 129 | 00:00 | Thakurgaon | 77 | 22:00
Banani | 56 | 11:00 | Faridpur | 130 | 22:00 | Kushtia | 114 | 22:00 | Payra | 0.92 | 09:00 | Tongi | 102 | 09:00
Bangabhaban | 22 | 11:00 | Fatullah | 63 | 09:00 | Lalbag | 96 | 11:00 | Purbachal | 17 | 00:00 | Ullon | 43 | 00:00
Barapukuria | 55 | 22:00 | Fenchuganj | 40 | 03:00 | Lalmonirhat | 47 | 07:00 | Purbasadipur | 112 | 07:00 | Uttara | 88 | 15:00
Barguna | 20 | 00:00 | Feni | 88 | 03:00 | Madanganj | 92 | 05:00 | Rahim | 28 | 15:00 | UttaraNew | 18 | 00:00
Barishal | 103 | 19:00 | GPH | 11 | 03:00 | Madaripur | 98 | 22:00 | Rajbari | 62 | 02:00 | Zigatola | 53 | 00:00
Barishal-230 | 72 | 19:30 | Ghorashal | 63 | 00:00 | Madartek | 80 | 00:00 | Rajendrapur | 106 | 00:00
Baroaulia | 72 | 23:00 | Goalpara | 28 | 12:00 | Madunaghat | 59 | 19:30 | Rajshahi | 158 | 22:00
Baroirhat | 55 | 19:30 | Gollamari | 56 | 19:30 | Magura | 54 | 21:00 | Rajshahi-230 | 34 | 00:00
Bashundhara | 149 | 09:00 | Gopalganj | 100.2 | 00:00 | Mahasthangarh | 68 | 21:00 | Ramganj | 100 | 21:00
BashundharaCement | 7 | 00:00 | Gulshan | 116 | 10:00 | Manikganj | 93 | 21:00 | Rampur | 15 | 00:00
Beanibazar | 50 | 01:00 | Halishahar | 106 | 08:00 | Maniknagar | 74 | 17:00 | Rangamati | 12 | 20:00
Benapole | 58 | 21:00 | HaripurSBU | 133 | 19:30 | Matarbari | 44 | 19:30 | Rangpur | 142 | 18:00
Bhaluka | 110 | 22:00 | Hasnabad | 88 | 22:00 | Matuail | 58 | 12:00 | Ruppur | 4.8 | 10:00
Bhandaria | 54 | 22:00 | Hathazari | 88 | 15:00 | Millgate | 72 | 16:00 | SSM | 18 | 00:00
Bhangura | 32 | 19:00 | Ishurdi | 74 | 22:00 | Mirpur | 128 | 18:00 | Saidpur | 99 | 20:00
Bheramara(GK) | 58 | 22:00 | Jaldhaka | 48 | 18:30 | Mirsorai | N/A | N/A | Satkhira | 108 | 21:00
Bhulta | 228 | 22:00 | Jamalpur | 132 | 18:30 | Mithapukur | 34 | 04:00 | Satmasjid | 100 | 00:00
Bog-Sherpur | 56 | 04:00 | Jashore | 126 | 21:00 | Modern | 0 | 00:00 | Savar | 169 | 21:00
Bogura | 163 | 21:00 | Jhenaidah | 114 | 21:00 | Mogbazar | 124 | 12:00 | Shahjadpur | 90 | 21:00
Borhanuddin | 41 | 00:00 | Joydebpur | 177 | 22:00 | Mongla | 32 | 12:00 | Shahjibazar | 100 | 22:00
Brahmanbaria | 150 | 22:00 | Joypurhat | 56 | 21:00 | Motijheel | 35 | 16:00 | Shahmirpur | 50.5 | 17:00
Cantonment | 140 | 14:00 | Juldah | 28 | 11:00 | Munshiganj | 98 | 22:00 | Shariatpur | 80 | 00:00
Chandpur | 61 | 21:00 | KSRM | 32.4 | 13:00 | Mymensingh | 199 | 18:30 | Sherpur | 116 | 22:00
Chandraghona | 30 | 19:00 | Kabirpur | 267 | 09:00 | Naogaon | 116 | 22:00 | Shikalbaha | 30 | 12:00
Chapai | 72 | 11:00 | Kachua | 66 | 23:00 | Narail | 45 | 22:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 44 | 14:00 | Kallyanpur | 99 | 00:00 | Narinda | 62 | 15:00 | Shitalakhya | 115 | 11:00
Chauddagram | 47 | 22:00 | Kalurghat | 5 | 15:00 | Narshingdi | 146 | 19:30 | Sholosohor | N/A | N/A
Chhatak | 26 | 20:00 | Kamrangirchar | 52 | 18:30 | Natore | 123 | 05:00 | Shyampur | 148 | 09:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 397 | 06:00 | 382 | 11:00 | Kaliakoir | 391 | 06:00 | 383 | 11:00
| Bibiana | 409 | 20:00 | 400 | 10:00 | Payra | 420 | 09:00 | 406 | 10:00
| BIPTC | 402 | 00:00 | 394 | 12:00
| Gopalganj_I | 414 | 18:00 | 395 | 03:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 225 | 06:00 | 213 | 10:00 | Hasnabad | 224 | 19:30 | 212 | 15:00
| AKSML | 237 | 08:00 | 222 | 14:00 | Hathazari | 237 | 21:00 | 229 | 14:00
| Aminbazar | 225 | 05:00 | 216 | 11:00 | Ishurdi | 236 | 00:00 | 229 | 05:00
| Ashuganj | 238 | 06:00 | 230 | 15:00 | Jhenaidah | 230 | 00:00 | 221 | 07:00
| Baghabari | 234 | 00:00 | 229 | 07:00 | Kaliakoir | 226 | 05:00 | 217 | 08:00
| Barapukuria | 223 | 11:00 | 215 | 06:00 | Keranigonj | 224 | 06:00 | 212 | 10:00
| Barishal | 245 | 08:00 | 235 | 23:00 | Khulna(S) | 241 | 08:00 | 230 | 21:00
| Bheramara | 233 | 00:00 | 225 | 03:00 | Maniknagar | 225 | 04:00 | 218 | 10:00
| Bhulta | 228 | 05:00 | 220 | 10:00 | Meghnaghat | 228 | 19:00 | 220 | 11:00
| Bibiana | 238 | 07:00 | 231 | 10:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 18:30 | 226 | 22:00 | Rajshahi | 233 | 00:00 | 225 | 03:00
| Bogura | 227 | 19:00 | 218 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 08:00 | 238 | 10:00 | Rampura | 235 | 01:00 | 218 | 10:00
| BSRM | 235 | 06:00 | 225 | 14:00 | Shikalbaha | 238 | 09:00 | 229 | 15:00
| Cumilla(N) | 229 | 18:00 | 222 | 11:00 | Shyampur | 223 | 04:00 | 214 | 10:00
| Fenchuganj | 238 | 18:30 | 234 | 00:00 | Siddhirganj | 227 | 20:00 | 218 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:00 | 228 | 07:00
| GPH | 234 | 00:00 | 227 | 13:00 | Tongi | 244 | 13:00 | 219 | 10:00
| Haripur | 225 | 20:00 | 217 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 06:00 | 120 | 14:00 | Lalbag | 135 | 06:00 | 127 | 10:00
| Agargaon | 134 | 06:00 | 125 | 10:00 | Lalmonirhat | 130 | 00:00 | 121 | 07:00
| Agrabad | 139 | 00:00 | 133 | 13:00 | Madanganj | 133 | 18:00 | 128 | 10:00
| AKS | 138 | 06:00 | 131 | 12:00 | Madaripur | 139 | 08:00 | 134 | 00:00
| Aminbazar | 132 | 20:00 | 123 | 11:00 | Madartek | 136 | 06:00 | 127 | 10:00
| Amnura | 132 | 18:30 | 126 | 05:00 | Madunaghat | 139 | 04:00 | 134 | 12:00
| Ashuganj | 136 | 06:00 | 134 | 10:00 | Magura | 140 | 08:00 | 130 | 22:00
| Bagerhat | 136 | 08:00 | 126 | 22:00 | Mahasthangarh | 135 | 18:30 | 127 | 07:00
| Bakulia | 140 | 00:00 | 134 | 11:00 | Manikganj | 135 | 20:00 | 129 | 01:00
| Banani | 134 | 06:00 | 127 | 09:00 | Maniknagar | 130 | 06:00 | 123 | 10:00
| Bangabhaban | 128 | 02:00 | 123 | 15:00 | Matarbari | 132 | 09:00 | 120 | 19:00
| Barapukuria | 137 | 11:00 | 130 | 06:00 | Matuail | 133 | 19:30 | 127 | 14:00
| Barguna | 138 | 18:30 | 130 | 10:00 | Millgate | 135 | 06:00 | 126 | 10:00
| Barishal | 139 | 09:00 | 128 | 11:00 | Mirpur | 131 | 20:00 | 122 | 14:00
| Barishal-230 | 140 | 08:00 | 132 | 23:00 | Mithapukur | 134 | 11:00 | 125 | 07:00
| Baroaulia | 140 | 00:00 | 135 | 13:00 | Modern | 139 | 00:00 | 134 | 12:00
| Baroirhat | 135 | 19:30 | 124 | 05:00 | Mogbazar | 136 | 03:00 | 127 | 15:00
| Bashundhara | 134 | 05:00 | 126 | 14:00 | Mongla | 135 | 08:00 | 126 | 21:00
| BashundharaCement | 133 | 18:00 | 128 | 10:00 | Motijheel | 128 | 02:00 | 123 | 15:00
| Beanibazar | 130 | 08:00 | 126 | 01:00 | Munshiganj | 135 | 20:00 | 128 | 10:00
| Benapole | 137 | 08:00 | 126 | 22:00 | Mymensingh | 131 | 15:00 | 120 | 07:00
| Bhaluka | 131 | 15:00 | 119 | 07:00 | Naogaon | 132 | 18:30 | 119 | 07:00
| Bhandaria | 138 | 10:00 | 127 | 22:00 | Narail | 137 | 18:00 | 129 | 22:00
| Bhangura | 139 | 18:00 | 134 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 00:00 | 134 | 04:00 | Narshingdi | 137 | 18:00 | 127 | 11:00
| Bheramara(GK) | 140 | 18:00 | 135 | 05:00 | Natore | 135 | 00:00 | 120 | 06:00
| Bhulta | 128 | 19:30 | 120 | 15:00 | Nawabganj | 135 | 05:00 | 127 | 10:00
| Bog-Sherpur | 136 | 00:00 | 128 | 07:00 | Netrakona | 130 | 16:00 | 123 | 00:00
| Bogura | 137 | 11:00 | 130 | 06:00 | New | 133 | 04:00 | 127 | 14:00
| Bogura-230 | 138 | 19:00 | 129 | 07:00 | Niamatpur | 129 | 09:00 | 113 | 07:00
| Brahmanbaria | 138 | 14:00 | 129 | 09:00 | Noapara | 139 | 08:00 | 129 | 14:00
| Cantonment | 132 | 06:00 | 123 | 10:00 | Pabna | 136 | 00:00 | 132 | 03:00
| Chandpur | 140 | 18:00 | 125 | 01:00 | Palashbari | 132 | 00:00 | 125 | 06:00
| Chandraghona | 140 | 08:00 | 134 | 14:00 | Panchagarh | 137 | 00:00 | 122 | 17:00
| Chapai | 131 | 00:00 | 125 | 07:00 | Patuakhali | 137 | 18:30 | 131 | 16:00
| Charsaidpur | 135 | 20:00 | 128 | 14:00 | Payra | 138 | 18:30 | 135 | 01:00
| Chauddagram | 135 | 20:00 | 125 | 04:00 | PHP | 135 | 19:30 | 124 | 03:00
| Chhatak | 130 | 07:00 | 126 | 00:00 | Purbachal | 134 | 06:00 | 126 | 09:00
| Chowmuhani | 134 | 21:00 | 117 | 05:00 | Purbasadipur | 133 | 10:00 | 125 | 18:00
| Chuadanga | 137 | 08:00 | 126 | 21:00 | Rahim | 134 | 20:00 | 129 | 10:00
| Coxsbazar | 131 | 09:00 | 120 | 14:00 | Rajbari | 135 | 09:00 | 129 | 03:00
| Cumilla(N) | 136 | 20:00 | 130 | 01:00 | Rajendrapur | 135 | 18:00 | 129 | 00:00
| Cumilla(S) | 135 | 19:30 | 127 | 02:00 | Rajshahi | 133 | 00:00 | 128 | 05:00
| Daudkandi | 133 | 18:00 | 127 | 02:00 | Rajshahi-230 | 133 | 00:00 | 127 | 07:00
| Dhaka | 136 | 06:00 | 128 | 10:00 | Ramganj | 135 | 18:00 | 121 | 03:00
| Dhamrai | 131 | 04:00 | 125 | 10:00 | Rampur | 139 | 09:00 | 133 | 14:00
| Dhanmondi | 136 | 01:00 | 129 | 10:00 | Rampura | 136 | 03:00 | 126 | 01:00
| Dohazari | 138 | 08:00 | 128 | 14:00 | Rangamati | 138 | 00:00 | 134 | 14:00
| Faridpur | 136 | 18:30 | 13 | 02:00 | Rangpur | 132 | 00:00 | 123 | 06:00
| Fatullah | 135 | 20:00 | 127 | 11:00 | Ruppur | 138 | 18:00 | 132 | 03:00
| Fenchuganj | 135 | 13:00 | 132 | 00:00 | Saidpur | 134 | 00:00 | 124 | 07:00
| Feni | 136 | 19:30 | 124 | 02:00 | Satkhira | 136 | 08:00 | 125 | 21:00
| Ghorashal | 138 | 01:00 | 135 | 15:00 | Satmasjid | 133 | 06:00 | 125 | 10:00
| Goalpara | 139 | 08:00 | 130 | 19:00 | Savar | 131 | 05:00 | 121 | 10:00
| Gollamari | 138 | 08:00 | 130 | 00:00 | Shahjadpur | 142 | 05:00 | 138 | 06:00
| Gopalganj | 142 | 08:00 | 135 | 19:00 | Shahjibazar | 135 | 13:00 | 131 | 19:00
| Gopalganj_I | 141 | 18:00 | 134 | 03:00 | Shahmirpur | 141 | 07:00 | 134 | 14:00
| Gulshan | 135 | 04:00 | 128 | 10:00 | Shariatpur | 139 | 18:00 | 130 | 00:00
| Halishahar | 139 | 00:00 | 133 | 12:00 | Sherpur | 134 | 16:00 | 119 | 07:00
| Haripur | 134 | 20:00 | 129 | 10:00 | Shikalbaha | 141 | 08:00 | 135 | 14:00
| HaripurSBU | 134 | 19:30 | 129 | 10:00 | Shikalbaha-230 | 141 | 09:00 | 134 | 15:00
| Hasnabad | 136 | 19:30 | 128 | 10:00 | Shitalakhya | 136 | 05:00 | 127 | 10:00
| Hathazari | 139 | 19:30 | 135 | 14:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 00:00 | 134 | 03:00 | Shyampur | 135 | 20:00 | 126 | 09:00
| Jaldhaka | 132 | 08:00 | 124 | 05:00 | Shyampur-230 | 134 | 19:30 | 126 | 10:00
| Jamalpur | 137 | 18:00 | 122 | 07:00 | Siddhirganj | 133 | 05:00 | 128 | 15:00
| Jashore | 139 | 08:00 | 125 | 22:00 | Sirajganj | 136 | 10:00 | 130 | 07:00
| Jhenaidah | 141 | 08:00 | 133 | 21:00 | Sonargaon | 134 | 19:30 | 128 | 14:00
| Jhenaidah-230 | 141 | 08:00 | 134 | 21:00 | Sreemongol | 135 | 05:00 | 132 | 23:00
| Joydebpur | 143 | 18:00 | 136 | 09:00 | Srinagar | 134 | 20:00 | 127 | 15:00
| Joypurhat | 132 | 18:30 | 116 | 07:00 | SSM | 142 | 00:00 | 138 | 13:00
| Juldah | 140 | 00:00 | 135 | 12:00 | Sunamganj | 128 | 10:00 | 125 | 03:00
| Kabirpur | 137 | 18:00 | 124 | 10:00 | Sylhet | 132 | 13:00 | 130 | 00:00
| Kachua | 139 | 18:00 | 125 | 04:00 | Tangail | 135 | 09:00 | 129 | 07:00
| Kaliakoir | 137 | 05:00 | 135 | 00:00 | Thakurgaon | 134 | 00:00 | 122 | 17:00
| Kallyanpur | 131 | 20:00 | 123 | 10:00 | TK | 141 | 03:00 | 134 | 14:00
Page 7 of 7

## L-Curve
Date | 2022-07-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 524 | 7583 | 4617 | 12200 |  |  |  | QF-LDC-11
0:30 | 614 | 7385.5 | 4586.5 | 11972 | Date: | 2022-07-20
1:00 | 704 | 7188 | 4556 | 11744
1:30 | 685 | 7189 | 4563 | 11752
2:00 | 666 | 7190 | 4570 | 11760
2:30 | 628 | 7176 | 4573.5 | 11749.5 | [5 empty] | Gen. at Eve. Peak | 12494 | 12494 MW (21:00 )
3:00 | 590 | 7162 | 4577 | 11739 | [6 empty] | 21:00
3:30 | 545 | 7184 | 4553 | 11737 | [5 empty] | Gen. at Day Peak | 11155 | 11155 MW (10:00 )
4:00 | 500 | 7206 | 4529 | 11735 | [6 empty] | 10:00
4:30 | 480 | 7202 | 4482.5 | 11684.5 | [5 empty] | Highest Generation | 12567
5:00 | 460 | 7198 | 4436 | 11634 | [6 empty] | 22:00
5:30 | 449 | 7144.5 | 4365 | 11509.5
6:00 | 438 | 7091 | 4294 | 11385
6:30 | 439 | 7098.5 | 4253 | 11351.5
7:00 | 440 | 7106 | 4212 | 11318
7:30 | 557 | 7092.5 | 4157.5 | 11250
8:00 | 674 | 7079 | 4103 | 11182
8:30 | 726 | 7055 | 4063 | 11118
9:00 | 778 | 7031 | 4023 | 11054
9:30 | 847 | 7001.5 | 4103 | 11104.5
10:00 | 916 | 6972 | 4183 | 11155
10:30 | 910 | 6959.5 | 4182 | 11141.5
11:00 | 904 | 6947 | 4181 | 11128
11:30 | 888 | 6894.5 | 4197.5 | 11092
12:00 | 872 | 6842 | 4214 | 11056
12:30 | 844 | 6881.5 | 4222.5 | 11104
13:00 | 816 | 6921 | 4231 | 11152
13:30 | 851 | 6940 | 4227.5 | 11167.5
14:00 | 886 | 6959 | 4224 | 11183
14:30 | 893 | 7029.5 | 4198.5 | 11228
15:00 | 900 | 7100 | 4173 | 11273
15:30 | 876 | 7047 | 4167 | 11214
16:00 | 852 | 6994 | 4161 | 11155
16:30 | 783 | 7054 | 4172 | 11226
17:00 | 714 | 7114 | 4183 | 11297
17:30 | 679 | 7164 | 4179.5 | 11343.5
18:00 | 644 | 7214 | 4176 | 11390
18:30 | 650 | 7389 | 4273 | 11662
19:00 | 656 | 7564 | 4370 | 11934
19:30 | 620 | 7727 | 4618 | 12345
20:00 | 586 | 7789 | 4598 | 12387 |  |  |  | Executive Engineer
20:30 | 532 | 7807.5 | 4633 | 12440.5 |  |  |  | Network Operation Division
21:00 | 478 | 7826 | 4668 | 12494
21:30 | 481 | 7838.5 | 4692 | 12530.5
22:00 | 484 | 7851 | 4716 | 12567 |  |  |  |  | Page 6 of 7
22:30 | 526 | 7777.5 | 4717 | 12494.5
23:00 | 568 | 7704 | 4718 | 12422
23:30 | 546 | 7643.5 | 4667.5 | 12311
24:00 | 524 | 7583 | 4617 | 12200
12494 MW (21:00 )
11155 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-20 |  | Energy |  | 282115426
[13 empty] | 2022-07-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3892 | 854 | 1652 | 0 | 3453 | 1259 | 126 | 213 | 838 | 126 | 0 | 0
0:30 | 3844.5 | 883 | 1611 | 0 | 3303.5 | 1264.5 | 126.5 | 210 | 809 | 130 | 0 | 0 | Date: | 2022-07-20
1:00 | 3797 | 912 | 1570 | 0 | 3154 | 1270 | 127 | 207 | 780 | 134 | 0 | 0
1:30 | 3796.5 | 912 | 1578.5 | 0 | 3159 | 1270 | 126 | 209.5 | 779 | 131 | 0 | 0 | [8 empty] | Total Energy | 282.1154 | Total Energy Gen 282.115 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 282.115 MKWHr
2:00 | 3796 | 912 | 1587 | 0 | 3164 | 1270 | 125 | 212 | 778 | 128 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3799 | 912 | 1600.5 | 0 | 3138.5 | 1270 | 125 | 212.5 | 777.5 | 127 | 0 | 0 | [8 empty] | Energy Requirement | 282.1154
3:00 | 3802 | 912 | 1614 | 0 | 3113 | 1270 | 125 | 213 | 777 | 126 | 0 | 0
3:30 | 3809.5 | 912 | 1616 | 0 | 3131 | 1245 | 125 | 213.5 | 772.5 | 126 | 0 | 0 | [6 empty] | Shortage
4:00 | 3817 | 912 | 1618 | 0 | 3149 | 1220 | 125 | 214 | 768 | 126 | 0 | 0
4:30 | 3821 | 912 | 1618 | 0 | 3140.5 | 1199.5 | 126 | 213 | 743.5 | 124 | 0 | 0
5:00 | 3825 | 912 | 1618 | 0 | 3132 | 1179 | 127 | 212 | 719 | 122 | 0 | 0
5:30 | 3800.5 | 912 | 1582.5 | 0 | 3100 | 1179 | 127 | 181 | 687.5 | 119 | 2 | 0
6:00 | 3776 | 912 | 1547 | 0 | 3068 | 1179 | 127 | 150 | 656 | 116 | 4 | 0
6:30 | 3775 | 912 | 1571.5 | 0 | 3032 | 1164 | 127 | 140 | 638.5 | 113 | 18.5 | 0 |  |  |  |  | Coal
7:00 | 3774 | 912 | 1596 | 0 | 2996 | 1149 | 127 | 130 | 621 | 110 | 33 | 0
7:30 | 3775 | 912 | 1530.5 | 0 | 2993 | 1149.5 | 127 | 130 | 615.5 | 105 | 42.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3776 | 912 | 1465 | 0 | 2990 | 1150 | 127 | 130 | 610 | 100 | 52 | 0
8:30 | 3751.5 | 911.5 | 1462.5 | 0 | 2997 | 1100 | 126.5 | 130 | 605.5 | 98 | 65.5 | 0
9:00 | 3727 | 911 | 1460 | 0 | 3004 | 1050 | 126 | 130 | 601 | 96 | 79 | 0
9:30 | 3743 | 894.5 | 1518.5 | 0 | 2991 | 1049.5 | 125.5 | 130 | 601.5 | 97 | 84 | 0
10:00 | 3759 | 878 | 1577 | 0 | 2978 | 1049 | 125 | 130 | 602 | 98 | 89 | 0
10:30 | 3754 | 878 | 1554 | 0 | 2997 | 1069.5 | 125 | 130 | 571.5 | 101 | 91.5 | 0
11:00 | 3749 | 878 | 1531 | 0 | 3016 | 1090 | 125 | 130 | 541 | 104 | 94 | 0
11:30 | 3658 | 875.5 | 1535 | 0 | 3035.5 | 1110 | 125.5 | 130 | 543 | 103 | 106.5 | 0
12:00 | 3567 | 873 | 1539 | 0 | 3055 | 1130 | 126 | 130 | 545 | 102 | 119 | 0
12:30 | 3558 | 872.5 | 1590 | 0 | 3029 | 1130 | 126.5 | 130 | 543 | 110 | 145 | 0
13:00 | 3549 | 872 | 1641 | 0 | 3003 | 1130 | 127 | 130 | 541 | 118 | 171 | 0
13:30 | 3549 | 872 | 1641 | 0 | 3003 | 1130 | 127 | 130 | 541 | 118 | 171 | 0
14:00 | 3549 | 872 | 1641 | 0 | 3003 | 1130 | 127 | 130 | 541 | 118 | 171 | 0
14:30 | 3674 | 870.5 | 1612 | 0 | 3003 | 1144.5 | 127 | 130 | 533 | 119 | 129.5 | 0
15:00 | 3799 | 869 | 1583 | 0 | 3003 | 1159 | 127 | 130 | 525 | 120 | 88 | 0
15:30 | 3742 | 869 | 1574 | 0 | 3004 | 1159 | 127 | 130 | 544 | 120 | 75 | 0
16:00 | 3685 | 869 | 1565 | 0 | 3005 | 1159 | 127 | 130 | 563 | 120 | 62 | 0
16:30 | 3696 | 868.5 | 1539.5 | 0 | 3105.5 | 1139.5 | 127 | 130 | 583 | 113 | 59.5 | 0
17:00 | 3696 | 868 | 1514 | 0 | 3206 | 1120 | 127 | 130 | 603 | 106 | 57 | 0
17:30 | 3677 | 868.5 | 1494 | 0 | 3303 | 1125 | 127 | 130 | 613.5 | 102 | 33.5 | 0
18:00 | 3658 | 869 | 1474 | 0 | 3400 | 1130 | 127 | 130 | 624 | 98 | 10 | 0
18:30 | 3703 | 861 | 1509.5 | 0 | 3583 | 1110 | 127 | 142 | 664.5 | 99 | 5 | 0
19:00 | 3748 | 853 | 1545 | 0 | 3766 | 1090 | 127 | 154 | 705 | 100 | 0 | 0
19:30 | 3769 | 854 | 1587 | 0 | 3916 | 1200 | 127 | 205 | 784 | 108 | 0 | 0
20:00 | 3786 | 855 | 1568 | 0 | 3942 | 1200 | 125 | 180 | 797 | 114 | 0 | 0
20:30 | 3784.5 | 854.5 | 1600 | 0 | 3941 | 1204.5 | 125 | 190.5 | 811 | 120 | 0 | 0
21:00 | 3783 | 854 | 1632 | 0 | 3940 | 1209 | 125 | 201 | 825 | 126 | 0 | 0
21:30 | 3793.5 | 854.5 | 1648.5 | 0 | 3940.5 | 1214 | 125 | 207.5 | 827.5 | 127 | 0 | 0
22:00 | 3804 | 855 | 1665 | 0 | 3941 | 1219 | 125 | 214 | 830 | 128 | 0 | 0
22:30 | 3806 | 854.5 | 1671.5 | 0 | 3845.5 | 1234 | 125.5 | 212 | 831.5 | 126 | 0 | 0
23:00 | 3808 | 854 | 1678 | 0 | 3750 | 1249 | 126 | 210 | 833 | 124 | 0 | 0
23:30 | 3850 | 854 | 1665 | 0 | 3601.5 | 1254 | 126 | 211.5 | 835.5 | 125 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.8° C
24:00 | 3892 | 854 | 1652 | 0 | 3453 | 1259 | 126 | 213 | 838 | 126 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 282.115 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 282.115 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 90 | 90 | 90 | 92 | 92 | 92 | 92 | 91 | 90 | 90 | 91 | 92 | 92 | 92 | 92 | 92 | 92 |  | 92 | 92 | 90 | 90 | 90 | 91 | 91 | 2165591
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 591057
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 12 | 2 | 7 | 16 | 17 | 4 | 7 | 0 | [11 empty] | 71280
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 57 | 68 | 68 | 68 | 68 | 1292769
12 | Hathazari 100 MW peaking PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 42 | 41 | 41 | 43 | 34 | 28 | 19 | 28 | 42 | 42 |  | 42 | 42 | 51 | 51 | 51 | 51 | 51 | 1053760
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2534181
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 41 | 41 | 41 | 48 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1089056
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 258 | 258 | 255 | 255 | 255 | 250 | 243 | 257 | 257 | 257 | 257 | 257 | 258 | 250 | 253 | 263 | 263 | 273 |  | 273 | 273 | 273 | 275 | 275 | 275 | 260 | 6242616
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 300 |  | 270 | 290 | 300 | 300 | 300 | 310 | 310 | 7193764
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 36 | 37 | 37 | 37 | 40 | 40 |  | 40 | 40 | 40 | 41 | 41 | 41 | 40 | 584856
33 | Ashuganj 225 MW CCPP | 213 | 211 | 212 | 212 | 211 | 213 | 211 | 212 | 212 | 209 | 209 | 208 | 213 | 209 | 174 | 167 | 190 | 204 |  | 206 | 210 | 211 | 208 | 206 | 205 | 211 | 4985000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 265 | 305 | 305 | 305 | 265 | 325 | 270 | 265 | 265 |  | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 7059000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 310 | 290 | 285 | 320 | 285 | 285 | 285 |  | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 7406100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 303 | 311 | 318 | 328 | 338 | 343 | 348 | 349 | 344 | 361 | 356 | 352 | 357 | 363 | 370 | 369 | 364 | 354 |  | 348 | 341 | 342 | 334 | 327 | 328 | 350 | 8367280
40 | Meghnaghat 450 MW CCPP(MPL) | 190 | 190 | 200 | 200 | 200 | 200 | 210 | 210 | 215 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4726000
41 | Haripur 360MW CCPP(HPL) | 213 | 233 | 244 | 243 | 223 | 216 | 261 | 274 | 282 | 278 | 255 | 257 | 268 | 272 | 273 | 265 | 262 | 262 |  | 250 | 250 | 251 | 243 | 235 | 235 | 252 | 6052000
42 | RPCL 210MW CCPP | 107 | 106 | 108 | 108 | 106 | 107 | 104 | 100 | 83 | 83 | 80 | 69 | 69 | 68 | 68 | 69 | 69 | 69 |  | 105 | 106 | 106 | 106 | 106 | 105 | 108 | 2125440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 7 | 5 | 20 | 18 | 27 | 33 | 54 | 32 | 8 | 14 | 18 | 4 |  | 0 | [6 empty] | 240560
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 934804
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 61 | 62 | 64 | 62 | 63 | 62 | 64 | 62 | 58 | 58 | 58 | 58 | 58 | 58 | 59 | 58 | 63 |  | 60 | 61 | 61 | 60 | 60 | 59 | 61 | 1437560
48 | Shahjibazar 86MW PP (Shahjibazar) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 78 | 25 | 25 | 25 | 25 | 25 |  | 25 | 50 | 50 | 50 | 50 | 50 | 25 | 816960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5376650
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238500
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [12 empty] | 22 | 0 | [11 empty] | 0 | 21600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 151392
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 290 | 305 | 280 | 275 | 285 | 260 | 290 | 270 | 290 | 300 | 280 | 315 | 300 | 280 | 280 |  | 270 | 280 | 290 | 300 | 320 | 330 | 310 | 7267500
| Bibiyana South 400 MW | 395 | 400 | 400 | 400 | 398 | 350 | 350 | 360 | 370 | 392 | 394 | 160 | 160 | 391 | 387 | 380 | 370 | 340 |  | 380 | 400 | 400 | 380 | 390 | 392 | 398 | 8763200
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 286512
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 20 | 20 | 22 | 22 | 22 | 12 | 14 | 22 | 22 | 15 | 22 | 22 | 22 | 22 | 14 | 17 |  | 22 | 22 | 22 | 22 | 18 | 19 | 22 | 486720
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 446208
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 410184
62 | Tangail 22 MW PP (Doreen) | 11 | 13 | 16 | 17 | 17 | 17 | 18 | 19 | 19 | 19 | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 8 | 8 | 338292
63 | Impoprt (Tripura) | 134 | 128 | 126 | 126 | 122 | 116 | 110 | 100 | 96 | 98 | 104 | 102 | 118 | 120 | 120 | 120 | 106 | 98 |  | 100 | 108 | 114 | 126 | 128 | 124 | 126 | 2760000
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 30 | 38 | 32 | 42 | 41 | 8 | 10 | 7 | 3 | 3 | 4 | 2 | 4 | 10 | 5 | 9 |  | 14 | 10 | 20 | 30 | 36 | 39 | 40 | 490560
65 | Feni 22MW PP (Doreen) | 21 | 21 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 431208
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 231480
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 28 | 25 | 25 | 14 | 10 |  |  | 16 | 16 | 16 | 16 | 25 | 33 | 30 |  | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 602500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 12 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 507930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 22 | 26 | 23 | 23 | 23 | 27 | 12 |  | 14 | 14 | 24 | 24 | 27 | 24 | 27 | 577440
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 620560
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 32 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 28 | 28 | 26 | 26 | 26 | 26 | 26 |  | 26 | 27 | 28 | 28 | 28 | 28 | 32 | 691800
73 | Ghorashal 108MW PP (Regent) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 86 | 86 | 84 | 80 | 82 | 80 | 80 | 81 |  | 88 | 92 | 85 | 88 | 88 | 88 | 88 | 2039681
| Feni Lanka Power | [19 empty] | 99 | 99 | 99 | 99 | 99 | 99 | 23 | 458280
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 10 | 9 |  | 12 | 56 | 56 | 56 | 58 | 58 | 58 | 477960
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 44 | 90 | 120 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 1892160
77 | Siddhirganj 100 PP(Dutch Bangla) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 776141
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 42 | 42 | 42 | 41 | 41 | 47 | 50 |  | 50 | 49 | 49 | 50 | 50 | 50 | 50 | 1129440
79 | Kodda 150MW PP | 125 | 125 | 125 | 125 | 130 | 130 | 115 | 115 | 115 | 115 | 115 | 125 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2931840
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 16 | 16 | 8 | 8 | 234744
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 105 | 105 | 105 | 105 | 90 | 105 | 90 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2454000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 2 | 3 | 1 | 1 | 6 | 1 | 1 | 0 | 0 | [8 empty] | 19080
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 908592
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2240608
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 39 | 39 | 37 | 40 | 43 | 39 | 40 | 39 | 40 | 40 | 40 | 40 | 40 | 36 | 32 | 32 | 30 | 24 |  | 30 | 35 | 33 | 30 | 28 | 22 | 31 | 864000
| Meghnaghat 104 MW PP (OPCL) | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 90 | 88 | 89 | 89 | 89 | 88 | 88 |  | 92 | 104 | 104 | 104 | 104 | 104 | 104 | 2222400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 786360
92 | Fenchuganj 44MW (Energyprima) | [12 empty] | 20 | 0 | [12 empty] | 21672
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1184321
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 86 | 93 | 93 | 85 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 86 | 93 | 2193696
95 | Patenga 50MW PP (Baraka) | 35 | 38 | 0 | 31 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 892320
96 | Chattogram 108 MW PP (ECPV) | 88 | 89 | 82 | 87 | 89 | 89 | 89 | 89 | 89 | 82 | 79 | 84 | 89 | 89 | 89 | 69 | 83 | 77 |  | 89 | 90 | 90 | 90 | 88 | 89 | 90 | 2073600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 1331210
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 50 | 55 | 55 | 55 | 55 | 35 | 0 | 269921
101 | Kushiara 163 MW CCPP (KP) | [25 empty] | 0 | 0
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 |  | 0 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 9300
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 641880
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 116 | 117 | 116 | 116 | 117 | 117 | 117 | 116 | 115 | 115 | 115 | 114 | 115 | 115 | 148 | 174 | 183 | 183 |  | 193 | 193 | 193 | 194 | 184 | 184 | 184 | 3388800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 144 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 143 | 131 | 131 | 135 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3557376
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 63 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1453440
116 | Chandpur 200MW (Desh energy) | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 151 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3502080
117 | Ashuganj 150MW PP (Midland) | 132 | 135 | 137 | 132 | 130 | 132 | 137 | 137 | 138 | 133 | 130 | 132 | 130 | 140 | 140 | 140 | 117 | 130 |  | 133 | 137 | 137 | 140 | 142 | 132 | 132 | 3226690
118 | Bibiyana-III 400 MW CCPP | 402 | 400 | 400 | 399 | 401 | 387 | 370 | 375 | 365 | 403 | 403 | 404 | 403 | 366 | 399 | 366 | 366 | 365 |  | 398 | 377 | 365 | 391 | 404 | 404 | 402 | 9290000
| Jamalpur 115 MW PP (United) | 58 | 59 | 58 | 58 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 104 |  | 105 | 105 | 104 | 104 | 104 | 103 | 58 | 1654800
| Anwara 300 MW PP (United) | 285 | 285 | 285 | 285 | 285 | 267 | 267 | 267 | 267 | 177 | 177 | 192 | 176 | 175 | 175 | 175 | 175 | 175 |  | 261 | 272 | 285 | 285 | 285 | 177 | 177 | 5565164
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 1065600
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 90 | 102 | 108 | 90 | 95 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2553000
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 20 | 17 | 17 | 17 | 17 | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 785880
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 12 | 24 | 24 | 24 | 11 | 6 | 15 | 16 | 3 | 1 | 0 | [8 empty] | 147458
| Chandpur 115(Doreen) | 42 | 53 | 54 | 53 | 53 | 54 | 53 | 54 | 54 | 53 | 54 | 53 | 54 | 53 | 72 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 55 | 1488960
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 46 | 40 | 55 | 55 | 55 | 55 | 0 | 15 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1258560
120 | Eastern Zone Total | 7188 | 7190 | 7162 | 7206 | 7198 | 7091 | 7106 | 7079 | 7031 | 6972 | 6947 | 6842 | 6921 | 6959 | 7100 | 6994 | 7114 | 7214 |  | 7564 | 7727 | 7789 | 7826 | 7851 | 7704 | 7583 | 174263398
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 49 | 65 | 83 | 80 | 80 | 80 | 79 | 61 | 88 | 92 |  | 93 | 94 | 94 | 94 | 111 | 110 | 110 | 1456320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 42 | 40 | 38 | 28 | 0 | [10 empty] | 14 | 39 | 39 |  | 39 | 39 | 44 | 44 | 44 | 44 | 44 | 463680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 75 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 74 | 93 | 75 | 75 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2128320
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 15 | 20 | 28 | 36 | 14 | 46 | 96 | 62 | 54 | 39 | 35 | 5 | [8 empty] | 486000
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [13 empty] | 2 | 10 | 17 | 17 | 17 | 17 | 219600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 154 | 164 | 182 | 183 | 182 | 184 | 218 | 216 | 220 | 195 | 150 |  | 220 | 225 | 183 | 217 | 220 | 220 | 220 | 4951064
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 48 | 48 | 48 | 35 | 32 | 32 | 32 | 719712
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 78 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1979944
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 31 | 31 | 26 | 25 | 23 | 21 | 20 | 19 | 18 | 20 | 22 | 26 | 24 | 24 | 24 |  | 31 | 33 | 32 | 31 | 37 | 36 | 37 | 639513
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 759750
143 | Gopalganj 100 MW Peaking PP | 58 | 58 | 58 | 58 | 58 | 57 | 58 | 55 | 55 | 55 | [6 empty] | 0 | 0 |  | 30 | 55 | 63 | 63 | 62 | 62 | 62 | 912640
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 88 | 85 | 85 | 88 | 88 | 88 | 88 | 88 | 89 | 88 | 89 | 88 | 89 | 104 | 89 | 89 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2305152
146 | Bheramara HVDC | 912 | 912 | 912 | 912 | 912 | 912 | 912 | 912 | 911 | 878 | 878 | 873 | 872 | 869 | 869 | 869 | 868 | 869 |  | 853 | 854 | 855 | 854 | 855 | 854 | 854 | 21275636
147 | Bheramara 410 MW CCPP | 210 | 210 | 205 | 205 | 205 | 205 | 215 | 225 | 220 | 215 | 205 | 200 | 195 | 195 | 190 | 200 | 200 | 200 |  | 200 | 200 | 205 | 205 | 205 | 205 | 205 | 5086944
148 | Payra 1320 MW | 1070 | 1070 | 1070 | 1020 | 980 | 980 | 950 | 950 | 850 | 850 | 890 | 930 | 930 | 930 | 960 | 960 | 920 | 930 |  | 890 | 1000 | 1000 | 1010 | 1020 | 1050 | 1060 | 25210000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 200 | 200 | 199 | 200 | 200 | 200 | 199 | 199 | 199 | 200 | 200 |  | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 4862700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 34 | 34 | 34 | 34 | 34 | 634160
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 1 | 1 | 5 | 2 | 2 | 3 | 3 | 2 | 0 | 0 | [8 empty] | 24840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 141 | 141 | 141 | 142 | 149 | 152 | 155 | 154 | 150 | 152 | 147 | 142 | 140 | 137 | 134 | 136 | 138 | 137 |  | 138 | 140 | 141 | 142 | 144 | 146 | 147 | 3683000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 207 | 212 | 213 | 214 | 212 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 154 | 205 | 180 | 201 | 214 | 210 | 213 | 4228636
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 134 | 124 | 124 | 124 | 124 | 128 | 137 | 137 | 137 | 137 | 137 | 136 | 135 | 133 | 132 | 133 | 135 | 135 |  | 135 | 135 | 135 | 136 | 136 | 137 | 137 | 3457855
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 357 | 365 | 378 | 386 | 397 | 353 | 354 | 302 | 304 | 372 | 373 | 361 | 344 | 341 | 326 | 324 | 325 | 325 |  | 327 | 327 | 337 | 353 | 359 | 360 | 359 | 8422182
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 24 | 24 | 24 | 24 | 0 | [7 empty] | 4 | 5 | 5 | 19 | 30 | 30 |  | 34 | 34 | 34 | 30 | 21 | 28 | 29 | 346232
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 19 | 19 | 18 | 17 | 17 | 18 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 459840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251010
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 776576
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 29 | 32 | 32 | 32 | 32 | 32 | 32 | 638500
168 | Santahar 50 MW Peaking PP | 27 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 33 |  | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 652520
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 43 | 43 | 43 | 43 | 43 | 8 | 355680
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 88 | 88 | 88 | 78 | 78 | 72 | 72 | 70 | 70 | 60 | 70 |  | 86 | 86 | 86 | 86 | 88 | 88 | 89 | 1953056
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | 1 | 88 | 110 | 113 | 106 | 113 | 94 | 94 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2109600
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 70 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1606560
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 100 | 104 | 104 | 104 | 88 | 83 | 83 | 83 | 77 | 79 | 85 | 85 | 83 | 83 | 82 | 82 | 102 | 105 |  | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 2234313
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 |  | 3 | 6 | 6 | 5 | 5 | 3 | 3 | 1 |  | 0 | [6 empty] | 32621
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 72 | 72 |  | 72 | 108 | 108 | 108 | 109 | 109 | 109 | 2527872
178