## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-22 | Friday
|  |  | Date (day): | 2022-07-22 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11406.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12635 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-21 | 2022-07-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 85 | 92 | 92 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 317 | 380 | 380 | 32 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 258 | 213 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 8 | 7 | 7 |  | 93 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 10 | 8 | 8 | 68 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 50 | 88 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 138 | 130 | 140 |  | 9 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 55 |  |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55 |  | 0 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 51 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 29 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 273 | 275 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 135 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 54 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 35 | 162 |  | 0 | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2640 | 2697 | 2675 | 2947 | 1853 | 1027
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 5 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 38 | 38 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 126 | 124 | 82 | 82 |  | 148 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 42 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 17 | 102 |  |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 30 | 30 | 30 | 30 | 70 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 31 | 30 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 76 | 85 | 81 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 177 | 285 | 175 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 100 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 10 | 10 | 10 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1023 | 1259 | 1043 | 1231 | 420 | 641
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 198 | 160 | 180 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 270 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 260 | 300 | 60 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 41 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 138 | 135 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 48 | 48
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 48 | 47 | 80 |  | 83 | Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 120 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 90 | 83 | 113
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 19 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 36 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 12 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 17 | 114 | 0 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 113 | 8 | 113 | 0 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 76 | 54 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1381 | 1711 | 1426 | 1887 | 767 | 127
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 97 | 104 | 85 | 85 |  | 117 | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 16 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 164 | 175 | 186 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 102 | 105 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 20 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 375 | 420 | 471.6 | 434 | 0 | 135
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 60 | 61 | 61
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 25 | 81 | 20 | 50 | 36 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 300 | 330 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1517 | 1569 | 1504 | 1564 | 398 | 505
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 856 | 886 | 871
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 32 | 107 | 32 | 100 | 15 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 44 |  | 10 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 55 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 200 | 225 | 215 | 195 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 8 | 40 |  |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 74 | 17 | 17 | 17 | 88 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1399 | 1425 | 1428 | 1452 | 644 | 59
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 32 | 48 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 30 | 23 | 33 |  | 7 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 82 | 82 | 82 | 82 | 112 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 890 | 1010 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 222 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1248 | 1393 | 1474 | 1500 | 112 | 7
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 34 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 24 | 16 | 30 |  | 41 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 143 | 144 | 170 | 170 | 40 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 142 | 183 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 141 | 139 | 160 | 160 | 60 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 360 | 300 | 340 | 74 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 88 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 70 | 113 |  |  | Fuel shortage
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 987 | 1352 | 1041 | 1207 | 774 | 142
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 79 | 105 | 84 | 105 |  | 8 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 108 | 52 | 108 |  |  | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 333 | 413 | 344 | 413 | 199 | 93
|  | Total |  |  |  |  | 22678 | 21396 | 10903 | 12239 | 11406.6 | 12635 | 5167 | 2736
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11827.0602 | 13276.29 | 12373.3417 | 13705.8521
| A. |  | 2022-07-21 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12239 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10866 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13797 | MW
| 3 | Day peak Generation : |  |  | 10903 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13276.29 | MW
| 4 | Evening peak Generation : |  |  | 12239 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1558 | MW
| 5 | Total Energy Generation : |  | 277.737 | MKWHr | By Solar | 1.3536 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 130.2008 | MKWHr |  | By Oil: | 89.4465 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.4454 | MKWHr |  | By Hydro: | 2.6907 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5167 | MW | Dhaka | 4641.5 | 4261.5 |  | 380
|  |  |  | For Plants S/D or M/C prob = |  |  | 2736 | MW | Chittagong | 1345.7 | 1205.7 |  | 140 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7903 | MW | Khulna | 1677.2 | 1477.2 |  | 200 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 967.9 | MMCFD |  |  | Rajshahi | 1451 | 1255 |  | 196 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 145486092.792 | ii) Oil : | Taka | 1224942887.55 | Comilla | 1241 | 1077 |  | 164 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 256183262 | Total | Taka | 1626612242.342 | Mymensingh | 1131 | 911 |  | 220 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 492 | 434 |  | 58 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 546 | MW (E to W) at | 21:00 | hrs | Barisal | 376.89 | 376.89 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 404 | MW at | 6:00 | hrs | Rangpur | 920 | 720 |  | 200 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 13276.29 | 11718.29 |  | 1558
| B. |  | 2022-07-22 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 236 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12635 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11350 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 292.7369 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10908 | MW at | 8:00 | 0 | 29 | 45 | 48 | 38 | 36 | 11 | 0 | 29
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2691 | MKWHr. | ii) HVDC Flow at Peak Time |  | 856 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3309 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.2 |  | (b) Today: | 91.1 |  | (c) Rule Curve: |  | 87.36
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 365 | 270 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 50 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 51 | 68 | 33 | 88 | 38 | 19 | 40 | 0 | 0 | 0 | 300 | 300 | 201 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 124 | 108 | 0 | 11 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 58 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 183 | 0 | 149 | 0 | 30 | 120 | 133 | 402 | 58 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 15 | 38 | 392 | 104 | 0 | 54 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 903 | 0 | 205 | 0 | 110 | 0 | 0 | 0 | 44 | 60 | 8 | 82 | 37 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 145 | 0 | 0 | 212 | 0 | 0 | 137 | 0 | 358 | 90 | 0 | 70 | 105 | 105 | 0 | 0 | 55 | 1040 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7267 | 4631 | 11898 | 3890 | 903 | 1659 | 0 | 3172 | 1239 | 81 | 212 | 830 | 124 | 0 | 0 | 91.24
2:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 366 | 269 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 32 | 50 | 0 | 47 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 51 | 68 | 33 | 89 | 38 | 19 | 40 | 0 | 0 | 0 | 300 | 300 | 193 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 124 | 106 | 0 | 14 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 25 | 0 | 220 | 0 | 0 | 10 | 315 | 8 | 0 | 0 | 275 | 0 | 0 | 183 | 0 | 149 | 0 | 30 | 120 | 135 | 402 | 59 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 0 | 54 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 904 | 0 | 205 | 0 | 113 | 0 | 0 | 0 | 44 | 60 | 8 | 82 | 36 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 362 | 74 | 0 | 70 | 105 | 105 | 0 | 0 | 55 | 1050 | 220 | 0 | 17 | 0 | 0 | 109 | 0 | 0 |  | 7280 | 4635 | 11915 | 3892 | 904 | 1676 | 0 | 3156 | 1250 | 82 | 213 | 831 | 124 | 0 | 0 | 91.23
3:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 368 | 269 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 32 | 50 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 68 | 33 | 83 | 38 | 19 | 40 | 0 | 0 | 0 | 300 | 300 | 185 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 122 | 108 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 174 | 0 | 149 | 0 | 30 | 120 | 130 | 402 | 59 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 54 | 55 | 0 |  | 903 | 0 | 205 | 0 | 112 | 0 | 0 | 0 | 44 | 59 | 8 | 82 | 35 | 32 | 0 | 0 | 0 | 34 | 32 | 88 | 0 | 34 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 374 | 74 | 0 | 70 | 105 | 105 | 0 | 0 | 55 | 1050 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7276 | 4621 | 11897 | 3890 | 903 | 1672 | 0 | 3122 | 1250 | 128 | 200 | 810 | 122 | 0 | 0 | 91.23
4:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 375 | 270 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 43 | 68 | 33 | 87 | 38 | 19 | 40 | 0 | 0 | 0 | 300 | 300 | 183 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 120 | 107 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 174 | 0 | 149 | 0 | 30 | 120 | 137 | 401 | 59 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 904 | 0 | 215 | 0 | 32 | 0 | 0 | 0 | 44 | 55 | 8 | 82 | 33 | 32 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 380 | 74 | 0 | 70 | 105 | 100 | 0 | 0 | 55 | 1040 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7275 | 4536 | 11811 | 3909 | 904 | 1677 | 0 | 3038 | 1240 | 127 | 200 | 796 | 120 | 0 | 0 | 91.22
5:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 382 | 269 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 43 | 68 | 33 | 85 | 38 | 19 | 40 | 0 | 0 | 0 | 280 | 280 | 193 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 116 | 107 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 273 | 0 | 0 | 164 | 0 | 138 | 0 | 30 | 120 | 137 | 401 | 59 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 0 | 53 | 55 | 0 |  | 904 | 0 | 215 | 0 | 32 | 0 | 0 | 0 | 44 | 55 | 8 | 82 | 32 | 32 | 0 | 0 | 0 | 34 | 33 | 88 | 0 | 34 | 16 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 406 | 74 | 0 | 70 | 105 | 98 | 0 | 0 | 55 | 1040 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7207 | 4557 | 11764 | 3889 | 904 | 1691 | 0 | 3006 | 1240 | 127 | 200 | 791 | 116 | 0 | 0 | 91.21
6:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 384 | 273 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 10 | 0 | 33 | 76 | 38 | 19 | 40 | 0 | 0 | 0 | 280 | 280 | 185 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 110 | 107 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 220 | 0 | 0 | 10 | 270 | 8 | 0 | 0 | 262 | 0 | 0 | 164 | 0 | 140 | 1 | 30 | 120 | 138 | 401 | 59 | 90 | 105 | 0 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 0 | 35 | 108 | 0 | 35 | 1 | 53 | 55 | 0 |  | 904 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 44 | 0 | 8 | 82 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 179 | 0 | 0 | 142 | 0 | 400 | 74 | 0 | 70 | 105 | 84 | 0 | 0 | 55 | 970 | 220 | 0 | 17 | 0 | 4 | 108 | 0 | 0 |  | 7052 | 4241 | 11293 | 3890 | 904 | 1665 | 0 | 2963 | 1169 | 127 | 179 | 459 | 110 | 6 | 0 | 91.2
7:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 368 | 263 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 76 | 38 | 19 | 40 | 0 | 0 | 0 | 280 | 280 | 195 | 8 | 0 | 37 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 33 | 20 | 102 | 107 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 10 | 285 | 8 | 0 | 0 | 265 | 0 | 0 | 164 | 0 | 148 | 4 | 30 | 120 | 137 | 404 | 59 | 90 | 105 | 1 | 177 | 36 | 92 | 17 | 8 | 38 | 400 | 104 | 7 | 35 | 108 | 0 | 35 | 5 | 53 | 55 | 0 |  | 904 | 0 | 215 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 130 | 0 | 0 | 142 | 0 | 391 | 74 | 0 | 70 | 105 | 84 | 0 | 1 | 55 | 950 | 220 | 0 | 17 | 1 | 28 | 52 | 0 | 0 |  | 6987 | 4035 | 11022 | 3876 | 904 | 1657 | 0 | 2916 | 1149 | 126 | 130 | 245 | 102 | 47 | 0 | 91.19
8:00 | 0 | 0 | 0 | 180 | 310 | 88 | 0 | 355 | 262 |  | 0 | 225 | 0 | 31 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 0 | 25 | 12 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 33 | 76 | 38 | 19 | 10 | 0 | 0 | 0 | 280 | 280 | 186 | 8 | 0 | 38 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 28 | 20 | 96 | 104 | 0 | 17 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 275 | 0 | 0 | 164 | 0 | 149 | 10 | 30 | 120 | 127 | 403 | 58 | 90 | 105 | 3 | 175 | 36 | 92 | 0 | 8 | 38 | 400 | 104 | 8 | 35 | 108 | 0 | 35 | 14 | 53 | 28 | 0 |  | 907 | 0 | 205 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 0 | 130 | 0 | 0 | 141 | 0 | 364 | 74 | 0 | 70 | 105 | 84 | 0 | 2 | 55 | 930 | 221 | 0 | 17 | 1 | 55 | 52 | 0 | 0 |  | 6859 | 4007 | 10866 | 3789 | 907 | 1621 | 0 | 2860 | 1129 | 126 | 130 | 245 | 96 | 93 | 0 | 91.18
9:00 | 0 | 0 | 0 | 180 | 310 | 85 | 0 | 351 | 258 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 24 | 25 | 30 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 76 | 38 | 19 | 11 | 0 | 0 | 0 | 280 | 300 | 197 | 8 | 0 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 19 | 20 | 98 | 97 | 0 | 17 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 8 | 315 | 8 | 0 | 0 | 275 | 0 | 0 | 164 | 0 | 149 | 5 | 30 | 120 | 125 | 403 | 58 | 90 | 105 | 4 | 177 | 36 | 92 | 0 | 8 | 38 | 392 | 104 | 20 | 35 | 108 | 0 | 35 | 14 | 53 | 55 | 0 |  | 906 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 142 | 0 | 0 | 141 | 0 | 360 | 74 | 0 | 70 | 105 | 79 | 0 | 3 | 55 | 890 | 222 | 0 | 17 | 3 | 74 | 52 | 0 | 0 |  | 6936 | 3967 | 10903 | 3821 | 906 | 1614 | 0 | 2868 | 1089 | 126 | 142 | 257 | 98 | 124 | 0 | 91.17
10:00 | 0 | 0 | 0 | 180 | 310 | 85 | 0 | 353 | 245 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 30 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 33 | 71 | 37 | 19 | 9 | 0 | 0 | 0 | 280 | 300 | 190 | 8 | 0 | 38 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 15 | 17 | 80 | 80 | 0 | 17 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 0 | 8 | 320 | 8 | 0 | 0 | 273 | 0 | 0 | 164 | 0 | 144 | 6 | 30 | 120 | 128 | 403 | 58 | 90 | 105 | 4 | 177 | 36 | 92 | 0 | 8 | 36 | 390 | 104 | 41 | 35 | 108 | 0 | 35 | 27 | 53 | 55 | 0 |  | 870 | 0 | 195 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 0 | 203 | 0 | 0 | 140 | 0 | 364 | 55 | 0 | 70 | 88 | 83 | 0 | 4 | 55 | 880 | 223 | 0 | 17 | 5 | 82 | 52 | 0 | 0 |  | 6894 | 3947 | 10841 | 3790 | 870 | 1591 | 0 | 2817 | 1079 | 126 | 203 | 318 | 80 | 170 | 0 | 91.17
11:00 | 0 | 0 | 0 | 180 | 310 | 85 | 0 | 343 | 213 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 32 | 85 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 30 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 3 | 0 | 33 | 73 | 38 | 19 | 5 | 0 | 0 | 0 | 280 | 310 | 184 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 15 | 19 | 86 | 80 | 0 | 17 | 2 | 41 | 42 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 220 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 275 | 0 | 0 | 125 | 0 | 132 | 19 | 30 | 120 | 122 | 405 | 58 | 90 | 105 | 5 | 177 | 36 | 92 | 0 | 8 | 32 | 387 | 89 | 32 | 35 | 108 | 0 | 35 | 30 | 53 | 55 | 0 |  | 871 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 212 | 0 | 0 | 136 | 0 | 336 | 55 | 0 | 70 | 88 | 84 | 0 | 6 | 55 | 930 | 215 | 0 | 17 | 4 | 89 | 52 | 0 | 0 |  | 6758 | 3973 | 10731 | 3779 | 871 | 1489 | 0 | 2713 | 1129 | 125 | 212 | 352 | 86 | 187 | 0 | 91.16
12:00 | 0 | 0 | 0 | 180 | 310 | 85 | 0 | 314 | 201 |  | 0 | 225 | 0 | 24 | 0 | 45 | 0 | 0 | 0 | 32 | 85 | 125 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 28 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 9 | 34 | 10 | 73 | 37 | 19 | 5 | 0 | 0 | 0 | 320 | 320 | 159 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 39 | 0 | 19 | 8 | 14 | 20 | 76 | 70 | 0 | 17 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 220 | 0 | 0 | 8 | 320 | 8 | 0 | 0 | 270 | 0 | 0 | 138 | 0 | 132 | 1 | 30 | 120 | 122 | 403 | 58 | 90 | 105 | 5 | 210 | 36 | 99 | 0 | 8 | 22 | 382 | 88 | 38 | 35 | 108 | 0 | 35 | 33 | 40 | 39 | 0 |  | 871 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 19 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 34 | 12 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 201 | 0 | 0 | 135 | 0 | 338 | 55 | 0 | 70 | 88 | 84 | 0 | 7 | 55 | 980 | 219 | 0 | 0 | 5 | 45 | 52 | 0 | 0 |  | 6792 | 3984 | 10776 | 3748 | 871 | 1513 | 0 | 2675 | 1179 | 125 | 201 | 454 | 76 | 135 | 0 | 91.16
13:00 | 0 | 0 | 0 | 180 | 310 | 81 | 0 | 311 | 197 |  | 0 | 225 | 0 | 24 | 0 | 45 | 0 | 0 | 0 | 27 | 93 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 25 | 28 | 42 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 9 | 38 | 10 | 73 | 0 | 19 | 4 | 0 | 0 | 0 | 320 | 320 | 148 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 42 | 0 | 19 | 8 | 7 | 20 | 84 | 68 | 0 | 17 | 1 | 42 | 42 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 215 | 0 | 0 | 8 | 315 | 8 | 0 | 0 | 255 | 0 | 0 | 130 | 0 | 126 | 18 | 30 | 129 | 123 | 366 | 58 | 90 | 105 | 6 | 213 | 36 | 110 | 0 | 8 | 10 | 390 | 88 | 46 | 35 | 108 | 0 | 35 | 35 | 49 | 37 | 0 |  | 871 | 0 | 185 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 20 | 16 | 0 | 0 | 0 | 34 | 5 | 42 | 0 | 34 | 16 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 138 | 0 | 0 | 200 | 0 | 0 | 133 | 0 | 334 | 55 | 0 | 70 | 88 | 77 | 0 | 7 | 55 | 1000 | 223 | 0 | 0 | 5 | 34 | 52 | 0 | 0 |  | 6701 | 4041 | 10742 | 3681 | 871 | 1500 | 0 | 2619 | 1199 | 125 | 200 | 511 | 84 | 152 | 0 | 91.15
14:00 | 0 | 0 | 0 | 180 | 310 | 81 | 0 | 306 | 197 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 93 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 25 | 28 | 42 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 25 | 51 | 10 | 73 | 7 | 19 | 2 | 0 | 0 | 0 | 300 | 300 | 137 | 8 | 50 | 39 | 5 | 0 | 51 | 0 | 47 | 0 | 19 | 8 | 15 | 20 | 82 | 68 | 0 | 17 | 1 | 42 | 41 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 215 | 0 | 0 | 8 | 310 | 8 | 0 | 0 | 265 | 0 | 0 | 130 | 0 | 114 | 15 | 30 | 136 | 125 | 390 | 58 | 90 | 105 | 2 | 210 | 36 | 110 | 0 | 8 | 10 | 390 | 88 | 51 | 53 | 108 | 0 | 35 | 26 | 74 | 37 | 0 |  | 871 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 19 | 16 | 0 | 0 | 0 | 34 | 19 | 42 | 0 | 34 | 16 | 8 | 36 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 137 | 0 | 0 | 204 | 0 | 0 | 130 | 0 | 320 | 55 | 0 | 70 | 88 | 81 | 0 | 6 | 55 | 1020 | 219 | 0 | 0 | 4 | 50 | 52 | 0 | 0 |  | 6802 | 4120 | 10922 | 3701 | 871 | 1472 | 0 | 2696 | 1219 | 127 | 204 | 599 | 82 | 155 | 0 | 90.15
15:00 | 0 | 0 | 0 | 180 | 310 | 81 | 0 | 308 | 194 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 85 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 25 | 28 | 41 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 25 | 44 | 10 | 73 | 20 | 19 | 2 | 0 | 0 | 0 | 300 | 300 | 152 | 8 | 50 | 35 | 5 | 0 | 51 | 0 | 47 | 0 | 19 | 8 | 15 | 20 | 88 | 68 | 0 | 16 | 1 | 42 | 42 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 215 | 0 | 0 | 8 | 310 | 8 | 0 | 0 | 275 | 0 | 0 | 156 | 0 | 115 | 13 | 30 | 136 | 125 | 371 | 56 | 90 | 105 | 2 | 212 | 36 | 110 | 0 | 25 | 10 | 380 | 95 | 45 | 55 | 108 | 0 | 35 | 15 | 64 | 38 | 0 |  | 870 | 0 | 170 | 0 | 31 | 0 | 0 | 0 | 14 | 0 | 8 | 82 | 21 | 32 | 0 | 0 | 0 | 34 | 18 | 42 | 0 | 34 | 16 | 8 | 36 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 204 | 0 | 0 | 125 | 0 | 174 | 55 | 0 | 70 | 105 | 83 | 0 | 5 | 55 | 980 | 214 | 0 | 0 | 1 | 49 | 52 | 0 | 0 |  | 6773 | 3948 | 10721 | 3658 | 870 | 1320 | 0 | 2788 | 1180 | 81 | 204 | 605 | 88 | 131 | 0 | 91.14
16:00 | 0 | 0 | 0 | 180 | 280 | 87 | 0 | 306 | 191 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 93 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 24 | 25 | 27 | 32 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 25 | 44 | 10 | 79 | 31 | 19 | 5 | 0 | 0 | 0 | 300 | 300 | 153 | 8 | 51 | 39 | 5 | 0 | 51 | 0 | 47 | 1 | 19 | 10 | 18 | 20 | 90 | 68 | 0 | 16 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 63 | 10 | 0 | 222 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 275 | 0 | 0 | 158 | 0 | 117 | 4 | 30 | 136 | 120 | 364 | 60 | 90 | 105 | 2 | 212 | 36 | 110 | 0 | 39 | 10 | 345 | 88 | 27 | 120 | 108 | 0 | 35 | 9 | 58 | 55 | 0 |  | 871 | 0 | 145 | 0 | 31 | 0 | 0 | 0 | 28 | 12 | 8 | 81 | 26 | 32 | 0 | 0 | 0 | 30 | 18 | 42 | 0 | 34 | 16 | 42 | 35 | 15 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 115 | 0 | 0 | 208 | 0 | 0 | 115 | 0 | 216 | 55 | 0 | 80 | 105 | 83 | 0 | 4 | 95 | 970 | 214 | 0 | 0 | 2 | 26 | 52 | 0 | 0 |  | 6797 | 4017 | 10814 | 3553 | 871 | 1351 | 0 | 2993 | 1170 | 81 | 208 | 630 | 90 | 75 | 0 | 91.14
17:00 | 0 | 0 | 0 | 180 | 310 | 91 | 0 | 305 | 193 |  | 0 | 225 | 0 | 16 | 0 | 55 | 0 | 0 | 0 | 24 | 64 | 137 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 19 | 25 | 24 | 25 | 27 | 35 | 0 | 46 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 37 | 10 | 79 | 36 | 19 | 14 | 0 | 0 | 0 | 300 | 300 | 165 | 8 | 50 | 39 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 24 | 12 | 86 | 68 | 0 | 8 | 0 | 42 | 42 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 220 | 0 | 0 | 8 | 290 | 8 | 0 | 0 | 275 | 0 | 0 | 176 | 0 | 131 | 2 | 30 | 158 | 125 | 361 | 102 | 105 | 105 | 1 | 212 | 36 | 92 | 0 | 113 | 10 | 379 | 88 | 12 | 132 | 108 | 0 | 35 | 10 | 64 | 55 | 0 |  | 871 | 0 | 205 | 0 | 31 | 0 | 0 | 0 | 39 | 20 | 0 | 87 | 22 | 32 | 0 | 0 | 0 | 30 | 27 | 42 | 0 | 34 | 32 | 1 | 35 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 414 | 18 | 0 | 112 | 105 | 105 | 0 | 2 | 95 | 900 | 219 | 0 | 0 | 1 | 28 | 52 | 0 | 0 |  | 7011 | 4232 | 11243 | 3729 | 871 | 1567 | 0 | 3147 | 1100 | 81 | 160 | 606 | 86 | 56 | 0 | 91.13
18:00 | 0 | 0 | 0 | 180 | 250 | 91 | 0 | 306 | 191 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 24 | 50 | 137 | 0 | 0 | 0 | 0 | 5 | 35 | 55 | 22 | 25 | 24 | 25 | 27 | 49 | 0 | 88 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 20 | 22 | 63 | 10 | 83 | 37 | 19 | 18 | 0 | 0 | 0 | 300 | 300 | 165 | 8 | 45 | 40 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 24 | 12 | 84 | 68 | 0 | 8 | 0 | 44 | 42 | 0 | 0 | 0 | 0 | 40 | 10 | 0 | 220 | 0 | 0 | 8 | 270 | 8 | 0 | 0 | 275 | 0 | 0 | 185 | 0 | 115 | 0 | 30 | 200 | 128 | 365 | 102 | 105 | 105 | 0 | 212 | 36 | 92 | 17 | 113 | 10 | 360 | 98 | 2 | 144 | 108 | 0 | 35 | 3 | 76 | 55 | 0 |  | 871 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 37 | 40 | 0 | 82 | 21 | 32 | 0 | 0 | 0 | 30 | 26 | 51 | 0 | 34 | 32 | 8 | 35 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 360 | 17 | 0 | 113 | 105 | 104 | 0 | 0 | 95 | 880 | 178 | 0 | 0 | 0 | 4 | 52 | 0 | 0 |  | 7110 | 4128 | 11238 | 3671 | 871 | 1455 | 0 | 3296 | 1079 | 123 | 130 | 650 | 84 | 9 | 0 | 91.13
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 307 | 191 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 24 | 50 | 137 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 18 | 25 | 27 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 34 | 101 | 10 | 84 | 37 | 19 | 17 | 0 | 0 | 0 | 280 | 280 | 176 | 8 | 50 | 39 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 27 | 12 | 104 | 103 | 0 | 11 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 275 | 0 | 0 | 180 | 0 | 115 | 0 | 30 | 200 | 133 | 398 | 102 | 105 | 105 | 0 | 281 | 36 | 94 | 17 | 113 | 10 | 372 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 870 | 0 | 210 | 0 | 96 | 0 | 0 | 0 | 38 | 65 | 32 | 82 | 29 | 32 | 0 | 0 | 0 | 32 | 26 | 88 | 0 | 34 | 32 | 43 | 35 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 135 | 0 | 0 | 142 | 0 | 383 | 17 | 0 | 113 | 105 | 104 | 0 | 0 | 95 | 890 | 195 | 0 | 11 | 0 | 0 | 108 | 0 | 0 |  | 7416 | 4423 | 11839 | 3780 | 870 | 1515 | 0 | 3587 | 1089 | 124 | 135 | 770 | 104 | 0 | 0 | 91.11
19:30 | 0 | 0 | 0 | 180 | 310 | 91 | 0 | 307 | 196 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 24 | 50 | 139 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 26 | 25 | 27 | 49 | 0 | 42 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 42 | 99 | 10 | 85 | 37 | 19 | 24 | 0 | 0 | 0 | 280 | 280 | 184 | 8 | 45 | 40 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 32 | 12 | 90 | 105 | 0 | 11 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 63 | 78 | 0 | 220 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 275 | 0 | 0 | 166 | 0 | 133 | 0 | 30 | 200 | 140 | 403 | 102 | 105 | 105 | 0 | 285 | 36 | 110 | 17 | 113 | 10 | 397 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 856 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 49 | 65 | 32 | 82 | 29 | 32 | 0 | 0 | 0 | 30 | 25 | 88 | 0 | 34 | 32 | 34 | 37 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 198 | 0 | 0 | 142 | 0 | 380 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1020 | 180 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7537 | 4594 | 12131 | 3830 | 856 | 1586 | 0 | 3620 | 1220 | 77 | 198 | 852 | 90 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 310 | 91 | 0 | 313 | 201 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 24 | 50 | 139 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 26 | 25 | 27 | 49 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 43 | 99 | 10 | 85 | 37 | 19 | 29 | 0 | 0 | 0 | 280 | 280 | 191 | 8 | 47 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 32 | 12 | 90 | 104 | 0 | 14 | 0 | 44 | 42 | 0 | 0 | 0 | 0 | 63 | 78 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 273 | 0 | 0 | 166 | 0 | 125 | 0 | 30 | 200 | 140 | 404 | 102 | 105 | 105 | 0 | 285 | 36 | 110 | 17 | 113 | 10 | 400 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 856 | 0 | 205 | 0 | 109 | 0 | 0 | 0 | 43 | 77 | 32 | 81 | 29 | 32 | 0 | 0 | 0 | 30 | 24 | 88 | 0 | 34 | 32 | 43 | 37 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 148 | 0 | 0 | 189 | 0 | 0 | 142 | 0 | 376 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1030 | 180 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7620 | 4608 | 12228 | 3845 | 856 | 1603 | 0 | 3629 | 1230 | 126 | 189 | 849 | 90 | 0 | 0 | 91.12
21:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 317 | 213 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 10 | 50 | 138 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 26 | 25 | 29 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 102 | 10 | 85 | 38 | 19 | 31 | 0 | 0 | 0 | 280 | 280 | 198 | 8 | 48 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 90 | 104 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 81 | 0 | 221 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 273 | 0 | 0 | 175 | 0 | 135 | 0 | 30 | 200 | 138 | 404 | 102 | 105 | 105 | 0 | 285 | 36 | 100 | 17 | 113 | 10 | 395 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 856 | 0 | 200 | 0 | 107 | 0 | 0 | 0 | 43 | 65 | 32 | 82 | 30 | 32 | 0 | 0 | 0 | 30 | 24 | 88 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 183 | 0 | 0 | 139 | 0 | 360 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1010 | 222 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7656 | 4583 | 12239 | 3844 | 856 | 1654 | 0 | 3622 | 1210 | 124 | 183 | 839 | 90 | 0 | 0 | 91.11
22:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 324 | 223 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 50 | 138 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 26 | 25 | 29 | 49 | 0 | 43 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 102 | 10 | 80 | 38 | 19 | 35 | 0 | 0 | 0 | 280 | 280 | 205 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 96 | 104 | 0 | 18 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 221 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 273 | 0 | 0 | 175 | 0 | 132 | 0 | 30 | 200 | 138 | 404 | 103 | 105 | 105 | 0 | 285 | 36 | 92 | 17 | 114 | 10 | 390 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 855 | 0 | 195 | 0 | 110 | 0 | 0 | 0 | 43 | 64 | 32 | 82 | 36 | 32 | 0 | 0 | 0 | 34 | 18 | 88 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 208 | 0 | 0 | 136 | 0 | 352 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1010 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7597 | 4591 | 12188 | 3846 | 855 | 1689 | 0 | 3553 | 1210 | 78 | 208 | 861 | 96 | 0 | 0 | 91.11
23:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 358 | 271 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 50 | 140 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 27 | 25 | 29 | 49 | 0 | 44 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 102 | 10 | 81 | 38 | 19 | 39 | 0 | 0 | 0 | 280 | 300 | 193 | 8 | 47 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 84 | 104 | 0 | 12 | 0 | 42 | 42 | 0 | 0 | 0 | 0 | 60 | 81 | 0 | 220 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 273 | 0 | 0 | 180 | 0 | 149 | 0 | 30 | 200 | 127 | 372 | 103 | 105 | 105 | 0 | 177 | 36 | 92 | 17 | 114 | 10 | 385 | 104 | 0 | 139 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 855 | 0 | 190 | 0 | 114 | 0 | 0 | 0 | 43 | 64 | 32 | 83 | 37 | 32 | 0 | 0 | 0 | 34 | 15 | 82 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 139 | 0 | 0 | 206 | 0 | 0 | 136 | 0 | 330 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1050 | 215 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7534 | 4593 | 12127 | 3835 | 855 | 1715 | 0 | 3457 | 1250 | 79 | 206 | 852 | 84 | 0 | 0 | 91.1
24:00 | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 382 | 281 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 50 | 140 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 45 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 50 | 102 | 10 | 82 | 38 | 19 | 38 | 0 | 0 | 0 | 280 | 300 | 197 | 8 | 48 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 94 | 105 | 0 | 7 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 276 | 0 | 0 | 181 | 0 | 149 | 0 | 30 | 200 | 130 | 403 | 103 | 105 | 105 | 0 | 177 | 36 | 92 | 52 | 32 | 10 | 399 | 104 | 0 | 95 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 855 | 0 | 210 | 0 | 114 | 0 | 0 | 0 | 43 | 64 | 32 | 82 | 37 | 32 | 0 | 0 | 0 | 34 | 15 | 87 | 0 | 34 | 32 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 148 | 0 | 0 | 209 | 0 | 0 | 137 | 0 | 394 | 17 | 0 | 70 | 105 | 105 | 0 | 0 | 55 | 1070 | 221 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7510 | 4602 | 12112 | 3940 | 855 | 1794 | 0 | 3220 | 1270 | 80 | 209 | 859 | 94 | 0 | 0 | 91.1
KWH | 0 | 0 | 0 | 4347000 | 7456682 | 2075227 | 0 | 8299350 | 5594000 |  | 0 | 4765500 | 0 | 549120 | 0 | 1325406 | 0 | 0 | 0 | 624000 | 1851120 | 3008160 | 0 | 0 | 0 | 0 | 329760 | 218234 | 298983 | 447012 | 600000 | 569340 | 614900 | 713700 | 1071360 | 0 | 1842660 | 848000 | 2400000 | 0 | 609273 | 0 | 0 | 0 | 0 |  | 488880 | 643152 | 1264026 | 510720 | 1927680 | 820320 | 451440 | 549600 | 0 | 0 | 0 | 7373900 | 7193000 | 4391000 | 217454 | 511200 | 922824 | 147840 | 0 | 1204288 | 0 | 881008 | 127387 | 442116 | 231120 | 630100 | 442490 | 2330880 | 2156160 | 0 | 328752 | 9950 | 1012000 | 970476 | 0 | 0 | 0 | 0 | 1429152 | 769920 | 0 | 5232210 | 0 | 0 | 224280 | 7497000 | 183408 | 0 | 0 | 6546216 | 0 | 0 | 3914400 | 0 | 3285648 | 108135 | 766080 | 3534720 | 3139709 | 9402000 | 1728000 | 2328000 | 2535854 | 31920 | 4915309 | 909466 | 2344317 | 258780 | 1039080 | 561600 | 9194000 | 2420160 | 316980 | 1872000 | 2605691 | 0 | 886680 | 226001 | 1482240 | 1233720 | 0 |  | 21269090 | 0 | 5080608 | 0 | 1386240 | 0 | 0 | 0 | 581760 | 713472 | 301125 | 1984435 | 640269 | 701088 | 0 | 0 | 0 | 550576 | 373965 | 1287552 | 0 | 778816 | 402600 | 337920 | 524270 | 450480 | 0 | 257886 | 0 | 0 | 4873600 | 0 | 0 | 3653591 | 0 | 0 | 4678745 | 0 | 0 | 3530027 | 0 | 8455636 | 1220160 | 0 | 2090016 | 2465280 | 2257660 | 0 | 44669 | 1648800 | 25571800 | 5157436 | 0 | 313200 | 34920 | 581040 | 1977024 | 0 | 0 |  | 171561226 | 106175756 | 277736982 | 92451879 | 21269090 | 37748930 | 0 | 74537242 | 30445400 | 2690660 | 4678745 | 10230541 | 2330880 | 1353615 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 8351483.84 | 2760051.91 | 0 | 8714317.5 | 6041520 |  | 0 | 5194395 | 0 | 6139161.6 | 0 | 17561629.5 | 0 | 0 | 0 | 9122880 | 26045258.4 | 48762273.6 | 0 | 0 | 0 | 0 | 4194547.2 | 2946159 | 4009362.03 | 335259 | 450000 | 0 | 0 | 0 | 18223833.6 | 0 | 497518.2 | 228960 | 4536000 | 0 | 9961613.55 | 0 | 0 | 0 | 0 |  | 6379884 | 10727775.36 | 21513722.52 | 6899827.2 | 24442982.4 | 9491102.4 | 573328.8 | 1830168 | 0 | 0 | 0 | 8185029 | 7840370 | 5093560 | 280515.66 | 623664 | 1042791.12 | 220281.6 | 0 | 2011160.96 | 0 | 15215008.16 | 1713355.15 | 605698.92 | 173340 | 1102675 | 331867.5 | 16735718.4 | 2350214.4 | 0 | 447102.72 | 158603 | 1386440 | 1281028.32 | 0 | 0 | 0 | 0 | 2772554.88 | 1755417.6 | 0 | 5284532.1 | 0 | 0 | 444074.4 | 7497000 | 137556 | 0 | 0 | 89355848.4 | 0 | 0 | 52766112 | 0 | 45506224.8 | 1264098.15 | 7905945.6 | 48284275.2 | 41663938.43 | 8649840 | 21012480 | 33662880 | 32078553.1 | 0 | 57705727.66 | 9904084.74 | 24920089.71 | 3511644.6 | 13393741.2 | 6615648 | 8458480 | 31341072 | 4580361 | 23755680 | 29652763.58 | 0 | 11580040.8 | 2700711.95 | 22189132.8 | 16248092.4 | 0 |  | 63807270 | 0 | 5690280.96 | 0 | 14430758.4 | 0 | 0 | 0 | 10477497.6 | 12842496 | 4327166.25 | 2222567.2 | 1242121.86 | 7641859.2 | 0 | 0 | 0 | 9233159.52 | 6540647.85 | 20137313.28 | 0 | 12897192.96 | 6807966 | 4605849.6 | 8844434.9 | 932493.6 | 0 | 195219.702 | 0 | 0 | 25781344 | 0 | 0 | 4238165.56 | 0 | 0 | 81690887.7 | 0 | 0 | 4094831.32 | 0 | 8371079.64 | 16398950.4 | 0 | 24724889.28 | 35623296 | 28672282 | 0 | 493592.45 | 20016432 | 230401918 | 5260584.72 | 0 | 2317680 | 394945.2 | 6815599.2 | 30307777.92 | 0 | 0 |  | 1005809069.62 | 718480550.272 | 1724289619.892 | 101645227.842 | 63807270 | 43840864.95 | 0 | 972149705.06 | 256183262 | 726478.2 | 81690887.7 | 171102294.79 | 16735718.4 | 16407910.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 310 | 85 | 0 | 351 | 258 |  | 0 | 225 | 0 | 32 | 0 | 55 | 0 | 0 | 0 | 32 | 93 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 24 | 25 | 30 | 42 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 33 | 76 | 38 | 19 | 11 | 0 | 0 | 0 | 280 | 300 | 197 | 8 | 0 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 19 | 20 | 98 | 97 | 0 | 17 | 1 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 0 | 8 | 315 | 8 | 0 | 0 | 275 | 0 | 0 | 164 | 0 | 149 | 5 | 30 | 120 | 125 | 403 | 58 | 90 | 105 | 4 | 177 | 36 | 92 | 0 | 8 | 38 | 392 | 104 | 20 | 35 | 108 | 0 | 35 | 14 | 53 | 55 | 0 |  | 906 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 142 | 0 | 0 | 141 | 0 | 360 | 74 | 0 | 70 | 105 | 79 | 0 | 3 | 55 | 890 | 222 | 0 | 17 | 3 | 74 | 52 | 0 | 0 |  | 10903 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 317 | 213 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 10 | 50 | 138 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 25 | 26 | 25 | 29 | 49 | 0 | 89 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 23 | 51 | 102 | 10 | 85 | 38 | 19 | 31 | 0 | 0 | 0 | 280 | 280 | 198 | 8 | 48 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 90 | 104 | 0 | 16 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 60 | 81 | 0 | 221 | 0 | 0 | 10 | 305 | 8 | 0 | 0 | 273 | 0 | 0 | 175 | 0 | 135 | 0 | 30 | 200 | 138 | 404 | 102 | 105 | 105 | 0 | 285 | 36 | 100 | 17 | 113 | 10 | 395 | 104 | 0 | 144 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 856 | 0 | 200 | 0 | 107 | 0 | 0 | 0 | 43 | 65 | 32 | 82 | 30 | 32 | 0 | 0 | 0 | 30 | 24 | 88 | 0 | 34 | 32 | 43 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 183 | 0 | 0 | 139 | 0 | 360 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1010 | 222 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 12239 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 380 | 300 | 0 | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 93 | 140 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 47 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 102 | 10 | 90 | 38 | 19 | 30 | 0 | 0 | 0 | 300 | 300 | 180 | 8 | 80 | 35 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 33 | 20 | 113 | 85 | 0 | 22 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 50 | 0 | 220 | 0 | 0 | 10 | 330 | 8 | 0 | 0 | 275 | 0 | 0 | 200 | 0 | 149 | 0 | 30 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 285 | 36 | 110 | 114 | 113 | 10 | 400 | 104 | 0 | 162 | 108 | 0 | 35 |  | 75 | 55 |  |  | 871 | 0 | 215 | 0 | 100 | 0 | 0 | 0 | 44 | 60 | 40 | 82 | 33 | 48 | 0 | 0 | 0 | 34 | 30 | 88 | 0 | 34 | 32 | 43 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 340 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 95 | 1100 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 380 | 300 | 0 | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 88 | 130 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 25 | 25 | 33 | 50 | 0 | 47 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 17 | 10 | 81 | 38 | 19 | 30 | 0 | 0 | 0 | 270 | 260 | 160 | 8 | 47 | 35 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 33 | 20 | 83 | 85 | 0 | 22 | 1.6 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 20 | 0 | 220 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 186 | 0 | 149 | 20 | 30 | 120 | 135 | 400 | 105 | 105 | 105 | 5 | 175 | 36 | 110 | 17 | 8 | 10 | 400 | 54 | 50 | 35 | 108 | 0 | 35 | 30 | 54 | 55 |  |  | 886 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 8 | 82 | 23 | 32 | 0 | 0 | 0 | 34 | 16 | 88 | 0 | 34 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 300 | 17 | 0 | 70 | 105 | 84 | 0 | 8 | 55 | 1100 | 220 |  | 17 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 310 | 92 | 0 | 406 | 337 | 0 | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 42 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 47 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 53 | 10 | 71 | 38 | 19 | 42 | 0 | 0 | 0 | 270 | 250 | 160 | 8 | 47 | 0 | 0 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 12 | 82 | 108 | 0 | 19 | 0 | 43 | 42 | 0 | 0 | 0 | 0 | 61 | 20 | 0 | 220 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 260 | 0 | 0 | 186 | 0 | 145 | 8 | 30 | 120 | 123 | 402 | 105 | 105 | 100 | 1 | 175 | 36 | 110 | 17 | 8 | 10 | 400 | 70 | 5 | 35 | 108 | 0 | 35 | 11 | 53 | 55 | 0 | 0 | 905 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 23 | 16 | 0 | 0 | 0 | 34 | 0 | 88 | 0 | 34 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 163 | 0 | 340 | 17 | 0 | 70 | 32 | 84 | 0 | 1 | 56 | 890 | 163 | 0 | 0 | 0 | 21 | 52 | 0 | 0 | 0 |  |  |  |  | 89446528 |  | 0
89446528
| Minimum Generation |  | 10866 | 8:00
| Highest Generation |  | 12239 | 21:00
| Day Peak Generation |  | 10903 | 9:00
| Evening Peak Generation |  | 12239 | 21:00
| HVDC Max Flow |  | 907 | 8:00
| HVDC EvPeak Flow |  | 856 | 21:00
| Load factor L.F |  | 94.55% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-22
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10903 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10908 | MW
Evening Peak Generation : |  | 12239 | MW Hour : | 21:00 | Available Max Generation : |  | 12635 | MW
E.P. Demand (at gen end) : |  | 13797 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12239 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 277.737 | System Load Factor : | 94.55% | Load Shed : |  | 236 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 404 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-22
Actual : | 91.1 | Ft.(MSL) , | Rule curve : | 87.36 | Ft.( MSL )
Gas Consumed : | Total = | 967.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145486092.792
: |  | Coal : | 256183262 | Oil : | 1224942887.55 | Total : | 1626612242.342
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 380 | 9120:00 | 4932.949 |  |  | 0 | 1.564%
Chittagong Area | 140 | 3360:00 | 1371.6292 |  |  | 29 | 12.43%
Khulna Area | 200 | 4800:00 | 1803.876 |  |  | 45 | 16.38%
Rajshahi Area | 196 | 4704:00 | 1592.1608 |  |  | 48 | 5.721%
Cumilla Area | 164 | 3936:00 | 1359.5125 |  |  | 38 | 3.621%
Mymensingh Area | 220 | 5280:00 | 1117.8642 |  |  | 36 | 6.463%
Sylhet Area | 58 | 1392:00 | 505.1131 |  |  | 11 | 3.084%
Barisal Area | 0 | 0:00 | 408.1749 |  |  | 0 | -6.167%
Rangpur Area | 200 | 4800:00 | 882.2159 |  |  | 29 | -1.976%
Total | 1558 |  | 13973.4956 |  |  | 236
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tongi 132/33 kV T-1 transformer was switched on at 10:20.
b) Shitalakshya-Madanganj 132 kV Ckt was shut down at 12:12 for C/M.
c) Rajshahi 230/132 kV T01 transformer was shut down at 11:10 for C/M.
d) Bogura 230/132 kV AT1 transformer tripped at 17:14 and was switched on at 17:32.
e) Ramganj 132/33 kV T-1 transformer was under shut down from 21:33 to 22:47 for R/H maintenance | [5 empty] | About 40 MW power interruption occurred under
Ramganj S/S area from 21:33 to 22:47.
f) Saidpur 132/33 kV T-2 transformer was under shut down from 07:02(22/7/2022) to 10:50 for C/M.
g) Gopalganj(N)-Gopalganj(O) 132 kV Ckt-1 was under shut down from 07:24(22/7/2022) to 09:45 for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7456682 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 92 | 2075227 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 317 | 8299350 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 213 | 5594000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4765500 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 549120 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1325406
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 447012
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 10 | 624000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 1851120 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 329760 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 138 | 3008160 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 218234 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 298983
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1169340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 713700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1071360 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 273 | 6546216 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 3285648 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2328000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2420160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1872000 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 226001
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1233720
| Dhaka area Total |  |  |  | 5847 | 2697 | 62670599
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 609273
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 108135
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 820320 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 124 | 2690660 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2535854
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 643152 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1264026 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 510720 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 30 | 766080 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451440
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 549600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1927680 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31920
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 4915309 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 909466 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 100 | 2344317 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 561600
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2605691 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1259 | 26645243
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4391000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7373900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7193000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 922824 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 147840 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1204288
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 3139709 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 881008
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 48 | 511200 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3534720
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 442116
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 2330880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 630100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 127387 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 442490 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 258780
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1039080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 886680 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 1482240 | Fuel shortage
| Cumilla Area Total |  |  |  | 2885 | 1711 | 37387816
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2156160 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 328752
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 175 | 3914400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1728000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 316980
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 488880
| Mymensingh Area Total |  |  |  | 614 | 420 | 8943122
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1012000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 970476 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1429152 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 769920 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5232210
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 183408 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7497000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9402000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 224280
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9194000
| Sylhet Area Total |  |  |  | 2477 | 1569 | 35914446
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 856 | 21269090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 107 | 1386240 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 581760 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 713472 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5080608 | FGMO & gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 301125
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 1220160 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2465280
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 581040
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1425 | 33598775
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 701088 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 640269 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 1984435 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1010 | 25571800 | FGMO
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5157436
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 313200 | Transformer O/L
| Barisal Area Total |  |  |  | 1958 | 1393 | 34368228
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 550576 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 24 | 373965 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 778816 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 402600 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 144 | 3653591 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4678745
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 139 | 3530027 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 8455636 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 524270 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 450480
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257886
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 337920 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 1287552 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2090016
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1648800 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
| Rajshahi Area Total |  |  |  | 2129 | 1352 | 29055800
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4873600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 2257660 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44669
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 1977024
| Rangpur Area Total |  |  |  | 720 | 413 | 9152953
| Total |  |  |  | 21396 | 12239 | 277736982
| Eastern Grid Total |  |  |  | 14205 | 7656 | 171561226
| Western Grid Total |  |  |  | 7191 | 4583 | 106175756
| National Grid Total |  |  |  | 21396 | 12239 | 277736982
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-21
(a) ENTIRE EASTERN GRID : |  | 7889.2 | MW | (b) ENTIRE WESTERN GRID : |  | 3829.09 | MW
i) Dhaka area |  | 4261.5 | MW | i) Khulna area |  | 1477.2 | MW
ii) Chittagong area |  | 1205.7 | MW | ii) Rajshahi area |  | 1255 | MW
iii) Comilla area |  | 1077 | MW | iii) Barisal area |  | 376.89 | MW
iv) Mymensingh area |  | 911 | MW | iv) Rangpur area |  | 720 | MW
v) Sylhet area |  | 434 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11718.29 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 10 | 11:00 | Chowmuhani | 176 | 22:00 | Kaptai | 4.5 | 20:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 148 | 23:00 | Chuadanga | 98 | 20:00 | Kazla | 78 | 19:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 17:00 | Coxsbazar | 107 | 00:00 | Keranigonj | 62 | 21:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 88 | 13:00 | Cumilla(N) | 142 | 22:00 | Khagrachori | 26 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 82 | 16:00 | Cumilla(S) | 167 | 01:00 | Khulna | 88 | 01:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 54 | 03:00 | Daudkandi | 194 | 06:00 | Khulshi | 192 | 16:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 36 | 23:00 | Dhaka | 38 | 11:00 | Kishoreganj | 118 | 04:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 162 | 09:00 | Dhamrai | 94 | 00:00 | Kodda | 279 | 19:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 91 | 02:00 | Dhanmondi | 124 | 12:00 | Kulaura | 40 | 04:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 127 | 16:00 | Dohazari | 62 | 03:00 | Kurigram | 55 | 21:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 55 | 17:00 | Faridpur | 131 | 03:00 | Kushtia | 120 | 18:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 12:00 | Fatullah | 65 | 16:00 | Lalbag | 99 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 55 | 23:00 | Fenchuganj | 40 | 04:00 | Lalmonirhat | 46 | 00:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 97 | 20:00 | Madanganj | 86 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 102 | 22:00 | GPH | 9 | 00:00 | Madaripur | 107 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 75 | 23:00 | Ghorashal | 63 | 23:00 | Madartek | 78 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 73 | 23:00 | Goalpara | 28 | 12:00 | Madunaghat | 61 | 21:00 | Rajshahi | 132 | 22:00
Baroirhat | 55 | 19:00 | Gollamari | 56 | 19:00 | Magura | 52 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 163 | 17:00 | Gopalganj | 99 | 23:00 | Mahasthangarh | 68 | 19:30 | Ramganj | 88 | 19:00
BashundharaCement | 7 | 00:00 | Gulshan | 124 | 17:00 | Manikganj | 85 | 12:00 | Rampur | 16 | 00:00
Beanibazar | 49 | 03:00 | Halishahar | 88.5 | 20:00 | Maniknagar | 76 | 15:00 | Rangamati | 14 | 19:00
Benapole | 50 | 01:00 | HaripurSBU | 124 | 10:00 | Matarbari | 39 | 22:00 | Rangpur | 105 | 08:00
Bhaluka | 110 | 22:00 | Hasnabad | 87 | 18:00 | Matuail | 62 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 52 | 00:00 | Hathazari | 92 | 21:00 | Millgate | 77 | 12:00 | SSM | 3 | 05:00
Bhangura | 30 | 00:00 | Ishurdi | 81 | 19:30 | Mirpur | 135 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 54 | 01:00 | Jaldhaka | 51 | 05:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 228 | 16:00 | Jamalpur | 122 | 21:00 | Mithapukur | 34 | 18:30 | Satmasjid | 101 | 19:00
Bog-Sherpur | 52 | 01:00 | Jashore | 116 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 159 | 18:00 | Jhenaidah | 106 | 00:00 | Mogbazar | 128 | 13:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 00:00 | Joydebpur | 168 | 00:00 | Mongla | 42 | 08:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 140 | 01:00 | Joypurhat | 58 | 04:00 | Motijheel | 38 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 150 | 15:00 | Juldah | 28 | 15:00 | Munshiganj | 126 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 61 | 19:30 | KSRM | 29.1 | 01:00 | Mymensingh | 215 | 21:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 18:30 | Kabirpur | 270 | 18:00 | Naogaon | 118 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 62 | 04:00 | Kachua | 64 | 19:00 | Narail | 44 | 19:30 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 44 | 16:00 | Kallyanpur | 99 | 17:00 | Narinda | 64 | 16:00 | Shitalakhya | 114 | 12:00
Chauddagram | 48 | 19:30 | Kalurghat | 8 | 00:00 | Narshingdi | 147 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 27 | 21:00 | Kamrangirchar | 53 | 19:30 | Natore | 137 | 03:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 397 | 06:00 | 380 | 12:00 | Kaliakoir | 392 | 05:00 | 381 | 12:00
| Bibiana | 409 | 20:00 | 400 | 16:00 | Payra | 420 | 16:00 | 411 | 05:00
| BIPTC | 401 | 06:00 | 396 | 00:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 414 | 18:00 | 396 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 224 | 06:00 | 212 | 17:00 | Hasnabad | 224 | 04:00 | 213 | 11:00
| AKSML | 236 | 20:00 | 221 | 09:00 | Hathazari | 240 | 19:30 | 228 | 11:00
| Aminbazar | 225 | 04:00 | 214 | 11:00 | Ishurdi | 237 | 16:00 | 226 | 07:00
| Ashuganj | 240 | 09:00 | 230 | 15:00 | Jhenaidah | 233 | 16:00 | 217 | 04:00
| Baghabari | 234 | 18:30 | 229 | 12:00 | Kaliakoir | 227 | 06:00 | 219 | 11:00
| Barapukuria | 226 | 16:00 | 214 | 07:00 | Keranigonj | 223 | 06:00 | 211 | 17:00
| Barishal | 248 | 18:30 | 236 | 23:00 | Khulna(S) | 240 | 16:00 | 223 | 07:00
| Bheramara | 233 | 16:00 | 222 | 07:00 | Maniknagar | 227 | 06:00 | 215 | 11:00
| Bhulta | 229 | 06:00 | 219 | 11:00 | Meghnaghat | 225 | 00:00 | 220 | 09:00
| Bibiana | 236 | 19:30 | 231 | 17:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 237 | 16:00 | 224 | 04:00 | Rajshahi | 235 | 16:00 | 221 | 05:00
| Bogura | 255 | 23:00 | 219 | 04:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 14:00 | 243 | 00:00 | Rampura | 228 | 04:00 | 216 | 12:00
| BSRM | 236 | 20:00 | 222 | 09:00 | Shikalbaha | 238 | 19:30 | 229 | 09:00
| Cumilla(N) | 229 | 20:00 | 221 | 11:00 | Shyampur | 224 | 06:00 | 213 | 17:00
| Fenchuganj | 237 | 06:00 | 232 | 11:00 | Siddhirganj | 227 | 06:00 | 218 | 16:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 260 | 00:00 | 228 | 03:00
| GPH | 237 | 20:00 | 224 | 09:00 | Tongi | 255 | 07:00 | 214 | 17:00
| Haripur | 226 | 06:00 | 215 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 05:00 | 127 | 12:00 | Lalbag | 135 | 06:00 | 126 | 17:00
| Agargaon | 133 | 04:00 | 125 | 17:00 | Lalmonirhat | 133 | 16:00 | 120 | 07:00
| Agrabad | 139 | 19:30 | 131 | 17:00 | Madanganj | 133 | 01:00 | 127 | 11:00
| AKS | 138 | 20:00 | 130 | 17:00 | Madaripur | 139 | 18:30 | 133 | 23:00
| Aminbazar | 130 | 00:00 | 123 | 11:00 | Madartek | 136 | 06:00 | 126 | 17:00
| Amnura | 134 | 16:00 | 120 | 07:00 | Madunaghat | 140 | 19:30 | 132 | 17:00
| Ashuganj | 136 | 06:00 | 134 | 11:00 | Magura | 142 | 16:00 | 130 | 01:00
| Bagerhat | 136 | 16:00 | 121 | 04:00 | Mahasthangarh | 135 | 15:00 | 128 | 04:00
| Bakulia | 139 | 19:30 | 131 | 17:00 | Manikganj | 135 | 16:00 | 129 | 19:00
| Banani | 134 | 06:00 | 123 | 17:00 | Maniknagar | 130 | 03:00 | 122 | 11:00
| Bangabhaban | 130 | 06:00 | 122 | 17:00 | Matarbari | 131 | 10:00 | 119 | 19:30
| Barapukuria | 138 | 16:00 | 130 | 03:00 | Matuail | 133 | 03:00 | 128 | 11:00
| Barguna | 137 | 18:30 | 130 | 13:00 | Millgate | 134 | 05:00 | 124 | 17:00
| Barishal | 138 | 18:00 | 129 | 13:00 | Mirpur | 130 | 05:00 | 121 | 17:00
| Barishal-230 | 140 | 18:30 | 133 | 23:00 | Mithapukur | 135 | 16:00 | 126 | 07:00
| Baroaulia | 142 | 20:00 | 133 | 09:00 | Modern | 140 | 19:30 | 132 | 16:00
| Baroirhat | 135 | 00:00 | 126 | 03:00 | Mogbazar | 136 | 03:00 | 127 | 15:00
| Bashundhara | 136 | 05:00 | 124 | 17:00 | Mongla | 136 | 16:00 | 123 | 05:00
| BashundharaCement | 133 | 01:00 | 127 | 11:00 | Motijheel | 130 | 06:00 | 122 | 17:00
| Beanibazar | 130 | 09:00 | 127 | 01:00 | Munshiganj | 133 | 01:00 | 127 | 13:00
| Benapole | 138 | 16:00 | 124 | 07:00 | Mymensingh | 132 | 16:00 | 122 | 01:00
| Bhaluka | 150 | 03:00 | 120 | 03:00 | Naogaon | 134 | 16:00 | 122 | 02:00
| Bhandaria | 138 | 18:30 | 127 | 01:00 | Narail | 140 | 16:00 | 128 | 01:00
| Bhangura | 138 | 15:00 | 134 | 01:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 16:00 | 132 | 07:00 | Narshingdi | 137 | 00:00 | 125 | 11:00
| Bheramara(GK) | 139 | 16:00 | 135 | 03:00 | Natore | 137 | 16:00 | 127 | 07:00
| Bhulta | 129 | 04:00 | 120 | 11:00 | Nawabganj | 135 | 06:00 | 127 | 11:00
| Bog-Sherpur | 138 | 16:00 | 129 | 07:00 | Netrakona | 131 | 13:00 | 122 | 19:30
| Bogura | 140 | 16:00 | 131 | 07:00 | New | 132 | 00:00 | 127 | 09:00
| Bogura-230 | 139 | 16:00 | 131 | 04:00 | Niamatpur | 129 | 15:00 | 117 | 04:00
| Brahmanbaria | 132 | 15:00 | 130 | 00:00 | Noapara | 139 | 16:00 | 125 | 07:00
| Cantonment | 132 | 06:00 | 122 | 11:00 | Pabna | 137 | 16:00 | 131 | 01:00
| Chandpur | 140 | 18:00 | 128 | 11:00 | Palashbari | 135 | 16:00 | 125 | 04:00
| Chandraghona | 141 | 20:00 | 133 | 09:00 | Panchagarh | 135 | 16:00 | 123 | 02:00
| Chapai | 132 | 16:00 | 122 | 07:00 | Patuakhali | 137 | 07:00 | 131 | 22:00
| Charsaidpur | 134 | 06:00 | 128 | 15:00 | Payra | 138 | 08:00 | 135 | 00:00
| Chauddagram | 135 | 18:30 | 126 | 09:00 | PHP | 135 | 18:30 | 126 | 03:00
| Chhatak | 130 | 10:00 | 127 | 00:00 | Purbachal | 133 | 03:00 | 124 | 17:00
| Chowmuhani | 134 | 18:00 | 122 | 01:00 | Purbasadipur | 135 | 10:00 | 121 | 07:00
| Chuadanga | 140 | 16:00 | 124 | 03:00 | Rahim | 134 | 06:00 | 128 | 17:00
| Coxsbazar | 131 | 10:00 | 121 | 16:00 | Rajbari | 137 | 16:00 | 129 | 01:00
| Cumilla(N) | 135 | 20:00 | 129 | 02:00 | Rajendrapur | 135 | 06:00 | 129 | 19:00
| Cumilla(S) | 134 | 20:00 | 128 | 00:00 | Rajshahi | 133 | 15:00 | 126 | 18:00
| Daudkandi | 132 | 20:00 | 125 | 11:00 | Rajshahi-230 | 133 | 15:00 | 124 | 07:00
| Dhaka | 137 | 06:00 | 128 | 11:00 | Ramganj | 138 | 20:00 | 123 | 11:00
| Dhamrai | 132 | 06:00 | 126 | 17:00 | Rampur | 139 | 20:00 | 132 | 09:00
| Dhanmondi | 135 | 02:00 | 127 | 11:00 | Rampura | 135 | 04:00 | 127 | 12:00
| Dohazari | 140 | 19:30 | 130 | 17:00 | Rangamati | 139 | 19:30 | 131 | 17:00
| Faridpur | 137 | 16:00 | 130 | 1:00 | Rangpur | 133 | 16:00 | 123 | 07:00
| Fatullah | 135 | 06:00 | 128 | 13:00 | Ruppur | 138 | 16:00 | 132 | 02:00
| Fenchuganj | 134 | 18:00 | 132 | 05:00 | Saidpur | 133 | 11:00 | 128 | 02:00
| Feni | 136 | 20:00 | 126 | 11:00 | Satkhira | 134 | 15:00 | 121 | 03:00
| Ghorashal | 138 | 19:30 | 135 | 17:00 | Satmasjid | 133 | 06:00 | 124 | 17:00
| Goalpara | 138 | 16:00 | 126 | 05:00 | Savar | 131 | 20:00 | 122 | 09:00
| Gollamari | 138 | 16:00 | 127 | 04:00 | Shahjadpur | 148 | 08:00 | 137 | 11:00
| Gopalganj | 141 | 16:00 | 133 | 06:00 | Shahjibazar | 133 | 06:00 | 130 | 01:00
| Gopalganj_I | 140 | 18:00 | 134 | 01:00 | Shahmirpur | 140 | 19:30 | 132 | 16:00
| Gulshan | 136 | 06:00 | 126 | 15:00 | Shariatpur | 138 | 18:30 | 129 | 00:00
| Halishahar | 139 | 19:30 | 129 | 17:00 | Sherpur | 136 | 16:00 | 124 | 03:00
| Haripur | 134 | 06:00 | 128 | 17:00 | Shikalbaha | 141 | 19:00 | 131 | 18:00
| HaripurSBU | 134 | 00:00 | 128 | 11:00 | Shikalbaha-230 | 140 | 19:30 | 133 | 17:00
| Hasnabad | 135 | 04:00 | 128 | 11:00 | Shitalakhya | 135 | 02:00 | 126 | 17:00
| Hathazari | 141 | 19:30 | 133 | 09:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 16:00 | 132 | 07:00 | Shyampur | 133 | 20:00 | 127 | 11:00
| Jaldhaka | 133 | 16:00 | 122 | 04:00 | Shyampur-230 | 135 | 05:00 | 128 | 17:00
| Jamalpur | 139 | 18:30 | 126 | 03:00 | Siddhirganj | 133 | 03:00 | 128 | 15:00
| Jashore | 138 | 16:00 | 125 | 04:00 | Sirajganj | 138 | 16:00 | 130 | 07:00
| Jhenaidah | 143 | 16:00 | 131 | 05:00 | Sonargaon | 134 | 00:00 | 125 | 12:00
| Jhenaidah-230 | 143 | 16:00 | 132 | 04:00 | Sreemongol | 134 | 09:00 | 131 | 00:00
| Joydebpur | 140 | 00:00 | 135 | 09:00 | Srinagar | 135 | 06:00 | 126 | 11:00
| Joypurhat | 134 | 16:00 | 123 | 03:00 | SSM | 141 | 20:00 | 135 | 09:00
| Juldah | 140 | 19:30 | 131 | 17:00 | Sunamganj | 129 | 14:00 | 126 | 00:00
| Kabirpur | 137 | 05:00 | 125 | 09:00 | Sylhet | 132 | 10:00 | 130 | 00:00
| Kachua | 136 | 18:30 | 127 | 03:00 | Tangail | 136 | 13:00 | 129 | 01:00
| Kaliakoir | 138 | 06:00 | 129 | 09:00 | Thakurgaon | 134 | 19:30 | 122 | 07:00
| Kallyanpur | 130 | 01:00 | 124 | 0.5 | TK | 140 | 19:30 | 131 | 17:00
| Kalurghat | 141 | 20:00 | 132 | 17:00 | Tongi | 135 | 04:00 | 126 | 17:00
| Kamrangirchar | 134 | 03:00 | 127 | 12:00 | Ullon | 136 | 05:00 | 127 | 11:00
| Kaptai | 138 | 18:30 | 135 | 00:00 | Uttara | 129 | 06:00 | 122 | 17:00
| Kazla | 129 | 06:00 | 121 | 13:00 | UttaraNew | 134 | 05:00 | 126 | 17:00
| Keranigonj | 134 | 06:00 | 126 | 17:00 | Zigatola | 134 | 07:00 | 126 | 12:00
| Khagrachori | 139 | 19:30 | 132 | 17:00
| Khulna | 138 | 16:00 | 126 | 07:00
| Khulna(S) | 138 | 16:00 | 126 | 07:00
| Khulshi | 138 | 19:30 | 130 | 08:00
| Kishoreganj | 132 | 10:00 | 125 | 03:00
| Kodda | 141 | 10:00 | 130 | 19:00
| KSRM | 140 | 20:00 | 132 | 09:00
| Kulaura | 133 | 13:00 | 131 | 03:00
| Kurigram | 131 | 16:00 | 124 | 04:00
| Kushtia | 139 | 16:00 | 131 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 644 | 7510 | 4602 | 12112 |  |  |  | QF-LDC-11
0:30 | 599 | 7388.5 | 4616.5 | 12005 | Date: | 2022-07-21
1:00 | 554 | 7267 | 4631 | 11898
1:30 | 547 | 7273.5 | 4633 | 11906.5
2:00 | 540 | 7280 | 4635 | 11915
2:30 | 531 | 7278 | 4628 | 11906 | [5 empty] | Gen. at Eve. Peak | 12239 | 12239 MW (21:00 )
3:00 | 522 | 7276 | 4621 | 11897 | [6 empty] | 21:00
3:30 | 498 | 7275.5 | 4578.5 | 11854 | [5 empty] | Gen. at Day Peak | 10903 | 10903 MW (09:00 )
4:00 | 474 | 7275 | 4536 | 11811 | [6 empty] | 9:00
4:30 | 475 | 7241 | 4546.5 | 11787.5 | [5 empty] | Highest Generation | 12239
5:00 | 476 | 7207 | 4557 | 11764 | [6 empty] | 21:00
5:30 | 440 | 7129.5 | 4399 | 11528.5
6:00 | 404 | 7052 | 4241 | 11293
6:30 | 435 | 7019.5 | 4138 | 11157.5
7:00 | 466 | 6987 | 4035 | 11022
7:30 | 517 | 6923 | 4021 | 10944
8:00 | 568 | 6859 | 4007 | 10866
8:30 | 676 | 6897.5 | 3987 | 10884.5
9:00 | 784 | 6936 | 3967 | 10903
9:30 | 771 | 6915 | 3957 | 10872
10:00 | 758 | 6894 | 3947 | 10841
10:30 | 773 | 6826 | 3960 | 10786
11:00 | 788 | 6758 | 3973 | 10731
11:30 | 763 | 6775 | 3978.5 | 10753.5
12:00 | 738 | 6792 | 3984 | 10776
12:30 | 777 | 6746.5 | 4012.5 | 10759
13:00 | 816 | 6701 | 4041 | 10742
13:30 | 833 | 6751.5 | 4080.5 | 10832
14:00 | 850 | 6802 | 4120 | 10922
14:30 | 838 | 6787.5 | 4034 | 10821.5
15:00 | 826 | 6773 | 3948 | 10721
15:30 | 860 | 6785 | 3982.5 | 10767.5
16:00 | 894 | 6797 | 4017 | 10814
16:30 | 882 | 6904 | 4124.5 | 11028.5
17:00 | 870 | 7011 | 4232 | 11243
17:30 | 805 | 7060.5 | 4180 | 11240.5
18:00 | 740 | 7110 | 4128 | 11238
18:30 | 664 | 7263 | 4275.5 | 11538.5
19:00 | 588 | 7416 | 4423 | 11839
19:30 | 630 | 7537 | 4594 | 12131
20:00 | 590 | 7620 | 4608 | 12228 |  |  |  | Executive Engineer
20:30 | 568 | 7638 | 4595.5 | 12233.5 |  |  |  | Network Operation Division
21:00 | 546 | 7656 | 4583 | 12239
21:30 | 566 | 7626.5 | 4587 | 12213.5
22:00 | 586 | 7597 | 4591 | 12188 |  |  |  |  | Page 6 of 7
22:30 | 589 | 7565.5 | 4592 | 12157.5
23:00 | 592 | 7534 | 4593 | 12127
23:30 | 618 | 7522 | 4597.5 | 12119.5
24:00 | 644 | 7510 | 4602 | 12112
12239 MW (21:00 )
10903 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-21 |  | Energy |  | 277736982
[13 empty] | 2022-07-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3940 | 855 | 1794 | 0 | 3220 | 1270 | 80 | 209 | 859 | 94 | 0 | 0
0:30 | 3915 | 879 | 1726.5 | 0 | 3196 | 1254.5 | 80.5 | 210.5 | 844.5 | 109 | 0 | 0 | Date: | 2022-07-21
1:00 | 3890 | 903 | 1659 | 0 | 3172 | 1239 | 81 | 212 | 830 | 124 | 0 | 0
1:30 | 3891 | 903.5 | 1667.5 | 0 | 3164 | 1244.5 | 81.5 | 212.5 | 830.5 | 124 | 0 | 0 | [8 empty] | Total Energy | 277.737 | Total Energy Gen 277.737 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 277.737 MKWHr
2:00 | 3892 | 904 | 1676 | 0 | 3156 | 1250 | 82 | 213 | 831 | 124 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3891 | 903.5 | 1674 | 0 | 3139 | 1250 | 105 | 206.5 | 820.5 | 123 | 0 | 0 | [8 empty] | Energy Requirement | 277.737
3:00 | 3890 | 903 | 1672 | 0 | 3122 | 1250 | 128 | 200 | 810 | 122 | 0 | 0
3:30 | 3899.5 | 903.5 | 1674.5 | 0 | 3080 | 1245 | 127.5 | 200 | 803 | 121 | 0 | 0 | [6 empty] | Shortage
4:00 | 3909 | 904 | 1677 | 0 | 3038 | 1240 | 127 | 200 | 796 | 120 | 0 | 0
4:30 | 3899 | 904 | 1684 | 0 | 3022 | 1240 | 127 | 200 | 793.5 | 118 | 0 | 0
5:00 | 3889 | 904 | 1691 | 0 | 3006 | 1240 | 127 | 200 | 791 | 116 | 0 | 0
5:30 | 3889.5 | 904 | 1678 | 0 | 2984.5 | 1204.5 | 127 | 189.5 | 625 | 113 | 3 | 0
6:00 | 3890 | 904 | 1665 | 0 | 2963 | 1169 | 127 | 179 | 459 | 110 | 6 | 0
6:30 | 3883 | 904 | 1661 | 0 | 2939.5 | 1159 | 126.5 | 154.5 | 352 | 106 | 26.5 | 0 |  |  |  |  | Coal
7:00 | 3876 | 904 | 1657 | 0 | 2916 | 1149 | 126 | 130 | 245 | 102 | 47 | 0
7:30 | 3832.5 | 905.5 | 1639 | 0 | 2888 | 1139 | 126 | 130 | 245 | 99 | 70 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3789 | 907 | 1621 | 0 | 2860 | 1129 | 126 | 130 | 245 | 96 | 93 | 0
8:30 | 3805 | 906.5 | 1617.5 | 0 | 2864 | 1109 | 126 | 136 | 251 | 97 | 108.5 | 0
9:00 | 3821 | 906 | 1614 | 0 | 2868 | 1089 | 126 | 142 | 257 | 98 | 124 | 0
9:30 | 3805.5 | 888 | 1602.5 | 0 | 2842.5 | 1084 | 126 | 172.5 | 287.5 | 89 | 147 | 0
10:00 | 3790 | 870 | 1591 | 0 | 2817 | 1079 | 126 | 203 | 318 | 80 | 170 | 0
10:30 | 3784.5 | 870.5 | 1540 | 0 | 2765 | 1104 | 125.5 | 207.5 | 335 | 83 | 178.5 | 0
11:00 | 3779 | 871 | 1489 | 0 | 2713 | 1129 | 125 | 212 | 352 | 86 | 187 | 0
11:30 | 3763.5 | 871 | 1501 | 0 | 2694 | 1154 | 125 | 206.5 | 403 | 81 | 161 | 0
12:00 | 3748 | 871 | 1513 | 0 | 2675 | 1179 | 125 | 201 | 454 | 76 | 135 | 0
12:30 | 3714.5 | 871 | 1506.5 | 0 | 2647 | 1189 | 125 | 200.5 | 482.5 | 80 | 143.5 | 0
13:00 | 3681 | 871 | 1500 | 0 | 2619 | 1199 | 125 | 200 | 511 | 84 | 152 | 0
13:30 | 3681 | 871 | 1500 | 0 | 2619 | 1199 | 125 | 200 | 511 | 84 | 152 | 0
14:00 | 3681 | 871 | 1500 | 0 | 2619 | 1199 | 125 | 200 | 511 | 84 | 152 | 0
14:30 | 3669.5 | 870.5 | 1410 | 0 | 2703.5 | 1189.5 | 103 | 202 | 558 | 86 | 141.5 | 0
15:00 | 3658 | 870 | 1320 | 0 | 2788 | 1180 | 81 | 204 | 605 | 88 | 131 | 0
15:30 | 3605.5 | 870.5 | 1335.5 | 0 | 2890.5 | 1175 | 81 | 206 | 617.5 | 89 | 103 | 0
16:00 | 3553 | 871 | 1351 | 0 | 2993 | 1170 | 81 | 208 | 630 | 90 | 75 | 0
16:30 | 3729 | 871 | 1459 | 0 | 3070 | 1135 | 81 | 184 | 618 | 88 | 65.5 | 0
17:00 | 3729 | 871 | 1567 | 0 | 3147 | 1100 | 81 | 160 | 606 | 86 | 56 | 0
17:30 | 3700 | 871 | 1511 | 0 | 3221.5 | 1089.5 | 102 | 145 | 628 | 85 | 32.5 | 0
18:00 | 3671 | 871 | 1455 | 0 | 3296 | 1079 | 123 | 130 | 650 | 84 | 9 | 0
18:30 | 3725.5 | 870.5 | 1485 | 0 | 3441.5 | 1084 | 123.5 | 132.5 | 710 | 94 | 4.5 | 0
19:00 | 3780 | 870 | 1515 | 0 | 3587 | 1089 | 124 | 135 | 770 | 104 | 0 | 0
19:30 | 3830 | 856 | 1586 | 0 | 3620 | 1220 | 77 | 198 | 852 | 90 | 0 | 0
20:00 | 3845 | 856 | 1603 | 0 | 3629 | 1230 | 126 | 189 | 849 | 90 | 0 | 0
20:30 | 3844.5 | 856 | 1628.5 | 0 | 3625.5 | 1220 | 125 | 186 | 844 | 90 | 0 | 0
21:00 | 3844 | 856 | 1654 | 0 | 3622 | 1210 | 124 | 183 | 839 | 90 | 0 | 0
21:30 | 3845 | 855.5 | 1671.5 | 0 | 3587.5 | 1210 | 101 | 195.5 | 850 | 93 | 0 | 0
22:00 | 3846 | 855 | 1689 | 0 | 3553 | 1210 | 78 | 208 | 861 | 96 | 0 | 0
22:30 | 3840.5 | 855 | 1702 | 0 | 3505 | 1230 | 78.5 | 207 | 856.5 | 90 | 0 | 0
23:00 | 3835 | 855 | 1715 | 0 | 3457 | 1250 | 79 | 206 | 852 | 84 | 0 | 0
23:30 | 3887.5 | 855 | 1754.5 | 0 | 3338.5 | 1260 | 79.5 | 207.5 | 855.5 | 89 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.5° C
24:00 | 3940 | 855 | 1794 | 0 | 3220 | 1270 | 80 | 209 | 859 | 94 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 277.737 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 277.737 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 47 | 93 | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 90 | 90 | 90 | 92 | 46 | 46 | 46 | 88 |  | 89 | 42 | 91 | 89 | 43 | 44 | 45 | 1842660
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 609273
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 10 | 5 | 6 | 19 | 1 | 18 | 15 | 13 | 4 | 2 | 0 | [8 empty] | 108135
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | [6 empty] | 34 | 38 | 51 | 44 | 44 | 37 | 63 |  | 101 | 99 | 99 | 102 | 102 | 102 | 102 | 1264026
12 | Hathazari 100 MW peaking PP | 51 | 51 | 51 | 43 | 43 | 10 |  |  |  |  | 3 | 9 | 9 | 25 | 25 | 25 |  | 22 |  | 34 | 42 | 43 | 51 | 51 | 51 | 50 | 643152
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2535854
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | 49 |  |  |  |  | 0 | 39 | 42 | 47 | 47 | 47 | 47 | 47 |  | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 881008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 275 | 275 | 275 | 273 | 262 | 265 | 275 | 275 | 273 | 275 | 270 | 255 | 265 | 275 | 275 | 275 | 275 |  | 275 | 275 | 273 | 273 | 273 | 273 | 276 | 6546216
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 280 | 310 | 250 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7456682
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 38 | 33 | 38 | 40 | 40 | 40 | 39 | 35 | 39 | 39 | 40 |  | 39 | 40 | 41 | 41 | 41 | 41 | 41 | 922824
33 | Ashuganj 225 MW CCPP | 201 | 193 | 185 | 183 | 193 | 185 | 195 | 186 | 197 | 190 | 184 | 159 | 148 | 137 | 152 | 153 | 165 | 165 |  | 176 | 184 | 191 | 198 | 205 | 193 | 197 | 4391000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 300 | 300 | 310 | 320 | 320 | 300 | 300 | 300 | 300 | 300 |  | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 7193000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 320 | 320 | 300 | 300 | 300 | 300 | 300 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7373900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 147840
36 | Chandpur 150 MW CCPP | [13 empty] | 50 | 50 | 51 | 50 | 45 |  | 50 | 45 | 47 | 48 | 50 | 47 | 48 | 511200
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 365 | 366 | 368 | 375 | 382 | 384 | 368 | 355 | 351 | 353 | 343 | 314 | 311 | 306 | 308 | 306 | 305 | 306 |  | 307 | 307 | 313 | 317 | 324 | 358 | 382 | 8299350
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4765500
41 | Haripur 360MW CCPP(HPL) | 270 | 269 | 269 | 270 | 269 | 273 | 263 | 262 | 258 | 245 | 213 | 201 | 197 | 197 | 194 | 191 | 193 | 191 |  | 191 | 196 | 201 | 213 | 223 | 271 | 281 | 5594000
42 | RPCL 210MW CCPP | 108 | 106 | 108 | 107 | 107 | 107 | 107 | 104 | 97 | 80 | 80 | 70 | 68 | 68 | 68 | 68 | 68 | 68 |  | 103 | 105 | 104 | 104 | 104 | 104 | 105 | 2156160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 8 | 20 | 41 | 32 | 38 | 46 | 51 | 45 | 27 | 12 | 2 | [8 empty] | 316980
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 43 | 42 | 42 | 42 | 43 | 42 | 44 |  | 43 | 43 | 44 | 43 | 43 | 42 | 43 | 1012000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 970476
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 58 | 59 | 60 | 64 | 64 | 64 | 61 | 61 | 61 | 61 | 60 | 59 | 61 | 61 | 59 | 63 | 60 | 40 |  | 59 | 63 | 63 | 60 | 61 | 60 | 61 | 1429152
48 | Shahjibazar 86MW PP (Shahjibazar) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 78 | 78 | 81 | 81 | 81 | 81 | 769920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 215 | 215 | 215 | 222 | 220 | 220 |  | 221 | 220 | 220 | 221 | 221 | 220 | 220 | 5232210
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 224280
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183408
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 315 | 300 | 300 | 290 | 270 | 285 | 310 | 315 | 320 | 290 | 320 | 315 | 310 | 310 | 290 | 290 | 270 |  | 280 | 290 | 300 | 305 | 330 | 330 | 330 | 7497000
| Bibiyana South 400 MW | 392 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 392 | 390 | 387 | 382 | 390 | 390 | 380 | 345 | 379 | 360 |  | 372 | 397 | 400 | 395 | 390 | 385 | 399 | 9194000
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 17 | 35 | 55 |  | 55 | 55 | 55 | 55 | 0 |  |  | 298983
59 | Tangail Palli Power Gen 22 MW | 17 | 16 | 22 | 21 | 16 | 19 | 18 | 17 | 18 | 19 | 17 | 22 | 22 | 22 | 22 | 22 | 18 | 20 |  | 22 | 22 | 23 | 23 | 23 | 23 | 22 | 488880
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 451440
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 447012
62 | Tangail 22 MW PP (Doreen) | 11 | 14 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 8 | 8 |  | 11 | 11 | 14 | 16 | 18 | 12 | 7 | 328752
63 | Impoprt (Tripura) | 124 | 124 | 122 | 120 | 116 | 110 | 102 | 96 | 98 | 80 | 86 | 76 | 84 | 82 | 88 | 90 | 86 | 84 |  | 104 | 90 | 90 | 90 | 96 | 84 | 94 | 2330880
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 11 | 9 | 5 | 5 | 4 | 2 | 2 | 5 | 14 | 18 |  | 17 | 24 | 29 | 31 | 35 | 39 | 38 | 549600
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442116
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 |  | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 231120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 19 | 15 | 15 | 14 | 7 | 15 | 15 | 18 | 24 | 24 |  | 27 | 32 | 32 | 33 | 33 | 33 | 33 | 630100
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 19 | 20 | 20 | 20 | 20 | 20 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 442490
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 27 | 27 | 28 | 28 | 28 | 28 | 0 | 24 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 |  | 18 | 26 | 26 | 26 | 26 | 27 | 27 | 569340
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614900
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 12 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 27 | 27 | 27 |  | 27 | 27 | 27 | 29 | 29 | 29 | 33 | 713700
73 | Ghorashal 108MW PP (Regent) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 | 85 | 85 | 81 | 81 | 81 | 87 | 91 | 91 |  | 92 | 91 | 91 | 92 | 92 | 92 | 92 | 2075227
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [8 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 258780
| Chowmuhani 113 MW | 15 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 39 | 113 | 113 |  | 113 | 113 | 113 | 113 | 114 | 114 | 32 | 1039080
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 55 | 120 | 132 | 144 |  | 144 | 144 | 144 | 144 | 144 | 139 | 95 | 1872000
77 | Siddhirganj 100 PP(Dutch Bangla) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 27 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 10 | 8 | 8 | 8 | 624000
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 32 | 35 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 1071360
79 | Kodda 150MW PP | 132 | 132 | 132 | 132 | 132 | 132 | 115 | 115 | 115 | 115 | 125 | 125 | 125 | 125 | 125 | 125 | 137 | 137 |  | 137 | 139 | 139 | 138 | 138 | 140 | 140 | 3008160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [8 empty] | 1 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 127387
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2328000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 6 | 2 | 2 | 2 | 1 | [9 empty] | 31920
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 909466
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 99 | 110 | 110 | 110 | 110 | 92 | 92 |  | 94 | 110 | 110 | 100 | 92 | 92 | 92 | 2344317
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 25 | 16 | 7 |  | 8 | 8 | 7 | 8 | 7 | 8 | 7 | 549120
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 89 | 88 | 88 | 88 | 95 | 88 | 88 | 98 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2420160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 510720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1204288
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 85 | 85 | 93 | 93 | 85 | 93 | 64 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1851120
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 38 | 37 |  | 7 | 20 | 31 | 36 | 37 |  | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 820320
96 | Chattogram 108 MW PP (ECPV) | 88 | 89 | 83 | 87 | 85 | 76 | 76 | 76 | 76 | 71 | 73 | 73 | 73 | 73 | 73 | 79 | 79 | 83 |  | 84 | 85 | 85 | 85 | 80 | 81 | 82 | 1927680
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1325406
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 5 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 218234
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 9950
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 5 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 329760
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 183 | 183 | 174 | 174 | 164 | 164 | 164 | 164 | 164 | 164 | 125 | 138 | 130 | 130 | 156 | 158 | 176 | 185 |  | 180 | 166 | 166 | 175 | 175 | 180 | 181 | 3914400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 138 | 140 | 148 | 149 | 149 | 144 | 132 | 132 | 126 | 114 | 115 | 117 | 131 | 115 |  | 115 | 133 | 125 | 135 | 132 | 149 | 149 | 3285648
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 766080
116 | Chandpur 200MW (Desh energy) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 129 | 136 | 136 | 136 | 158 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3534720
117 | Ashuganj 150MW PP (Midland) | 133 | 135 | 130 | 137 | 137 | 138 | 137 | 127 | 125 | 128 | 122 | 122 | 123 | 125 | 125 | 120 | 125 | 128 |  | 133 | 140 | 140 | 138 | 138 | 127 | 130 | 3139709
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 401 | 401 | 404 | 403 | 403 | 403 | 405 | 403 | 366 | 390 | 371 | 364 | 361 | 365 |  | 398 | 403 | 404 | 404 | 404 | 372 | 403 | 9402000
| Jamalpur 115 MW PP (United) | 58 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 56 | 60 | 102 | 102 |  | 102 | 102 | 102 | 102 | 103 | 103 | 103 | 1728000
| Anwara 300 MW PP (United) | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 175 | 177 | 177 | 177 | 210 | 213 | 210 | 212 | 212 | 212 | 212 |  | 281 | 285 | 285 | 285 | 285 | 177 | 177 | 4915309
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 36 | 32 | 22 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 561600
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2605691
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 886680
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 14 | 14 | 27 | 30 | 33 | 35 | 26 | 15 | 9 | 10 | 3 | [8 empty] | 226001
| Chandpur 115(Doreen) | 53 | 53 | 54 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 40 | 49 | 74 | 64 | 58 | 64 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1482240
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 28 | 55 | 55 | 55 | 39 | 37 | 37 | 38 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1233720
120 | Eastern Zone Total | 7267 | 7280 | 7276 | 7275 | 7207 | 7052 | 6987 | 6859 | 6936 | 6894 | 6758 | 6792 | 6701 | 6802 | 6773 | 6797 | 7011 | 7110 |  | 7416 | 7537 | 7620 | 7656 | 7597 | 7534 | 7510 | 171561226
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 110 | 113 | 112 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 20 | 32 | 31 | 31 | 31 | 32 |  | 96 | 99 | 109 | 107 | 110 | 114 | 114 | 1386240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 44 | 44 | 44 | 44 | 44 | 44 | [8 empty] | 14 | 28 | 39 | 37 |  | 38 | 49 | 43 | 43 | 43 | 43 | 43 | 581760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 18 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 1220160
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 28 | 55 | 74 | 82 | 89 | 45 | 34 | 50 | 49 | 26 | 28 | 4 | [8 empty] | 581040
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 313200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 222 | 223 | 215 | 219 | 223 | 219 | 214 | 214 | 219 | 178 |  | 195 | 180 | 180 | 222 | 220 | 215 | 221 | 5157436
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 701088
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 84 | 82 | 82 | 82 | 82 | 81 | 87 | 82 |  | 82 | 82 | 81 | 82 | 82 | 83 | 82 | 1984435
140 | Bhola 33 MW PP (Venture) | 37 | 36 | 35 | 33 | 32 | 28 | 24 | 21 | 21 | 18 | 19 | 19 | 20 | 19 | 21 | 26 | 22 | 21 |  | 29 | 29 | 29 | 30 | 36 | 37 | 37 | 640269
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 301125
143 | Gopalganj 100 MW Peaking PP | 60 | 60 | 59 | 55 | 55 | [10 empty] | 12 | 20 | 40 |  | 65 | 65 | 77 | 65 | 64 | 64 | 64 | 713472
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 88 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2465280
146 | Bheramara HVDC | 903 | 904 | 903 | 904 | 904 | 904 | 904 | 907 | 906 | 870 | 871 | 871 | 871 | 871 | 870 | 871 | 871 | 871 |  | 870 | 856 | 856 | 856 | 855 | 855 | 855 | 21269090
147 | Bheramara 410 MW CCPP | 205 | 205 | 205 | 215 | 215 | 220 | 215 | 205 | 200 | 195 | 195 | 190 | 185 | 185 | 170 | 145 | 205 | 225 |  | 210 | 210 | 205 | 200 | 195 | 190 | 210 | 5080608
148 | Payra 1320 MW | 1040 | 1050 | 1050 | 1040 | 1040 | 970 | 950 | 930 | 890 | 880 | 930 | 980 | 1000 | 1020 | 980 | 970 | 900 | 880 |  | 890 | 1020 | 1030 | 1010 | 1010 | 1050 | 1070 | 25571800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 199 |  | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 4873600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | [6 empty] | 34 | 34 | 34 | 34 | 30 | 30 | 30 |  | 32 | 30 | 30 | 30 | 34 | 34 | 34 | 550576
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 1 | 3 | 5 | 4 | 5 | 5 | 4 | 1 | 2 | 1 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 145 | 145 | 144 | 145 | 145 | 144 | 144 | 146 | 143 | 141 | 140 | 139 | 138 | 137 | 132 | 115 | 145 | 160 |  | 152 | 150 | 148 | 144 | 140 | 139 | 148 | 3653591
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 212 | 213 | 200 | 200 | 200 | 179 | 130 | 130 | 142 | 203 | 212 | 201 | 200 | 204 | 204 | 208 | 160 | 130 |  | 135 | 198 | 189 | 183 | 208 | 206 | 209 | 4678745
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 137 | 137 | 137 | 137 | 140 | 142 | 142 | 141 | 141 | 140 | 136 | 135 | 133 | 130 | 125 | 115 | 140 | 145 |  | 142 | 142 | 142 | 139 | 136 | 136 | 137 | 3530027
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 358 | 362 | 374 | 380 | 406 | 400 | 391 | 364 | 360 | 364 | 336 | 338 | 334 | 320 | 174 | 216 | 414 | 360 |  | 383 | 380 | 376 | 360 | 352 | 330 | 394 | 8455636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 32 | 32 | 32 | 30 | 33 | [7 empty] | 5 | 19 | 18 | 18 | 27 | 26 |  | 26 | 25 | 24 | 24 | 18 | 15 | 15 | 373965
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 19 | 19 | 19 | 17 | 17 | 15 | 17 | 19 |  | 19 | 19 | 20 | 21 | 21 | 21 | 21 | 450480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257886
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 778816
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 24 | 24 | 16 | 0 |  |  |  |  | 12 | 12 | 16 | 16 | 16 | 16 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 402600
168 | Santahar 50 MW Peaking PP | 28 | 28 | 29 | 29 | 29 | [8 empty] | 36 | 36 | 35 | 35 | 35 |  | 35 | 37 | 37 | 35 | 35 | 35 | 35 | 524270
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 8 | 8 | 42 | 1 | 8 |  | 43 | 34 | 43 | 43 | 43 | 43 | 8 | 337920
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 45 | [6 empty] | 42 | 42 | 42 | 42 | 42 | 51 |  | 88 | 88 | 88 | 88 | 88 | 82 | 87 | 1287552
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 112 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2090016
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1648800
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 105 | 105 | 105 | 100 | 98 | 84 | 84 | 84 | 79 | 83 | 84 | 84 | 77 | 81 | 83 | 83 | 105 | 104 |  | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 2257660
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 7 | 6 | 5 | 4 | 2 | 0 | [8 empty] | 44669
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 109 | 108 | 108 | 108 | 108 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1977024
178