## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-24 | Sunday
|  |  | Date (day): | 2022-07-24 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11241.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12313 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-23 | 2022-07-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 180 | 180 | 180 |  | 185 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 83 | 92 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 409 | 410 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 327 | 320 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 8 | 8 | 8 |  | 92 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 8 | 8 | 8 | 92 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 7 | 7 | 7 |  | 95 | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 145 | 150 | 132 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 52 | 53 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 292 | 275 | 292 |  | 8 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 140 | 143 | 134 | 143 |  | 6 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 90 | 88 | 90 |  |  | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 |  |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2254 | 2659 | 2448 | 2712 | 1815 | 1220
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 4 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 25 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 127 | 127 | 127 |  | 103 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 42 | 51 | 51 | 51 |  | 47 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 |  |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 11 | 11 | 11 | 11 | 89 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 29 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 78 | 12 | 12 | 89 |  | 19 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 176 | 285 | 175 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 92 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 |  | 90 | Engine problem
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 945 | 1097 | 955 | 1196 | 439 | 687
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 177 | 212 | 212 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 280 | 320 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 320 | 320 | 300 | 60 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 42 | 36 | 36 |  | 9 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 54 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 118 | 130 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 48 | 49
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 30 | 135 |  | 28 | Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 100 | 100 | 100
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 152 | 172 | 125 | 15
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 115 | 8 | 95 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 93 | 54 | 95 | 20 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3059 | 2885 | 1674 | 1948 | 1640 | 1876 | 670 | 61
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 107 | 102 | 107 | 95 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 210 | 200 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 72 | 106 | 105 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 55 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 481 | 451 | 500.6 | 454 | 95 | 18
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 14 | 11 | 11 | 40 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 45 | 10 | 10 | 10 | 40 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 53 | 63 | 59 | 63
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 81 | 5 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 120 | 120 | 120 |  |  | Gas shortage
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 15 | 10 | 10 | 10 | 40 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 295 | 300 | 330 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 381 | 399 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1345 | 1494 | 1422 | 1527 | 336 | 506
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 867 | 853 | 885 | 870
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 32 | 80 | 32 | 115
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 44 |  | 10 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 56 | 55 | 55 |  | 54 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 175 | 165 | 190 | 180 | 230 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 8 | 40 |  |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 88 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 110 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 330 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2718 | 2384 | 1297 | 1350 | 1392 | 1426 | 664 | 64
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 28 | 23 | 28 |  | 12 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 82 | 82 | 82 | 82 | 112 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 870 | 1010 | 1100 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 210 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1195 | 1389 | 1458 | 1479 | 112 | 12
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 32 | 34 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 25 | 16 | 25 |  | 46 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 25 | 25 | 25 |  | 25 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 153 | 137 | 170 | 170 | 40 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 210 | 217 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 141 | 122 | 160 | 160 | 60 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 315 | 314 | 330 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 89 | 87 | 88 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 70 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 76 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1149 | 1337 | 1082 | 1230 | 755 | 138
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 84 | 99 | 84 | 105 |  | 8 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 108 | 108 | 52 | 108 | 7 |  | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 400 | 406 | 344 | 413 | 206 | 93
|  | Total |  |  |  |  | 22678 | 21396 | 10740 | 12131 | 11241.6 | 12313 | 5092 | 2799
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11799.631 | 13327.87 | 12350.7199 | 13527.8265
| A. |  | 2022-07-23 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12134 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10662 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13914 | MW
| 3 | Day peak Generation : |  |  | 10740 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13327.87 | MW
| 4 | Evening peak Generation : |  |  | 12131 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1783 | MW
| 5 | Total Energy Generation : |  | 274.7697 | MKWHr | By Solar | 1.0592 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 131.7882 | MKWHr |  | By Oil: | 84.2438 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 29.6844 | MKWHr |  | By Hydro: | 3.06 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5092 | MW | Dhaka | 4583.77 | 4183.77 |  | 400
|  |  |  | For Plants S/D or M/C prob = |  |  | 2799 | MW | Chittagong | 1239 | 1156 |  | 83 |  | 18:00 |  | 752
|  |  |  | Total = |  |  | 7891 | MW | Khulna | 1719 | 1439 |  | 280
| 7 | Total Gas Supplied : |  |  | 1000.82 | MMCFD |  |  | Rajshahi | 1537.4 | 1277.4 |  | 260 |  | 19:00 |  | 1387
| 8 | Fuel Cost : | i) Gas : | Taka | 147516173.82 | ii) Oil : | Taka | 1160012054.03 | Comilla | 1296 | 1056 |  | 240 |  | 19:30 |  | 1789
|  |  | iii) Coal : |  | 249387288 | Total | Taka | 1556915515.85 | Mymensingh | 1165 | 895 |  | 270 |  | 20:00 |  | 1882
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 491 | 401 |  | 90 |  | 21:00 |  | 1783
|  | ii) During Peak Demand : |  |  | 430 | MW (E to W) at | 21:00 | hrs | Barisal | 388.7 | 388.7 |  | 0 |  | 22:00 |  | 1718
|  | iii) Maximum : |  |  | 430 | MW at | 21:00 | hrs | Rangpur | 908 | 748 |  | 160 |  | 23:00 |  | 1653
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 13327.87 | 11544.87 |  | 1783
| B. |  | 2022-07-24 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1616 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12313 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 317.0245 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10428 | MW at | 8:00 | 474 | 165 | 230 | 210 | 185 | 160 | 65 | 0 | 127
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.168 | MKWHr. | ii) HVDC Flow at Peak Time |  | 853 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7661 | MKWHr. | iii) Maximum HVDC Flow : |  | 903 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.1 |  | (b) Today: | 91.07 |  | (c) Rule Curve: |  | 87.68
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 406 | 333 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 140 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 17 | 33 | 49 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 295 | 320 | 196 | 8 | 90 | 42 | 56 | 0 | 51 | 0 | 47 | 16 | 19 | 11 | 33 | 20 | 162 | 106 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 6 | 10 | 320 | 8 | 0 | 0 | 280 | 0 | 0 | 200 | 0 | 143 | 0 | 21 | 154 | 118 | 400 | 105 | 105 | 105 | 0 | 178 | 36 | 92 | 114 | 14 | 10 | 398 | 17 | 0 | 54 | 107 | 0 | 35 | 0 | 57 | 55 | 0 |  | 856 | 0 | 210 | 0 | 115 | 0 | 0 | 0 | 36 | 57 | 8 | 82 | 36 | 32 | 0 | 0 | 0 | 32 | 26 | 89 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 164 | 0 | 0 | 212 | 0 | 0 | 151 | 0 | 414 | 17 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 1070 | 222 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7489 | 4628 | 12117 | 4065 | 856 | 1857 | 0 | 3031 | 1270 | 127 | 212 | 749 | 162 | 0 | 199 | 91.1
2:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 410 | 333 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 140 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 330 | 340 | 189 | 8 | 91 | 42 | 56 | 0 | 51 | 0 | 47 | 19 | 19 | 11 | 33 | 20 | 162 | 105 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 55 | 10 | 0 | 220 | 0 | 6 | 10 | 315 | 8 | 0 | 0 | 280 | 0 | 0 | 185 | 0 | 137 | 0 | 21 | 115 | 117 | 228 | 105 | 105 | 105 | 0 | 178 | 36 | 92 | 114 | 8 | 10 | 393 | 17 | 0 | 54 | 107 | 0 | 35 | 0 | 53 | 55 | 0 |  | 901 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 36 | 57 | 8 | 82 | 36 | 32 | 0 | 0 | 0 | 32 | 26 | 89 | 0 | 34 | 32 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 158 | 0 | 414 | 17 | 0 | 70 | 105 | 98 | 0 | 0 | 76 | 1070 | 223 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7276 | 4702 | 11978 | 3958 | 901 | 1853 | 0 | 2956 | 1270 | 127 | 214 | 751 | 162 | 0 | 140 | 91.1
3:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 409 | 336 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 140 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 23 | 0 | 0 | 0 | 0 |  | 22 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 310 | 300 | 187 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 47 | 42 | 19 | 11 | 33 | 20 | 160 | 105 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 55 | 10 | 0 | 220 | 0 | 6 | 10 | 325 | 8 | 0 | 0 | 280 | 0 | 0 | 200 | 0 | 132 | 0 | 21 | 100 | 128 | 372 | 105 | 105 | 105 | 0 | 178 | 36 | 92 | 34 | 8 | 10 | 397 | 17 | 0 | 38 | 107 | 0 | 35 | 0 | 54 | 55 | 0 |  | 901 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 36 | 57 | 8 | 82 | 35 | 32 | 0 | 0 | 0 | 32 | 26 | 89 | 0 | 34 | 24 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 179 | 0 | 0 | 213 | 0 | 0 | 163 | 0 | 414 | 17 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 1040 | 223 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7302 | 4692 | 11994 | 4066 | 901 | 1864 | 0 | 2895 | 1239 | 127 | 213 | 742 | 160 | 0 | 0 | 91.1
4:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 411 | 337 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 320 | 305 | 202 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 47 | 43 | 19 | 0 | 33 | 20 | 158 | 105 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 55 | 10 | 0 | 221 | 0 | 6 | 10 | 315 | 8 | 0 | 0 | 293 | 0 | 0 | 200 | 0 | 143 | 0 | 21 | 100 | 128 | 402 | 105 | 105 | 105 | 0 | 178 | 36 | 92 | 17 | 8 | 10 | 394 | 17 | 0 | 35 | 107 | 0 | 35 | 0 | 53 | 55 | 0 |  | 901 | 0 | 245 | 0 | 42 | 0 | 0 | 0 | 36 | 50 | 8 | 82 | 33 | 16 | 0 | 0 | 0 | 32 | 26 | 89 | 0 | 34 | 24 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 185 | 0 | 0 | 170 | 0 | 0 | 168 | 0 | 414 | 17 | 0 | 70 | 105 | 106 | 0 | 0 | 76 | 1000 | 223 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7347 | 4528 | 11875 | 4131 | 901 | 1853 | 0 | 2812 | 1199 | 127 | 170 | 694 | 158 | 0 | 0 | 91.1
5:00 | 0 | 0 | 0 | 180 | 310 | 89 | 0 | 410 | 338 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 310 | 300 | 199 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 47 | 43 | 19 | 11 | 33 | 20 | 152 | 105 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 56 | 10 | 0 | 221 | 0 | 6 | 10 | 320 | 8 | 0 | 0 | 288 | 0 | 0 | 200 | 0 | 143 | 0 | 21 | 100 | 130 | 402 | 105 | 105 | 105 | 0 | 178 | 36 | 92 | 17 | 8 | 10 | 396 | 17 | 0 | 35 | 107 | 0 | 35 | 0 | 53 | 55 | 0 |  | 902 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 40 | 8 | 82 | 32 | 16 | 0 | 0 | 0 | 24 | 26 | 89 | 0 | 34 | 24 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 193 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 70 | 105 | 100 | 0 | 0 | 76 | 1000 | 223 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 7362 | 4423 | 11785 | 4153 | 902 | 1858 | 0 | 2794 | 1199 | 127 | 130 | 600 | 152 | 0 | 0 | 91.1
6:00 | 0 | 0 | 0 | 180 | 310 | 87 | 0 | 415 | 339 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 126 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 50 | 0 | 10 | 89 | 38 | 19 | 42 | 0 | 0 | 0 | 285 | 265 | 211 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 0 | 13 | 19 | 11 | 33 | 20 | 148 | 106 | 0 | 8 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 6 | 10 | 300 | 8 | 0 | 0 | 273 | 0 | 0 | 200 | 0 | 143 | 1 | 21 | 100 | 130 | 402 | 105 | 105 | 68 | 0 | 178 | 36 | 92 | 17 | 8 | 10 | 360 | 17 | 1 | 35 | 107 | 0 | 35 | 1 | 53 | 55 | 0 |  | 900 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 27 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 0 | 173 | 0 | 414 | 17 | 0 | 70 | 105 | 106 | 0 | 0 | 76 | 950 | 224 | 0 | 0 | 0 | 3 | 108 | 0 | 0 |  | 7106 | 4276 | 11382 | 4092 | 900 | 1833 | 0 | 2707 | 1149 | 128 | 130 | 419 | 148 | 6 | 0 | 91.1
7:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 415 | 339 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 42 | 0 | 93 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 49 | 37 | 19 | 39 | 0 | 0 | 0 | 280 | 265 | 209 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 140 | 106 | 0 | 19 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 58 | 10 | 0 | 220 | 0 | 6 | 10 | 305 | 8 | 0 | 0 | 260 | 0 | 0 | 210 | 0 | 143 | 1 | 21 | 100 | 128 | 366 | 105 | 105 | 68 | 1 | 178 | 36 | 92 | 17 | 8 | 10 | 370 | 17 | 2 | 35 | 107 | 0 | 35 | 4 | 53 | 55 | 0 |  | 902 | 0 | 245 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 193 | 0 | 0 | 130 | 0 | 0 | 169 | 0 | 414 | 17 | 0 | 70 | 105 | 85 | 0 | 2 | 76 | 920 | 224 | 0 | 0 | 0 | 15 | 108 | 0 | 0 |  | 7003 | 4220 | 11223 | 4057 | 902 | 1828 | 0 | 2613 | 1119 | 128 | 130 | 411 | 140 | 25 | 0 | 91.1
8:00 | 0 | 0 | 0 | 180 | 310 | 86 | 0 | 414 | 341 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 42 | 0 | 92 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 54 | 32 | 19 | 12 | 0 | 0 | 0 | 280 | 265 | 180 | 8 | 90 | 42 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 14 | 20 | 136 | 108 | 0 | 19 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 63 | 10 | 0 | 220 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 141 | 3 | 21 | 100 | 130 | 365 | 105 | 105 | 81 | 2 | 176 | 36 | 92 | 17 | 8 | 10 | 370 | 17 | 6 | 35 | 108 | 0 | 35 | 4 | 54 | 55 | 0 |  | 900 | 0 | 215 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 70 | 105 | 85 | 0 | 4 | 76 | 870 | 176 | 0 | 0 | 1 | 36 | 108 | 0 | 0 |  | 6923 | 4087 | 11010 | 3954 | 900 | 1739 | 0 | 2617 | 1070 | 127 | 130 | 411 | 136 | 56 | 316 | 91.1
9:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 409 | 342 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 26 | 25 | 33 | 42 | 0 | 91 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 79 | 32 | 19 | 8 | 0 | 0 | 0 | 340 | 300 | 202 | 8 | 90 | 41 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 16 | 20 | 138 | 105 | 0 | 19 | 0 | 43 | 42 | 8 | 5 | 0 | 0 | 58 | 10 | 0 | 0 | 0 | 6 | 10 | 310 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 145 | 2 | 21 | 100 | 128 | 404 | 86 | 105 | 105 | 4 | 177 | 36 | 92 | 17 | 8 | 10 | 385 | 17 | 23 | 35 | 108 | 0 | 35 | 11 | 53 | 55 | 0 |  | 903 | 0 | 195 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 16 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 162 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 375 | 17 | 0 | 70 | 105 | 85 | 0 | 4 | 76 | 870 | 177 | 0 | 0 | 1 | 61 | 108 | 0 | 0 |  | 6637 | 4025 | 10662 | 3535 | 903 | 1711 | 0 | 2646 | 1070 | 126 | 130 | 427 | 138 | 106 | 822 | 91.1
10:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 403 | 336 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 42 | 0 | 90 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 35 | 0 | 10 | 75 | 30 | 19 | 8 | 0 | 0 | 0 | 330 | 330 | 196 | 26 | 91 | 40 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 30 | 20 | 146 | 103 | 0 | 19 | 1 | 43 | 42 | 44 | 25 | 0 | 0 | 54 | 10 | 0 | 0 | 0 | 8 | 10 | 315 | 8 | 0 | 0 | 253 | 0 | 0 | 210 | 0 | 144 | 6 | 11 | 85 | 123 | 403 | 65 | 90 | 105 | 3 | 177 | 36 | 92 | 17 | 8 | 10 | 387 | 17 | 56 | 35 | 90 | 0 | 35 | 18 | 53 | 55 | 0 |  | 867 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 19 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 19 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 155 | 0 | 0 | 174 | 0 | 0 | 144 | 0 | 355 | 17 | 0 | 70 | 105 | 85 | 0 | 5 | 76 | 870 | 191 | 0 | 0 | 1 | 65 | 108 | 0 | 0 |  | 6689 | 4012 | 10701 | 3527 | 867 | 1783 | 0 | 2561 | 1070 | 125 | 174 | 467 | 146 | 155 | 972 | 91.1
11:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 402 | 332 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 145 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 78 | 25 | 19 | 4 | 0 | 0 | 0 | 345 | 330 | 184 | 26 | 90 | 40 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 152 | 102 | 0 | 19 | 1 | 43 | 42 | 50 | 45 | 0 | 0 | 53 | 10 | 0 | 0 | 0 | 15 | 8 | 320 | 8 | 0 | 0 | 245 | 0 | 0 | 210 | 0 | 140 | 4 | 11 | 85 | 118 | 381 | 72 | 90 | 105 | 1 | 176 | 36 | 92 | 17 | 8 | 10 | 370 | 17 | 55 | 35 | 90 | 0 | 35 | 33 | 48 | 55 | 0 |  | 867 | 0 | 175 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 153 | 0 | 0 | 210 | 0 | 0 | 141 | 0 | 315 | 17 | 0 | 70 | 88 | 84 | 0 | 8 | 76 | 870 | 210 | 0 | 0 | 3 | 110 | 108 | 0 | 0 |  | 6699 | 4041 | 10740 | 3475 | 867 | 1786 | 0 | 2540 | 1070 | 125 | 210 | 510 | 152 | 215 | 1075 | 91.1
12:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 396 | 332 |  | 0 | 225 | 0 | 8 | 0 | 45 | 0 | 0 | 0 | 8 | 16 | 145 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 89 | 26 | 19 | 3 | 0 | 0 | 0 | 340 | 325 | 164 | 8 | 90 | 39 | 54 | 0 | 51 | 0 | 17 | 8 | 19 | 11 | 33 | 20 | 152 | 94 | 0 | 19 | 2 | 43 | 42 | 50 | 45 | 0 | 0 | 56 | 10 | 0 | 0 | 0 | 26 | 10 | 320 | 8 | 0 | 0 | 245 | 0 | 0 | 209 | 0 | 135 | 2 | 11 | 85 | 117 | 379 | 56 | 90 | 105 | 5 | 176 | 36 | 92 | 17 | 8 | 10 | 380 | 17 | 46 | 35 | 90 | 0 | 35 | 28 | 36 | 55 | 0 |  | 867 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 148 | 0 | 0 | 204 | 0 | 0 | 138 | 0 | 304 | 17 | 0 | 70 | 89 | 83 | 0 | 8 | 76 | 860 | 204 | 0 | 0 | 3 | 39 | 108 | 0 | 0 |  | 6631 | 3927 | 10558 | 3426 | 867 | 1766 | 0 | 2508 | 1060 | 125 | 204 | 521 | 152 | 133 | 1381 | 91.1
13:00 | 0 | 0 | 0 | 180 | 20 | 89 | 0 | 395 | 332 |  | 0 | 225 | 0 | 7 | 0 | 45 | 0 | 0 | 0 | 8 | 7 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 21 | 25 | 33 | 41 | 0 | 88 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 10 | 0 | 19 | 7 | 0 | 0 | 0 | 315 | 330 | 170 | 8 | 90 | 39 | 53 | 0 | 51 | 0 | 50 | 8 | 19 | 11 | 0 | 20 | 162 | 80 | 0 | 19 | 2 | 43 | 42 | 50 | 47 | 0 | 0 | 58 | 10 | 0 | 0 | 0 | 26 | 10 | 320 | 8 | 0 | 0 | 243 | 0 | 0 | 209 | 0 | 133 | 1 | 11 | 85 | 117 | 398 | 65 | 90 | 105 | 3 | 177 | 36 | 87 | 17 | 8 | 10 | 385 | 17 | 53 | 35 | 90 | 0 | 35 | 26 | 51 | 55 | 0 |  | 867 | 0 | 165 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 24 | 16 | 0 | 0 | 0 | 24 | 5 | 89 | 0 | 34 | 16 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 203 | 0 | 0 | 136 | 0 | 302 | 17 | 0 | 70 | 89 | 83 | 0 | 7 | 76 | 890 | 204 | 0 | 0 | 4 | 7 | 108 | 0 | 0 |  | 6573 | 3924 | 10497 | 3389 | 867 | 1775 | 0 | 2408 | 1090 | 123 | 203 | 580 | 162 | 103 | 1298 | 91.1
14:00 | 0 | 0 | 0 | 180 | 20 | 90 | 0 | 397 | 332 |  | 0 | 225 | 0 | 7 | 0 | 50 | 0 | 0 | 0 | 8 | 7 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 19 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 12 | 12 | 19 | 8 | 0 | 0 | 0 | 300 | 330 | 166 | 8 | 90 | 36 | 51 | 0 | 51 | 0 | 49 | 8 | 19 | 11 | 33 | 20 | 168 | 80 | 0 | 19 | 2 | 43 | 40 | 50 | 43 | 0 | 0 | 60 | 10 | 0 | 0 | 0 | 26 | 10 | 320 | 8 | 0 | 0 | 245 | 0 | 0 | 209 | 0 | 138 | 2 | 11 | 85 | 115 | 397 | 60 | 90 | 105 | 1 | 177 | 36 | 72 | 17 | 8 | 10 | 380 | 17 | 52 | 35 | 90 | 0 | 35 | 21 | 52 | 55 | 0 |  | 867 | 0 | 165 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 26 | 16 | 0 | 0 | 0 | 24 | 16 | 86 | 0 | 34 | 28 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 204 | 0 | 0 | 135 | 0 | 300 | 17 | 0 | 70 | 88 | 82 | 0 | 7 | 76 | 900 | 220 | 0 | 0 | 4 | 13 | 108 | 0 | 0 |  | 6564 | 3977 | 10541 | 3379 | 867 | 1787 | 0 | 2413 | 1100 | 125 | 204 | 600 | 168 | 102 | 1249 | 91.09
15:00 | 0 | 0 | 0 | 180 | 80 | 84 | 0 | 397 | 334 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 7 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 21 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 12 | 26 | 19 | 3 | 0 | 0 | 0 | 310 | 335 | 172 | 8 | 90 | 37 | 51 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 33 | 20 | 172 | 80 | 0 | 19 | 2 | 43 | 40 | 44 | 46 | 0 | 0 | 61 | 10 | 0 | 0 | 0 | 26 | 10 | 320 | 8 | 0 | 0 | 281 | 0 | 0 | 206 | 0 | 142 | 4 | 11 | 85 | 115 | 400 | 73 | 88 | 105 | 0 | 178 | 36 | 75 | 17 | 8 | 10 | 384 | 17 | 37 | 69 | 90 | 0 | 35 | 11 | 52 | 55 | 0 |  | 867 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 25 | 16 | 0 | 0 | 0 | 24 | 18 | 84 | 0 | 34 | 32 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 202 | 0 | 0 | 122 | 0 | 287 | 17 | 0 | 70 | 88 | 82 | 0 | 6 | 76 | 900 | 220 | 0 | 0 | 4 | 37 | 108 | 0 | 0 |  | 6714 | 3965 | 10679 | 3445 | 867 | 1760 | 0 | 2508 | 1100 | 125 | 202 | 601 | 172 | 101 | 1307 | 91.09
16:00 | 0 | 0 | 0 | 180 | 75 | 82 | 0 | 407 | 335 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 7 | 142 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 25 | 21 | 25 | 33 | 42 | 0 | 90 | 35 | 100 | 0 | 24 | 0 | 0 | 0 | 0 |  | 21 | 51 | 0 | 10 | 12 | 0 | 19 | 3 | 0 | 0 | 0 | 315 | 335 | 167 | 8 | 90 | 36 | 51 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 33 | 20 | 160 | 81 | 0 | 19 | 1 | 43 | 41 | 50 | 45 | 0 | 0 | 61 | 10 | 0 | 0 | 0 | 26 | 10 | 280 | 8 | 0 | 0 | 273 | 0 | 0 | 200 | 0 | 143 | 2 | 11 | 85 | 108 | 365 | 82 | 90 | 105 | 0 | 178 | 36 | 90 | 17 | 40 | 10 | 360 | 17 | 10 | 122 | 105 | 0 | 35 | 7 | 52 | 55 | 0 |  | 867 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 28 | 16 | 0 | 0 | 0 | 24 | 25 | 84 | 0 | 25 | 32 | 8 | 35 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 134 | 0 | 0 | 184 | 0 | 0 | 119 | 0 | 287 | 17 | 0 | 100 | 88 | 76 | 0 | 5 | 76 | 900 | 220 | 0 | 0 | 2 | 23 | 108 | 0 | 0 |  | 6670 | 3986 | 10656 | 3388 | 867 | 1728 | 0 | 2615 | 1099 | 125 | 184 | 624 | 160 | 50 | 1198 | 91.09
17:00 | 0 | 0 | 0 | 180 | 75 | 89 | 0 | 408 | 334 |  | 0 | 225 | 0 | 9 | 0 | 40 | 0 | 0 | 0 | 8 | 7 | 142 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 0 | 10 | 12 | 1 | 19 | 12 | 0 | 0 | 0 | 325 | 340 | 162 | 8 | 90 | 36 | 51 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 33 | 20 | 144 | 82 | 0 | 19 | 0 | 43 | 41 | 50 | 43 | 0 | 0 | 60 | 10 | 0 | 15 | 0 | 28 | 10 | 280 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 143 | 1 | 11 | 97 | 100 | 367 | 105 | 90 | 105 | 0 | 178 | 36 | 92 | 17 | 94 | 10 | 360 | 17 | 7 | 144 | 108 | 0 | 35 | 4 | 71 | 55 | 0 |  | 867 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 25 | 16 | 0 | 0 | 0 | 30 | 22 | 84 | 0 | 25 | 32 | 8 | 34 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 166 | 0 | 0 | 119 | 0 | 285 | 17 | 0 | 112 | 88 | 90 | 0 | 2 | 113 | 900 | 220 | 0 | 0 | 0 | 26 | 108 | 0 | 0 |  | 6873 | 4028 | 10901 | 3438 | 867 | 1739 | 0 | 2840 | 1100 | 125 | 166 | 608 | 144 | 40 | 903 | 91.09
18:00 | 0 | 0 | 0 | 180 | 65 | 89 | 0 | 406 | 334 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 7 | 145 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 24 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 12 | 21 | 19 | 5 | 0 | 0 | 0 | 355 | 340 | 145 | 8 | 90 | 40 | 51 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 150 | 83 | 0 | 19 | 0 | 43 | 41 | 50 | 43 | 0 | 0 | 60 | 10 | 0 | 50 | 0 | 28 | 10 | 300 | 8 | 0 | 0 | 263 | 0 | 0 | 200 | 0 | 143 | 0 | 11 | 100 | 107 | 404 | 105 | 90 | 105 | 0 | 178 | 36 | 92 | 114 | 114 | 10 | 385 | 17 | 1 | 144 | 108 | 0 | 35 | 2 | 94 | 55 | 0 |  | 867 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 5 | 30 | 8 | 82 | 18 | 16 | 0 | 0 | 0 | 30 | 22 | 84 | 0 | 25 | 32 | 8 | 34 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 159 | 0 | 0 | 119 | 0 | 287 | 17 | 0 | 113 | 88 | 98 | 0 | 0 | 113 | 900 | 223 | 0 | 0 | 0 | 7 | 108 | 0 | 0 |  | 7197 | 4044 | 11241 | 3545 | 867 | 1751 | 0 | 3054 | 1100 | 125 | 159 | 639 | 150 | 10 | 752 | 91.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
19:00 | 0 | 0 | 0 | 180 | 120 | 89 | 0 | 406 | 334 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 7 | 145 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 12 | 37 | 20 | 18 | 0 | 0 | 0 | 300 | 320 | 153 | 8 | 90 | 42 | 56 | 0 | 51 | 0 | 47 | 43 | 22 | 10 | 33 | 20 | 180 | 103 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 60 | 10 | 0 | 90 | 0 | 11 | 10 | 300 | 8 | 0 | 0 | 276 | 0 | 0 | 200 | 0 | 128 | 0 | 11 | 100 | 118 | 404 | 106 | 90 | 105 | 0 | 275 | 36 | 92 | 114 | 116 | 10 | 397 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 92 | 55 | 0 |  | 853 | 0 | 160 | 0 | 64 | 0 | 0 | 0 | 38 | 60 | 40 | 82 | 29 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 34 | 34 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 212 | 0 | 0 | 119 | 0 | 286 | 17 | 0 | 113 | 105 | 96 | 0 | 0 | 113 | 940 | 220 | 0 | 3 | 0 | 0 | 108 | 0 | 0 |  | 7432 | 4325 | 11757 | 3614 | 853 | 1692 | 0 | 3337 | 1140 | 127 | 212 | 814 | 180 | 0 | 1387 | 91.09
19:30 | 0 | 0 | 0 | 180 | 150 | 89 | 0 | 408 | 334 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 147 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 12 | 24 | 20 | 21 | 0 | 0 | 0 | 300 | 320 | 159 | 8 | 90 | 47 | 55 | 0 | 51 | 0 | 47 | 43 | 22 | 10 | 33 | 20 | 170 | 107 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 65 | 45 | 0 | 90 | 0 | 11 | 10 | 250 | 8 | 0 | 0 | 276 | 0 | 0 | 200 | 0 | 142 | 0 | 11 | 100 | 110 | 399 | 106 | 90 | 105 | 0 | 280 | 36 | 92 | 114 | 116 | 10 | 389 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 852 | 0 | 160 | 0 | 64 | 0 | 0 | 0 | 42 | 80 | 32 | 82 | 29 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 43 | 36 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 214 | 0 | 0 | 119 | 0 | 298 | 17 | 0 | 113 | 105 | 94 | 0 | 0 | 113 | 950 | 180 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7475 | 4348 | 11823 | 3654 | 852 | 1651 | 0 | 3375 | 1150 | 127 | 214 | 844 | 170 | 0 | 1789 | 0
20:00 | 0 | 0 | 0 | 180 | 180 | 90 | 0 | 405 | 334 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 51 | 10 | 12 | 37 | 20 | 17 | 0 | 0 | 0 | 280 | 320 | 161 | 8 | 90 | 42 | 56 | 0 | 51 | 0 | 47 | 43 | 22 | 10 | 33 | 20 | 162 | 107 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 61 | 60 | 0 | 100 | 0 | 11 | 10 | 270 | 8 | 0 | 0 | 276 | 0 | 0 | 200 | 0 | 135 | 0 | 11 | 100 | 108 | 400 | 106 | 90 | 105 | 0 | 285 | 36 | 92 | 114 | 115 | 10 | 400 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 94 | 55 | 0 |  | 852 | 0 | 160 | 0 | 80 | 0 | 0 | 0 | 50 | 75 | 32 | 82 | 25 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 135 | 0 | 0 | 216 | 0 | 0 | 120 | 0 | 318 | 17 | 0 | 113 | 105 | 97 | 0 | 0 | 113 | 950 | 172 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7536 | 4388 | 11924 | 3680 | 852 | 1692 | 0 | 3411 | 1149 | 127 | 216 | 851 | 162 | 0 | 1882 | 91.09
21:00 | 0 | 0 | 0 | 180 | 180 | 83 | 0 | 409 | 327 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 51 | 10 | 12 | 25 | 20 | 29 | 0 | 0 | 0 | 280 | 320 | 177 | 8 | 91 | 42 | 55 | 0 | 51 | 0 | 48 | 43 | 22 | 11 | 33 | 20 | 172 | 107 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 63 | 81 | 0 | 120 | 0 | 10 | 10 | 295 | 8 | 0 | 0 | 292 | 0 | 0 | 200 | 0 | 143 | 0 | 11 | 100 | 118 | 399 | 106 | 90 | 105 | 0 | 285 | 36 | 92 | 114 | 115 | 10 | 400 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 853 | 0 | 165 | 0 | 80 | 0 | 0 | 0 | 42 | 56 | 32 | 82 | 28 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 137 | 0 | 0 | 217 | 0 | 0 | 122 | 0 | 314 | 17 | 0 | 113 | 105 | 99 | 0 | 0 | 113 | 1010 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7649 | 4482 | 12131 | 3732 | 853 | 1782 | 0 | 3430 | 1209 | 127 | 217 | 826 | 172 | 0 | 1783 | 91.09
22:00 | 0 | 0 | 0 | 180 | 180 | 90 | 0 | 409 | 322 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 147 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 12 | 25 | 20 | 28 | 0 | 0 | 0 | 280 | 320 | 193 | 8 | 99 | 42 | 55 | 0 | 51 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 172 | 105 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 61 | 81 | 0 | 120 | 0 | 11 | 10 | 300 | 8 | 0 | 0 | 291 | 0 | 0 | 200 | 0 | 143 | 0 | 11 | 100 | 122 | 365 | 105 | 90 | 105 | 0 | 285 | 36 | 92 | 110 | 115 | 10 | 360 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 853 | 0 | 170 | 0 | 80 | 0 | 0 | 0 | 41 | 56 | 32 | 82 | 32 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 217 | 0 | 0 | 123 | 0 | 321 | 17 | 0 | 113 | 105 | 99 | 0 | 0 | 113 | 1040 | 222 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7602 | 4532 | 12134 | 3686 | 853 | 1802 | 0 | 3432 | 1239 | 127 | 217 | 823 | 172 | 0 | 1718 | 91.09
23:00 | 0 | 0 | 0 | 180 | 180 | 90 | 0 | 407 | 345 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 147 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 19 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 12 | 25 | 20 | 36 | 0 | 0 | 0 | 280 | 320 | 200 | 8 | 90 | 38 | 55 | 0 | 51 | 0 | 49 | 25 | 22 | 11 | 33 | 20 | 178 | 106 | 0 | 7 | 0 | 43 | 42 | 14 | 10 | 0 | 0 | 62 | 81 | 0 | 120 | 0 | 11 | 10 | 330 | 8 | 0 | 0 | 291 | 0 | 0 | 200 | 0 | 145 | 0 | 11 | 100 | 120 | 402 | 105 | 90 | 87 | 0 | 212 | 36 | 92 | 98 | 115 | 10 | 398 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 67 | 55 | 0 |  | 852 | 0 | 180 | 0 | 65 | 0 | 0 | 0 | 41 | 56 | 32 | 82 | 31 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 212 | 0 | 0 | 122 | 0 | 355 | 17 | 0 | 113 | 105 | 99 | 0 | 0 | 113 | 1050 | 223 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7570 | 4564 | 12134 | 3744 | 852 | 1897 | 0 | 3271 | 1249 | 125 | 212 | 818 | 178 | 0 | 1653 | 91.09
24:00 | 0 | 0 | 0 | 180 | 180 | 90 | 0 | 406 | 345 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 147 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 19 | 25 | 33 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 51 | 10 | 12 | 25 | 20 | 38 | 0 | 0 | 0 | 280 | 320 | 204 | 8 | 90 | 39 | 55 | 0 | 51 | 0 | 49 | 25 | 22 | 11 | 33 | 20 | 158 | 106 | 0 | 6 | 0 | 43 | 42 | 14 | 10 | 0 | 0 | 62 | 81 | 0 | 120 | 0 | 11 | 10 | 325 | 8 | 0 | 0 | 291 | 0 | 0 | 200 | 0 | 145 | 0 | 11 | 100 | 128 | 402 | 38 | 88 | 105 | 0 | 212 | 36 | 92 | 98 | 18 | 10 | 396 | 17 | 0 | 76 | 108 | 0 | 35 | 0 | 55 | 55 | 0 |  | 853 | 0 | 195 | 0 | 65 | 0 | 0 | 0 | 41 | 56 | 8 | 82 | 32 | 32 | 0 | 0 | 0 | 32 | 24 | 87 | 0 | 25 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 204 | 0 | 0 | 127 | 0 | 414 | 17 | 0 | 70 | 105 | 99 | 0 | 0 | 113 | 1050 | 224 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 7237 | 4539 | 11776 | 3778 | 853 | 1955 | 0 | 2849 | 1249 | 125 | 204 | 809 | 158 | 0 | 1878 | 91.09
KWH | 0 | 0 | 0 | 4347000 | 3787291 | 2064772 | 0 | 9893890 | 8026000 |  | 0 | 5001450 | 0 | 196800 | 0 | 1229657 | 0 | 0 | 0 | 196589 | 300672 | 3366720 | 0 | 0 | 0 | 0 | 350640 | 297069 | 282904 | 355572 | 600000 | 568980 | 602200 | 786900 | 1109280 | 0 | 2220022 | 840000 | 2300000 | 0 | 534600 | 0 | 0 | 0 | 0 |  | 525840 | 1135968 | 269152 | 258600 | 1104960 | 665760 | 448608 | 597600 | 0 | 0 | 0 | 7847500 | 7720000 | 4435000 | 250909 | 2139060 | 950832 | 1300320 | 0 | 1207954 | 0 | 807712 | 472997 | 468936 | 226080 | 762000 | 513010 | 3766080 | 2314560 | 0 | 361368 | 10550 | 1013000 | 953088 | 569400 | 486216 | 0 | 0 | 1415 | 623040 | 0 | 2560290 | 0 | 309200 | 238140 | 7522500 | 182352 | 0 | 0 | 6506070 | 0 | 0 | 4826400 | 0 | 3406608 | 30240 | 345600 | 2435040 | 2883781 | 9131000 | 2176800 | 2294400 | 2473963 | 18121 | 4792364 | 907149 | 2193772 | 1255140 | 1006320 | 253440 | 9112800 | 429120 | 310730 | 1844640 | 2487764 | 0 | 885240 | 193128 | 1497600 | 1337040 | 0 |  | 21168000 | 0 | 4754592 | 0 | 1256640 | 0 | 0 | 0 | 360960 | 604800 | 314625 | 1986199 | 642403 | 542784 | 0 | 0 | 0 | 664171 | 355514 | 2072432 | 0 | 712016 | 441800 | 393120 | 459450 | 448560 | 0 | 210150 | 0 | 0 | 4857300 | 0 | 0 | 3937691 | 0 | 0 | 4704891 | 0 | 0 | 3629082 | 0 | 8423018 | 416160 | 0 | 2134080 | 2420784 | 2221747 | 0 | 60337 | 2129088 | 24827100 | 5176255 | 0 | 92400 | 26400 | 409680 | 2602176 | 0 | 0 |  | 169313275 | 105456405 | 274769680 | 88900446 | 21168000 | 42887737 | 0 | 69000239 | 29684400 | 3060022 | 4704891 | 10538679 | 3766080 | 1059186 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 4241765.92 | 2746146.76 | 0 | 10388584.5 | 8668080 |  | 0 | 5451580.5 | 0 | 2200224 | 0 | 16292955.25 | 0 | 0 | 0 | 2874131.18 | 4230455.04 | 54574531.2 | 0 | 0 | 0 | 0 | 4460140.8 | 4010431.5 | 3793742.64 | 266679 | 450000 | 0 | 0 | 0 | 18868852.8 | 0 | 599405.94 | 226800 | 4347000 | 0 | 8740710 | 0 | 0 | 0 | 0 |  | 6862212 | 18947946.24 | 4580967.04 | 3493686 | 14010892.8 | 7702843.2 | 569732.16 | 1990008 | 0 | 0 | 0 | 8710725 | 8414800 | 5144600 | 323672.61 | 2609653.2 | 1074440.16 | 1937476.8 | 0 | 2017283.18 | 0 | 13949186.24 | 6361809.65 | 642442.32 | 169560 | 1333500 | 384757.5 | 27040454.4 | 2522870.4 | 0 | 491460.48 | 168167 | 1387810 | 1258076.16 | 990756 | 841153.68 | 0 | 0 | 2745.1 | 1420531.2 | 0 | 2585892.9 | 0 | 460708 | 471517.2 | 7522500 | 136764 | 0 | 0 | 88807855.5 | 0 | 0 | 65059872 | 0 | 47181520.8 | 353505.6 | 3566592 | 33262646.4 | 38267773.87 | 8400520 | 26469888 | 33177024 | 31295631.95 | 0 | 56262353.36 | 9878852.61 | 23319796.36 | 17032249.8 | 12971464.8 | 2985523.2 | 8383776 | 5557104 | 4490048.5 | 23408481.6 | 28310754.32 | 0 | 11561234.4 | 2307879.6 | 22419072 | 17608816.8 | 0 |  | 63504000 | 0 | 5325143.04 | 0 | 13081622.4 | 0 | 0 | 0 | 6500889.6 | 10886400 | 4521161.25 | 2224542.88 | 1246261.82 | 5916345.6 | 0 | 0 | 0 | 11138147.67 | 6217939.86 | 32412836.48 | 0 | 11790984.96 | 7470838 | 5358225.6 | 7750921.5 | 928519.2 | 0 | 159083.55 | 0 | 0 | 25695117 | 0 | 0 | 4567721.56 | 0 | 0 | 82147396.86 | 0 | 0 | 4209735.12 | 0 | 8338787.82 | 5593190.4 | 0 | 25246166.4 | 34980328.8 | 28216186.9 | 0 | 666723.85 | 25847128.32 | 223692171 | 5279780.1 | 0 | 683760 | 298584 | 4805546.4 | 39891358.08 | 0 | 0 |  | 944783085.12 | 716593546.02 | 1661376631.14 | 96881410.95 | 63504000 | 50634762.87 | 0 | 903434053.34 | 249387288 | 826205.94 | 82147396.86 | 174430603.83 | 27040454.4 | 13090454.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 402 | 332 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 16 | 145 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 23 | 25 | 33 | 41 | 0 | 90 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 42 | 0 | 10 | 78 | 25 | 19 | 4 | 0 | 0 | 0 | 345 | 330 | 184 | 26 | 90 | 40 | 54 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 152 | 102 | 0 | 19 | 1 | 43 | 42 | 50 | 45 | 0 | 0 | 53 | 10 | 0 | 0 | 0 | 15 | 8 | 320 | 8 | 0 | 0 | 245 | 0 | 0 | 210 | 0 | 140 | 4 | 11 | 85 | 118 | 381 | 72 | 90 | 105 | 1 | 176 | 36 | 92 | 17 | 8 | 10 | 370 | 17 | 55 | 35 | 90 | 0 | 35 | 33 | 48 | 55 | 0 |  | 867 | 0 | 175 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 89 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 153 | 0 | 0 | 210 | 0 | 0 | 141 | 0 | 315 | 17 | 0 | 70 | 88 | 84 | 0 | 8 | 76 | 870 | 210 | 0 | 0 | 3 | 110 | 108 | 0 | 0 |  | 10740 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 180 | 83 | 0 | 409 | 327 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | 51 | 10 | 12 | 25 | 20 | 29 | 0 | 0 | 0 | 280 | 320 | 177 | 8 | 91 | 42 | 55 | 0 | 51 | 0 | 48 | 43 | 22 | 11 | 33 | 20 | 172 | 107 | 0 | 20 | 0 | 43 | 41 | 14 | 10 | 0 | 0 | 63 | 81 | 0 | 120 | 0 | 10 | 10 | 295 | 8 | 0 | 0 | 292 | 0 | 0 | 200 | 0 | 143 | 0 | 11 | 100 | 118 | 399 | 106 | 90 | 105 | 0 | 285 | 36 | 92 | 114 | 115 | 10 | 400 | 17 | 0 | 144 | 108 | 0 | 35 | 0 | 93 | 55 | 0 |  | 853 | 0 | 165 | 0 | 80 | 0 | 0 | 0 | 42 | 56 | 32 | 82 | 28 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 25 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 137 | 0 | 0 | 217 | 0 | 0 | 122 | 0 | 314 | 17 | 0 | 113 | 105 | 99 | 0 | 0 | 113 | 1010 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 12131 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 180 | 92 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 51 | 10 | 89 | 38 | 20 | 20 | 0 | 0 | 0 | 300 | 300 | 212 | 8 | 135 | 36 | 55 | 0 | 51 | 0 | 49 | 43 | 19 | 11 | 33 | 20 | 15 | 107 | 0 | 20 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 63 | 81 | 0 | 120 | 0 | 10 | 10 | 330 | 8 | 0 | 0 | 292 | 0 | 0 | 200 | 0 | 143 | 0 | 11 | 100 | 150 | 400 | 105 | 90 | 105 | 0 | 285 | 36 | 110 | 114 | 95 | 10 | 400 | 17 | 0 | 162 | 108 | 0 | 35 |  | 95 | 55 |  |  | 870 | 0 | 180 | 0 | 115 | 0 | 0 | 0 | 44 | 55 | 40 | 82 | 28 | 32 | 0 | 0 | 0 | 34 | 25 | 88 | 0 | 25 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 113 | 1100 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 180 | 92 | 0 | 410 | 320 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 0 | 10 | 12 | 25 | 20 | 5 | 0 | 0 | 0 | 320 | 320 | 212 | 8 | 30 | 36 | 55 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 20 | 125 | 102 | 0 | 20 | 1.6 | 43 | 41 | 11 | 10 | 0 | 0 | 59 | 10 | 0 | 120 | 0 | 10 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 200 | 0 | 134 | 20 | 11 | 100 | 130 | 400 | 105 | 88 | 105 | 5 | 175 | 36 | 110 | 17 | 8 | 10 | 400 | 17 | 50 | 35 | 108 | 0 | 35 | 30 | 54 | 55 |  |  | 885 | 0 | 190 | 0 | 32 | 0 | 0 | 0 | 0 | 55 | 8 | 82 | 23 | 16 | 0 | 0 | 0 | 34 | 16 | 88 | 0 | 25 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 330 | 17 | 0 | 70 | 105 | 84 | 0 | 8 | 75 | 1100 | 220 |  | 17 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 180 | 92 | 0 | 406 | 336 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 132 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 51 | 0 | 10 | 12 | 25 | 20 | 6 | 0 | 0 | 0 | 360 | 320 | 212 | 8 | 30 | 36 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 19 | 132 | 102 | 0 | 20 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 59 | 10 | 0 | 120 | 0 | 11 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 200 | 0 | 134 | 4 | 11 | 50 | 118 | 402 | 39 | 88 | 105 | 1 | 65 | 36 | 92 | 17 | 8 | 10 | 400 | 17 | 3 | 35 | 108 | 0 | 35 | 10 | 53 | 55 | 0 | 0 | 904 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 130 | 0 | 0 | 159 | 0 | 330 | 17 | 0 | 70 | 105 | 49 | 0 | 1 | 75 | 910 | 182 | 0 | 17 | 1 | 8 | 17 | 0 | 0 | 0 |  |  |  |  | 84243809 |  | 0
84243809
| Minimum Generation |  | 10662 | 9:00
| Highest Generation |  | 12134 | 22:00
| Day Peak Generation |  | 10740 | 11:00
| Evening Peak Generation |  | 12131 | 21:00
| HVDC Max Flow |  | 903 | 9:00
| HVDC EvPeak Flow |  | 853 | 21:00
| Load factor L.F |  | 94.35% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-24
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10740 | MW Hour : | 11:00 | Min. Gen. at | 8:00 | 10428 | MW
Evening Peak Generation : |  | 12131 | MW Hour : | 21:00 | Available Max Generation : |  | 12313 | MW
E.P. Demand (at gen end) : |  | 13914 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12134 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 274.7697 | System Load Factor : | 94.35% | Load Shed : |  | 1616 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 430 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-24
Actual : | 91.07 | Ft.(MSL) , | Rule curve : | 87.68 | Ft.( MSL )
Gas Consumed : | Total = | 1000.82 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147516173.82
: |  | Coal : | 249387288 | Oil : | 1160012054.03 | Total : | 1556915515.85
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 400 | 9600:00 | 5419.5449 |  |  | 474 | 18.1%
Chittagong Area | 83 | 1992:00 | 1506.4898 |  |  | 165 | 15.89%
Khulna Area | 280 | 6720:00 | 1982.3479 |  |  | 230 | 15.53%
Rajshahi Area | 260 | 6240:00 | 1751.7914 |  |  | 210 | 15.07%
Cumilla Area | 240 | 5760:00 | 1493.9578 |  |  | 185 | 15.28%
Mymensingh Area | 270 | 6480:00 | 1230.1456 |  |  | 160 | 14.9%
Sylhet Area | 90 | 2160:00 | 553.8591 |  |  | 65 | 15.74%
Barisal Area | 0 | 0:00 | 447.6448 |  |  | 0 | 14.76%
Rangpur Area | 160 | 3840:00 | 970.8227 |  |  | 127 | 14.84%
Total | 1783 |  | 15356.6039 |  |  | 1616
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-B.Baria 132 kV Ckt-2 was under shut down from 10:12 to 11:58 for C/M.
b) Rajbari-Faridpur 132 kV Ckt-2 was under shut down from 08:10 to 13:11 for C/M.
c) Rajbari-Faridpur 132 kV Ckt-1 was under shut down from 13:15 to 16:14 for C/M.
d) Jhenaidah(N)-Chuadanga 132 kV Ckt was under shut down from 09:05 to 15:12 for C/M.
e) Jhenaidah(N)-Jessore 132 kV Ckt-1 was under shut down from 09:25 to 17:55 for C/M.
f) Barisal(S) 132/33 kV T-2 transformer was under shut down from 09:43 to 12:52 for C/M.
g) Ghorasal Unit-2 tripped at 08:02 and was synchrionzed at 12:46.
h) Chattak 132/33 kV T-2 transformer tripped at 20:24 due to 33 kV PBS feeder fault and was switched
on at 10:41(24-07-2022).
i) Sylhet 225 MW GT was synchronized at 16:55.
j) Thakurgaon S/S -Thakurgaon P/P 132 kV Ckt was under shut down at from 03:55(24-07-2022) to 05:45 | [5 empty] | About 106 MW power interruption has been running under
Thakurgaon, Panchagar area from 03:55 to 05:45.
k) Agargaon 230/132 kV T-1 transformer was shut down at 06:39(24-07-2022) for C/M.
l) Khulna© 132/33 kV T3 transformer tripped at 06:03(24-07-2022) showing no relay and was switched
on at 06:31(24-07-2022).
j) Thakurgaon 132/33 kV T-3 transformer on fire at 03:55(24-07-2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 180 | 3787291 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 83 | 2064772 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9893890
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 8026000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5001450 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 196800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1229657
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 355572
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 196589 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 300672 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 350640 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3366720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 297069
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 282904 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1168980 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 602200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 786900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1109280 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 292 | 6506070 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 143 | 3406608
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 2294400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 429120 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1844640 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 193128
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1337040
| Dhaka area Total |  |  |  | 5847 | 2659 | 59375392
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 534600
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 30240
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 665760 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 127 | 3060022 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2473963
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 1135968 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 269152 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 258600 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 11 | 345600 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 448608
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 597600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 1104960 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 4792364 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 907149 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2193772 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 253440
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2487764 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1097 | 23877683
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4435000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7847500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7720000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 0 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 950832
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1300320
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 250909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1207954
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 2883781 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 807712
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2139060 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 2435040 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 468936
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 172 | 3766080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 762000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 472997 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 513010 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1255140
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1006320
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 885240 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1497600 | Engine problem
| Cumilla Area Total |  |  |  | 2885 | 1948 | 42831511
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2314560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 361368
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 4826400
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 2176800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 310730
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 525840
| Mymensingh Area Total |  |  |  | 614 | 451 | 10526248
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1013000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 953088 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 14 | 569400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 486216 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1415
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 623040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2560290 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 10 | 309200 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 182352 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7522500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 399 | 9131000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238140
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9112800
| Sylhet Area Total |  |  |  | 2477 | 1494 | 32702441
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 853 | 21168000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 80 | 1256640 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 360960 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 56 | 604800 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 165 | 4754592 | FGMO & gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 314625 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 416160 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2420784
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 409680
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1350 | 31706241
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 542784 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 642403 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 1986199 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1010 | 24827100 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5176255
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 92400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1389 | 33267141
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 664171 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 25 | 355514 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 712016 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 441800 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 137 | 3937691 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 217 | 4704891
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 122 | 3629082 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 314 | 8423018 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 459450 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 448560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210150
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 393120
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 2072432 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2134080
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2129088
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26400
| Rajshahi Area Total |  |  |  | 2129 | 1337 | 30741463
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4857300 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 2221747 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 60337
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 2602176 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 406 | 9741560
| Total |  |  |  | 21396 | 12131 | 274769680
| Eastern Grid Total |  |  |  | 14205 | 7649 | 169313275
| Western Grid Total |  |  |  | 7191 | 4482 | 105456405
| National Grid Total |  |  |  | 21396 | 12131 | 274769680
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-23
(a) ENTIRE EASTERN GRID : |  | 7691.77 | MW | (b) ENTIRE WESTERN GRID : |  | 3853.1 | MW
i) Dhaka area |  | 4183.77 | MW | i) Khulna area |  | 1439 | MW
ii) Chittagong area |  | 1156 | MW | ii) Rajshahi area |  | 1277.4 | MW
iii) Comilla area |  | 1056 | MW | iii) Barisal area |  | 388.7 | MW
iv) Mymensingh area |  | 895 | MW | iv) Rangpur area |  | 748 | MW
v) Sylhet area |  | 401 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11544.87 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 15 | 09:00 | Chowmuhani | 181 | 18:30 | Kaptai | 4 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 68 | 11:00 | Chuadanga | 117 | 21:00 | Kazla | 88 | 12:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 00:00 | Coxsbazar | 114 | 00:00 | Keranigonj | 62 | 13:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 82 | 13:00 | Cumilla(N) | 148 | 19:00 | Khagrachori | 26 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 76 | 18:00 | Cumilla(S) | 180 | 19:00 | Khulna | 86 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 52 | 21:00 | Daudkandi | 128 | 18:30 | Khulshi | 153 | 23:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 41 | 23:00 | Dhaka | 32 | 10:00 | Kishoreganj | 136 | 04:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 125 | 01:00 | Dhamrai | 100 | 11:00 | Kodda | 312 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 92 | 01:00 | Dhanmondi | 113 | 14:00 | Kulaura | 48 | 00:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 121 | 18:30 | Dohazari | 80 | 21:00 | Kurigram | 62 | 07:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 53 | 15:00 | Faridpur | 140 | 00:00 | Kushtia | 124 | 18:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 10 | 11:00 | Fatullah | 66 | 12:00 | Lalbag | 106 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 52 | 00:00 | Fenchuganj | 49 | 01:00 | Lalmonirhat | 46 | 03:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 109 | 00:00 | Madanganj | 92 | 14:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 102 | 21:00 | GPH | 9 | 23:00 | Madaripur | 109 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 76 | 22:00 | Ghorashal | 68 | 00:00 | Madartek | 90 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 73 | 01:00 | Goalpara | 27 | 00:00 | Madunaghat | 57 | 03:00 | Rajshahi | 132 | 22:00
Baroirhat | 57 | 19:00 | Gollamari | 54 | 19:30 | Magura | 54 | 00:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 166 | 17:00 | Gopalganj | 102.2 | 00:00 | Mahasthangarh | 72 | 23:00 | Ramganj | 88 | 19:00
BashundharaCement | 12 | 12:00 | Gulshan | 104 | 17:00 | Manikganj | 83 | 22:00 | Rampur | 16 | 00:00
Beanibazar | 60 | 02:00 | Halishahar | 89 | 20:00 | Maniknagar | 66 | 14:00 | Rangamati | 14 | 19:00
Benapole | 48 | 07:00 | HaripurSBU | 113 | 11:00 | Matarbari | 42 | 00:00 | Rangpur | 105 | 08:00
Bhaluka | 144 | 18:00 | Hasnabad | 82 | 14:00 | Matuail | 62 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 52 | 00:00 | Hathazari | 93 | 19:00 | Millgate | 74 | 15:00 | SSM | 3 | 05:00
Bhangura | 32 | 01:00 | Ishurdi | 66 | 21:00 | Mirpur | 138 | 17:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 52 | 00:00 | Jaldhaka | 62 | 03:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 225 | 21:00 | Jamalpur | 150 | 20:00 | Mithapukur | 32 | 04:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 54 | 03:00 | Jashore | 121 | 00:00 | Modern | 0 | 04:00 | Savar | 156 | 09:00
Bogura | 158 | 01:00 | Jhenaidah | 99 | 03:00 | Mogbazar | 121 | 17:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 01:00 | Joydebpur | 171 | 18:30 | Mongla | 32 | 08:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 150 | 03:00 | Joypurhat | 59 | 02:00 | Motijheel | 37 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 151 | 17:00 | Juldah | 20.2 | 08:00 | Munshiganj | 93 | 04:00 | Shariatpur | 78 | 22:00
Chandpur | 61 | 03:00 | KSRM | 31.7 | 18:30 | Mymensingh | 244 | 20:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 00:00 | Kabirpur | 289 | 16:00 | Naogaon | 114 | 03:00 | Shikalbaha | 28 | 19:00
Chapai | 66 | 02:00 | Kachua | 74 | 03:00 | Narail | 42 | 00:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 44 | 09:00 | Kallyanpur | 96 | 00:00 | Narinda | 63 | 17:00 | Shitalakhya | 114 | 12:00
Chauddagram | 43 | 03:00 | Kalurghat | 6 | 12:00 | Narshingdi | 178 | 01:00 | Sholosohor | N/A | N/A
Chhatak | 33 | 00:00 | Kamrangirchar | 56 | 15:00 | Natore | 121 | 03:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 393 | 06:00 | 363 | 11:00 | Kaliakoir | 392 | 19:30 | 375 | 09:00
| Bibiana | 410 | 19:30 | 397 | 09:00 | Payra | 419 | 08:00 | 411 | 00:00
| BIPTC | 402 | 06:00 | 397 | 00:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 411 | 12:00 | 396 | 02:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 19:30 | 206 | 11:00 | Hasnabad | 220 | 00:00 | 205 | 09:00
| AKSML | 234 | 20:00 | 222 | 02:00 | Hathazari | 237 | 19:30 | 227 | 07:00
| Aminbazar | 222 | 06:00 | 206 | 12:00 | Ishurdi | 235 | 19:30 | 228 | 02:00
| Ashuganj | 236 | 20:00 | 225 | 11:00 | Jhenaidah | 230 | 15:00 | 219 | 05:00
| Baghabari | 233 | 19:30 | 200 | 08:00 | Kaliakoir | 225 | 06:00 | 212 | 09:00
| Barapukuria | 225 | 16:00 | 213 | 03:00 | Keranigonj | 220 | 06:00 | 205 | 11:00
| Barishal | 244 | 12:00 | 237 | 00:00 | Khulna(S) | 237 | 20:00 | 227 | 00:00
| Bheramara | 233 | 03:00 | 223 | 02:00 | Maniknagar | 224 | 19:30 | 209 | 11:00
| Bhulta | 227 | 19:30 | 213 | 11:00 | Meghnaghat | 226 | 00:00 | 212 | 11:00
| Bibiana | 238 | 19:30 | 228 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 19:30 | 225 | 02:00 | Rajshahi | 231 | 19:30 | 224 | 00:00
| Bogura | 228 | 16:00 | 219 | 04:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 11:00 | 240 | 07:00 | Rampura | 225 | 04:00 | 211 | 11:00
| BSRM | 235 | 19:30 | 225 | 09:00 | Shikalbaha | 236 | 20:00 | 230 | 02:00
| Cumilla(N) | 229 | 19:30 | 217 | 11:00 | Shyampur | 221 | 19:30 | 207 | 10:00
| Fenchuganj | 238 | 19:00 | 231 | 09:00 | Siddhirganj | 225 | 06:00 | 216 | 17:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 19:30 | 227 | 03:00
| GPH | 235 | 19:30 | 225 | 09:00 | Tongi | 228 | 03:00 | 210 | 12:00
| Haripur | 223 | 21:00 | 209 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 21:00 | 125 | 10:00 | Lalbag | 136 | 19:30 | 125 | 09:00
| Agargaon | 137 | 19:30 | 124 | 09:00 | Lalmonirhat | 132 | 15:00 | 122 | 07:00
| Agrabad | 137 | 19:30 | 131 | 09:00 | Madanganj | 131 | 19:00 | 122 | 09:00
| AKS | 136 | 18:30 | 131 | 09:00 | Madaripur | 137 | 07:00 | 130 | 00:00
| Aminbazar | 132 | 19:30 | 122 | 12:00 | Madartek | 138 | 19:30 | 124 | 11:00
| Amnura | 132 | 16:00 | 125 | 00:00 | Madunaghat | 138 | 18:30 | 132 | 23:00
| Ashuganj | 137 | 08:00 | 134 | 10:00 | Magura | 140 | 13:00 | 131 | 00:00
| Bagerhat | 131 | 13:00 | 123 | 00:00 | Mahasthangarh | 136 | 15:00 | 127 | 04:00
| Bakulia | 139 | 19:30 | 132 | 09:00 | Manikganj | 135 | 19:00 | 128 | 16:00
| Banani | 134 | 19:30 | 122 | 11:00 | Maniknagar | 133 | 19:30 | 120 | 10:00
| Bangabhaban | 134 | 21:00 | 121 | 10:00 | Matarbari | 133 | 15:00 | 115 | 00:00
| Barapukuria | 138 | 15:00 | 130 | 03:00 | Matuail | 132 | 02:00 | 123 | 11:00
| Barguna | 135 | 20:00 | 129 | 00:00 | Millgate | 133 | 04:00 | 122 | 09:00
| Barishal | 139 | 08:00 | 129 | 00:00 | Mirpur | 133 | 19:30 | 117 | 09:00
| Barishal-230 | 139 | 12:00 | 132 | 00:00 | Mithapukur | 135 | 09:00 | 125 | 04:00
| Baroaulia | 136 | 01:00 | 134 | 10:00 | Modern | 138 | 19:00 | 134 | 10:00
| Baroirhat | 136 | 19:30 | 126 | 04:00 | Mogbazar | 137 | 20:00 | 125 | 11:00
| Bashundhara | 133 | 06:00 | 121 | 09:00 | Mongla | 131 | 13:00 | 122 | 00:00
| BashundharaCement | 131 | 19:00 | 122 | 09:00 | Motijheel | 134 | 21:00 | 121 | 10:00
| Beanibazar | 132 | 19:30 | 125 | 02:00 | Munshiganj | 132 | 06:00 | 124 | 11:00
| Benapole | 136 | 15:00 | 127 | 00:00 | Mymensingh | 133 | 15:00 | 116 | 04:00
| Bhaluka | 133 | 15:00 | 115 | 05:00 | Naogaon | 133 | 19:30 | 121 | 08:00
| Bhandaria | 140 | 12:00 | 127 | 00:00 | Narail | 137 | 13:00 | 129 | 00:00
| Bhangura | 138 | 20:00 | 134 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 19:30 | 135 | 18:30 | Narshingdi | 137 | 19:30 | 120 | 00:00
| Bheramara(GK) | 139 | 06:00 | 134 | 22:00 | Natore | 135 | 19:30 | 128 | 03:00
| Bhulta | 125 | 19:30 | 114 | 09:00 | Nawabganj | 136 | 07:00 | 122 | 09:00
| Bog-Sherpur | 137 | 16:00 | 129 | 04:00 | Netrakona | 133 | 15:00 | 115 | 04:00
| Bogura | 138 | 16:00 | 130 | 03:00 | New | 138 | 00:00 | 121 | 09:00
| Bogura-230 | 139 | 19:30 | 131 | 04:00 | Niamatpur | 129 | 15:00 | 117 | 07:00
| Brahmanbaria | 132 | 13:00 | 128 | 11:00 | Noapara | 136 | 19:30 | 128 | 00:00
| Cantonment | 135 | 19:30 | 122 | 09:00 | Pabna | 136 | 19:30 | 132 | 00:00
| Chandpur | 136 | 17:00 | 128 | 03:00 | Palashbari | 134 | 16:00 | 125 | 04:00
| Chandraghona | 138 | 19:00 | 134 | 09:00 | Panchagarh | 137 | 17:00 | 125 | 03:00
| Chapai | 131 | 15:00 | 126 | 00:00 | Patuakhali | 135 | 20:00 | 129 | 00:00
| Charsaidpur | 132 | 19:30 | 123 | 09:00 | Payra | 137 | 19:30 | 133 | 00:00
| Chauddagram | 135 | 19:30 | 127 | 03:00 | PHP | 137 | 19:30 | 125 | 04:00
| Chhatak | 133 | 20:00 | 124 | 00:00 | Purbachal | 134 | 19:30 | 121 | 10:00
| Chowmuhani | 136 | 19:00 | 124 | 02:00 | Purbasadipur | 136 | 15:00 | 125 | 03:00
| Chuadanga | 139 | 09:00 | 124 | 22:00 | Rahim | 131 | 06:00 | 124 | 11:00
| Coxsbazar | 128 | 12:00 | 112 | 01:00 | Rajbari | 136 | 19:30 | 129 | 00:00
| Cumilla(N) | 136 | 19:30 | 128 | 09:00 | Rajendrapur | 135 | 02:00 | 128 | 17:00
| Cumilla(S) | 136 | 19:30 | 124 | 15:00 | Rajshahi | 132 | 13:00 | 127 | 02:00
| Daudkandi | 132 | 19:30 | 123 | 09:00 | Rajshahi-230 | 132 | 13:00 | 127 | 00:00
| Dhaka | 137 | 19:30 | 124 | 09:00 | Ramganj | 134 | 18:30 | 122 | 05:00
| Dhamrai | 132 | 19:30 | 121 | 10:00 | Rampur | 136 | 21:00 | 132 | 23:00
| Dhanmondi | 132 | 03:00 | 124 | 11:00 | Rampura | 137 | 19:30 | 125 | 11:00
| Dohazari | 136 | 19:00 | 130 | 00:00 | Rangamati | 137 | 15:00 | 134 | 00:00
| Faridpur | 135 | 16:00 | 128 | 00:00 | Rangpur | 134 | 16:00 | 124 | 07:00
| Fatullah | 133 | 06:00 | 124 | 11:00 | Ruppur | 137 | 16:00 | 133 | 00:00
| Fenchuganj | 137 | 19:30 | 131 | 01:00 | Saidpur | 136 | 15:00 | 132 | 06:00
| Feni | 137 | 19:30 | 125 | 04:00 | Satkhira | 132 | 20:00 | 123 | 00:00
| Ghorashal | 137 | 00:00 | 122 | 11:00 | Satmasjid | 136 | 19:30 | 125 | 09:00
| Goalpara | 136 | 20:00 | 126 | 05:00 | Savar | 134 | 19:30 | 116 | 09:00
| Gollamari | 135 | 20:00 | 127 | 04:00 | Shahjadpur | 142 | 19:30 | 139 | 00:00
| Gopalganj | 139 | 19:30 | 132 | 00:00 | Shahjibazar | 134 | 15:00 | 130 | 05:00
| Gopalganj_I | 140 | 19:30 | 138 | 19:00 | Shahmirpur | 138 | 19:30 | 132 | 09:00
| Gulshan | 137 | 20:00 | 124 | 11:00 | Shariatpur | 137 | 18:30 | 128 | 00:00
| Halishahar | 138 | 19:30 | 132 | 09:00 | Sherpur | 138 | 08:00 | 122 | 04:00
| Haripur | 132 | 21:00 | 124 | 11:00 | Shikalbaha | 139 | 18:30 | 132 | 18:00
| HaripurSBU | 137 | 07:00 | 125 | 10:00 | Shikalbaha-230 | 138 | 19:30 | 134 | 02:00
| Hasnabad | 140 | 21:00 | 125 | 09:00 | Shitalakhya | 137 | 20:00 | 122 | 09:00
| Hathazari | 140 | 19:30 | 133 | 07:00 | Sholosohor | N/A | N/A | N/A | N/A
| Ishurdi | 138 | 19:30 | 133 | 00:00 | Shyampur | 133 | 20:00 | 126 | 09:00
| Jaldhaka | 133 | 12:00 | 122 | 03:00 | Shyampur-230 | 133 | 06:00 | 124 | 11:00
| Jamalpur | 140 | 18:30 | 124 | 04:00 | Siddhirganj | 131 | 19:30 | 124 | 11:00
| Jashore | 136 | 15:00 | 127 | 00:00 | Sirajganj | 136 | 16:00 | 131 | 02:00
| Jhenaidah | 142 | 15:00 | 133 | 00:00 | Sonargaon | 130 | 00:00 | 124 | 10:00
| Jhenaidah-230 | 141 | 15:00 | 132 | 00:00 | Sreemongol | 136 | 21:00 | 130 | 09:00
| Joydebpur | 145 | 19:30 | 135 | 11:00 | Srinagar | 136 | 19:00 | 123 | 09:00
| Joypurhat | 135 | 19:30 | 121 | 07:00 | SSM | 137 | 00:00 | 135 | 15:00
| Juldah | 138 | 19:30 | 133 | 03:00 | Sunamganj | 134 | 20:00 | 122 | 00:00
| Kabirpur | 137 | 19:30 | 120 | 09:00 | Sylhet | 134 | 19:30 | 126 | 09:00
| Kachua | 136 | 19:30 | 126 | 09:00 | Tangail | 136 | 19:30 | 129 | 04:00
| Kaliakoir | 138 | 01:00 | 132 | 09:00 | Thakurgaon | 136 | 08:00 | 120 | 23:00
| Kallyanpur | 133 | 19:30 | 121 | 09:00 | TK | 139 | 19:30 | 133 | 09:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 752 | 7237 | 4539 | 11776 |  |  |  | QF-LDC-11
0:30 | 710 | 7363 | 4583.5 | 11946.5 | Date: | 2022-07-23
1:00 | 668 | 7489 | 4628 | 12117
1:30 | 683 | 7382.5 | 4665 | 12047.5
2:00 | 698 | 7276 | 4702 | 11978
2:30 | 668 | 7289 | 4697 | 11986 | [5 empty] | Gen. at Eve. Peak | 12131 | 12131 MW (21:00 )
3:00 | 638 | 7302 | 4692 | 11994 | [6 empty] | 21:00
3:30 | 620 | 7324.5 | 4610 | 11934.5 | [5 empty] | Gen. at Day Peak | 10740 | 10740 MW (11:00 )
4:00 | 602 | 7347 | 4528 | 11875 | [6 empty] | 11:00
4:30 | 589 | 7354.5 | 4475.5 | 11830 | [5 empty] | Highest Generation | 12134
5:00 | 576 | 7362 | 4423 | 11785 | [6 empty] | 22:00
5:30 | 592 | 7234 | 4349.5 | 11583.5
6:00 | 608 | 7106 | 4276 | 11382
6:30 | 578 | 7054.5 | 4248 | 11302.5
7:00 | 548 | 7003 | 4220 | 11223
7:30 | 652 | 6963 | 4153.5 | 11116.5
8:00 | 756 | 6923 | 4087 | 11010
8:30 | 889 | 6780 | 4056 | 10836
9:00 | 1022 | 6637 | 4025 | 10662
9:30 | 1037 | 6663 | 4018.5 | 10681.5
10:00 | 1052 | 6689 | 4012 | 10701
10:30 | 1051 | 6694 | 4026.5 | 10720.5
11:00 | 1050 | 6699 | 4041 | 10740
11:30 | 1031 | 6665 | 3984 | 10649
12:00 | 1012 | 6631 | 3927 | 10558
12:30 | 1013 | 6602 | 3925.5 | 10527.5
13:00 | 1014 | 6573 | 3924 | 10497
13:30 | 996 | 6568.5 | 3950.5 | 10519
14:00 | 978 | 6564 | 3977 | 10541
14:30 | 980 | 6639 | 3971 | 10610
15:00 | 982 | 6714 | 3965 | 10679
15:30 | 1006 | 6692 | 3975.5 | 10667.5
16:00 | 1030 | 6670 | 3986 | 10656
16:30 | 952 | 6771.5 | 4007 | 10778.5
17:00 | 874 | 6873 | 4028 | 10901
17:30 | 847 | 7035 | 4036 | 11071
18:00 | 820 | 7197 | 4044 | 11241
18:30 | 680 | 7314.5 | 4184.5 | 11499
19:00 | 540 | 7432 | 4325 | 11757
19:30 | 466 | 7475 | 4348 | 11823
20:00 | 520 | 7536 | 4388 | 11924 |  |  |  | Executive Engineer
20:30 | 475 | 7592.5 | 4435 | 12027.5 |  |  |  | Network Operation Division
21:00 | 430 | 7649 | 4482 | 12131
21:30 | 447 | 7625.5 | 4507 | 12132.5
22:00 | 464 | 7602 | 4532 | 12134 |  |  |  |  | Page 6 of 7
22:30 | 543 | 7586 | 4548 | 12134
23:00 | 622 | 7570 | 4564 | 12134
23:30 | 687 | 7403.5 | 4551.5 | 11955
24:00 | 752 | 7237 | 4539 | 11776
12131 MW (21:00 )
10740 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-23 |  | Energy |  | 274769680
[13 empty] | 2022-07-23 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3778 | 853 | 1955 | 0 | 2849 | 1249 | 125 | 204 | 809 | 158 | 0 | 1878
0:30 | 3921.5 | 854.5 | 1906 | 0 | 2940 | 1259.5 | 126 | 208 | 779 | 160 | 0 | 1038.5 | Date: | 2022-07-23
1:00 | 4065 | 856 | 1857 | 0 | 3031 | 1270 | 127 | 212 | 749 | 162 | 0 | 199
1:30 | 4011.5 | 878.5 | 1855 | 0 | 2993.5 | 1270 | 127 | 213 | 750 | 162 | 0 | 169.5 | [7 empty] | Total Energy | 274.7697 | Total Energy Gen 274.770 MKWHr Energy Not Served 22.059 MKWHr Energy Requirement 296.829 MKWHr
2:00 | 3958 | 901 | 1853 | 0 | 2956 | 1270 | 127 | 214 | 751 | 162 | 0 | 140 | [7 empty] | Energy not Served | 22.0591
2:30 | 4012 | 901 | 1858.5 | 0 | 2925.5 | 1254.5 | 127 | 213.5 | 746.5 | 161 | 0 | 70 | [7 empty] | Energy Requirement | 296.8288
3:00 | 4066 | 901 | 1864 | 0 | 2895 | 1239 | 127 | 213 | 742 | 160 | 0 | 0
3:30 | 4098.5 | 901 | 1858.5 | 0 | 2853.5 | 1219 | 127 | 191.5 | 718 | 159 | 0 | 0 | [5 empty] | Shortage
4:00 | 4131 | 901 | 1853 | 0 | 2812 | 1199 | 127 | 170 | 694 | 158 | 0 | 0
4:30 | 4142 | 901.5 | 1855.5 | 0 | 2803 | 1199 | 127 | 150 | 647 | 155 | 0 | 0
5:00 | 4153 | 902 | 1858 | 0 | 2794 | 1199 | 127 | 130 | 600 | 152 | 0 | 0
5:30 | 4122.5 | 901 | 1845.5 | 0 | 2750.5 | 1174 | 127.5 | 130 | 509.5 | 150 | 3 | 0
6:00 | 4092 | 900 | 1833 | 0 | 2707 | 1149 | 128 | 130 | 419 | 148 | 6 | 0
6:30 | 4074.5 | 901 | 1830.5 | 0 | 2660 | 1134 | 128 | 130 | 415 | 144 | 15.5 | 0 |  |  |  | Coal
7:00 | 4057 | 902 | 1828 | 0 | 2613 | 1119 | 128 | 130 | 411 | 140 | 25 | 0
7:30 | 4005.5 | 901 | 1783.5 | 0 | 2615 | 1094.5 | 127.5 | 130 | 411 | 138 | 40.5 | 158 |  |  | Oil |  |  |  | ,
8:00 | 3954 | 900 | 1739 | 0 | 2617 | 1070 | 127 | 130 | 411 | 136 | 56 | 316
8:30 | 3744.5 | 901.5 | 1725 | 0 | 2631.5 | 1070 | 126.5 | 130 | 419 | 137 | 81 | 569
9:00 | 3535 | 903 | 1711 | 0 | 2646 | 1070 | 126 | 130 | 427 | 138 | 106 | 822
9:30 | 3531 | 885 | 1747 | 0 | 2603.5 | 1070 | 125.5 | 152 | 447 | 142 | 130.5 | 897
10:00 | 3527 | 867 | 1783 | 0 | 2561 | 1070 | 125 | 174 | 467 | 146 | 155 | 972
10:30 | 3501 | 867 | 1784.5 | 0 | 2550.5 | 1070 | 125 | 192 | 488.5 | 149 | 185 | 1023.5
11:00 | 3475 | 867 | 1786 | 0 | 2540 | 1070 | 125 | 210 | 510 | 152 | 215 | 1075
11:30 | 3450.5 | 867 | 1776 | 0 | 2524 | 1065 | 125 | 207 | 515.5 | 152 | 174 | 1228
12:00 | 3426 | 867 | 1766 | 0 | 2508 | 1060 | 125 | 204 | 521 | 152 | 133 | 1381
12:30 | 3407.5 | 867 | 1770.5 | 0 | 2458 | 1075 | 124 | 203.5 | 550.5 | 157 | 118 | 1339.5
13:00 | 3389 | 867 | 1775 | 0 | 2408 | 1090 | 123 | 203 | 580 | 162 | 103 | 1298
13:30 | 3389 | 867 | 1775 | 0 | 2408 | 1090 | 123 | 203 | 580 | 162 | 103 | 1298
14:00 | 3389 | 867 | 1775 | 0 | 2408 | 1090 | 123 | 203 | 580 | 162 | 103 | 1298
14:30 | 3417 | 867 | 1767.5 | 0 | 2458 | 1095 | 124 | 202.5 | 590.5 | 167 | 102 | 1302.5
15:00 | 3445 | 867 | 1760 | 0 | 2508 | 1100 | 125 | 202 | 601 | 172 | 101 | 1307
15:30 | 3416.5 | 867 | 1744 | 0 | 2561.5 | 1099.5 | 125 | 193 | 612.5 | 166 | 75.5 | 1252.5
16:00 | 3388 | 867 | 1728 | 0 | 2615 | 1099 | 125 | 184 | 624 | 160 | 50 | 1198
16:30 | 3438 | 867 | 1733.5 | 0 | 2727.5 | 1099.5 | 125 | 175 | 616 | 152 | 45 | 1050.5
17:00 | 3438 | 867 | 1739 | 0 | 2840 | 1100 | 125 | 166 | 608 | 144 | 40 | 903
17:30 | 3491.5 | 867 | 1745 | 0 | 2947 | 1100 | 125 | 162.5 | 623.5 | 147 | 25 | 827.5
18:00 | 3545 | 867 | 1751 | 0 | 3054 | 1100 | 125 | 159 | 639 | 150 | 10 | 752
18:30 | 3579.5 | 860 | 1721.5 | 0 | 3195.5 | 1120 | 126 | 185.5 | 726.5 | 165 | 5 | 1069.5
19:00 | 3614 | 853 | 1692 | 0 | 3337 | 1140 | 127 | 212 | 814 | 180 | 0 | 1387
19:30 | 3654 | 852 | 1651 | 0 | 3375 | 1150 | 127 | 214 | 844 | 170 | 0 | 1789
20:00 | 3680 | 852 | 1692 | 0 | 3411 | 1149 | 127 | 216 | 851 | 162 | 0 | 1882
20:30 | 3706 | 852.5 | 1737 | 0 | 3420.5 | 1179 | 127 | 216.5 | 838.5 | 167 | 0 | 1832.5
21:00 | 3732 | 853 | 1782 | 0 | 3430 | 1209 | 127 | 217 | 826 | 172 | 0 | 1783
21:30 | 3709 | 853 | 1792 | 0 | 3431 | 1224 | 127 | 217 | 824.5 | 172 | 0 | 1750.5
22:00 | 3686 | 853 | 1802 | 0 | 3432 | 1239 | 127 | 217 | 823 | 172 | 0 | 1718
22:30 | 3715 | 852.5 | 1849.5 | 0 | 3351.5 | 1244 | 126 | 214.5 | 820.5 | 175 | 0 | 1685.5
23:00 | 3744 | 852 | 1897 | 0 | 3271 | 1249 | 125 | 212 | 818 | 178 | 0 | 1653
23:30 | 3761 | 852.5 | 1926 | 0 | 3060 | 1249 | 125 | 208 | 813.5 | 168 | 0 | 1765.5 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 3778 | 853 | 1955 | 0 | 2849 | 1249 | 125 | 204 | 809 | 158 | 0 | 1878
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 274.770 MKWHr Energy Not Served 22.059 MKWHr Energy Requirement 296.829 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-07-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 92 | 92 | 93 | 93 | 92 | 91 | 90 | 90 | 90 | 88 | 90 | 90 | 90 | 90 | 90 |  | 92 | 92 | 92 | 92 | 92 | 90 | 90 | 2220022
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 23 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 22 | 24 | 25 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 534600
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 1 | 3 | 2 | 6 | 4 | 2 | 1 | 2 | 4 | 2 | 1 | 0 | [8 empty] | 30240
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 269152
12 | Hathazari 100 MW peaking PP | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 42 | 42 | 35 | 42 | 42 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1135968
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 81 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 87 | 105 | 2473963
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 47 | 47 | 47 | 47 | 47 | [6 empty] | 17 | 50 | 49 | 48 | 47 | 47 | 47 |  | 47 | 47 | 47 | 48 | 49 | 49 | 49 | 807712
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 280 | 280 | 280 | 293 | 288 | 273 | 260 | 260 | 258 | 253 | 245 | 245 | 243 | 245 | 281 | 273 | 258 | 263 |  | 276 | 276 | 276 | 292 | 291 | 291 | 291 | 6506070
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 250909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 0 |  |  |  | 20 | 20 | 80 | 75 | 75 | 65 |  | 120 | 150 | 180 | 180 | 180 | 180 | 180 | 3787291
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 40 | 39 | 39 | 36 | 37 | 36 | 36 | 40 |  | 42 | 47 | 42 | 42 | 42 | 38 | 39 | 950832
33 | Ashuganj 225 MW CCPP | 196 | 189 | 187 | 202 | 199 | 211 | 209 | 180 | 202 | 196 | 184 | 164 | 170 | 166 | 172 | 167 | 162 | 145 |  | 153 | 159 | 161 | 177 | 193 | 200 | 204 | 4435000
34 | Ashuganj 450 MW CCPP(South) | 320 | 340 | 300 | 305 | 300 | 265 | 265 | 265 | 300 | 330 | 330 | 325 | 330 | 330 | 335 | 335 | 340 | 340 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7720000
| Ashuganj 450 MW CCPP(North) | 295 | 330 | 310 | 320 | 310 | 285 | 280 | 280 | 340 | 330 | 345 | 340 | 315 | 300 | 310 | 315 | 325 | 355 |  | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 7847500
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 55 | 54 | 54 | 53 | 51 | 51 | 51 | 51 | 51 |  | 56 | 55 | 56 | 55 | 55 | 55 | 55 | 1300320
36 | Chandpur 150 MW CCPP | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 91 | 99 | 90 | 90 | 2139060
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 406 | 410 | 409 | 411 | 410 | 415 | 415 | 414 | 409 | 403 | 402 | 396 | 395 | 397 | 397 | 407 | 408 | 406 |  | 406 | 408 | 405 | 409 | 409 | 407 | 406 | 9893890
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5001450
41 | Haripur 360MW CCPP(HPL) | 333 | 333 | 336 | 337 | 338 | 339 | 339 | 341 | 342 | 336 | 332 | 332 | 332 | 332 | 334 | 335 | 334 | 334 |  | 334 | 334 | 334 | 327 | 322 | 345 | 345 | 8026000
42 | RPCL 210MW CCPP | 106 | 105 | 105 | 105 | 105 | 106 | 106 | 108 | 105 | 103 | 102 | 94 | 80 | 80 | 80 | 81 | 82 | 83 |  | 103 | 107 | 107 | 107 | 105 | 106 | 106 | 2314560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 2 | 6 | 23 | 56 | 55 | 46 | 53 | 52 | 37 | 10 | 7 | 1 | [8 empty] | 310730
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1013000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 953088
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 55 | 55 | 55 | 56 | 56 | 58 | 63 | 58 | 54 | 53 | 56 | 58 | 60 | 61 | 61 | 60 | 60 |  | 60 | 65 | 61 | 63 | 61 | 62 | 62 | 1415
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 45 | 60 | 81 | 81 | 81 | 81 | 623040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 221 | 221 | 220 | 220 | 220 | [8 empty] | 15 | 50 |  | 90 | 90 | 100 | 120 | 120 | 120 | 120 | 2560290
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 15 | 26 | 26 | 26 | 26 | 26 | 28 | 28 |  | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 309200
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238140
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 44 | 50 | 50 | 50 | 50 | 44 | 50 | 50 | 50 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 569400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 182352
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 315 | 325 | 315 | 320 | 300 | 305 | 290 | 310 | 315 | 320 | 320 | 320 | 320 | 320 | 280 | 280 | 300 |  | 300 | 250 | 270 | 295 | 300 | 330 | 325 | 7522500
| Bibiyana South 400 MW | 398 | 393 | 397 | 394 | 396 | 360 | 370 | 370 | 385 | 387 | 370 | 380 | 385 | 380 | 384 | 360 | 360 | 385 |  | 397 | 389 | 400 | 400 | 360 | 398 | 396 | 9112800
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 11 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 282904
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 21 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 22 |  | 23 | 23 | 22 | 18 | 23 | 23 | 23 | 525840
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 448608
61 | Narshingdi 22 MW PP (Doreen) | 22 |  |  |  | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 355572
62 | Tangail 22 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 7 | 6 | 361368
63 | Impoprt (Tripura) | 162 | 162 | 160 | 158 | 152 | 148 | 140 | 136 | 138 | 146 | 152 | 152 | 162 | 168 | 172 | 160 | 144 | 150 |  | 180 | 170 | 162 | 172 | 172 | 178 | 158 | 3766080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 12 | 8 | 8 | 4 | 3 | 7 | 8 | 3 | 3 | 12 | 5 |  | 18 | 21 | 17 | 29 | 28 | 36 | 38 | 597600
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 468936
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 226080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 14 | 16 | 30 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 762000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 513010
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 23 | 23 | 21 | 21 | 21 | 21 | 21 | 24 | 24 |  | 24 | 24 | 27 | 27 | 27 | 19 | 19 | 568980
71 | Maona 33 MW PP(Summit) | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 602200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 786900
73 | Ghorashal 108MW PP (Regent) | 89 | 89 | 89 | 89 | 89 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 89 | 90 | 84 | 82 | 89 | 89 |  | 89 | 89 | 90 | 83 | 90 | 90 | 90 | 2064772
| Feni Lanka Power | 114 | 114 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 114 |  | 114 | 114 | 114 | 114 | 110 | 98 | 98 | 1255140
| Chowmuhani 113 MW | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 | 94 | 114 |  | 116 | 116 | 115 | 115 | 115 | 115 | 18 | 1006320
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 38 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 69 | 122 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 76 | 1844640
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196589
78 | Gazipur 52 MW PP | 49 | 50 | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 42 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1109280
79 | Kodda 150MW PP | 140 | 140 | 140 | 142 | 142 | 126 | 126 | 126 | 142 | 145 | 145 | 145 | 142 | 142 | 142 | 142 | 142 | 145 |  | 145 | 147 | 150 | 150 | 147 | 147 | 147 | 3366720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 19 | 42 | 43 | 43 | 13 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 25 | 25 | 472997
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 88 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 2294400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 3 | 1 | 5 | 3 | 1 | 0 | 0 | 0 | [9 empty] | 18121
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 907149
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 87 | 72 | 75 | 90 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2193772
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 8 | 7 | 7 | 7 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 7 | 9 | 8 |  | 7 | 8 | 8 | 8 | 7 | 8 | 7 | 196800
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 429120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258600
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 45 | 45 | 47 | 43 | 46 | 45 | 43 | 43 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 486216
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1207954
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 300672
95 | Patenga 50MW PP (Baraka) | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 32 | 32 | 30 | 25 | 26 | 0 | 12 | 26 |  | 1 | 21 |  | 37 | 24 | 37 | 25 | 25 | 25 | 25 | 665760
96 | Chattogram 108 MW PP (ECPV) | 89 | 89 | 89 | 89 | 89 | 89 | 49 | 54 | 79 | 75 | 78 | 89 | 10 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 1104960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 50 | 40 | 40 | 40 | 30 |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 1229657
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 |  | 297069
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 10550
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 350640
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 185 | 200 | 200 | 200 | 200 | 210 | 200 | 200 | 210 | 210 | 209 | 209 | 209 | 206 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4826400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 143 | 137 | 132 | 143 | 143 | 143 | 143 | 141 | 145 | 144 | 140 | 135 | 133 | 138 | 142 | 143 | 143 | 143 |  | 128 | 142 | 135 | 143 | 143 | 145 | 145 | 3406608
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 345600
116 | Chandpur 200MW (Desh energy) | 154 | 115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 97 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2435040
117 | Ashuganj 150MW PP (Midland) | 118 | 117 | 128 | 128 | 130 | 130 | 128 | 130 | 128 | 123 | 118 | 117 | 117 | 115 | 115 | 108 | 100 | 107 |  | 118 | 110 | 108 | 118 | 122 | 120 | 128 | 2883781
118 | Bibiyana-III 400 MW CCPP | 400 | 228 | 372 | 402 | 402 | 402 | 366 | 365 | 404 | 403 | 381 | 379 | 398 | 397 | 400 | 365 | 367 | 404 |  | 404 | 399 | 400 | 399 | 365 | 402 | 402 | 9131000
| Jamalpur 115 MW PP (United) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 86 | 65 | 72 | 56 | 65 | 60 | 73 | 82 | 105 | 105 |  | 106 | 106 | 106 | 106 | 105 | 105 | 38 | 2176800
| Anwara 300 MW PP (United) | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 176 | 177 | 177 | 176 | 176 | 177 | 177 | 178 | 178 | 178 | 178 |  | 275 | 280 | 285 | 285 | 285 | 212 | 212 | 4792364
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253440
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 90 | 90 | 90 | 90 | 90 | 90 | 105 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2487764
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885240
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 4 | 11 | 18 | 33 | 28 | 26 | 21 | 11 | 7 | 4 | 2 | [8 empty] | 193128
| Chandpur 115(Doreen) | 57 | 53 | 54 | 53 | 53 | 53 | 53 | 54 | 53 | 53 | 48 | 36 | 51 | 52 | 52 | 52 | 71 | 94 |  | 92 | 93 | 94 | 93 | 93 | 67 | 55 | 1497600
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1337040
120 | Eastern Zone Total | 7489 | 7276 | 7302 | 7347 | 7362 | 7106 | 7003 | 6923 | 6637 | 6689 | 6699 | 6631 | 6573 | 6564 | 6714 | 6670 | 6873 | 7197 |  | 7432 | 7475 | 7536 | 7649 | 7602 | 7570 | 7237 | 169313275
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 42 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 32 | 32 | 32 | 32 |  | 64 | 64 | 80 | 80 | 80 | 65 | 65 | 1256640
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 36 | 36 | 36 | 36 | [13 empty] | 5 |  | 38 | 42 | 50 | 42 | 41 | 41 | 41 | 360960
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 416160
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 15 | 36 | 61 | 65 | 110 | 39 | 7 | 13 | 37 | 23 | 26 | 7 | [8 empty] | 409680
131
132 | United Payra Power Ltd. | [19 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 92400
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 223 | 223 | 223 | 223 | 224 | 224 | 176 | 177 | 191 | 210 | 204 | 204 | 220 | 220 | 220 | 220 | 223 |  | 220 | 180 | 172 | 220 | 222 | 223 | 224 | 5176255
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 542784
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 81 | 81 | 82 | 82 | 82 | 81 | 81 | 81 | 81 | 81 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1986199
140 | Bhola 33 MW PP (Venture) | 36 | 36 | 35 | 33 | 32 | 27 | 21 | 21 | 16 | 19 | 17 | 21 | 24 | 26 | 25 | 28 | 25 | 18 |  | 29 | 29 | 25 | 28 | 32 | 31 | 32 | 642403
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 32 | 32 | 32 | 32 | 32 | 8 | 314625
143 | Gopalganj 100 MW Peaking PP | 57 | 57 | 57 | 50 | 40 | [12 empty] | 30 |  | 60 | 80 | 75 | 56 | 56 | 56 | 56 | 604800
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 89 | 89 | 88 | 88 | 88 | 88 | 88 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2420784
146 | Bheramara HVDC | 856 | 901 | 901 | 901 | 902 | 900 | 902 | 900 | 903 | 867 | 867 | 867 | 867 | 867 | 867 | 867 | 867 | 867 |  | 853 | 852 | 852 | 853 | 853 | 852 | 853 | 21168000
147 | Bheramara 410 MW CCPP | 210 | 230 | 240 | 245 | 250 | 250 | 245 | 215 | 195 | 185 | 175 | 170 | 165 | 165 | 155 | 155 | 155 | 155 |  | 160 | 160 | 160 | 165 | 170 | 180 | 195 | 4754592
148 | Payra 1320 MW | 1070 | 1070 | 1040 | 1000 | 1000 | 950 | 920 | 870 | 870 | 870 | 870 | 860 | 890 | 900 | 900 | 900 | 900 | 900 |  | 940 | 950 | 950 | 1010 | 1040 | 1050 | 1050 | 24827100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 |  | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 4857300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 664171
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 1 | 3 | 3 | 4 | 4 | 4 | 2 | 0 | 0 | [8 empty] | 26400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 164 | 170 | 179 | 185 | 193 | 198 | 193 | 175 | 162 | 155 | 153 | 148 | 135 | 135 | 135 | 134 | 134 | 134 |  | 134 | 135 | 135 | 137 | 139 | 139 | 152 | 3937691
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 212 | 214 | 213 | 170 | 130 | 130 | 130 | 130 | 130 | 174 | 210 | 204 | 203 | 204 | 202 | 184 | 166 | 159 |  | 212 | 214 | 216 | 217 | 217 | 212 | 204 | 4704891
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 151 | 158 | 163 | 168 | 160 | 173 | 169 | 160 | 150 | 144 | 141 | 138 | 136 | 135 | 122 | 119 | 119 | 119 |  | 119 | 119 | 120 | 122 | 123 | 122 | 127 | 3629082
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 375 | 355 | 315 | 304 | 302 | 300 | 287 | 287 | 285 | 287 |  | 286 | 298 | 318 | 314 | 321 | 355 | 414 | 8423018
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 26 | 26 | 26 | 26 | 26 | 0 | [6 empty] | 5 | 16 | 18 | 25 | 22 | 22 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 355514
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 17 | 17 | 17 | 16 | 17 | 18 | 19 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 448560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210150
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 712016
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 24 | 24 | 24 | 0 | [6 empty] | 16 | 28 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 441800
168 | Santahar 50 MW Peaking PP | 28 | 28 | 28 | 28 | 28 | 0 | [9 empty] | 35 | 34 | 34 |  | 34 | 36 | 35 | 35 | 35 | 35 | 35 | 459450
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 43 | 52 | 52 | 52 | 52 | 8 | 393120
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 84 | 84 | 84 | 84 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2072432
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 112 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2134080
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2129088
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 105 | 98 | 105 | 106 | 100 | 106 | 85 | 85 | 85 | 85 | 84 | 83 | 83 | 82 | 82 | 76 | 90 | 98 |  | 96 | 94 | 97 | 99 | 99 | 99 | 99 | 2221747
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 4 | 4 | 5 | 8 | 8 | 7 | 7 | 6 | 5 | 2 | 0 | [8 empty] | 60337
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2602176
178