## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-28 | Thursday
|  |  | Date (day): | 2022-07-28 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10911.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12876 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-27 | 2022-07-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 160 | 300 | 300 | 300 |  | 65 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 82 | 86 | 88 |  | 20 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 404 | 400 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 316 | 326 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 72 | 8 | 90 |  | 10 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 90 | 8 | 90 | 10 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 94 | 7 | 94 |  | 8 | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 100 | 150 |  | -1 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 22 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 52 | 51 | 50 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 238 | 240 | 245 | 245
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 106 | 119 | 110 | 120 |  | 29 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 104 | 17 | 104 | 1 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 17 | 162 | -58 |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2287 | 3077 | 2445 | 3103 | 1688 | 949
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 20 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 37 | 30 | 31 |  | 19 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 127 | 129 | 127 | 127 |  | 103 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 71 | 88 | 105 | 105 |  | 0 | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 51 | 52 | 51 | 52 |  | 46 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 36 | 0 | 36 | 66 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 44 | 10 | 44 | 56 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 11 | 90 | 11 | 90 | 10 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 17 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 30 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 93 | 90 | 90 | 18 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 172 | 300 | 175 | 285 |  | 15 | Engine problem
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 36 | 54 |  | 0 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110 |  | 0 | Engine problem
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 10 | 100 | 0 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 884 | 1314 | 960 | 1400 | 410 | 566
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 170 | 200 | 180 | 211 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 320 | 300 | 330 | 30 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 20 | 20 | 20 |  | 25 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 117 | 117 | 130 |  | 20 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 49 | 46 | 48 | 48
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 130 | 135 | 130 | 130 |  | 33 | Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 158 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 107 | 104 | 107 | 113 |  |  | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 76 | 36 | 95 | 20 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1698 | 2013 | 1688 | 2082 | 690 | 102
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 85 | 103 | 90 | 104 | 98 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 200 | 192 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 38 | 96 | 40 | 92 |  | 23 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 34 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 402 | 435 | 423.6 | 438 | 98 | 31
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 43 |  | 47 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 110 | 110 | 53 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 47 | 20 | 31 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 49 | 45 | 43 | 43 | 7 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 0 | 0 | 11 |  | Gas shortage
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 5 |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 26 | 32 | 25 | 32 | 18 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 24 | 8 | 24 | 1 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 315 | 300 | 330 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1316 | 1359 | 1389 | 1416 | 146 | 887
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 900 | 849 | 876 | 912
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 33 | 63 | 33 | 83 | 32 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 46 | 0 | 40 |  | 14 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 0 | 66 |  | 43 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 160 | 200 | 160 | 250 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 24 | 8 | 24
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1321 | 1305 | 1339 | 1407 | 716 | 57
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 28 | 15 | 25 |  | 15 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 21 | 82 | 65 | 85 | 109 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 910 | 1020 | 910 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1189 | 1382 | 1231 | 1479 | 109 | 15
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 32 | 34 | 34 |  | 18 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 25 |  | 46 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 0 | 25 | 25 |  | 25 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 24 | 24 | 24 |  | 26 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 163 | 142 | 150 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 210 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 139 | 129 | 150 | 140 | 80 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 290 | 330 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 35 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 89 | 91 | 88 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 70 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1189 | 1292 | 1028 | 1138 | 839 | 146
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 81 | 106 | 92 | 105 |  | 8 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 72 | 90 | 108 | 108 |  | 7 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 352 | 395 | 408 | 413 | 199 | 100
|  | Total |  |  |  |  | 22482 | 21680 | 10638 | 12572 | 10911.6 | 12876 | 4895 | 2853
| A. |  | 2022-07-27 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12736 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10386 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13500 | MW
| 3 | Day peak Generation : |  |  | 10638 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13327.68 | MW
| 4 | Evening peak Generation : |  |  | 12572 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1132 | MW
| 5 | Total Energy Generation : |  | 271.3653 | MKWHr | By Solar | 1.4846 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 126.5795 | MKWHr |  | By Oil: | 85.7408 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 29.8341 | MKWHr |  | By Hydro: | 3.0582 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4895 | MW | Dhaka | 4805 | 4660 |  | 145
|  |  |  | For Plants S/D or M/C prob = |  |  | 2853 | MW | Chittagong | 1344.4 | 1283.4 |  | 61 |  | 18:00 |  | 114
|  |  |  | Total = |  |  | 7748 | MW | Khulna | 1654.6 | 1434.6 |  | 220
| 7 | Total Gas Supplied : |  |  | 963.54 | MMCFD |  |  | Rajshahi | 1453.8 | 1243.8 |  | 210 |  | 19:00 |  | 704
| 8 | Fuel Cost : | i) Gas : | Taka | 144208400.13 | ii) Oil : | Taka | 1172645824.8 | Comilla | 1210 | 1044 |  | 166 |  | 19:30 |  | 902
|  |  | iii) Coal : |  | 250698141 | Total | Taka | 1567552365.93 | Mymensingh | 1029 | 839 |  | 190 |  | 20:00 |  | 1224
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 607 | 607 |  | 0 |  | 21:00 |  | 1132
|  | ii) During Peak Demand : |  |  | 408 | MW (E to W) at | 21:00 | hrs | Barisal | 378.88 | 378.88 |  | 0 |  | 22:00 |  | 888
|  | iii) Maximum : |  |  | 408 | MW at | 21:00 | hrs | Rangpur | 845 | 705 |  | 140 |  | 23:00 |  | 912
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.7° C |  |  | Total | 13327.68 | 12195.68 |  | 1132
| B. |  | 2022-07-28 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1036.3034 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12876 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11900 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 298.2973 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10761 | MW at | 8:00 | 287.4537 | 110.0766 | 152.1809 | 143.644 | 118.0008 | 103.2832 | 40.6049 | 0 | 81.0594
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.0807 | MKWHr. | ii) HVDC Flow at Peak Time |  | 849 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5875 | MKWHr. | iii) Maximum HVDC Flow : |  | 900 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.34 |  | (b) Today: | 91.54 |  | (c) Rule Curve: |  | 88.32
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 85 | 0 | 407 | 315 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 25 | 32 | 51 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 10 | 88 | 30 | 19 | 38 | 0 | 0 | 0 | 275 | 260 | 205 | 8 | 131 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 33 | 21 | 150 | 101 | 0 | 3 | 0 | 43 | 42 | 25 | 22 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 6 | 10 | 310 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 105 | 0 | 11 | 155 | 120 | 402 | 38 | 105 | 88 | 0 | 177 | 36 | 110 | 17 | 113 | 10 | 180 | 20 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 898 | 0 | 210 | 0 | 26 | 0 | 0 | 0 | 46 | 65 | 8 | 65 | 27 | 32 | 0 | 0 | 0 | 34 | 20 | 89 | 0 | 25 | 24 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 167 | 0 | 0 | 130 | 0 | 0 | 144 | 0 | 372 | 0 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 950 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 |  | 6929 | 4354 | 11283 | 3689 | 898 | 1822 | 0 | 2753 | 1150 | 127 | 130 | 694 | 150 | 0 | 937 | 91.24
2:00 | 0 | 0 | 0 | 180 | 200 | 85 | 0 | 406 | 285 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 51 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 44 | 0 | 10 | 89 | 31 | 19 | 38 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 129 | 41 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 10 | 33 | 21 | 148 | 101 | 0 | 3 | 0 | 43 | 42 | 25 | 25 | 0 | 0 | 40 | 81 | 0 | 220 | 0 | 6 | 10 | 280 | 8 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 92 | 0 | 11 | 120 | 123 | 402 | 38 | 105 | 88 | 0 | 177 | 36 | 110 | 17 | 113 | 10 | 145 | 17 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 899 | 0 | 220 | 0 | 50 | 0 | 0 | 0 | 46 | 62 | 8 | 65 | 27 | 32 | 0 | 0 | 0 | 34 | 20 | 89 | 0 | 25 | 24 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 130 | 0 | 0 | 151 | 0 | 351 | 0 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 950 | 180 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 6745 | 4316 | 11061 | 3676 | 899 | 1704 | 0 | 2732 | 1150 | 126 | 130 | 626 | 148 | 0 | 773 | 91.26
3:00 | 0 | 0 | 0 | 180 | 200 | 85 | 0 | 407 | 320 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 51 | 0 | 91 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 44 | 0 | 10 | 83 | 31 | 16 | 38 | 0 | 0 | 0 | 275 | 260 | 212 | 8 | 129 | 41 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 21 | 144 | 101 | 0 | 5 | 0 | 43 | 42 | 41 | 25 | 0 | 0 | 64 | 81 | 0 | 220 | 0 | 12 | 10 | 305 | 8 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 89 | 0 | 11 | 120 | 123 | 402 | 38 | 105 | 88 | 0 | 163 | 36 | 110 | 17 | 113 | 10 | 0 | 17 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 900 | 0 | 230 | 0 | 50 | 0 | 0 | 0 | 46 | 59 | 8 | 65 | 27 | 32 | 0 | 0 | 0 | 34 | 20 | 89 | 0 | 25 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 181 | 0 | 0 | 130 | 0 | 0 | 154 | 0 | 424 | 0 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 950 | 184 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 6565 | 4365 | 10930 | 3460 | 900 | 1863 | 0 | 2664 | 1149 | 126 | 130 | 624 | 144 | 0 | 617 | 91.28
4:00 | 0 | 0 | 0 | 180 | 200 | 85 | 0 | 406 | 337 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 51 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 44 | 0 | 10 | 85 | 31 | 16 | 7 | 0 | 0 | 0 | 275 | 260 | 194 | 8 | 129 | 41 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 21 | 142 | 101 | 0 | 5 | 0 | 43 | 42 | 47 | 36 | 0 | 0 | 65 | 81 | 0 | 220 | 0 | 16 | 10 | 280 | 8 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 89 | 0 | 11 | 120 | 128 | 401 | 38 | 105 | 88 | 0 | 177 | 36 | 110 | 17 | 108 | 10 | 0 | 17 | 0 | 17 | 108 | 0 | 35 | 0 | 36 | 55 | 0 |  | 898 | 0 | 240 | 0 | 50 | 0 | 0 | 0 | 46 | 57 | 8 | 65 | 25 | 32 | 0 | 0 | 0 | 34 | 19 | 89 | 0 | 25 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 426 | 0 | 0 | 70 | 105 | 105 | 0 | 0 | 76 | 930 | 185 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 6542 | 4357 | 10899 | 3456 | 898 | 1846 | 0 | 2681 | 1130 | 125 | 130 | 621 | 142 | 0 | 370 | 91.3
5:00 | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 406 | 340 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 51 | 0 | 90 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 48 | 0 | 10 | 89 | 31 | 16 | 30 | 0 | 0 | 0 | 275 | 260 | 180 | 8 | 130 | 41 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 21 | 136 | 94 | 0 | 5 | 0 | 43 | 42 | 47 | 42 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 22 | 10 | 280 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 107 | 0 | 11 | 120 | 130 | 401 | 38 | 105 | 88 | 0 | 177 | 36 | 110 | 17 | 108 | 10 | 0 | 17 | 0 | 17 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 899 | 0 | 240 | 0 | 33 | 0 | 0 | 0 | 46 | 57 | 8 | 65 | 27 | 32 | 0 | 0 | 0 | 34 | 19 | 89 | 0 | 25 | 24 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 158 | 0 | 427 | 0 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 930 | 185 | 0 | 0 | 0 | 0 | 108 | 0 | 0 |  | 6575 | 4331 | 10906 | 3443 | 899 | 1885 | 0 | 2663 | 1130 | 125 | 130 | 625 | 136 | 0 | 0 | 91.32
6:00 | 0 | 0 | 0 | 180 | 200 | 89 | 0 | 406 | 302 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 51 | 0 | 91 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 51 | 0 | 10 | 89 | 31 | 16 | 20 | 0 | 0 | 0 | 275 | 260 | 182 | 8 | 130 | 42 | 5 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 0 | 21 | 128 | 93 | 0 | 5 | 0 | 43 | 42 | 47 | 46 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 26 | 10 | 290 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 105 | 1 | 11 | 120 | 132 | 352 | 38 | 105 | 51 | 0 | 50 | 36 | 110 | 17 | 108 | 10 | 0 | 16 | 2 | 17 | 108 | 0 | 35 | 1 | 36 | 55 | 0 |  | 900 | 0 | 250 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 26 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 140 | 0 | 358 | 0 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 930 | 185 | 0 | 0 | 0 | 3 | 108 | 0 | 0 |  | 6306 | 4080 | 10386 | 3317 | 900 | 1788 | 0 | 2483 | 1130 | 126 | 130 | 507 | 128 | 7 | 0 | 91.34
7:00 | 0 | 0 | 0 | 180 | 200 | 89 | 0 | 407 | 302 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 52 | 0 | 91 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 51 | 0 | 10 | 89 | 31 | 16 | 27 | 0 | 0 | 0 | 280 | 270 | 190 | 8 | 130 | 42 | 5 | 0 | 51 | 0 | 49 | 8 | 0 | 10 | 33 | 20 | 120 | 86 | 0 | 19 | 0 | 43 | 42 | 47 | 46 | 0 | 0 | 63 | 78 | 0 | 220 | 0 | 26 | 10 | 300 | 8 | 0 | 0 | 258 | 0 | 0 | 200 | 0 | 107 | 5 | 11 | 120 | 132 | 353 | 38 | 105 | 51 | 1 | 50 | 36 | 110 | 17 | 108 | 10 | 0 | 16 | 9 | 17 | 108 | 0 | 35 | 8 | 36 | 55 | 0 |  | 899 | 0 | 240 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 24 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 890 | 185 | 0 | 0 | 1 | 21 | 108 | 0 | 0 |  | 6357 | 4038 | 10395 | 3329 | 899 | 1795 | 0 | 2484 | 1090 | 126 | 130 | 507 | 120 | 45 | 0 | 91.36
8:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 408 | 302 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 78 | 31 | 16 | 2 | 0 | 0 | 0 | 305 | 270 | 185 | 8 | 130 | 42 | 5 | 0 | 51 | 0 | 49 | 8 | 0 | 10 | 33 | 20 | 126 | 85 | 0 | 20 | 0 | 43 | 42 | 47 | 43 | 0 | 0 | 62 | 78 | 0 | 220 | 0 | 27 | 10 | 295 | 8 | 0 | 0 | 245 | 0 | 0 | 200 | 0 | 106 | 10 | 11 | 120 | 130 | 353 | 38 | 105 | 56 | 3 | 170 | 36 | 110 | 17 | 108 | 10 | 0 | 17 | 34 | 17 | 108 | 0 | 35 | 16 | 36 | 55 | 0 |  | 900 | 0 | 225 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 23 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 140 | 0 | 356 | 0 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 890 | 225 | 0 | 0 | 1 | 68 | 108 | 0 | 0 |  | 6490 | 4041 | 10531 | 3289 | 900 | 1806 | 0 | 2586 | 1090 | 127 | 130 | 475 | 126 | 132 | 0 | 91.36
9:00 | 0 | 0 | 0 | 180 | 160 | 86 | 0 | 406 | 316 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 9 | 25 | 31 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 82 | 31 | 16 | 6 | 0 | 0 | 0 | 300 | 300 | 170 | 8 | 130 | 38 | 5 | 0 | 51 | 0 | 49 | 8 | 0 | 10 | 28 | 20 | 134 | 85 | 0 | 20 | 1 | 43 | 42 | 47 | 49 | 0 | 0 | 60 | 81 | 0 | 220 | 0 | 26 | 10 | 330 | 8 | 0 | 0 | 238 | 0 | 0 | 200 | 0 | 106 | 15 | 11 | 120 | 132 | 400 | 38 | 105 | 71 | 3 | 172 | 36 | 110 | 17 | 107 | 10 | 0 | 16 | 34 | 17 | 108 | 0 | 35 | 24 | 36 | 55 | 0 |  | 900 | 0 | 200 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 21 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 163 | 0 | 0 | 130 | 0 | 0 | 139 | 0 | 398 | 0 | 0 | 70 | 105 | 81 | 0 | 0 | 75 | 910 | 221 | 0 | 0 | 2 | 75 | 72 | 0 | 0 |  | 6587 | 4051 | 10638 | 3279 | 900 | 1901 | 0 | 2559 | 1109 | 127 | 130 | 475 | 134 | 154 | 424 | 91.39
10:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 404 | 341 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 9 | 25 | 31 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 79 | 31 | 19 | 10 | 0 | 0 | 0 | 300 | 300 | 154 | 8 | 129 | 34 | 5 | 0 | 51 | 0 | 40 | 8 | 7 | 10 | 24 | 18 | 140 | 70 | 0 | 20 | 2 | 43 | 42 | 47 | 46 | 0 | 0 | 56 | 81 | 0 | 220 | 0 | 27 | 10 | 320 | 16 | 11 | 0 | 238 | 0 | 0 | 194 | 0 | 106 | 18 | 11 | 120 | 123 | 390 | 38 | 90 | 88 | 5 | 177 | 36 | 110 | 17 | 110 | 10 | 0 | 17 | 37 | 17 | 108 | 0 | 35 | 29 | 36 | 55 | 0 |  | 865 | 0 | 180 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 23 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 163 | 0 | 0 | 155 | 0 | 0 | 134 | 0 | 360 | 0 | 0 | 70 | 89 | 85 | 0 | 0 | 75 | 920 | 216 | 0 | 0 | 1 | 73 | 72 | 0 | 0 |  | 6419 | 3968 | 10387 | 3064 | 865 | 1875 | 0 | 2540 | 1120 | 127 | 155 | 491 | 140 | 165 | 934 | 91.4
11:00 | 0 | 0 | 0 | 180 | 20 | 86 | 0 | 401 | 344 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 31 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 81 | 31 | 19 | 8 | 0 | 0 | 0 | 300 | 300 | 178 | 8 | 130 | 34 | 5 | 0 | 51 | 0 | 46 | 8 | 16 | 10 | 13 | 18 | 148 | 70 | 0 | 20 | 2 | 43 | 42 | 50 | 44 | 0 | 0 | 58 | 81 | 0 | 220 | 0 | 26 | 10 | 320 | 16 | 11 | 0 | 230 | 0 | 0 | 200 | 0 | 119 | 19 | 11 | 120 | 122 | 380 | 47 | 105 | 89 | 4 | 177 | 36 | 110 | 17 | 105 | 10 | 0 | 16 | 46 | 17 | 108 | 0 | 35 | 33 | 47 | 55 | 0 |  | 835 | 0 | 180 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 18 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 159 | 0 | 0 | 130 | 0 | 0 | 125 | 0 | 345 | 0 | 0 | 70 | 89 | 85 | 0 | 1 | 75 | 850 | 176 | 0 | 0 | 4 | 100 | 72 | 0 | 0 |  | 6505 | 3861 | 10366 | 3145 | 835 | 1815 | 0 | 2566 | 1049 | 127 | 130 | 472 | 148 | 209 | 1183 | 91.41
12:00 | 0 | 0 | 0 | 180 | 70 | 89 | 0 | 402 | 322 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 31 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 87 | 31 | 19 | 10 | 0 | 0 | 0 | 300 | 300 | 174 | 8 | 130 | 40 | 5 | 0 | 51 | 0 | 37 | 8 | 19 | 10 | 8 | 18 | 154 | 70 | 0 | 20 | 3 | 44 | 42 | 50 | 45 | 0 | 0 | 58 | 81 | 0 | 220 | 0 | 26 | 10 | 325 | 16 | 11 | 0 | 220 | 0 | 0 | 200 | 0 | 124 | 20 | 11 | 120 | 122 | 404 | 46 | 90 | 89 | 5 | 177 | 36 | 110 | 17 | 105 | 10 | 0 | 19 | 25 | 17 | 108 | 0 | 35 | 34 | 58 | 55 | 0 |  | 865 | 0 | 170 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 19 | 16 | 0 | 0 | 0 | 34 | 0 | 78 | 0 | 25 | 24 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 140 | 0 | 0 | 126 | 0 | 336 | 0 | 0 | 70 | 89 | 85 | 0 | 1 | 75 | 900 | 216 | 0 | 0 | 3 | 100 | 72 | 0 | 0 |  | 6540 | 3959 | 10499 | 3205 | 865 | 1836 | 0 | 2568 | 1099 | 127 | 140 | 454 | 154 | 191 | 1291 | 91.42
13:00 | 0 | 0 | 0 | 180 | 130 | 89 | 0 | 400 | 311 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 25 | 52 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 86 | 31 | 19 | 10 | 0 | 0 | 0 | 300 | 300 | 174 | 8 | 130 | 40 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 10 | 16 | 18 | 152 | 71 | 0 | 20 | 2 | 43 | 42 | 50 | 45 | 0 | 0 | 58 | 81 | 0 | 220 | 0 | 28 | 10 | 320 | 16 | 11 | 0 | 225 | 0 | 0 | 183 | 0 | 125 | 19 | 11 | 120 | 122 | 400 | 49 | 90 | 89 | 5 | 177 | 36 | 103 | 17 | 102 | 10 | 0 | 24 | 3 | 17 | 108 | 0 | 35 | 23 | 72 | 55 | 0 |  | 865 | 0 | 160 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 19 | 16 | 0 | 0 | 0 | 34 | 5 | 78 | 0 | 25 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 0 | 119 | 0 | 322 | 0 | 0 | 70 | 88 | 85 | 0 | 1 | 75 | 970 | 217 | 0 | 0 | 5 | 74 | 72 | 0 | 0 |  | 6557 | 4035 | 10592 | 3242 | 865 | 1808 | 0 | 2568 | 1170 | 128 | 197 | 527 | 152 | 132 | 1390 | 91.43
14:00 | 0 | 0 | 0 | 180 | 230 | 89 | 0 | 405 | 320 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 25 | 52 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 0 | 10 | 86 | 31 | 18 | 2 | 0 | 0 | 0 | 300 | 300 | 188 | 8 | 127 | 38 | 5 | 0 | 51 | 0 | 40 | 8 | 19 | 10 | 16 | 18 | 160 | 71 | 0 | 20 | 2 | 43 | 42 | 50 | 42 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 28 | 10 | 305 | 16 | 11 | 0 | 225 | 0 | 0 | 183 | 0 | 121 | 17 | 11 | 120 | 107 | 404 | 49 | 89 | 88 | 4 | 177 | 36 | 106 | 17 | 102 | 10 | 0 | 35 | 10 | 17 | 108 | 0 | 35 | 32 | 72 | 55 | 0 |  | 865 | 0 | 160 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 21 | 16 | 0 | 0 | 0 | 34 | 18 | 89 | 0 | 25 | 32 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 130 | 0 | 0 | 133 | 0 | 311 | 0 | 0 | 70 | 88 | 85 | 0 | 1 | 75 | 980 | 218 | 0 | 0 | 4 | 94 | 72 | 0 | 0 |  | 6667 | 4022 | 10689 | 3370 | 865 | 1783 | 0 | 2556 | 1179 | 128 | 130 | 484 | 160 | 164 | 1319 | 91.44
15:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 402 | 319 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 26 | 49 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 31 | 0 | 10 | 85 | 31 | 18 | 2 | 0 | 0 | 0 | 300 | 300 | 196 | 8 | 130 | 38 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 16 | 20 | 168 | 71 | 0 | 20 | 2 | 43 | 42 | 50 | 44 | 0 | 0 | 60 | 81 | 0 | 221 | 0 | 29 | 10 | 325 | 23 | 11 | 0 | 223 | 0 | 0 | 183 | 0 | 105 | 12 | 11 | 120 | 117 | 398 | 48 | 105 | 88 | 4 | 195 | 36 | 110 | 17 | 105 | 10 | 0 | 36 | 14 | 17 | 108 | 0 | 35 | 24 | 72 | 55 | 0 |  | 864 | 0 | 155 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 22 | 16 | 0 | 0 | 0 | 34 | 17 | 86 | 0 | 25 | 32 | 8 | 31 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 126 | 0 | 283 | 0 | 0 | 70 | 88 | 85 | 0 | 2 | 75 | 990 | 216 | 0 | 0 | 4 | 25 | 72 | 0 | 0 |  | 6787 | 3952 | 10739 | 3436 | 864 | 1771 | 0 | 2590 | 1189 | 128 | 130 | 506 | 168 | 87 | 1392 | 91.45
16:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 402 | 318 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 25 | 24 | 50 | 0 | 91 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 28 | 0 | 10 | 87 | 35 | 18 | 4 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 130 | 34 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 28 | 20 | 164 | 70 | 0 | 20 | 1 | 44 | 42 | 53 | 45 | 0 | 0 | 60 | 81 | 0 | 220 | 0 | 29 | 10 | 310 | 24 | 11 | 0 | 240 | 0 | 0 | 182 | 0 | 108 | 10 | 20 | 120 | 118 | 388 | 48 | 105 | 88 | 1 | 177 | 36 | 110 | 17 | 105 | 10 | 0 | 36 | 28 | 28 | 108 | 0 | 35 | 9 | 45 | 55 | 0 |  | 864 | 0 | 150 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 22 | 16 | 0 | 0 | 0 | 34 | 17 | 86 | 0 | 0 | 32 | 8 | 36 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 122 | 0 | 280 | 0 | 0 | 87 | 88 | 84 | 0 | 4 | 100 | 970 | 216 | 0 | 0 | 3 | 57 | 72 | 0 | 0 |  | 6763 | 3999 | 10762 | 3426 | 864 | 1758 | 0 | 2634 | 1169 | 126 | 130 | 508 | 164 | 113 | 1325 | 91.45
17:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 404 | 320 |  | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 25 | 9 | 25 | 25 | 50 | 0 | 91 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 0 | 44 | 90 | 35 | 18 | 5 | 0 | 0 | 0 | 300 | 300 | 189 | 8 | 130 | 38 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 33 | 20 | 158 | 71 | 0 | 20 | 1 | 44 | 42 | 53 | 42 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 31 | 10 | 300 | 24 | 11 | 0 | 243 | 0 | 0 | 182 | 0 | 107 | 5 | 50 | 148 | 98 | 404 | 54 | 90 | 88 | 1 | 159 | 41 | 110 | 17 | 104 | 20 | 0 | 35 | 14 | 162 | 108 | 0 | 35 | 7 | 51 | 55 | 0 |  | 865 | 0 | 155 | 0 | 64 | 0 | 0 | 0 | 0 | 4 | 8 | 81 | 21 | 16 | 0 | 0 | 0 | 34 | 22 | 86 | 0 | 0 | 32 | 8 | 36 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 124 | 0 | 280 | 0 | 0 | 110 | 105 | 84 | 0 | 2 | 113 | 930 | 183 | 0 | 0 | 1 | 13 | 34 | 0 | 0 |  | 7000 | 3910 | 10910 | 3452 | 865 | 1717 | 0 | 2887 | 1129 | 126 | 130 | 532 | 158 | 44 | 820 | 91.45
18:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 406 | 321 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 32 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 25 | 19 | 25 | 25 | 50 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 43 | 0 | 44 | 87 | 36 | 18 | 12 | 0 | 0 | 0 | 300 | 300 | 189 | 8 | 130 | 38 | 5 | 0 | 51 | 0 | 47 | 8 | 19 | 10 | 33 | 20 | 150 | 86 | 0 | 20 | 0 | 44 | 42 | 53 | 45 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 30 | 10 | 290 | 24 | 11 | 0 | 230 | 0 | 0 | 190 | 0 | 107 | 1 | 90 | 186 | 100 | 403 | 104 | 105 | 88 | 0 | 294 | 54 | 110 | 17 | 104 | 90 | 0 | 57 | 3 | 162 | 108 | 0 | 35 | 1 | 56 | 55 | 0 |  | 866 | 0 | 155 | 0 | 64 | 0 | 0 | 0 | 20 | 35 | 8 | 82 | 20 | 16 | 0 | 0 | 0 | 34 | 23 | 86 | 0 | 0 | 32 | 8 | 36 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 130 | 0 | 0 | 123 | 0 | 280 | 0 | 0 | 113 | 105 | 105 | 0 | 2 | 113 | 890 | 162 | 0 | 0 | 0 | 4 | 34 | 0 | 0 |  | 7511 | 3915 | 11426 | 3478 | 866 | 1696 | 0 | 3391 | 1089 | 127 | 130 | 618 | 150 | 11 | 114 | 91.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 405 | 327 |  | 0 | 225 | 0 | 18 | 0 | 55 | 0 | 0 | 0 | 50 | 82 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 17 | 25 | 26 | 50 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 44 | 92 | 36 | 18 | 14 | 0 | 0 | 0 | 300 | 320 | 186 | 8 | 130 | 41 | 5 | 0 | 51 | 0 | 47 | 17 | 19 | 10 | 33 | 20 | 180 | 102 | 0 | 20 | 0 | 43 | 42 | 53 | 45 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 33 | 10 | 295 | 24 | 11 | 0 | 235 | 0 | 0 | 192 | 0 | 108 | 0 | 90 | 200 | 103 | 400 | 95 | 105 | 88 | 0 | 300 | 54 | 110 | 17 | 105 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 850 | 0 | 155 | 0 | 64 | 0 | 0 | 0 | 42 | 60 | 24 | 82 | 27 | 32 | 0 | 0 | 0 | 34 | 24 | 86 | 0 | 0 | 32 | 12 | 36 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 138 | 0 | 0 | 137 | 0 | 0 | 123 | 0 | 280 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 910 | 212 | 0 | 0 | 0 | 0 | 72 | 0 | 0 |  | 7837 | 4099 | 11936 | 3505 | 850 | 1695 | 0 | 3720 | 1109 | 127 | 137 | 750 | 180 | 0 | 704 | 91.47
19:30 | 0 | 0 | 0 | 180 | 250 | 80 | 0 | 409 | 325 |  | 0 | 225 | 0 | 61 | 0 | 55 | 0 | 0 | 0 | 70 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 26 | 50 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 44 | 93 | 36 | 18 | 10 | 0 | 0 | 0 | 300 | 320 | 188 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 47 | 43 | 19 | 10 | 33 | 20 | 160 | 104 | 0 | 20 | 0 | 43 | 42 | 53 | 45 | 0 | 0 | 59 | 75 | 0 | 220 | 18 | 32 | 10 | 260 | 24 | 11 | 0 | 235 | 0 | 0 | 192 | 0 | 110 | 0 | 90 | 200 | 115 | 402 | 95 | 105 | 88 | 0 | 300 | 54 | 110 | 70 | 105 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 850 | 0 | 155 | 0 | 64 | 0 | 0 | 0 | 51 | 60 | 24 | 81 | 27 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 0 | 32 | 52 | 36 | 20 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 208 | 0 | 0 | 123 | 0 | 294 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1020 | 190 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7982 | 4339 | 12321 | 3476 | 850 | 1710 | 0 | 3948 | 1219 | 128 | 208 | 830 | 160 | 0 | 902 | 0
20:00 | 0 | 0 | 0 | 180 | 290 | 85 | 0 | 407 | 326 |  | 0 | 225 | 0 | 54 | 0 | 55 | 0 | 0 | 0 | 82 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 26 | 51 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 51 | 44 | 93 | 37 | 18 | 24 | 0 | 0 | 0 | 300 | 320 | 197 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 47 | 43 | 19 | 10 | 33 | 20 | 158 | 103 | 0 | 20 | 0 | 43 | 42 | 53 | 45 | 0 | 0 | 59 | 81 | 0 | 220 | 18 | 32 | 10 | 270 | 24 | 11 | 0 | 240 | 0 | 0 | 192 | 0 | 112 | 0 | 90 | 200 | 108 | 365 | 95 | 105 | 88 | 0 | 300 | 54 | 110 | 114 | 104 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 850 | 0 | 160 | 0 | 66 | 0 | 0 | 0 | 46 | 60 | 24 | 81 | 24 | 32 | 0 | 0 | 0 | 32 | 25 | 87 | 0 | 0 | 32 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 0 | 213 | 0 | 0 | 123 | 0 | 275 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1000 | 182 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8075 | 4297 | 12372 | 3490 | 850 | 1717 | 0 | 4000 | 1199 | 128 | 213 | 830 | 158 | 0 | 1224 | 91.46
21:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 404 | 326 |  | 0 | 225 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 22 | 51 | 0 | 94 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 36 | 44 | 93 | 37 | 18 | 30 | 0 | 0 | 0 | 300 | 320 | 200 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 46 | 43 | 18 | 10 | 33 | 20 | 158 | 103 | 0 | 20 | 0 | 43 | 42 | 53 | 45 | 0 | 0 | 61 | 81 | 0 | 220 | 18 | 32 | 10 | 315 | 24 | 11 | 0 | 240 | 0 | 0 | 192 | 0 | 119 | 0 | 90 | 200 | 117 | 404 | 96 | 105 | 88 | 0 | 300 | 54 | 110 | 114 | 104 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 849 | 0 | 160 | 0 | 63 | 0 | 0 | 0 | 46 | 58 | 24 | 82 | 28 | 32 | 0 | 0 | 0 | 32 | 28 | 91 | 0 | 0 | 24 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 0 | 210 | 0 | 0 | 129 | 0 | 290 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1020 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8198 | 4374 | 12572 | 3546 | 849 | 1822 | 0 | 4040 | 1219 | 129 | 210 | 809 | 158 | 0 | 1132 | 91.47
22:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 407 | 325 |  | 0 | 225 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 93 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 27 | 25 | 28 | 51 | 0 | 94 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 51 | 44 | 93 | 37 | 18 | 35 | 0 | 0 | 0 | 300 | 320 | 206 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 48 | 43 | 19 | 10 | 33 | 20 | 162 | 103 | 0 | 20 | 0 | 43 | 42 | 53 | 43 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 32 | 10 | 310 | 24 | 11 | 0 | 243 | 0 | 0 | 192 | 0 | 119 | 0 | 90 | 200 | 118 | 404 | 105 | 105 | 88 | 0 | 300 | 54 | 110 | 114 | 112 | 100 | 0 | 104 | 0 | 162 | 92 | 0 | 35 | 0 | 76 | 55 | 0 |  | 849 | 0 | 170 | 0 | 65 | 0 | 0 | 0 | 46 | 57 | 8 | 82 | 32 | 32 | 0 | 0 | 0 | 32 | 31 | 89 | 0 | 0 | 24 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 215 | 0 | 0 | 133 | 0 | 320 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1060 | 223 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8281 | 4455 | 12736 | 3560 | 849 | 1969 | 0 | 3979 | 1259 | 129 | 215 | 829 | 162 | 0 | 888 | 91.47
23:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 408 | 325 |  | 0 | 225 | 0 | 80 | 0 | 55 | 0 | 0 | 0 | 98 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 25 | 27 | 25 | 33 | 51 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 51 | 44 | 93 | 37 | 18 | 38 | 0 | 0 | 0 | 300 | 320 | 210 | 8 | 136 | 20 | 5 | 0 | 51 | 0 | 48 | 43 | 19 | 10 | 33 | 21 | 170 | 105 | 0 | 20 | 0 | 43 | 42 | 53 | 46 | 110 | 0 | 64 | 81 | 0 | 220 | 0 | 32 | 10 | 310 | 24 | 11 | 0 | 243 | 0 | 0 | 192 | 0 | 118 | 0 | 90 | 200 | 117 | 402 | 105 | 105 | 88 | 0 | 142 | 54 | 110 | 114 | 115 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 71 | 55 | 0 |  | 849 | 0 | 170 | 0 | 65 | 0 | 0 | 0 | 46 | 57 | 8 | 88 | 31 | 32 | 0 | 0 | 0 | 32 | 34 | 89 | 0 | 0 | 24 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 216 | 0 | 0 | 133 | 0 | 342 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1080 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8156 | 4504 | 12660 | 3561 | 849 | 1994 | 0 | 3846 | 1279 | 128 | 216 | 833 | 170 | 0 | 912 | 91.48
24:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 406 | 326 |  | 0 | 225 | 0 | 41 | 0 | 55 | 0 | 0 | 0 | 60 | 32 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 25 | 51 | 0 | 93 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 52 | 51 | 44 | 92 | 36 | 18 | 38 | 0 | 0 | 0 | 300 | 320 | 205 | 8 | 137 | 20 | 5 | 0 | 51 | 0 | 38 | 16 | 19 | 0 | 33 | 21 | 170 | 105 | 0 | 20 | 0 | 43 | 42 | 53 | 46 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 320 | 24 | 11 | 0 | 243 | 0 | 0 | 192 | 0 | 116 | 0 | 90 | 200 | 115 | 400 | 49 | 105 | 88 | 0 | 142 | 54 | 110 | 17 | 110 | 100 | 0 | 17 | 0 | 17 | 108 | 0 | 35 | 0 | 54 | 55 | 0 |  | 849 | 0 | 165 | 0 | 66 | 0 | 0 | 0 | 46 | 57 | 8 | 85 | 31 | 32 | 0 | 0 | 0 | 32 | 34 | 89 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 143 | 0 | 0 | 214 | 0 | 0 | 133 | 0 | 325 | 0 | 0 | 70 | 105 | 107 | 0 | 0 | 113 | 1060 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7498 | 4372 | 11870 | 3543 | 849 | 1991 | 0 | 3109 | 1259 | 128 | 214 | 821 | 170 | 0 | 1318 | 91.48
KWH | 0 | 0 | 0 | 4347000 | 5094936 | 2037590 | 0 | 9865210 | 7658000 |  | 0 | 5054950 | 0 | 483840 | 0 | 1326083 | 0 | 0 | 0 | 622080 | 618192 | 2647680 | 0 | 0 | 0 | 0 | 379080 | 297421 | 259508 | 377604 | 600000 | 454320 | 617600 | 695300 | 1234080 | 0 | 2210182 | 848000 | 100000 | 0 | 610948 | 0 | 0 | 0 | 0 |  | 583440 | 1114992 | 327994 | 508560 | 2104320 | 796800 | 398688 | 466080 | 0 | 0 | 0 | 7342000 | 7189000 | 4652000 | 217454 | 3111470 | 849456 | 144480 | 0 | 1232430 | 0 | 1116416 | 366269 | 379044 | 221040 | 673400 | 499520 | 3587520 | 2041920 | 0 | 346608 | 15000 | 1020000 | 965456 | 1119000 | 1017000 | 287918 | 0 | 1428864 | 1841280 | 0 | 5254410 | 52000 | 580160 | 243540 | 7521000 | 377928 | 165251 | 0 | 5838652 | 0 | 0 | 4615200 | 0 | 2652912 | 140670 | 804480 | 3488640 | 2867054 | 9431000 | 1332000 | 2469600 | 2048245 | 36840 | 4518873 | 1051074 | 2670497 | 836760 | 2584680 | 840960 | 459000 | 1014720 | 262590 | 1484640 | 2586873 | 0 | 888480 | 255981 | 1271040 | 1339200 | 0 |  | 21080727 | 0 | 4702464 | 0 | 1092480 | 0 | 0 | 0 | 478080 | 661248 | 229500 | 1664389 | 572446 | 564480 | 0 | 0 | 0 | 785088 | 337631 | 2044176 | 0 | 373193 | 558363 | 490560 | 554800 | 468480 | 0 | 266670 | 0 | 0 | 4867500 | 0 | 0 | 3959745 | 0 | 0 | 3909555 | 0 | 0 | 3492382 | 0 | 8173782 | 12 | 0 | 2124672 | 2451024 | 2276160 | 0 | 13343 | 2141088 | 24966600 | 4848191 | 0 | 22560 | 32220 | 727920 | 2043840 | 0 | 0 |  | 168389973 | 102975369 | 271365342 | 83095675 | 21080727 | 43483781 | 0 | 71204770 | 29834100 | 3058182 | 3909555 | 10626468 | 3587520 | 1484564 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 5706328.32 | 2709994.7 | 0 | 10358470.5 | 8270640 |  | 0 | 5509895.5 | 0 | 5409331.2 | 0 | 17570599.75 | 0 | 0 | 0 | 9094809.6 | 8697961.44 | 42918892.8 | 0 | 0 | 0 | 0 | 4821897.6 | 4015183.5 | 3480002.28 | 283203 | 450000 | 0 | 0 | 0 | 20991700.8 | 0 | 596749.14 | 228960 | 189000 | 0 | 9988999.8 | 0 | 0 | 0 | 0 |  | 7613892 | 18598066.56 | 5582457.88 | 6870645.6 | 26682777.6 | 9218976 | 506333.76 | 1552046.4 | 0 | 0 | 0 | 8149620 | 7836010 | 5396320 | 280515.66 | 3795993.4 | 959885.28 | 215275.2 | 0 | 2058158.1 | 0 | 19280504.32 | 4926318.05 | 519290.28 | 165780 | 1178450 | 374640 | 25758393.6 | 2225692.8 | 0 | 471386.88 | 239100 | 1397400 | 1274401.92 | 1947060 | 1759410 | 331105.7 | 0 | 2771996.16 | 4198118.4 | 0 | 5306954.1 | 111800 | 864438.4 | 482209.2 | 7521000 | 283446 | 125590.76 | 0 | 79697599.8 | 0 | 0 | 62212896 | 0 | 36742831.2 | 1644432.3 | 8302233.6 | 47654822.4 | 38045806.58 | 8676520 | 16197120 | 35710416 | 25910299.25 | 0 | 53051569.02 | 11446195.86 | 28387383.11 | 11354833.2 | 33316525.2 | 9906508.8 | 422280 | 13140624 | 3794425.5 | 18840081.6 | 29438614.74 | 0 | 11603548.8 | 3058972.95 | 19027468.8 | 17637264 | 0 |  | 63242181 | 0 | 5266759.68 | 0 | 11372716.8 | 0 | 0 | 0 | 8610220.8 | 11902464 | 3297915 | 1864115.68 | 1110545.24 | 6152832 | 0 | 0 | 0 | 13165925.76 | 5905166.19 | 31970912.64 | 0 | 6180076.08 | 9441918.33 | 6686332.8 | 9359476 | 969753.6 | 0 | 201869.19 | 0 | 0 | 25749075 | 0 | 0 | 4593304.2 | 0 | 0 | 68260830.3 | 0 | 0 | 4051163.12 | 0 | 8092044.18 | 161.28 | 0 | 25134869.76 | 35417296.8 | 28907232 | 0 | 147440.15 | 25992808.32 | 224949066 | 4945154.82 | 0 | 166944 | 364408.2 | 8538501.6 | 31332067.2 | 0 | 0 |  | 981822382.65 | 693343547.72 | 1675165930.37 | 91391035.03 | 63242181 | 52817365.1 | 0 | 927648989.22 | 250698141 | 825709.14 | 68260830.3 | 176736005.28 | 25758393.6 | 17787280.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 160 | 86 | 0 | 406 | 316 |  | 0 | 225 | 0 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 9 | 25 | 31 | 52 | 0 | 92 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 51 | 0 | 10 | 82 | 31 | 16 | 6 | 0 | 0 | 0 | 300 | 300 | 170 | 8 | 130 | 38 | 5 | 0 | 51 | 0 | 49 | 8 | 0 | 10 | 28 | 20 | 134 | 85 | 0 | 20 | 1 | 43 | 42 | 47 | 49 | 0 | 0 | 60 | 81 | 0 | 220 | 0 | 26 | 10 | 330 | 8 | 0 | 0 | 238 | 0 | 0 | 200 | 0 | 106 | 15 | 11 | 120 | 132 | 400 | 38 | 105 | 71 | 3 | 172 | 36 | 110 | 17 | 107 | 10 | 0 | 16 | 34 | 17 | 108 | 0 | 35 | 24 | 36 | 55 | 0 |  | 900 | 0 | 200 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 21 | 16 | 0 | 0 | 0 | 34 | 0 | 89 | 0 | 25 | 24 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 163 | 0 | 0 | 130 | 0 | 0 | 139 | 0 | 398 | 0 | 0 | 70 | 105 | 81 | 0 | 0 | 75 | 910 | 221 | 0 | 0 | 2 | 75 | 72 | 0 | 0 |  | 10638 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 404 | 326 | 0 | 0 | 225 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 22 | 51 | 0 | 94 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 52 | 36 | 44 | 93 | 37 | 18 | 30 | 0 | 0 | 0 | 300 | 320 | 200 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 46 | 43 | 18 | 10 | 33 | 20 | 158 | 103 | 0 | 20 | 0 | 43 | 42 | 53 | 45 | 0 | 0 | 61 | 81 | 0 | 220 | 18 | 32 | 10 | 315 | 24 | 11 | 0 | 240 | 0 | 0 | 192 | 0 | 119 | 0 | 90 | 200 | 117 | 404 | 96 | 105 | 88 | 0 | 300 | 54 | 110 | 114 | 104 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 849 | 0 | 160 | 0 | 63 | 0 | 0 | 0 | 46 | 58 | 24 | 82 | 28 | 32 | 0 | 0 | 0 | 32 | 28 | 91 | 0 | 0 | 24 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 0 | 210 | 0 | 0 | 129 | 0 | 290 | 0 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1020 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 12572 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 90 | 0 | 55 | 0 | 0 | 0 | 90 | 94 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 51 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 36 | 44 | 90 | 31 | 18 | 25 | 0 | 0 | 0 | 300 | 330 | 211 | 8 | 130 | 20 | 5 | 0 | 51 | 0 | 48 | 43 | 19 | 11 | 33 | 20 | 166 | 104 | 0 | 20 | 0 | 43 | 43 | 20 | 43 | 110 | 0 | 60 | 81 | 0 | 220 | 0 | 32 | 10 | 330 | 24 | 0 | 0 | 245 | 0 | 0 | 200 | 0 | 120 | 0 | 90 | 200 | 130 | 400 | 92 | 105 | 105 | 0 | 285 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 |  | 95 | 55 |  |  | 912 | 0 | 160 | 0 | 83 | 0 | 0 | 0 | 40 | 66 | 24 | 85 | 25 | 32 | 0 | 0 | 0 | 34 | 25 | 88 | 0 | 25 | 24 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 17 | 0 | 113 | 105 | 105 | 0 | 0 | 113 | 1100 | 220 |  | 17 |  |  | 108
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 400 | 300 | 0 | 0 | 225 | 0 | 8 | 0 | 55 | 0 | 0 | 0 | 8 | 7 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 20 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 0 | 10 | 90 | 30 | 17 | 10 | 0 | 0 | 0 | 300 | 300 | 180 | 8 | 130 | 20 | 5 | 0 | 51 | 0 | 48 | 8 | 19 | 11 | 33 | 20 | 143 | 90 | 0 | 20 | 1.6 | 43 | 42 | 47 | 43 | 110 | 0 | 60 | 81 | 0 | 220 | 0 | 25 | 10 | 300 | 8 | 0 | 0 | 245 | 0 | 0 | 200 | 0 | 110 | 20 | 11 | 100 | 117 | 400 | 40 | 105 | 105 | 5 | 175 | 36 | 110 | 17 | 107 | 10 | 0 | 17 | 50 | 17 | 108 | 0 | 35 | 30 | 36 | 55 |  |  | 876 | 0 | 200 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 15 | 16 | 0 | 0 | 0 | 34 | 0 | 88 | 0 | 25 | 24 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 330 | 17 | 0 | 70 | 105 | 92 | 0 | 8 | 75 | 910 | 225 |  | 0 | 6 | 100 | 108
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 409 | 313 | 0 | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 32 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 17 | 51 | 0 | 92 | 35 | 85 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 34 | 0 | 44 | 83 | 35 | 17 | 10 | 0 | 0 | 0 | 275 | 340 | 180 | 8 | 135 | 20 | 5 | 0 | 51 | 0 | 40 | 8 | 0 | 0 | 33 | 20 | 146 | 104 | 0 | 20 | 0 | 44 | 41 | 53 | 45 | 110 | 0 | 64 | 10 | 0 | 220 | 0 | 32 | 10 | 300 | 24 | 11 | 0 | 193 | 0 | 0 | 183 | 0 | 117 | 11 | 90 | 120 | 112 | 340 | 49 | 88 | 105 | 1 | 141 | 36 | 92 | 17 | 108 | 100 | 0 | 17 | 7 | 17 | 108 | 0 | 35 | 11 | 54 | 55 | 0 | 0 | 900 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 18 | 16 | 0 | 0 | 0 | 24 | 0 | 82 | 0 | 0 | 32 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 323 | 0 | 0 | 70 | 75 | 85 | 0 | 1 | 75 | 850 | 157 | 0 | 0 | 2 | 51 | 90 | 0 | 0 | 0 |  |  |  |  | 85740793 |  | 0
85740793
| Minimum Generation |  | 10386 | 6:00
| Highest Generation |  | 12736 | 22:00
| Day Peak Generation |  | 10638 | 9:00
| Evening Peak Generation |  | 12572 | 21:00
| HVDC Max Flow |  | 900 | 3:00
| HVDC EvPeak Flow |  | 849 | 21:00
| Load factor L.F |  | 88.78% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-28
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10638 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10761 | MW
Evening Peak Generation : |  | 12572 | MW Hour : | 21:00 | Available Max Generation : |  | 12876 | MW
E.P. Demand (at gen end) : |  | 13500 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12736 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 271.3653 | System Load Factor : | 88.78% | Load Shed : |  | 1036.3034 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 408 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-28
Actual : | 91.54 | Ft.(MSL) , | Rule curve : | 88.32 | Ft.( MSL )
Gas Consumed : | Total = | 963.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144208400.13
: |  | Coal : | 250698141 | Oil : | 1172645824.8 | Total : | 1567552365.93
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 145 | 3480:00 | 4483.4624 |  |  | 287.4537 | 6.411%
Chittagong Area | 61 | 1464:00 | 1269.5617 |  |  | 110.0766 | 8.67%
Khulna Area | 220 | 5280:00 | 1675.9763 |  |  | 152.1809 | 9.08%
Rajshahi Area | 210 | 5040:00 | 1487.6064 |  |  | 143.644 | 9.656%
Cumilla Area | 166 | 3984:00 | 1265.6911 |  |  | 118.0008 | 9.323%
Mymensingh Area | 190 | 4560:00 | 1046.3563 |  |  | 103.2832 | 9.871%
Sylhet Area | 0 | 0:00 | 467.0542 |  |  | 40.6049 | 8.694%
Barisal Area | 0 | 0:00 | 380.6105 |  |  | 0 | 0%
Rangpur Area | 140 | 3360:00 | 825.7312 |  |  | 81.0594 | 9.817%
Total | 1132 |  | 12902.05 |  |  | 1036.3034
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Nawabganj 132/33 kV T-2 transformer was under shut down from 07:39 to 08:43 for R/H maintenance.
b) Cumilla(N)-Kachua 132 kV Ckt was under shut down from 09:14 to 12:44 for C/M.
c) Sirajganj-Baghabari 230 kV Ckt-2 was under shut down from 09:20 to 12:33 for C/M.
d) Rajshahi 132/33 kV T-2 transformer was under shut down from 09:20 to 12:33 for C/M.
e) Tongi-Kaliakoir 230 kV Ckt was under shut down from 10:25 to 17:52 for D/W.
f) Cumilla(S)-Kachua 132 kV Ckt was under shut down from 13:07 to 16:30 for C/M.
g) Sirajganj-Bogura 230 kV Ckt-1 was under shut down from 13:13 to 13:45 for C/M.
h) Ghorashal Unit-7 GT was synchronized at 10:52 & ST at 12:41.
i) Bhola 225 MW ST was synchronized at 10:27.
j) Sirajganj-Bogura 230 kV Ckt-2 was under shut down from 13:46 to 14:19 for C/M.
k) Ghorashal(GIS)-Ishwardi 230 kV Ckt-2 tripped at 09:55 from Ghorashal end showing Dist. B-φ and was switched on at 11:32.
l) Ghorashal(GIS)-Ishwardi 230 kV Ckt-1 tripped at 10:40 from Ghorashal end showing Dist. B-φ and was switched on at 11:32.
m) Rampura-Bhulta 230 kV Ckt-2 tripped at 11:02 from both ends showing Dist. at Rampura end & E/F at Bhulta
end and was switched on at 15:31.
n) Rampura 230 kV Bus-1 tripped at 11:02 and was switched on at 11:40.
o) Ghorashal(GIS)-Ishwardi 230 kV Ckt-1 was under shutdown from 16:17 to 17:51 for PBS pole removal work.
p) Chapainawabganj-Rohanpur 132 kV Ckt was switched on at 15:57.
q) Barishal(N) 132/33 kV T-1 & T-2 transformers tripped at 16:57 as Bird fall on 33 kV Bus PT and was switched | [5 empty] | About 40 MW power interruption occurred under
on at 20:12. | [5 empty] | Barishal S/S area from 16:57 to 20:12.
r) Kushiara 163 MW GT was synchronized at 21:10.
s) Feni 132/33 kV T-1 transformer & 33 kV Bus were shut down at 06:36(28/07/2022) for C/M. | [5 empty] | About 05 MW power interruption has been occurring
under Feni S/S area since 06:36(28/07/2022).
t) Khulna(C)-Khulna(S) 132 kV Ckt-1 is under shut down since 07:21(28/07/2022) due to Khulna(S) R-φ CT temperature
high.
u) Bagerhat-Bhandaria 132 kV Ckt was switched on at 06:42(28/07/2022).
v) Raozan Unit-1 was synchronized at 06:42(28/07/2022).
w) Bhola 225 MW ST was Force shutdown at 07:02(28/07/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 5094936 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 82 | 2037590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 404 | 9865210
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7658000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5054950 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 72 | 483840 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1326083
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 377604
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 90 | 622080 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 618192 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 379080 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2647680
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 297421
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 259508
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1054320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 617600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 695300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 1234080 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 240 | 5838652 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 119 | 2652912 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2469600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1014720
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1484640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 255981
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1339200
| Dhaka area Total |  |  |  | 5847 | 3077 | 59726179
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 100000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 610948
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 140670
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 796800 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 129 | 3058182 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 2048245 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 1114992 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 36 | 327994 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 44 | 508560 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 804480 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 398688 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 466080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 2104320 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36840
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 4518873
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1051074
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2670497
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 840960
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2586873 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1314 | 24185076
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4652000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7342000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7189000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 849456 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 144480 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1232430
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 117 | 2867054 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 1116416
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3111470 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3488640
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 379044 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 221040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3587520
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 673400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 366269 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 499520 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 836760
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 2584680 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 888480 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 1271040 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2013 | 43518153
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2041920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 346608
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 192 | 4615200
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1332000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 262590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 583440
| Mymensingh Area Total |  |  |  | 614 | 435 | 9196758
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1020000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 965456 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 287918 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1119000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 45 | 1017000
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 165251
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1428864
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1841280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5254410
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 52000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 32 | 580160 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 377928
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7521000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9431000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243540
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 459000 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1359 | 31763807
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 849 | 21080727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 63 | 1092480 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 46 | 478080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 58 | 661248 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 4702464 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 24 | 229500 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 12 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2451024
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 727920
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1305 | 31423455
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 564480 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 572446 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 1664389 | Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 24966600 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4848191
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 22560 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1382 | 32638666
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 785088 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 337631 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 373193 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 558363 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 142 | 3959745 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 210 | 3909555
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 129 | 3492382 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 290 | 8173782 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 554800 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 468480
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 266670
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 490560
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 2044176 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2124672
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2141088
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32220
| Rajshahi Area Total |  |  |  | 2129 | 1292 | 29712405
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4867500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 2276160 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 13343
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 2043840 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 395 | 9200843
| Total |  |  |  | 21680 | 12572 | 271365342
| Eastern Grid Total |  |  |  | 14489 | 8198 | 168389973
| Western Grid Total |  |  |  | 7191 | 4374 | 102975369
| National Grid Total |  |  |  | 21680 | 12572 | 271365342
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-27
(a) ENTIRE EASTERN GRID : |  | 8433.4 | MW | (b) ENTIRE WESTERN GRID : |  | 3762.28 | MW
i) Dhaka area |  | 4660 | MW | i) Khulna area |  | 1434.6 | MW
ii) Chittagong area |  | 1283.4 | MW | ii) Rajshahi area |  | 1243.8 | MW
iii) Comilla area |  | 1044 | MW | iii) Barisal area |  | 378.88 | MW
iv) Mymensingh area |  | 839 | MW | iv) Rangpur area |  | 705 | MW
v) Sylhet area |  | 607 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12195.68 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 12 | 15:00 | Chowmuhani | 178 | 23:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 14 | 13:00 | Chuadanga | 93 | 05:00 | Kazla | 86 | 19:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 17:00 | Coxsbazar | 106 | 01:00 | Keranigonj | 58 | 19:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 88 | 13:00 | Cumilla(N) | 141 | 19:00 | Khagrachori | 28 | 21:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 86 | 19:00 | Cumilla(S) | 180 | 19:00 | Khulna | 86 | 20:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 54 | 01:00 | Daudkandi | 138 | 19:00 | Khulshi | 183 | 12:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 40 | 23:00 | Dhaka | 38 | 11:00 | Kishoreganj | 106 | 23:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 128 | 00:00 | Dhamrai | 114 | 21:00 | Kodda | 318 | 08:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 80 | 18:00 | Dhanmondi | 126 | 13:00 | Kulaura | 50 | 19:30 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 134 | 19:00 | Dohazari | 104 | 19:00 | Kurigram | 52 | 19:30 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 54 | 17:00 | Faridpur | 125 | 22:00 | Kushtia | 140 | 16:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 10:00 | Fatullah | 71 | 10:00 | Lalbag | 96 | 17:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 48 | 19:30 | Fenchuganj | 51 | 19:00 | Lalmonirhat | 41 | 23:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 22:00 | Feni | 80 | 23:00 | Madanganj | 85 | 21:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 116 | 19:00 | GPH | 10 | 00:00 | Madaripur | 105 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 64 | 23:00 | Ghorashal | 59 | 19:30 | Madartek | 83 | 22:00 | Rajendrapur | 92 | 05:00
Baroaulia | 72 | 00:00 | Goalpara | 26 | 12:00 | Madunaghat | 61 | 22:00 | Rajshahi | 132 | 22:00
Baroirhat | 62 | 21:00 | Gollamari | 50 | 12:00 | Magura | 48 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 153 | 17:00 | Gopalganj | 104 | 23:00 | Mahasthangarh | 64 | 19:30 | Ramganj | 88 | 19:00
BashundharaCement | 13 | 18:30 | Gulshan | 112 | 17:00 | Manikganj | 99 | 20:00 | Rampur | 16 | 00:00
Beanibazar | 70 | 20:00 | Halishahar | 91 | 10:00 | Maniknagar | 74 | 17:00 | Rangamati | 14 | 19:00
Benapole | 50 | 06:00 | HaripurSBU | 124 | 16:00 | Matarbari | 40 | 00:00 | Rangpur | 105 | 08:00
Bhaluka | 100 | 23:00 | Hasnabad | 86 | 19:00 | Matuail | 64 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 52 | 19:30 | Hathazari | 99 | 22:00 | Millgate | 74 | 09:00 | SSM | 3 | 05:00
Bhangura | 30 | 19:30 | Ishurdi | 72 | 23:00 | Mirpur | 136.5 | 17:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 63 | 22:00 | Jaldhaka | 50 | 07:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 219 | 00:00 | Jamalpur | 128 | 06:00 | Mithapukur | 28 | 18:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 58 | 20:00 | Jashore | 149 | 08:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 146 | 19:30 | Jhenaidah | 102 | 07:00 | Mogbazar | 122 | 16:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 22:00 | Joydebpur | 184 | 20:00 | Mongla | 30 | 07:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 136 | 19:30 | Joypurhat | 55 | 20:00 | Motijheel | 34 | 18:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 142 | 18:00 | Juldah | 25 | 00:00 | Munshiganj | 119 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 54 | 21:00 | KSRM | 24.7 | 19:30 | Mymensingh | 208 | 22:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 23:00 | Kabirpur | 311 | 22:00 | Naogaon | 113 | 23:00 | Shikalbaha | 28 | 19:00
Chapai | 70 | 08:00 | Kachua | 68 | 23:00 | Narail | 36 | 21:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 45 | 10:00 | Kallyanpur | 99 | 19:30 | Narinda | 69 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 52 | 23:00 | Kalurghat | 7 | 15:00 | Narshingdi | 172 | 21:00 | Sholosohor | N/A | N/A
Chhatak | 34 | 21:00 | Kamrangirchar | 57 | 18:30 | Natore | 120 | 19:30 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 380 | 01:00 | 363 | 11:00 | Kaliakoir | 388 | 06:00 | 375 | 14:00
| Bibiana | 406 | 19:00 | 392 | 14:00 | Payra | 415 | 05:00 | 409 | 22:00
| BIPTC | 402 | 04:00 | 397 | 10:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 409 | 11:00 | 397 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 219 | 05:00 | 205 | 10:00 | Hasnabad | 218 | 23:00 | 205 | 12:00
| AKSML | 237 | 17:00 | 228 | 03:00 | Hathazari | 240 | 19:30 | 225 | 15:00
| Aminbazar | 221 | 19:30 | 208 | 11:00 | Ishurdi | 235 | 19:30 | 225 | 12:00
| Ashuganj | 235 | 02:00 | 225 | 10:00 | Jhenaidah | 229 | 19:30 | 217 | 12:00
| Baghabari | 232 | 17:00 | 227 | 09:00 | Kaliakoir | 222 | 05:00 | 212 | 12:00
| Barapukuria | 222 | 15:00 | 217 | 18:30 | Keranigonj | 218 | 19:30 | 204 | 10:00
| Barishal | 248 | 18:30 | 240 | 00:00 | Khulna(S) | 237 | 19:30 | 226 | 12:00
| Bheramara | 232 | 19:30 | 222 | 09:00 | Maniknagar | 221 | 04:00 | 210 | 10:00
| Bhulta | 225 | 05:00 | 213 | 11:00 | Meghnaghat | 223 | 19:30 | 212 | 14:00
| Bibiana | 237 | 19:30 | 227 | 14:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 19:30 | 223 | 12:00 | Rajshahi | 231 | 19:30 | 222 | 12:00
| Bogura | 228 | 19:30 | 220 | 14:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 18:00 | 240 | 19:00 | Rampura | 223 | 19:30 | 210 | 10:00
| BSRM | 233 | 19:30 | 222 | 15:00 | Shikalbaha | 239 | 19:30 | 227 | 07:00
| Cumilla(N) | 228 | 23:00 | 219 | 10:00 | Shyampur | 219 | 19:30 | 205 | 10:00
| Fenchuganj | 238 | 01:00 | 232 | 15:00 | Siddhirganj | 222 | 19:30 | 211 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 16:00 | 226 | 11:00
| GPH | 237 | 19:30 | 222 | 15:00 | Tongi | 224 | 05:00 | 212 | 12:00
| Haripur | 220 | 19:00 | 210 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 128 | 10:00 | Lalbag | 134 | 01:00 | 125 | 10:00
| Agargaon | 136 | 04:00 | 126 | 10:00 | Lalmonirhat | 132 | 19:30 | 125 | 07:00
| Agrabad | 139 | 19:00 | 131 | 15:00 | Madanganj | 130 | 01:00 | 123 | 10:00
| AKS | 138 | 18:30 | 128 | 14:00 | Madaripur | 138 | 18:00 | 133 | 00:00
| Aminbazar | 132 | 19:30 | 122 | 11:00 | Madartek | 137 | 05:00 | 126 | 10:00
| Amnura | 133 | 19:30 | 125 | 12:00 | Madunaghat | 141 | 18:00 | 133 | 03:00
| Ashuganj | 136 | 18:30 | 134 | 19:00 | Magura | 138 | 19:30 | 132 | 07:00
| Bagerhat | 136 | 18:00 | 122 | 12:00 | Mahasthangarh | 135 | 19:30 | 131 | 14:00
| Bakulia | 141 | 19:30 | 131 | 15:00 | Manikganj | 133 | 19:30 | 127 | 08:00
| Banani | 131 | 02:00 | 121 | 12:00 | Maniknagar | 132 | 01:00 | 123 | 17:00
| Bangabhaban | 132 | 04:00 | 123 | 10:00 | Matarbari | 130 | 19:00 | 117 | 01:00
| Barapukuria | 136 | 19:30 | 131 | 18:30 | Matuail | 130 | 19:30 | 122 | 10:00
| Barguna | 133 | 01:00 | 126 | 22:00 | Millgate | 132 | 01:00 | 122 | 09:00
| Barishal | 140 | 18:00 | 125 | 14:00 | Mirpur | 130 | 23:00 | 120 | 11:00
| Barishal-230 | 141 | 17:00 | 135 | 00:00 | Mithapukur | 135 | 19:30 | 128 | 05:00
| Baroaulia | 139 | 19:30 | 134 | 05:00 | Modern | 135 | 00:00 | 133 | 08:00
| Baroirhat | 136 | 19:30 | 130 | 02:00 | Mogbazar | 136 | 07:00 | 128 | 12:00
| Bashundhara | 132 | 03:00 | 124 | 12:00 | Mongla | 130 | 19:30 | 123 | 00:00
| BashundharaCement | 130 | 01:00 | 123 | 10:00 | Motijheel | 132 | 04:00 | 123 | 12:00
| Beanibazar | 132 | 12:00 | 126 | 19:00 | Munshiganj | 134 | 05:00 | 123 | 15:00
| Benapole | 136 | 19:30 | 125 | 09:00 | Mymensingh | 135 | 16:00 | 124 | 05:00
| Bhaluka | 134 | 11:00 | 124 | 06:00 | Naogaon | 131 | 18:00 | 126 | 11:00
| Bhandaria | 140 | 17:00 | 130 | 00:00 | Narail | 137 | 19:30 | 130 | 09:00
| Bhangura | 138 | 19:30 | 134 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 19:30 | 133 | 09:00 | Narshingdi | 135 | 01:00 | 122 | 09:00
| Bheramara(GK) | 139 | 04:00 | 134 | 15:00 | Natore | 135 | 19:30 | 128 | 12:00
| Bhulta | 124 | 20:00 | 118 | 10:00 | Nawabganj | 134 | 06:00 | 125 | 10:00
| Bog-Sherpur | 135 | 01:00 | 131 | 12:00 | Netrakona | 134 | 16:00 | 122 | 08:00
| Bogura | 137 | 19:30 | 132 | 13:00 | New | 131 | 04:00 | 121 | 17:00
| Bogura-230 | 138 | 19:30 | 133 | 11:00 | Niamatpur | 129 | 16:00 | 123 | 12:00
| Brahmanbaria | 133 | 16:00 | 129 | 22:00 | Noapara | 136 | 19:30 | 126 | 09:00
| Cantonment | 135 | 20:00 | 124 | 10:00 | Pabna | 135 | 19:30 | 130 | 12:00
| Chandpur | 140 | 19:00 | 134 | 01:00 | Palashbari | 133 | 19:30 | 128 | 05:00
| Chandraghona | 140 | 19:30 | 133 | 15:00 | Panchagarh | 134 | 13:00 | 121 | 17:00
| Chapai | 132 | 19:30 | 125 | 12:00 | Patuakhali | 133 | 00:00 | 128 | 22:00
| Charsaidpur | 131 | 19:30 | 123 | 15:00 | Payra | 136 | 01:00 | 133 | 22:00
| Chauddagram | 135 | 20:00 | 129 | 15:00 | PHP | 136 | 19:30 | 128 | 15:00
| Chhatak | 133 | 16:00 | 126 | 21:00 | Postogola | 138 | 13:00 | 126 | 09:00
| Chowmuhani | 135 | 17:00 | 130 | 05:00 | Purbachal | 132 | 05:00 | 122 | 10:00
| Chuadanga | 135 | 19:30 | 126 | 09:00 | Purbasadipur | 133 | 19:30 | 124 | 17:00
| Coxsbazar | 129 | 11:00 | 116 | 02:00 | Rahim | 131 | 19:00 | 125 | 11:00
| Cumilla(N) | 134 | 20:00 | 129 | 15:00 | Rajbari | 135 | 19:30 | 129 | 12:00
| Cumilla(S) | 135 | 19:30 | 124 | 19:00 | Rajendrapur | 133 | 17:00 | 124 | 18:00
| Daudkandi | 131 | 23:00 | 124 | 10:00 | Rajshahi | 132 | 19:30 | 126 | 12:00
| Dhaka | 137 | 01:00 | 128 | 10:00 | Rajshahi-230 | 133 | 19:30 | 126 | 12:00
| Dhamrai | 129 | 01:00 | 122 | 10:00 | Ramganj | 135 | 19:30 | 129 | 01:00
| Dhanmondi | 131 | 19:30 | 123 | 12:00 | Rampur | 139 | 19:30 | 130 | 15:00
| Dohazari | 137 | 17:00 | 126 | 11:00 | Rampura | 137 | 04:00 | 127 | 10:00
| Faridpur | 134 | 04:00 | 130 | 00:00 | Rangamati | 139 | 19:30 | 131 | 15:00
| Fatullah | 132 | 19:30 | 123 | 15:00 | Rangpur | 132 | 13:00 | 126 | 18:00
| Fenchuganj | 136 | 13:00 | 133 | 18:30 | Ruppur | 136 | 20:00 | 132 | 12:00
| Feni | 137 | 20:00 | 130 | 02:00 | Saidpur | 133 | 19:30 | 124 | 17:00
| Ghorashal | 136 | 01:00 | 135 | 00:00 | Satkhira | 131 | 16:00 | 124 | 12:00
| Goalpara | 135 | 19:30 | 127 | 12:00 | Satmasjid | 134 | 05:00 | 125 | 10:00
| Gollamari | 135 | 19:30 | 129 | 00:00 | Savar | 132 | 19:30 | 120 | 10:00
| Gopalganj | 139 | 19:30 | 133 | 12:00 | Shahjadpur | 139 | 02:00 | 135 | 12:00
| Gopalganj_I | 138 | 04:00 | 134 | 12:00 | Shahjibazar | 135 | 11:00 | 130 | 19:00
| Gulshan | 136 | 06:00 | 127 | 11:00 | Shahmirpur | 140 | 19:30 | 130 | 15:00
| Halishahar | 139 | 19:00 | 131 | 14:00 | Shariatpur | 136 | 11:00 | 130 | 22:00
| Haripur | 131 | 19:00 | 125 | 11:00 | Sherpur | 140 | 16:00 | 127 | 05:00
| HaripurSBU | 132 | 19:30 | 125 | 10:00 | Shikalbaha | 141 | 18:00 | 125 | 14:00
| Hasnabad | 138 | 19:30 | 127 | 12:00 | Shikalbaha-230 | 140 | 19:30 | 133 | 07:00
| Hathazari | 140 | 20:00 | 133 | 15:00 | Shitalakhya | 137 | 19:00 | 124 | 12:00
| Ishurdi | 137 | 19:30 | 132 | 09:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 132 | 19:30 | 123 | 18:00 | Shyampur | 130 | 03:00 | 125 | 09:00
| Jamalpur | 139 | 11:00 | 130 | 06:00 | Shyampur-230 | 132 | 19:30 | 123 | 10:00
| Jashore | 135 | 19:30 | 126 | 09:00 | Siddhirganj | 131 | 19:30 | 124 | 10:00
| Jhenaidah | 140 | 19:30 | 132 | 12:00 | Sirajganj | 135 | 20:00 | 132 | 08:00
| Jhenaidah-230 | 140 | 19:30 | 131 | 12:00 | Sonargaon | 131 | 19:30 | 123 | 10:00
| Joydebpur | 145 | 01:00 | 136 | 14:00 | Sreemongol | 136 | 08:00 | 132 | 19:00
| Joypurhat | 131 | 18:00 | 124 | 12:00 | Srinagar | 133 | 04:00 | 125 | 11:00
| Juldah | 139 | 17:00 | 133 | 02:00 | SSM | 140 | 19:30 | 133 | 10:00
| Kabirpur | 136 | 16:00 | 119 | 09:00 | Sunamganj | 131 | 10:00 | 123 | 21:00
| Kachua | 136 | 20:00 | 131 | 02:00 | Sylhet | 133 | 07:00 | 130 | 19:00
| Kaliakoir | 137 | 19:00 | 132 | 11:00 | Tangail | 136 | 16:00 | 129 | 08:00
| Kallyanpur | 130 | 03:00 | 122 | 10:00 | Thakurgaon | 136 | 19:30 | 121 | 18:30
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 722 | 7498 | 4372 | 11870 |  |  |  | QF-LDC-11
0:30 | 713 | 7213.5 | 4363 | 11576.5 | Date: | 2022-07-27
1:00 | 704 | 6929 | 4354 | 11283
1:30 | 708 | 6837 | 4335 | 11172
2:00 | 712 | 6745 | 4316 | 11061
2:30 | 727 | 6655 | 4340.5 | 10995.5 | [5 empty] | Gen. at Eve. Peak | 12572 | 12572 MW (21:00 )
3:00 | 742 | 6565 | 4365 | 10930 | [6 empty] | 21:00
3:30 | 746 | 6553.5 | 4361 | 10914.5 | [5 empty] | Gen. at Day Peak | 10638 | 10638 MW (09:00 )
4:00 | 750 | 6542 | 4357 | 10899 | [6 empty] | 9:00
4:30 | 745 | 6558.5 | 4344 | 10902.5 | [5 empty] | Highest Generation | 12736
5:00 | 740 | 6575 | 4331 | 10906 | [6 empty] | 22:00
5:30 | 745 | 6440.5 | 4205.5 | 10646
6:00 | 750 | 6306 | 4080 | 10386
6:30 | 694 | 6331.5 | 4059 | 10390.5
7:00 | 638 | 6357 | 4038 | 10395
7:30 | 695 | 6423.5 | 4039.5 | 10463
8:00 | 752 | 6490 | 4041 | 10531
8:30 | 850 | 6538.5 | 4046 | 10584.5
9:00 | 948 | 6587 | 4051 | 10638
9:30 | 915.5 | 6503 | 4009.5 | 10512.5
10:00 | 883 | 6419 | 3968 | 10387
10:30 | 836.5 | 6462 | 3914.5 | 10376.5
11:00 | 790 | 6505 | 3861 | 10366
11:30 | 816 | 6522.5 | 3910 | 10432.5
12:00 | 842 | 6540 | 3959 | 10499
12:30 | 876 | 6548.5 | 3997 | 10545.5
13:00 | 910 | 6557 | 4035 | 10592
13:30 | 871 | 6612 | 4028.5 | 10640.5
14:00 | 832 | 6667 | 4022 | 10689
14:30 | 860 | 6727 | 3987 | 10714
15:00 | 888 | 6787 | 3952 | 10739
15:30 | 789 | 6775 | 3975.5 | 10750.5
16:00 | 690 | 6763 | 3999 | 10762
16:30 | 642.5 | 6881.5 | 3954.5 | 10836
17:00 | 595 | 7000 | 3910 | 10910
17:30 | 609.5 | 7255.5 | 3912.5 | 11168
18:00 | 624 | 7511 | 3915 | 11426
18:30 | 588 | 7674 | 4007 | 11681
19:00 | 552 | 7837 | 4099 | 11936
19:30 | 468 | 7982 | 4339 | 12321
20:00 | 440 | 8075 | 4297 | 12372 |  |  |  | Executive Engineer
20:30 | 424 | 8136.5 | 4335.5 | 12472 |  |  |  | Network Operation Division
21:00 | 408 | 8198 | 4374 | 12572
21:30 | 442 | 8239.5 | 4414.5 | 12654
22:00 | 476 | 8281 | 4455 | 12736 |  |  |  |  | Page 6 of 7
22:30 | 494 | 8218.5 | 4479.5 | 12698
23:00 | 512 | 8156 | 4504 | 12660
23:30 | 617 | 7827 | 4438 | 12265
24:00 | 722 | 7498 | 4372 | 11870
12572 MW (21:00 )
10638 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-27 |  | Energy |  | 271365342
[13 empty] | 2022-07-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3543 | 849 | 1991 | 0 | 3109 | 1259 | 128 | 214 | 821 | 170 | 0 | 1318
0:30 | 3616 | 873.5 | 1906.5 | 0 | 2931 | 1204.5 | 127.5 | 172 | 757.5 | 160 | 0 | 1127.5 | Date: | 2022-07-27
1:00 | 3689 | 898 | 1822 | 0 | 2753 | 1150 | 127 | 130 | 694 | 150 | 0 | 937
1:30 | 3682.5 | 898.5 | 1763 | 0 | 2742.5 | 1150 | 126.5 | 130 | 660 | 149 | 0 | 855 | [8 empty] | Total Energy | 271.3653 | Total Energy Gen 271.365 MKWHr Energy Not Served 18.975 MKWHr Energy Requirement 290.341 MKWHr
2:00 | 3676 | 899 | 1704 | 0 | 2732 | 1150 | 126 | 130 | 626 | 148 | 0 | 773 | [8 empty] | Energy not Served | 18.9754
2:30 | 3568 | 899.5 | 1783.5 | 0 | 2698 | 1149.5 | 126 | 130 | 625 | 146 | 0 | 695 | [8 empty] | Energy Requirement | 290.3407
3:00 | 3460 | 900 | 1863 | 0 | 2664 | 1149 | 126 | 130 | 624 | 144 | 0 | 617
3:30 | 3458 | 899 | 1854.5 | 0 | 2672.5 | 1139.5 | 125.5 | 130 | 622.5 | 143 | 0 | 493.5 | [6 empty] | Shortage
4:00 | 3456 | 898 | 1846 | 0 | 2681 | 1130 | 125 | 130 | 621 | 142 | 0 | 370
4:30 | 3449.5 | 898.5 | 1865.5 | 0 | 2672 | 1130 | 125 | 130 | 623 | 139 | 0 | 185
5:00 | 3443 | 899 | 1885 | 0 | 2663 | 1130 | 125 | 130 | 625 | 136 | 0 | 0
5:30 | 3380 | 899.5 | 1836.5 | 0 | 2573 | 1130 | 125.5 | 130 | 566 | 132 | 3.5 | 0
6:00 | 3317 | 900 | 1788 | 0 | 2483 | 1130 | 126 | 130 | 507 | 128 | 7 | 0
6:30 | 3323 | 899.5 | 1791.5 | 0 | 2483.5 | 1110 | 126 | 130 | 507 | 124 | 26 | 0 |  |  |  |  | Coal
7:00 | 3329 | 899 | 1795 | 0 | 2484 | 1090 | 126 | 130 | 507 | 120 | 45 | 0
7:30 | 3309 | 899.5 | 1800.5 | 0 | 2535 | 1090 | 126.5 | 130 | 491 | 123 | 88.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3289 | 900 | 1806 | 0 | 2586 | 1090 | 127 | 130 | 475 | 126 | 132 | 0
8:30 | 3284 | 900 | 1853.5 | 0 | 2572.5 | 1099.5 | 127 | 130 | 475 | 130 | 143 | 212
9:00 | 3279 | 900 | 1901 | 0 | 2559 | 1109 | 127 | 130 | 475 | 134 | 154 | 424
9:30 | 3171.5 | 882.5 | 1888 | 0 | 2549.5 | 1114.5 | 127 | 142.5 | 483 | 137 | 159.5 | 679
10:00 | 3064 | 865 | 1875 | 0 | 2540 | 1120 | 127 | 155 | 491 | 140 | 165 | 934
10:30 | 3104.5 | 850 | 1845 | 0 | 2553 | 1084.5 | 127 | 142.5 | 481.5 | 144 | 187 | 1058.5
11:00 | 3145 | 835 | 1815 | 0 | 2566 | 1049 | 127 | 130 | 472 | 148 | 209 | 1183
11:30 | 3175 | 850 | 1825.5 | 0 | 2567 | 1074 | 127 | 135 | 463 | 151 | 200 | 1237
12:00 | 3205 | 865 | 1836 | 0 | 2568 | 1099 | 127 | 140 | 454 | 154 | 191 | 1291
12:30 | 3223.5 | 865 | 1822 | 0 | 2568 | 1134.5 | 127.5 | 168.5 | 490.5 | 153 | 161.5 | 1340.5
13:00 | 3242 | 865 | 1808 | 0 | 2568 | 1170 | 128 | 197 | 527 | 152 | 132 | 1390
13:30 | 3242 | 865 | 1808 | 0 | 2568 | 1170 | 128 | 197 | 527 | 152 | 132 | 1390
14:00 | 3242 | 865 | 1808 | 0 | 2568 | 1170 | 128 | 197 | 527 | 152 | 132 | 1390
14:30 | 3339 | 864.5 | 1789.5 | 0 | 2579 | 1179.5 | 128 | 163.5 | 516.5 | 160 | 109.5 | 1391
15:00 | 3436 | 864 | 1771 | 0 | 2590 | 1189 | 128 | 130 | 506 | 168 | 87 | 1392
15:30 | 3431 | 864 | 1764.5 | 0 | 2612 | 1179 | 127 | 130 | 507 | 166 | 100 | 1358.5
16:00 | 3426 | 864 | 1758 | 0 | 2634 | 1169 | 126 | 130 | 508 | 164 | 113 | 1325
16:30 | 3452 | 864.5 | 1737.5 | 0 | 2760.5 | 1149 | 126 | 130 | 520 | 161 | 78.5 | 1072.5
17:00 | 3452 | 865 | 1717 | 0 | 2887 | 1129 | 126 | 130 | 532 | 158 | 44 | 820
17:30 | 3465 | 865.5 | 1706.5 | 0 | 3139 | 1109 | 126.5 | 130 | 575 | 154 | 27.5 | 467
18:00 | 3478 | 866 | 1696 | 0 | 3391 | 1089 | 127 | 130 | 618 | 150 | 11 | 114
18:30 | 3491.5 | 858 | 1695.5 | 0 | 3555.5 | 1099 | 127 | 133.5 | 684 | 165 | 5.5 | 409
19:00 | 3505 | 850 | 1695 | 0 | 3720 | 1109 | 127 | 137 | 750 | 180 | 0 | 704
19:30 | 3476 | 850 | 1710 | 0 | 3948 | 1219 | 128 | 208 | 830 | 160 | 0 | 902
20:00 | 3490 | 850 | 1717 | 0 | 4000 | 1199 | 128 | 213 | 830 | 158 | 0 | 1224
20:30 | 3518 | 849.5 | 1769.5 | 0 | 4020 | 1209 | 128.5 | 211.5 | 819.5 | 158 | 0 | 1178
21:00 | 3546 | 849 | 1822 | 0 | 4040 | 1219 | 129 | 210 | 809 | 158 | 0 | 1132
21:30 | 3553 | 849 | 1895.5 | 0 | 4009.5 | 1239 | 129 | 212.5 | 819 | 160 | 0 | 1010
22:00 | 3560 | 849 | 1969 | 0 | 3979 | 1259 | 129 | 215 | 829 | 162 | 0 | 888
22:30 | 3560.5 | 849 | 1981.5 | 0 | 3912.5 | 1269 | 128.5 | 215.5 | 831 | 166 | 0 | 900
23:00 | 3561 | 849 | 1994 | 0 | 3846 | 1279 | 128 | 216 | 833 | 170 | 0 | 912
23:30 | 3552 | 849 | 1992.5 | 0 | 3477.5 | 1269 | 128 | 215 | 827 | 170 | 0 | 1115 | Max Temp. in Dhaka |  | 24.7° C | 33.7° C
24:00 | 3543 | 849 | 1991 | 0 | 3109 | 1259 | 128 | 214 | 821 | 170 | 0 | 1318
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 271.365 MKWHr Energy Not Served 18.975 MKWHr Energy Requirement 290.341 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 91 | 91 | 90 | 90 | 91 | 91 | 92 | 92 | 92 | 92 | 92 | 93 | 93 | 93 | 91 | 91 | 92 |  | 92 | 93 | 93 | 94 | 94 | 93 | 93 | 2210182
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1 | 100 | 100 | [24 empty] | 100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 610948
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 15 | 18 | 19 | 20 | 19 | 17 | 12 | 10 | 5 | 1 |  | 0 | [6 empty] | 140670
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | [18 empty] | 51 | 51 | 51 | 36 | 51 | 51 | 51 | 327994
12 | Hathazari 100 MW peaking PP | 51 | 44 | 44 | 44 | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 43 | 31 | 28 | 43 | 43 |  | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 1114992
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 88 | 88 | 88 | 88 | 88 | 51 | 51 | 56 | 71 | 88 | 89 | 89 | 89 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2048245
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 40 | 46 | 37 | 40 | 40 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 46 | 48 | 48 | 38 | 1116416
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 258 | 260 | 260 | 260 | 258 | 258 | 258 | 245 | 238 | 238 | 230 | 220 | 225 | 225 | 223 | 240 | 243 | 230 |  | 235 | 235 | 240 | 240 | 243 | 243 | 243 | 5838652
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 160 | 0 | 20 | 70 | 130 | 230 | 300 | 300 | 300 | 300 |  | 300 | 250 | 290 | 300 | 300 | 300 | 300 | 5094936
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 38 | 34 | 34 | 40 | 40 | 38 | 38 | 34 | 38 | 38 |  | 41 | 20 | 20 | 20 | 20 | 20 | 20 | 849456
33 | Ashuganj 225 MW CCPP | 205 | 211 | 212 | 194 | 180 | 182 | 190 | 185 | 170 | 154 | 178 | 174 | 174 | 188 | 196 | 200 | 189 | 189 |  | 186 | 188 | 197 | 200 | 206 | 210 | 205 | 4652000
34 | Ashuganj 450 MW CCPP(South) | 260 | 270 | 260 | 260 | 260 | 260 | 270 | 270 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7189000
| Ashuganj 450 MW CCPP(North) | 275 | 280 | 275 | 275 | 275 | 275 | 280 | 305 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7342000
| Ashuganj 420 MW CCPP(East) | [25 empty] | 0 | 0
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144480
36 | Chandpur 150 MW CCPP | 131 | 129 | 129 | 129 | 130 | 130 | 130 | 130 | 130 | 129 | 130 | 130 | 130 | 127 | 130 | 130 | 130 | 130 |  | 130 | 135 | 135 | 135 | 135 | 136 | 137 | 3111470
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 407 | 406 | 407 | 406 | 406 | 406 | 407 | 408 | 406 | 404 | 401 | 402 | 400 | 405 | 402 | 402 | 404 | 406 |  | 405 | 409 | 407 | 404 | 407 | 408 | 406 | 9865210
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5054950
41 | Haripur 360MW CCPP(HPL) | 315 | 285 | 320 | 337 | 340 | 302 | 302 | 302 | 316 | 341 | 344 | 322 | 311 | 320 | 319 | 318 | 320 | 321 |  | 327 | 325 | 326 | 326 | 325 | 325 | 326 | 7658000
42 | RPCL 210MW CCPP | 101 | 101 | 101 | 101 | 94 | 93 | 86 | 85 | 85 | 70 | 70 | 70 | 71 | 71 | 71 | 70 | 71 | 86 |  | 102 | 104 | 103 | 103 | 103 | 105 | 105 | 2041920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 9 | 34 | 34 | 37 | 46 | 25 | 3 | 10 | 14 | 28 | 14 | 3 |  | 0 | [6 empty] | 262590
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 44 | 44 | 44 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 965456
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 40 | 64 | 65 | 64 | 64 | 63 | 62 | 60 | 56 | 58 | 58 | 58 | 61 | 60 | 60 | 61 | 62 |  | 59 | 59 | 59 | 61 | 62 | 64 | 61 | 1428864
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  | 10 | 75 | 81 | 81 | 81 | 81 | 81 | 1841280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 220 | 220 | 220 |  | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 5254410
51 | Sylhet 20 MW GTPP | [20 empty] | 18 | 18 | 18 | 0 |  |  | 52000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 12 | 16 | 22 | 26 | 26 | 27 | 26 | 27 | 26 | 26 | 28 | 28 | 29 | 29 | 31 | 30 |  | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 580160
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243540
54 | Hobiganj 11MW PP Cofidence-E | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 165251
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 41 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1119000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 23 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 377928
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 280 | 305 | 280 | 280 | 290 | 300 | 295 | 330 | 320 | 320 | 325 | 320 | 305 | 325 | 310 | 300 | 290 |  | 295 | 260 | 270 | 315 | 310 | 310 | 320 | 7521000
| Bibiyana South 400 MW | 180 | 145 | [24 empty] | 459000
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 | 0 |  | 0 | 259508
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 583440
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 398688
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 377604
62 | Tangail 22 MW PP (Doreen) | 3 | 3 | 5 | 5 | 5 | 5 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 346608
63 | Impoprt (Tripura) | 150 | 148 | 144 | 142 | 136 | 128 | 120 | 126 | 134 | 140 | 148 | 154 | 152 | 160 | 168 | 164 | 158 | 150 |  | 180 | 160 | 158 | 158 | 162 | 170 | 170 | 3587520
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 7 | 30 | 20 | 27 | 2 | 6 | 10 | 8 | 10 | 10 | 2 | 2 | 4 | 5 | 12 |  | 14 | 10 | 24 | 30 | 35 | 38 | 38 | 466080
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  |  | 7 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 379044
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 221040
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 28 | 24 | 13 | 8 | 16 | 16 | 16 | 28 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 673400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 499520
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 28 | 28 | 28 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 19 |  | 17 | 27 | 27 | 27 | 27 | 27 | 27 | 454320
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 617600
72 | Rupganj 33 MW PP(Summit) | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 31 | 25 | 25 | 26 | 24 | 25 | 25 |  | 26 | 26 | 26 | 22 | 28 | 33 | 25 | 695300
73 | Ghorashal 108MW PP (Regent) | 85 | 85 | 85 | 85 | 86 | 89 | 89 | 87 | 86 | 86 | 86 | 89 | 89 | 89 | 83 | 83 | 83 | 83 |  | 80 | 80 | 85 | 82 | 85 | 85 | 88 | 2037590
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 70 | 114 | 114 | 114 | 114 | 17 | 836760
| Chowmuhani 113 MW | 113 | 113 | 113 | 108 | 108 | 108 | 108 | 108 | 107 | 110 | 105 | 105 | 102 | 102 | 105 | 105 | 104 | 104 |  | 105 | 105 | 104 | 104 | 112 | 115 | 110 | 2584680
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 17 | 1484640
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 50 | 70 | 82 | 90 | 93 | 98 | 60 | 622080
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 49 | 50 | 50 | 50 |  | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 1234080
79 | Kodda 150MW PP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 132 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2647680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 43 | 43 | 43 | 43 | 43 | 16 | 366269
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 90 | 90 | 89 | 105 | 105 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2469600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 3 | 5 | 4 | 5 | 5 | 4 | 4 | 1 | 1 | 0 | [8 empty] | 36840
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 41 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1051074
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 103 | 106 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2670497
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 8 | 7 |  | 18 | 61 | 54 | 72 | 72 | 80 | 41 | 483840
| Meghnaghat 104 MW PP (OPCL) | 20 | 17 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 17 | 16 | 19 | 24 | 35 | 36 | 36 | 35 | 57 |  | 104 | 104 | 104 | 104 | 104 | 104 | 17 | 1014720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 508560
92 | Fenchuganj 44MW (Energyprima) | 22 | 25 | 25 | 36 | 42 | 46 | 46 | 43 | 49 | 46 | 44 | 45 | 45 | 42 | 44 | 45 | 42 | 45 |  | 45 | 45 | 45 | 45 | 43 | 46 | 46 | 1017000
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1232430
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 32 |  | 82 | 94 | 94 | 94 | 94 | 94 | 32 | 618192
95 | Patenga 50MW PP (Baraka) | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 35 | 35 | 36 |  | 36 | 36 | 37 | 37 | 37 | 37 | 36 | 796800
96 | Chattogram 108 MW PP (ECPV) | 88 | 89 | 83 | 85 | 89 | 89 | 89 | 78 | 82 | 79 | 81 | 87 | 86 | 86 | 85 | 87 | 90 | 87 |  | 92 | 93 | 93 | 93 | 93 | 93 | 92 | 2104320
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1326083
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 297421
101 | Kushiara 163 MW CCPP (KP) | [23 empty] | 110 | 110 | 110 | 287918
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 15000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [6 empty] | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 379080
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 194 | 200 | 200 | 183 | 183 | 183 | 182 | 182 | 190 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 4615200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 105 | 92 | 89 | 89 | 107 | 105 | 107 | 106 | 106 | 106 | 119 | 124 | 125 | 121 | 105 | 108 | 107 | 107 |  | 108 | 110 | 112 | 119 | 119 | 118 | 116 | 2652912
115 | Juldah 100 MW PP Unit-3 (Acorn) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 20 | 50 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 804480
116 | Chandpur 200MW (Desh energy) | 155 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 148 | 186 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3488640
117 | Ashuganj 150MW PP (Midland) | 120 | 123 | 123 | 128 | 130 | 132 | 132 | 130 | 132 | 123 | 122 | 122 | 122 | 107 | 117 | 118 | 98 | 100 |  | 103 | 115 | 108 | 117 | 118 | 117 | 115 | 2867054
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 401 | 352 | 353 | 353 | 400 | 390 | 380 | 404 | 400 | 404 | 398 | 388 | 404 | 403 |  | 400 | 402 | 365 | 404 | 404 | 402 | 400 | 9431000
| Jamalpur 115 MW PP (United) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 47 | 46 | 49 | 49 | 48 | 48 | 54 | 104 |  | 95 | 95 | 95 | 96 | 105 | 105 | 49 | 1332000
| Anwara 300 MW PP (United) | 177 | 177 | 163 | 177 | 177 | 50 | 50 | 170 | 172 | 177 | 177 | 177 | 177 | 177 | 195 | 177 | 159 | 294 |  | 300 | 300 | 300 | 300 | 300 | 142 | 142 | 4518873
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 840960
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 92 | 108 | 108 | 2586873
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 888480
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 8 | 16 | 24 | 29 | 33 | 34 | 23 | 32 | 24 | 9 | 7 | 1 |  | 0 | 0 | [5 empty] | 255981
| Chandpur 115(Doreen) | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 47 | 58 | 72 | 72 | 72 | 45 | 51 | 56 |  | 75 | 76 | 76 | 76 | 76 | 71 | 54 | 1271040
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1339200
120 | Eastern Zone Total | 6929 | 6745 | 6565 | 6542 | 6575 | 6306 | 6357 | 6490 | 6587 | 6419 | 6505 | 6540 | 6557 | 6667 | 6787 | 6763 | 7000 | 7511 |  | 7837 | 7982 | 8075 | 8198 | 8281 | 8156 | 7498 | 168389973
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 26 | 50 | 50 | 50 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 37 | 38 | 32 | 38 | 64 | 64 | 64 |  | 64 | 64 | 66 | 63 | 65 | 65 | 66 | 1092480
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 46 | 46 | 46 | 46 | 46 | [12 empty] | 20 |  | 42 | 51 | 46 | 46 | 46 | 46 | 46 | 478080
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 12
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 21 | 68 | 75 | 73 | 100 | 100 | 74 | 94 | 25 | 57 | 13 | 4 |  | 0 | [6 empty] | 727920
131
132 | United Payra Power Ltd. | 17 | [24 empty] | 0 | 22560
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 184 | 185 | 185 | 185 | 185 | 225 | 221 | 216 | 176 | 216 | 217 | 218 | 216 | 216 | 183 | 162 |  | 212 | 190 | 182 | 220 | 223 | 221 | 220 | 4848191
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 564480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 20 | 21 | 20 | 82 | 82 | 82 | 82 | 82 | 81 | 81 | 82 |  | 82 | 81 | 81 | 82 | 82 | 88 | 85 | 1664389
140 | Bhola 33 MW PP (Venture) | 27 | 27 | 27 | 25 | 27 | 26 | 24 | 23 | 21 | 23 | 18 | 19 | 19 | 21 | 22 | 22 | 21 | 20 |  | 27 | 27 | 24 | 28 | 32 | 31 | 31 | 572446
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 229500
143 | Gopalganj 100 MW Peaking PP | 65 | 62 | 59 | 57 | 57 | [11 empty] | 4 | 35 |  | 60 | 60 | 60 | 58 | 57 | 57 | 57 | 661248
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 89 | 88 | 88 | 88 | 88 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2451024
146 | Bheramara HVDC | 898 | 899 | 900 | 898 | 899 | 900 | 899 | 900 | 900 | 865 | 835 | 865 | 865 | 865 | 864 | 864 | 865 | 866 |  | 850 | 850 | 850 | 849 | 849 | 849 | 849 | 21080727
147 | Bheramara 410 MW CCPP | 210 | 220 | 230 | 240 | 240 | 250 | 240 | 225 | 200 | 180 | 180 | 170 | 160 | 160 | 155 | 150 | 155 | 155 |  | 155 | 155 | 160 | 160 | 170 | 170 | 165 | 4702464
148 | Payra 1320 MW | 950 | 950 | 950 | 930 | 930 | 930 | 890 | 890 | 910 | 920 | 850 | 900 | 970 | 980 | 990 | 970 | 930 | 890 |  | 910 | 1020 | 1000 | 1020 | 1060 | 1080 | 1060 | 24966600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 199 | 199 | 200 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4867500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 32 | 32 | 32 | 32 | 32 | 32 | 785088
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 2 | 1 | 4 | 3 | 5 | 4 | 4 | 3 | 1 | 0 | [8 empty] | 32220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 167 | 175 | 181 | 184 | 190 | 150 | 150 | 150 | 163 | 163 | 159 | 152 | 150 | 144 | 140 | 140 | 140 | 139 |  | 138 | 139 | 139 | 142 | 143 | 143 | 143 | 3959745
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 155 | 130 | 140 | 197 | 130 | 130 | 130 | 130 | 130 |  | 137 | 208 | 213 | 210 | 215 | 216 | 214 | 3909555
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 144 | 151 | 154 | 156 | 158 | 140 | 140 | 140 | 139 | 134 | 125 | 126 | 119 | 133 | 126 | 122 | 124 | 123 |  | 123 | 123 | 123 | 129 | 133 | 133 | 133 | 3492382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 372 | 351 | 424 | 426 | 427 | 358 | 350 | 356 | 398 | 360 | 345 | 336 | 322 | 311 | 283 | 280 | 280 | 280 |  | 280 | 294 | 275 | 290 | 320 | 342 | 325 | 8173782
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 20 | 20 | 20 | 19 | 19 | [7 empty] | 5 | 18 | 17 | 17 | 22 | 23 |  | 24 | 25 | 25 | 28 | 31 | 34 | 34 | 337631
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 18 | 18 | 17 | 17 | 18 | 18 | 19 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 22 | 468480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 266670
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [9 empty] | 0 | 373193
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 558363
168 | Santahar 50 MW Peaking PP | 36 | 29 | 29 | 29 | 29 | 30 | 30 | 0 | [6 empty] | 31 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 34 | 34 | 34 | 554800
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 12 | 52 | 52 | 52 | 52 | 52 | 8 | 490560
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 78 | 78 | 89 | 86 | 86 | 86 | 86 |  | 86 | 87 | 87 | 91 | 89 | 89 | 89 | 2044176
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 87 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2124672
172 | Confidence Power Bogura Unit-1 113 MW | 76 | 76 | 76 | 76 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 100 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2141088
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 105 | 105 | 105 | 105 | 85 | 85 | 85 | 85 | 81 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 105 |  | 106 | 106 | 106 | 106 | 106 | 106 | 107 | 2276160
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 4 | 2 | 2 |  | 0 | [6 empty] | 13343
178 | Energypac Power Venture Thakurgaon Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 34 | 34 |  | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 2043840
178