## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-07-30 | Saturday
|  |  | Date (day): | 2022-07-30 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11239.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13105 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-29 | 2022-07-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 89 | 86 | 89 |  | 19 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 408 | 400 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 332 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 16 | 66 | 25 | 80 |  | 20 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 20 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 24 | 96 | 24 | 96
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 94 | 24 | 94 |  | 8 | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 146 | 100 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 50 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 278 | 245 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 117 | 97 | 100 | 100 |  | 49 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 32 | 91 | 17 | 90 | 15 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 51 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2439 | 3073 | 2622 | 3218 | 1631 | 999
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 36 | 35 | 36 |  | 14 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 128 | 126 | 92 | 127 |  | 103 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 103 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 51 | 52 |  | 46 | Engine problem
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 | 34 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 65 | 80 | 80 | 80 | 20 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 | 10 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 38 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 74 | 81 | 80 | 81 | 27 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 300 | 150 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 36 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 90 | 20 | 90 | 10 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 978 | 1477 | 1133 | 1468 | 361 | 551
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 164 | 204 | 200 | 204 | 17 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 330 | 300 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 330 | 300 | 330 | 30 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 31 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 38 | 35 | 38 |  | 7 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 30 | 30 | 25 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 137 | 125 | 137 |  | 13 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 49 | 48 | 49
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 135 | 135 | 135 | 135 |  | 28 | Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 46 | 200 | 50 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 174 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 115 | 107 | 113 |  |  | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 35 | 17 | 35 | 80 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1562 | 2145 | 1694 | 2104 | 712 | 71
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 80 | 100 | 100 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 82 | 200 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 106 | 50 | 106 |  | 9 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 14 | 18 | 18 | 18 |  | 4 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 282 | 444 | 439.6 | 444 | 102 | 21
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 53 | 33 | 51 |  |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 42 | 30 | 42 | 8 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 60 | 61
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 78 | 82
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 30 | 32 | 25 | 32 | 18 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 300 | 330 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 405 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1339 | 1445 | 1377 | 1449 | 55 | 943
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 859 | 844 | 861 | 876
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 32 | 80 | 33 | 80 | 35 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 44 |  | 10 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 60 |  | 49 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 165 | 170 | 170 | 240 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 24 | 8 | 24 | 16 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 70 | 35 | 70 | 35 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 102 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1296 | 1392 | 1312 | 1429 | 672 | 59
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 24 | 32 | 23 | 32 |  | 8 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 | 134 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 950 | 1000 | 970 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 216 | 220 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1266 | 1361 | 1294 | 1461 | 134 | 8
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 24 | 24 | 24 |  | 28 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 28 |  | 43 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 31 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 149 | 145 | 150 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 176 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 129 | 137 | 140 | 140 | 80 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 290 | 309 | 300 | 320 | 94 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 30 | 30 | 30 |  | 20 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 0 | 8 | 40 | 12 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 81 | 87 | 85 | 87 |  | 17 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 70 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1106 | 1227 | 978 | 1135 | 837 | 151
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 79 | 107 | 92 | 107 |  | 6 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 90 | 90 | 90 |  | 25 | Engine problem
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 337 | 397 | 390 | 397 | 199 | 116
|  | Total |  |  |  |  | 22482 | 21680 | 10605 | 12961 | 11239.6 | 13105 | 4703 | 2919
| A. |  | 2022-07-29 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12992 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10519 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13500 | MW
| 3 | Day peak Generation : |  |  | 10605 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12717.7 | MW
| 4 | Evening peak Generation : |  |  | 12961 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 128 | MW
| 5 | Total Energy Generation : |  | 273.0681 | MKWHr | By Solar | 1.5509 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 131.8511 | MKWHr |  | By Oil: | 81.2241 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.6954 | MKWHr |  | By Hydro: | 3.0502 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4703 | MW | Dhaka | 4301.65 | 4301.65 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2919 | MW | Chittagong | 1276.95 | 1276.95 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7622 | MW | Khulna | 1664.2 | 1646.2 |  | 18
| 7 | Total Gas Supplied : |  |  | 1016.21 | MMCFD |  |  | Rajshahi | 1319 | 1299 |  | 20 |  | 19:00 |  | 423
| 8 | Fuel Cost : | i) Gas : | Taka | 151772014.834 | ii) Oil : | Taka | 1112572342.21 | Comilla | 1236 | 1221 |  | 15 |  | 19:30 |  | 332
|  |  | iii) Coal : |  | 258378846 | Total | Taka | 1522723203.044 | Mymensingh | 1092 | 1035 |  | 57 |  | 20:00 |  | 248
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 571 | 571 |  | 0 |  | 21:00 |  | 128
|  | ii) During Peak Demand : |  |  | 34 | MW (E to W) at | 21:00 | hrs | Barisal | 366.9 | 366.9 |  | 0 |  | 22:00 |  | 76.4907
|  | iii) Maximum : |  |  | 34 | MW at | 21:00 | hrs | Rangpur | 890 | 872 |  | 18 |  | 23:00 |  | 211.9623
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 12717.7 | 12589.7 |  | 128
| B. |  | 2022-07-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 640 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13105 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 290.0507 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10748 | MW at | 7:00 | 150 | 76 | 100 | 100 | 60 | 100 | 14 | 0 | 40
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.0109 | MKWHr. | ii) HVDC Flow at Peak Time |  | 844 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6854 | MKWHr. | iii) Maximum HVDC Flow : |  | 895 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.88 |  | (b) Today: | 91.96 |  | (c) Rule Curve: |  | 88.66
.

## YesterdayGen
2022-07-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 407 | 323 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 50 | 51 | 80 | 86 | 32 | 17 | 38 | 0 | 0 | 0 | 325 | 315 | 208 | 8 | 136 | 38 | 15 | 0 | 43 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 168 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 78 | 0 | 220 | 0 | 32 | 10 | 315 | 16 | 11 | 0 | 175 | 0 | 0 | 87 | 0 | 116 | 0 | 21 | 113 | 129 | 397 | 49 | 105 | 105 | 0 | 88 | 45 | 110 | 17 | 108 | 44 | 0 | 17 | 0 | 82 | 90 | 0 | 35 | 0 | 39 | 55 | 0 |  | 895 | 0 | 160 | 0 | 81 | 0 | 0 | 0 | 38 | 55 | 8 | 60 | 31 | 32 | 0 | 0 | 0 | 34 | 34 | 88 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 165 | 0 | 0 | 216 | 0 | 0 | 131 | 0 | 283 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1090 | 222 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7113 | 4430 | 11543 | 3684 | 895 | 1905 | 0 | 2707 | 1289 | 128 | 216 | 767 | 168 | 0 | 1343 | 91.78
2:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 411 | 308 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 17 | 50 | 51 | 80 | 86 | 37 | 17 | 38 | 0 | 0 | 0 | 350 | 335 | 208 | 8 | 135 | 35 | 15 | 0 | 43 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 166 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 40 | 0 | 220 | 0 | 30 | 10 | 325 | 16 | 11 | 0 | 190 | 0 | 0 | 87 | 0 | 113 | 0 | 21 | 50 | 125 | 402 | 49 | 105 | 105 | 0 | 88 | 36 | 102 | 17 | 104 | 20 | 0 | 17 | 0 | 54 | 100 | 0 | 35 | 0 | 35 | 55 | 0 |  | 895 | 0 | 155 | 0 | 67 | 0 | 0 | 0 | 38 | 55 | 8 | 63 | 30 | 32 | 0 | 0 | 0 | 34 | 34 | 88 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 164 | 0 | 0 | 217 | 0 | 0 | 130 | 0 | 289 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1090 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6982 | 4400 | 11382 | 3730 | 895 | 1863 | 0 | 2559 | 1290 | 127 | 217 | 752 | 166 | 0 | 1261 | 91.8
3:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 412 | 308 |  | 0 | 225 | 0 | 22 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 17 | 51 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 50 | 51 | 80 | 87 | 37 | 17 | 39 | 0 | 0 | 0 | 330 | 320 | 209 | 8 | 136 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 164 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 64 | 20 | 0 | 220 | 0 | 31 | 10 | 325 | 16 | 11 | 0 | 195 | 0 | 0 | 87 | 0 | 102 | 0 | 21 | 50 | 125 | 403 | 49 | 105 | 105 | 0 | 88 | 36 | 110 | 17 | 115 | 25 | 0 | 17 | 0 | 54 | 106 | 0 | 35 | 0 | 35 | 55 | 0 |  | 895 | 0 | 155 | 0 | 81 | 0 | 0 | 0 | 38 | 55 | 8 | 60 | 30 | 32 | 0 | 0 | 0 | 32 | 34 | 88 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 218 | 0 | 0 | 130 | 0 | 306 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1070 | 223 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6963 | 4411 | 11374 | 3683 | 895 | 1888 | 0 | 2597 | 1270 | 126 | 218 | 751 | 164 | 0 | 1038 | 91.82
4:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 412 | 299 |  | 0 | 225 | 0 | 23 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 50 | 51 | 80 | 85 | 37 | 17 | 40 | 0 | 0 | 0 | 340 | 325 | 208 | 8 | 128 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 162 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 31 | 10 | 325 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 112 | 0 | 21 | 50 | 133 | 402 | 49 | 105 | 105 | 0 | 88 | 36 | 110 | 17 | 115 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 895 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 38 | 55 | 8 | 60 | 29 | 32 | 0 | 0 | 0 | 34 | 34 | 88 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 164 | 0 | 0 | 219 | 0 | 0 | 131 | 0 | 318 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1070 | 222 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6986 | 4337 | 11323 | 3702 | 895 | 1890 | 0 | 2525 | 1270 | 125 | 219 | 754 | 162 | 0 | 900 | 91.84
5:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 409 | 298 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 41 | 51 | 80 | 82 | 37 | 17 | 40 | 0 | 0 | 0 | 345 | 330 | 196 | 8 | 128 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 158 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 31 | 10 | 325 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 115 | 0 | 21 | 50 | 136 | 403 | 49 | 105 | 105 | 0 | 88 | 36 | 110 | 17 | 105 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 895 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 38 | 55 | 8 | 61 | 28 | 16 | 0 | 0 | 0 | 34 | 34 | 88 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 164 | 0 | 0 | 214 | 0 | 0 | 133 | 0 | 319 | 35 | 0 | 70 | 105 | 95 | 0 | 0 | 75 | 1060 | 223 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6962 | 4302 | 11264 | 3711 | 895 | 1890 | 0 | 2485 | 1260 | 125 | 214 | 740 | 158 | 0 | 678 | 91.86
6:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 409 | 294 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 42 | 51 | 80 | 82 | 37 | 17 | 41 | 0 | 0 | 0 | 325 | 275 | 212 | 8 | 129 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 150 | 106 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 64 | 20 | 0 | 220 | 0 | 31 | 10 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 110 | 1 | 21 | 50 | 141 | 402 | 49 | 105 | 105 | 0 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 1 | 54 | 108 | 0 | 23 | 2 | 35 | 55 | 0 |  | 895 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 38 | 55 | 8 | 55 | 26 | 16 | 0 | 0 | 0 | 34 | 34 | 81 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 164 | 0 | 0 | 202 | 0 | 0 | 133 | 0 | 322 | 35 | 0 | 70 | 105 | 98 | 0 | 0 | 75 | 980 | 200 | 0 | 0 | 0 | 3 | 52 | 0 | 0 |  | 6840 | 4180 | 11020 | 3650 | 895 | 1822 | 0 | 2469 | 1179 | 126 | 202 | 722 | 150 | 7 | 350 | 91.88
7:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 294 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 42 | 51 | 80 | 82 | 37 | 17 | 42 | 0 | 0 | 0 | 320 | 275 | 185 | 8 | 129 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 21 | 140 | 105 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 31 | 10 | 280 | 16 | 0 | 0 | 195 | 0 | 0 | 72 | 0 | 113 | 5 | 21 | 0 | 132 | 364 | 49 | 105 | 105 | 1 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 16 | 5 | 54 | 108 | 0 | 17 | 7 | 35 | 55 | 0 |  | 894 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 26 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 165 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 285 | 35 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 980 | 224 | 0 | 0 | 0 | 24 | 52 | 0 | 0 |  | 6681 | 3983 | 10664 | 3573 | 894 | 1810 | 0 | 2377 | 1179 | 126 | 130 | 523 | 140 | 42 | 171 | 91.9
8:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 314 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 0 | 25 | 33 | 51 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 80 | 79 | 37 | 17 | 42 | 0 | 0 | 0 | 320 | 275 | 170 | 8 | 135 | 35 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 0 | 33 | 21 | 138 | 105 | 0 | 20 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 40 | 10 | 0 | 220 | 0 | 31 | 10 | 260 | 16 | 0 | 0 | 195 | 0 | 0 | 83 | 0 | 117 | 10 | 21 | 0 | 125 | 365 | 49 | 105 | 97 | 3 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 26 | 54 | 108 | 0 | 17 | 15 | 36 | 55 | 0 |  | 895 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 58 | 23 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 163 | 0 | 0 | 130 | 0 | 0 | 136 | 0 | 251 | 35 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 970 | 184 | 0 | 0 | 1 | 50 | 52 | 0 | 0 |  | 6597 | 3924 | 10521 | 3507 | 895 | 1722 | 0 | 2376 | 1169 | 127 | 130 | 481 | 138 | 106 | 100 | 91.9
9:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 410 | 322 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 12 | 25 | 33 | 51 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 81 | 37 | 17 | 30 | 0 | 0 | 0 | 300 | 310 | 162 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 30 | 21 | 140 | 97 | 0 | 20 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 40 | 10 | 0 | 220 | 0 | 31 | 10 | 285 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 116 | 14 | 21 | 0 | 127 | 367 | 49 | 105 | 105 | 4 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 39 | 54 | 108 | 0 | 17 | 14 | 35 | 55 | 0 |  | 895 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 0 | 130 | 0 | 0 | 136 | 0 | 250 | 35 | 0 | 70 | 89 | 83 | 0 | 1 | 75 | 950 | 184 | 0 | 0 | 3 | 75 | 52 | 0 | 0 |  | 6606 | 3913 | 10519 | 3520 | 895 | 1738 | 0 | 2368 | 1150 | 127 | 130 | 430 | 140 | 151 | 121 | 91.91
10:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 408 | 328 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 73 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 25 | 33 | 51 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 66 | 78 | 0 | 17 | 20 | 0 | 0 | 0 | 270 | 295 | 162 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 25 | 20 | 142 | 92 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 40 | 10 | 0 | 220 | 0 | 32 | 10 | 310 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 116 | 18 | 21 | 0 | 134 | 404 | 49 | 90 | 105 | 4 | 87 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 48 | 54 | 108 | 0 | 17 | 30 | 33 | 55 | 0 |  | 860 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 158 | 0 | 0 | 130 | 0 | 0 | 133 | 0 | 310 | 35 | 0 | 70 | 89 | 85 | 0 | 5 | 75 | 950 | 219 | 0 | 0 | 2 | 88 | 52 | 0 | 0 |  | 6575 | 3977 | 10552 | 3494 | 860 | 1855 | 0 | 2305 | 1150 | 128 | 130 | 421 | 142 | 197 | 136 | 91.91
11:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 405 | 332 |  | 0 | 225 | 0 | 23 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 16 | 25 | 33 | 51 | 0 | 93 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 73 | 75 | 7 | 17 | 20 | 0 | 0 | 0 | 270 | 305 | 167 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 21 | 20 | 146 | 81 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 59 | 10 | 0 | 221 | 0 | 32 | 10 | 315 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 102 | 13 | 21 | 1 | 130 | 404 | 49 | 90 | 105 | 5 | 88 | 36 | 110 | 17 | 97 | 20 | 0 | 17 | 45 | 54 | 108 | 0 | 17 | 34 | 35 | 55 | 0 |  | 860 | 0 | 160 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 19 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 152 | 0 | 0 | 137 | 0 | 0 | 131 | 0 | 298 | 35 | 0 | 70 | 105 | 78 | 0 | 5 | 75 | 940 | 216 | 0 | 0 | 3 | 104 | 52 | 0 | 0 |  | 6602 | 3969 | 10571 | 3492 | 860 | 1848 | 0 | 2309 | 1140 | 128 | 137 | 437 | 146 | 211 | 165 | 91.91
12:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 400 | 322 |  | 0 | 225 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 12 | 25 | 33 | 51 | 0 | 93 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 65 | 74 | 31 | 17 | 30 | 0 | 0 | 0 | 270 | 275 | 164 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 16 | 20 | 130 | 80 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 30 | 10 | 320 | 16 | 11 | 0 | 195 | 0 | 0 | 82 | 0 | 117 | 20 | 21 | 46 | 132 | 402 | 49 | 90 | 105 | 5 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 32 | 35 | 54 | 108 | 0 | 17 | 34 | 35 | 55 | 0 |  | 859 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 24 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 31 | 8 | 30 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 0 | 129 | 0 | 290 | 35 | 0 | 70 | 105 | 79 | 0 | 6 | 75 | 950 | 216 | 0 | 0 | 2 | 102 | 52 | 0 | 0 |  | 6600 | 4005 | 10605 | 3433 | 859 | 1843 | 0 | 2376 | 1150 | 128 | 181 | 480 | 130 | 206 | 180 | 91.91
13:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 327 |  | 0 | 225 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 12 | 25 | 33 | 51 | 0 | 86 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 15 | 0 | 51 | 65 | 77 | 36 | 17 | 39 | 0 | 0 | 0 | 300 | 265 | 187 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 19 | 10 | 16 | 20 | 142 | 72 | 0 | 20 | 1 | 44 | 42 | 33 | 30 | 110 | 0 | 40 | 10 | 0 | 220 | 0 | 32 | 10 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 102 | 19 | 21 | 50 | 130 | 365 | 49 | 90 | 105 | 5 | 88 | 36 | 110 | 17 | 97 | 14 | 0 | 17 | 55 | 54 | 108 | 0 | 17 | 35 | 35 | 55 | 0 |  | 860 | 0 | 155 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 26 | 16 | 0 | 0 | 0 | 34 | 5 | 78 | 0 | 0 | 31 | 8 | 30 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 146 | 0 | 0 | 185 | 0 | 0 | 128 | 0 | 290 | 35 | 0 | 70 | 105 | 85 | 0 | 5 | 75 | 970 | 165 | 0 | 0 | 0 | 104 | 52 | 0 | 0 |  | 6616 | 3978 | 10594 | 3424 | 860 | 1760 | 0 | 2356 | 1170 | 121 | 185 | 537 | 142 | 224 | 121 | 91.91
14:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 408 | 282 |  | 0 | 225 | 0 | 16 | 0 | 45 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 12 | 25 | 33 | 51 | 0 | 90 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 65 | 74 | 36 | 17 | 34 | 0 | 0 | 0 | 270 | 310 | 204 | 8 | 135 | 36 | 30 | 0 | 51 | 0 | 40 | 8 | 19 | 10 | 25 | 20 | 146 | 71 | 0 | 20 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 50 | 10 | 0 | 220 | 0 | 32 | 10 | 260 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 100 | 18 | 21 | 50 | 128 | 363 | 49 | 105 | 105 | 4 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 39 | 54 | 108 | 0 | 26 | 23 | 35 | 55 | 0 |  | 859 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 26 | 16 | 0 | 0 | 0 | 34 | 15 | 78 | 0 | 0 | 31 | 8 | 30 | 18 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 0 | 130 | 0 | 0 | 129 | 0 | 285 | 35 | 0 | 70 | 105 | 85 | 0 | 5 | 75 | 920 | 210 | 0 | 0 | 0 | 66 | 52 | 0 | 0 |  | 6612 | 3889 | 10501 | 3475 | 859 | 1741 | 0 | 2389 | 1119 | 125 | 130 | 491 | 146 | 156 | 276 | 91.92
15:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 402 | 332 |  | 0 | 225 | 0 | 16 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 12 | 25 | 32 | 50 | 0 | 89 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 65 | 73 | 35 | 17 | 34 | 0 | 0 | 0 | 290 | 325 | 197 | 8 | 135 | 36 | 30 | 0 | 51 | 0 | 32 | 8 | 19 | 10 | 25 | 21 | 146 | 71 | 0 | 20 | 1 | 43 | 42 | 33 | 30 | 110 | 0 | 59 | 10 | 0 | 220 | 0 | 32 | 10 | 320 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 99 | 14 | 21 | 50 | 125 | 403 | 49 | 105 | 105 | 3 | 88 | 36 | 110 | 17 | 97 | 20 | 0 | 17 | 46 | 54 | 100 | 0 | 35 | 9 | 42 | 55 | 0 |  | 857 | 0 | 145 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 24 | 16 | 0 | 0 | 0 | 34 | 20 | 78 | 0 | 0 | 31 | 8 | 30 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 128 | 0 | 285 | 35 | 0 | 70 | 105 | 85 | 0 | 6 | 75 | 940 | 210 | 0 | 0 | 1 | 64 | 52 | 0 | 0 |  | 6785 | 3900 | 10685 | 3534 | 857 | 1853 | 0 | 2399 | 1140 | 124 | 130 | 488 | 146 | 144 | 198 | 91.92
16:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 406 | 322 |  | 0 | 225 | 0 | 16 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 17 | 25 | 32 | 50 | 0 | 88 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 65 | 78 | 36 | 17 | 33 | 0 | 0 | 0 | 290 | 265 | 208 | 8 | 135 | 35 | 30 | 0 | 51 | 0 | 34 | 8 | 22 | 10 | 33 | 21 | 146 | 98 | 0 | 20 | 0 | 44 | 42 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 32 | 10 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 83 | 0 | 90 | 9 | 21 | 50 | 132 | 404 | 49 | 105 | 105 | 2 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 17 | 10 | 162 | 90 | 0 | 35 | 20 | 57 | 55 | 0 |  | 858 | 0 | 160 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 23 | 16 | 0 | 0 | 0 | 34 | 20 | 78 | 0 | 0 | 31 | 8 | 30 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 128 | 0 | 303 | 40 | 0 | 80 | 105 | 85 | 0 | 4 | 108 | 980 | 200 | 0 | 0 | 3 | 42 | 52 | 0 | 0 |  | 6843 | 3990 | 10833 | 3551 | 858 | 1830 | 0 | 2565 | 1180 | 123 | 130 | 490 | 146 | 90 | 108 | 91.92
17:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 411 | 332 |  | 0 | 225 | 0 | 17 | 0 | 30 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 17 | 25 | 32 | 50 | 0 | 88 | 35 | 95 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 20 | 44 | 36 | 17 | 36 | 0 | 0 | 0 | 290 | 265 | 207 | 8 | 135 | 32 | 30 | 0 | 51 | 0 | 49 | 8 | 22 | 10 | 33 | 21 | 142 | 98 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 32 | 10 | 280 | 10 | 11 | 0 | 202 | 0 | 0 | 83 | 0 | 81 | 4 | 21 | 68 | 130 | 366 | 49 | 105 | 51 | 1 | 85 | 46 | 51 | 34 | 65 | 20 | 0 | 35 | 4 | 54 | 90 | 0 | 35 | 10 | 45 | 55 | 0 |  | 857 | 0 | 160 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 28 | 27 | 86 | 0 | 0 | 31 | 8 | 30 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 306 | 45 | 0 | 100 | 105 | 56 | 0 | 2 | 111 | 940 | 224 | 0 | 0 | 1 | 15 | 52 | 0 | 0 |  | 6484 | 3956 | 10440 | 3508 | 857 | 1849 | 0 | 2270 | 1140 | 123 | 130 | 514 | 142 | 37 | 0 | 91.92
18:00 | 0 | 0 | 0 | 180 | 280 | 55 | 0 | 410 | 279 |  | 0 | 225 | 0 | 17 | 0 | 30 | 0 | 0 | 0 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 25 | 17 | 25 | 32 | 50 | 0 | 88 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 10 | 40 | 30 | 17 | 38 | 0 | 0 | 0 | 290 | 265 | 179 | 8 | 135 | 35 | 30 | 0 | 51 | 0 | 49 | 8 | 22 | 10 | 33 | 21 | 136 | 98 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 32 | 10 | 270 | 13 | 11 | 0 | 242 | 0 | 0 | 120 | 0 | 60 | 1 | 65 | 68 | 135 | 365 | 87 | 105 | 17 | 0 | 85 | 54 | 51 | 34 | 24 | 50 | 0 | 35 | 1 | 54 | 98 | 0 | 35 | 1 | 35 | 55 | 0 |  | 857 | 0 | 160 | 0 | 35 | 0 | 0 | 0 | 15 | 15 | 8 | 60 | 21 | 16 | 0 | 0 | 0 | 28 | 27 | 87 | 0 | 0 | 31 | 8 | 30 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 305 | 17 | 0 | 50 | 105 | 55 | 0 | 1 | 35 | 880 | 204 | 0 | 0 | 0 | 8 | 52 | 0 | 0 |  | 6448 | 3741 | 10189 | 3467 | 857 | 1731 | 0 | 2256 | 1080 | 123 | 130 | 527 | 136 | 12 | 0 | 91.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 405 | 332 |  | 0 | 225 | 0 | 23 | 0 | 40 | 0 | 0 | 0 | 28 | 50 | 100 | 0 | 0 | 0 | 0 | 20 | 55 | 55 | 19 | 25 | 17 | 25 | 32 | 50 | 0 | 90 | 35 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 2 | 68 | 80 | 54 | 30 | 17 | 38 | 0 | 0 | 0 | 290 | 310 | 202 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 49 | 18 | 22 | 10 | 33 | 21 | 168 | 100 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 310 | 16 | 11 | 0 | 247 | 0 | 0 | 127 | 0 | 68 | 0 | 72 | 74 | 137 | 401 | 106 | 105 | 19 | 0 | 200 | 54 | 58 | 114 | 47 | 60 | 0 | 36 | 0 | 64 | 65 | 0 | 35 | 0 | 31 | 55 | 0 |  | 857 | 0 | 160 | 0 | 68 | 0 | 0 | 0 | 32 | 40 | 24 | 60 | 27 | 16 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 31 | 0 | 30 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 139 | 0 | 0 | 132 | 0 | 305 | 35 | 0 | 35 | 105 | 68 | 0 | 0 | 100 | 880 | 214 | 0 | 2 | 0 | 0 | 90 | 0 | 0 |  | 7280 | 3961 | 11241 | 3597 | 857 | 1938 | 0 | 2846 | 1080 | 125 | 139 | 630 | 168 | 0 | 423 | 91.93
19:30 | 0 | 0 | 0 | 180 | 280 | 85 | 0 | 410 | 332 |  | 0 | 225 | 0 | 59 | 0 | 55 | 0 | 0 | 0 | 50 | 94 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 25 | 32 | 50 | 0 | 90 | 35 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 18 | 21 | 68 | 80 | 74 | 36 | 17 | 38 | 0 | 0 | 0 | 290 | 275 | 206 | 8 | 135 | 34 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 164 | 100 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 64 | 81 | 0 | 220 | 0 | 32 | 10 | 240 | 16 | 11 | 0 | 260 | 0 | 0 | 200 | 0 | 85 | 0 | 90 | 200 | 13 | 367 | 106 | 105 | 85 | 0 | 289 | 54 | 90 | 114 | 116 | 90 | 0 | 88 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 857 | 0 | 170 | 0 | 68 | 0 | 0 | 0 | 40 | 50 | 24 | 54 | 25 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 32 | 0 | 30 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 135 | 0 | 308 | 82 | 0 | 60 | 105 | 105 | 0 | 0 | 113 | 970 | 181 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8021 | 4219 | 12240 | 3530 | 857 | 1840 | 0 | 3816 | 1170 | 125 | 160 | 738 | 164 | 0 | 332 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 409 | 333 |  | 0 | 225 | 0 | 55 | 0 | 55 | 0 | 0 | 0 | 72 | 94 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 25 | 25 | 50 | 0 | 90 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 68 | 80 | 77 | 35 | 17 | 38 | 0 | 0 | 0 | 290 | 285 | 207 | 8 | 135 | 34 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 24 | 21 | 164 | 100 | 0 | 20 | 0 | 43 | 41 | 33 | 35 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 32 | 10 | 270 | 16 | 11 | 0 | 265 | 0 | 0 | 200 | 0 | 97 | 0 | 90 | 175 | 137 | 366 | 106 | 105 | 75 | 0 | 300 | 54 | 102 | 114 | 114 | 90 | 0 | 88 | 0 | 162 | 108 | 0 | 35 | 0 | 30 | 55 | 32 |  | 844 | 0 | 170 | 0 | 71 | 0 | 0 | 0 | 50 | 67 | 24 | 60 | 26 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 160 | 0 | 0 | 136 | 0 | 308 | 82 | 0 | 105 | 105 | 106 | 0 | 0 | 113 | 990 | 214 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8285 | 4346 | 12631 | 3585 | 844 | 1913 | 0 | 4015 | 1190 | 125 | 160 | 795 | 164 | 0 | 248 | 91.93
21:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 332 |  | 0 | 225 | 0 | 66 | 0 | 55 | 0 | 0 | 0 | 96 | 94 | 146 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 27 | 25 | 25 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 51 | 68 | 80 | 81 | 36 | 17 | 38 | 0 | 0 | 0 | 330 | 330 | 204 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 174 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 42 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 9 | 320 | 16 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 97 | 0 | 90 | 200 | 137 | 405 | 106 | 105 | 103 | 0 | 300 | 54 | 110 | 114 | 115 | 90 | 0 | 91 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 51 | 31 |  | 844 | 0 | 165 | 0 | 80 | 0 | 0 | 0 | 44 | 60 | 24 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 176 | 0 | 0 | 137 | 0 | 309 | 70 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 1000 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8584 | 4377 | 12961 | 3716 | 844 | 2003 | 0 | 4103 | 1200 | 126 | 176 | 795 | 174 | 0 | 128 | 91.93
22:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 408 | 322 |  | 0 | 225 | 0 | 75 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 15 | 52 | 68 | 80 | 87 | 37 | 17 | 29 | 0 | 0 | 0 | 300 | 325 | 179 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 176 | 99 | 0 | 20 | 0 | 44 | 41 | 53 | 45 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 325 | 16 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 97 | 0 | 90 | 200 | 140 | 405 | 106 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 115 | 90 | 0 | 91 | 0 | 162 | 108 | 0 | 35 | 0 | 20 | 55 | 31 |  | 843 | 0 | 165 | 0 | 79 | 0 | 0 | 0 | 45 | 60 | 8 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 309 | 70 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 1030 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8513 | 4479 | 12992 | 3664 | 843 | 1995 | 0 | 4123 | 1230 | 127 | 213 | 834 | 176 | 0 | 76.4907 | 91.93
23:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 410 | 331 |  | 0 | 225 | 0 | 86 | 0 | 55 | 0 | 0 | 99 | 100 | 90 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 93 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 52 | 68 | 80 | 86 | 37 | 17 | 37 | 0 | 0 | 0 | 300 | 260 | 185 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 170 | 100 | 0 | 20 | 0 | 44 | 41 | 53 | 42 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 32 | 10 | 310 | 16 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 97 | 0 | 90 | 200 | 140 | 403 | 106 | 105 | 87 | 0 | 86 | 54 | 110 | 114 | 115 | 90 | 0 | 91 | 0 | 162 | 108 | 0 | 35 | 0 | 18 | 55 | 31 |  | 844 | 0 | 170 | 0 | 33 | 0 | 0 | 0 | 45 | 55 | 8 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 27 | 87 | 0 | 0 | 32 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 217 | 0 | 0 | 137 | 0 | 320 | 70 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1040 | 222 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8321 | 4449 | 12770 | 3710 | 844 | 2005 | 0 | 3841 | 1240 | 128 | 217 | 832 | 170 | 0 | 211.9623 | 91.94
24:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 330 |  | 0 | 225 | 0 | 39 | 0 | 55 | 0 | 0 | 97 | 41 | 24 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 52 | 68 | 80 | 85 | 37 | 17 | 42 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 172 | 100 | 0 | 20 | 0 | 44 | 41 | 53 | 44 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 32 | 10 | 300 | 20 | 11 | 0 | 248 | 0 | 0 | 87 | 0 | 99 | 0 | 21 | 200 | 136 | 404 | 49 | 105 | 87 | 0 | 88 | 54 | 110 | 17 | 115 | 54 | 0 | 25 | 0 | 162 | 108 | 0 | 35 | 0 | 18 | 55 | 0 |  | 843 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 42 | 55 | 8 | 60 | 31 | 32 | 0 | 0 | 0 | 24 | 33 | 87 | 0 | 0 | 32 | 43 | 30 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 219 | 0 | 0 | 137 | 0 | 320 | 35 | 0 | 70 | 105 | 104 | 0 | 0 | 113 | 1060 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7592 | 4388 | 11980 | 3724 | 843 | 1997 | 0 | 3069 | 1259 | 127 | 219 | 789 | 172 | 0 | 847.849 | 91.94
KWH | 0 | 0 | 0 | 4378500 | 7152355 | 2058500 | 0 | 9922550 | 7598000 |  | 0 | 5058200 | 0 | 729600 | 0 | 1263117 | 0 | 0 | 168000 | 880464 | 865584 | 2242080 | 0 | 0 | 0 | 0 | 612720 | 299893 | 256647 | 376380 | 600000 | 483300 | 614900 | 745200 | 1199040 | 0 | 2210225 | 840000 | 2400000 | 0 | 556554 | 0 | 0 | 0 | 0 |  | 421920 | 591552 | 1053950 | 1659240 | 1841280 | 824160 | 401328 | 842400 | 0 | 0 | 0 | 7647900 | 7280000 | 4666000 | 217454 | 3208320 | 850464 | 719040 | 0 | 1188748 | 0 | 1025288 | 396811 | 491832 | 231840 | 729700 | 517230 | 3685440 | 2225280 | 0 | 452268 | 10950 | 1026000 | 960968 | 876000 | 838800 | 2598790 | 0 | 1380288 | 846720 | 0 | 5284140 | 0 | 747600 | 239940 | 7391500 | 412566 | 235872 | 0 | 4983052 | 0 | 0 | 2565600 | 0 | 2456064 | 145665 | 835200 | 1855680 | 3207253 | 9342000 | 1484400 | 2473200 | 2283263 | 36961 | 2847818 | 1064080 | 2559261 | 938220 | 2418360 | 885120 | 0 | 786240 | 339280 | 1971360 | 2482745 | 0 | 734040 | 220274 | 835200 | 1337040 | 90500 |  | 21010909 | 0 | 4069440 | 0 | 1076160 | 0 | 0 | 0 | 458880 | 645504 | 229875 | 1418000 | 618789 | 547488 | 0 | 0 | 0 | 712880 | 410602 | 1999768 | 0 | 0 | 661100 | 265200 | 676380 | 476880 | 0 | 250992 | 0 | 0 | 4888900 | 0 | 0 | 3854545 | 0 | 0 | 4319545 | 0 | 0 | 3416936 | 0 | 7221163 | 1004640 | 0 | 1986912 | 2547360 | 2193436 | 0 | 40409 | 2037888 | 25806500 | 5026964 | 0 | 124800 | 24360 | 732960 | 1602624 | 0 | 0 |  | 170709264 | 102358789 | 273068053 | 87285594 | 21010909 | 44565488 | 0 | 66426609 | 30695400 | 3050225 | 4319545 | 10477984 | 3685440 | 1550859 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 8010637.6 | 2737805 | 0 | 10418677.5 | 8205840 |  | 0 | 5513438 | 0 | 8156928 | 0 | 16736300.25 | 0 | 0 | 294000 | 12872383.68 | 12178766.88 | 36344116.8 | 0 | 0 | 0 | 0 | 7793798.4 | 4048555.5 | 3441636.27 | 282285 | 450000 | 0 | 0 | 0 | 20395670.4 | 0 | 596760.75 | 226800 | 4536000 | 0 | 9099657.9 | 0 | 0 | 0 | 0 |  | 5506056 | 9867087.36 | 17938229 | 22416332.4 | 23347430.4 | 9535531.2 | 509686.56 | 2805192 | 0 | 0 | 0 | 8489169 | 7935200 | 5412560 | 280515.66 | 3914150.4 | 961024.32 | 1071369.6 | 0 | 1985209.16 | 0 | 17706723.76 | 5337107.95 | 673809.84 | 173880 | 1276975 | 387922.5 | 26461459.2 | 2425555.2 | 0 | 615084.48 | 174543 | 1405620 | 1268477.76 | 1524240 | 1451124 | 2988608.5 | 0 | 2677758.72 | 1930521.6 | 0 | 5336981.4 | 0 | 1113924 | 475081.2 | 7391500 | 309424.5 | 179262.72 | 0 | 68018659.8 | 0 | 0 | 34584288 | 0 | 34016486.4 | 1702823.85 | 8619264 | 25348588.8 | 42560247.31 | 8594640 | 18050304 | 35762472 | 28883276.95 | 0 | 33433383.32 | 11587831.2 | 27204944.43 | 12731645.4 | 31172660.4 | 10426713.6 | 0 | 10181808 | 4902596 | 25016558.4 | 28253638.1 | 0 | 9586562.4 | 2632274.3 | 12502944 | 17608816.8 | 0 |  | 63032727 | 0 | 4557772.8 | 0 | 11202825.6 | 0 | 0 | 0 | 8264428.8 | 11619072 | 3303303.75 | 1588160 | 1200450.66 | 5967619.2 | 0 | 0 | 0 | 11954997.6 | 7181428.98 | 31276371.52 | 0 | 0 | 11179201 | 3614676 | 11410530.6 | 987141.6 | 0 | 190000.944 | 0 | 0 | 25862281 | 0 | 0 | 4471272.2 | 0 | 0 | 75419255.7 | 0 | 0 | 3963645.76 | 0 | 7148951.37 | 13502361.6 | 0 | 23505168.96 | 36809352 | 27856637.2 | 0 | 446519.45 | 24739960.32 | 232516565 | 5127503.28 | 0 | 923520 | 275511.6 | 8597620.8 | 24568225.92 | 0 | 0 |  | 927507778.78 | 704265060.214 | 1631772838.994 | 97833599.204 | 63032727 | 53938415.63 | 0 | 862410899.09 | 258378846 | 823560.75 | 75419255.7 | 174742187.42 | 26461459.2 | 18731889 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 400 | 322 |  | 0 | 225 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 24 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 12 | 25 | 33 | 51 | 0 | 93 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | 65 | 74 | 31 | 17 | 30 | 0 | 0 | 0 | 270 | 275 | 164 | 8 | 135 | 37 | 30 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 16 | 20 | 130 | 80 | 0 | 20 | 2 | 44 | 42 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 30 | 10 | 320 | 16 | 11 | 0 | 195 | 0 | 0 | 82 | 0 | 117 | 20 | 21 | 46 | 132 | 402 | 49 | 90 | 105 | 5 | 88 | 36 | 110 | 17 | 98 | 20 | 0 | 32 | 35 | 54 | 108 | 0 | 17 | 34 | 35 | 55 | 0 |  | 859 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 24 | 16 | 0 | 0 | 0 | 34 | 0 | 81 | 0 | 0 | 31 | 8 | 30 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 0 | 129 | 0 | 290 | 35 | 0 | 70 | 105 | 79 | 0 | 6 | 75 | 950 | 216 | 0 | 0 | 2 | 102 | 52 | 0 | 0 |  | 10605 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 332 | 0 | 0 | 225 | 0 | 66 | 0 | 55 | 0 | 0 | 0 | 96 | 94 | 146 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 27 | 25 | 25 | 50 | 0 | 91 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | 68 | 80 | 81 | 36 | 17 | 38 | 0 | 0 | 0 | 330 | 330 | 204 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 174 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 42 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 9 | 320 | 16 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 97 | 0 | 90 | 200 | 137 | 405 | 106 | 105 | 103 | 0 | 300 | 54 | 110 | 114 | 115 | 90 | 0 | 91 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 51 | 31 |  | 844 | 0 | 165 | 0 | 80 | 0 | 0 | 0 | 44 | 60 | 24 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 0 | 32 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 176 | 0 | 0 | 137 | 0 | 309 | 70 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 1000 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 12961 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 80 | 0 | 55 | 0 | 0 | 100 | 96 | 94 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 68 | 80 | 81 | 36 | 17 | 25 | 0 | 0 | 0 | 330 | 330 | 204 | 8 | 135 | 38 | 30 | 0 | 51 | 0 | 49 | 43 | 22 | 10 | 33 | 21 | 166 | 100 | 0 | 20 | 0 | 43 | 41 | 51 | 42 | 110 | 0 | 61 | 82 | 0 | 220 | 0 | 32 | 10 | 330 | 16 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 100 | 0 | 90 | 200 | 137 | 400 | 106 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 90 | 0 | 90 | 0 | 162 | 108 | 0 | 35 |  | 35 | 55 |  |  | 876 | 0 | 170 | 0 | 80 | 0 | 0 | 0 | 44 | 60 | 24 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 28 | 87 | 0 | 25 | 32 | 40 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 70 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 1100 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 400 | 300 | 0 | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 100 | 24 | 24 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 27 | 25 | 33 | 50 | 0 | 92 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 51 | 68 | 80 | 80 | 35 | 17 | 10 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 135 | 35 | 30 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 143 | 100 | 0 | 20 | 1.6 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 78 | 0 | 220 | 0 | 25 | 10 | 300 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 100 | 20 | 21 | 50 | 125 | 400 | 50 | 105 | 105 | 5 | 150 | 36 | 110 | 17 | 107 | 20 | 0 | 17 | 50 | 54 | 108 | 0 | 35 | 30 | 17 | 55 |  |  | 861 | 0 | 170 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 23 | 16 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 25 | 32 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 35 | 0 | 70 | 105 | 92 | 0 | 8 | 75 | 970 | 225 |  | 0 | 6 | 100 | 90
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 410 | 282 | 0 | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 97 | 24 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 92 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 68 | 68 | 88 | 34 | 17 | 14 | 0 | 0 | 0 | 280 | 290 | 208 | 8 | 135 | 38 | 55 | 0 | 51 | 0 | 49 | 8 | 19 | 10 | 33 | 20 | 146 | 104 | 0 | 20 | 0 | 43 | 42 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 31 | 10 | 290 | 24 | 11 | 0 | 193 | 0 | 0 | 87 | 0 | 111 | 11 | 21 | 50 | 124 | 402 | 48 | 88 | 87 | 1 | 82 | 36 | 92 | 17 | 107 | 20 | 0 | 17 | 10 | 54 | 108 | 0 | 35 | 11 | 17 | 38 | 0 | 0 | 895 | 0 | 190 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 32 | 8 | 30 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 130 | 0 | 0 | 144 | 0 | 300 | 35 | 0 | 70 | 88 | 85 | 0 | 2 | 76 | 920 | 223 | 0 | 0 | 1 | 40 | 52 | 0 | 0 | 0 |  |  |  |  | 81224138 |  | 0
81224138
| Minimum Generation |  | 10519 | 9:00
| Highest Generation |  | 12992 | 22:00
| Day Peak Generation |  | 10605 | 12:00
| Evening Peak Generation |  | 12961 | 21:00
| HVDC Max Flow |  | 895 | 1:00
| HVDC EvPeak Flow |  | 844 | 21:00
| Load factor L.F |  | 87.58% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-07-30
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10605 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10748 | MW
Evening Peak Generation : |  | 12961 | MW Hour : | 21:00 | Available Max Generation : |  | 13105 | MW
E.P. Demand (at gen end) : |  | 13500 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 12992 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 273.0681 | System Load Factor : | 87.58% | Load Shed : |  | 640 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 34 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-07-30
Actual : | 91.96 | Ft.(MSL) , | Rule curve : | 88.66 | Ft.( MSL )
Gas Consumed : | Total = | 1016.21 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151772014.834
: |  | Coal : | 258378846 | Oil : | 1112572342.21 | Total : | 1522723203.044
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4419.4129 |  |  | 150 | 5.055%
Chittagong Area | 0 | 0:00 | 1251.4251 |  |  | 76 | 7.347%
Khulna Area | 18 | 432:00 | 1652.0338 |  |  | 100 | 7.762%
Rajshahi Area | 20 | 480:00 | 1466.3548 |  |  | 100 | 8.347%
Cumilla Area | 15 | 360:00 | 1247.6098 |  |  | 60 | 8.009%
Mymensingh Area | 57 | 1368:00 | 1031.4083 |  |  | 100 | 8.565%
Sylhet Area | 0 | 0:00 | 460.382 |  |  | 14 | 7.371%
Barisal Area | 0 | 0:00 | 375.1732 |  |  | 0 | 0%
Rangpur Area | 18 | 432:00 | 813.935 |  |  | 40 | 8.51%
Total | 128 |  | 12717.735 |  |  | 640
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kachua 132/33 kV T-2 transformer was under shut down from 09:27 to 12:31 for C/M.
b) Naogaon 132/33 kV T-2 transformer and its associated 33 kV bus were shut down at 10:10 due to red hot maint. | [5 empty] | About 15 MW power interruption occurred under
and was switched on at 15:05. | [5 empty] | Naogaon S/S area from 10:10 to 15:05.
c) Shahjibazar 132/33 kV T-4 transformer was under shut down from 09:36 to 12:15 for red hot maintenance.
d) Sirajganj-Ashuganj 230 kV Ckt-2 tripped at 12:44 showing ARC at Sirajganj end & dist.Z1 at Ashuganj end and
was switched on at 12:58.
e) Mymensing-Bhaluka 132 kV Ckt-1 tripped at 14:59 showing dist.relay and was switched on at 15:08.
f) Bakulia-Sikalbaha 132 kV Ckt-1 & 2 tripped at 17:10 showing dist.Z1,3-phase and was switched on at 19:34.
g) Kishorganj 132/33 kV T-3 transformer tripped at 19:40 due to piling rig fall on transformer 33 kV incoming line | [5 empty] | About 28 MW power interruption occurred under
and was switched on at 11:03(30/7/22). | [5 empty] | Kishorganj S/S area from 19:40 to 20:02.
h) Niamatpur 132/33 kV T-1 transformer was shut down at 20:45 due to 33 kV DS red hot maintenance and was | [5 empty] | About 15 MW power interruption occurred under
switched on at 21:58 and again shut down at 23:30 for same reason and was switched on at 01:33(30/7/22). | [5 empty] | Niamatpur S/S area from 20:45 to 21:58.
i) Bhandaria 132/33 kV T-1 & T-2 transformers tripped at 17:28 due to 33 kV Kathalia feeder CT burst and were | [5 empty] | About 34 MW power interruption occurred under
switched on at 18:28 & 21:05 respectively. | [5 empty] | Bhandaria S/S area from 17:28 to 18:28.
j) Rangpur 33 kV bus section-2 was under shut down at 06:10(30/7/22) due to replacement of 33 kV isolator of | [5 empty] | About 50 MW power interruption occurred under
Kaunia feeder and was switched on at 09:35(30/7/22). | [5 empty] | Rangpur S/S area from 06:10 to 09:35(30/7/22).
k) Cumilla(N) 132/33 kV T-3 transformer is shut down since 06:41(30/7/22) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7152355 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 89 | 2058500 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 408 | 9922550
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7598000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5058200 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 66 | 729600 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1263117
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 376380
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 168000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 96 | 880464 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 865584 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 612720 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 2242080
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 299893
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 256647
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1083300 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 745200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1199040 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 4983052 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 97 | 2456064 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2473200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 786240 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1971360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 220274
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 51 | 1337040
| Dhaka area Total |  |  |  | 5847 | 3073 | 61732260
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 556554
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 145665
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 36 | 824160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 126 | 3050225 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 103 | 2283263
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 591552 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1053950 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 80 | 1659240 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 835200 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 401328 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 842400
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 81 | 1841280 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36961
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 2847818
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1064080
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2559261
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 885120
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2482745 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1477 | 26360802
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4666000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7647900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7280000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 31 | 90500 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 850464 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 719040 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1188748
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3207253 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 1025288 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3208320 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 1855680
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 491832
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 231840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 174 | 3685440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 729700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 396811 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 517230 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 938220
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2418360
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 734040 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 35 | 835200 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 2145 | 42935320
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2225280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 452268
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 2565600
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 1484400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 339280
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 421920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 444 | 7499698
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1026000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 960968 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2598790 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 876000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 838800 | Engine problem
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 235872
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1380288
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 846720 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5284140
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 32 | 747600 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 412566 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7391500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 405 | 9342000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 239940
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1445 | 32181184
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 844 | 21010909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 80 | 1076160 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 44 | 458880 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 645504 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 165 | 4069440 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 24 | 229875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1004640 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2547360
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 732960
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1392 | 31775728
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 547488 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 618789 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1418000 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1000 | 25806500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5026964
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 124800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1361 | 33542541
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 712880 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 410602 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 661100 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3854545 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 176 | 4319545
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 137 | 3416936 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 309 | 7221163 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 676380 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 476880
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250992
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 265200 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1999768 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1986912
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2037888
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24360
| Rajshahi Area Total |  |  |  | 2129 | 1227 | 28315151
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4888900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2193436
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40409
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1602624 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 397 | 8725369
| Total |  |  |  | 21680 | 12961 | 273068053
| Eastern Grid Total |  |  |  | 14489 | 8584 | 170709264
| Western Grid Total |  |  |  | 7191 | 4377 | 102358789
| National Grid Total |  |  |  | 21680 | 12961 | 273068053
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-29
(a) ENTIRE EASTERN GRID : |  | 8405.6 | MW | (b) ENTIRE WESTERN GRID : |  | 4184.1 | MW
i) Dhaka area |  | 4301.65 | MW | i) Khulna area |  | 1646.2 | MW
ii) Chittagong area |  | 1276.95 | MW | ii) Rajshahi area |  | 1299 | MW
iii) Comilla area |  | 1221 | MW | iii) Barisal area |  | 366.9 | MW
iv) Mymensingh area |  | 1035 | MW | iv) Rangpur area |  | 872 | MW
v) Sylhet area |  | 571 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12589.7 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 12 | 00:00 | Chowmuhani | 208 | 19:30 | Kaptai | 4.5 | 19:00 | Nawabganj | 47.2 | 22:00 | Sholosohor | N/A | N/A
AKSML | 4 | 06:00 | Chuadanga | 110 | 20:00 | Kazla | 83 | 23:00 | Netrakona | 107 | 18:00 | Shyampur | 164 | 00:00
Aftabnagar | 32 | 23:00 | Coxsbazar | 122 | 22:00 | Keranigonj | 54 | 00:00 | New | 66 | 00:00 | Siddhirganj | 108 | 00:00
Agargaon | 80 | 23:00 | Cumilla(N) | 159 | 20:00 | Khagrachori | 30 | 19:30 | Niamatpur | 74 | 19:30 | Sirajganj | 92 | 19:30
Agrabad | 74 | 19:30 | Cumilla(S) | 176 | 22:00 | Khulna | 92 | 21:00 | Noapara | 51 | 20:00 | Sonargaon | 88 | 00:00
Amnura | 59 | 21:00 | Daudkandi | 130 | 22:00 | Khulshi | 183 | 22:00 | PHP | 3 | 16:00 | Sreemongol | 58 | 21:00
Ashuganj | 39 | 01:00 | Dhaka | 20 | 15:00 | Kishoreganj | 114 | 07:00 | Pabna | 102 | 20:00 | Srinagar | 47.65 | 22:00
BSRM | 140 | 14:00 | Dhamrai | 86 | 21:00 | Kodda | 252 | 00:00 | Palashbari | 130 | 23:00 | Sunamganj | 57 | 20:00
Bagerhat | 98 | 21:00 | Dhanmondi | 107 | 19:00 | Kulaura | 52 | 20:00 | Panchagarh | 65 | 21:00 | Sylhet | 149 | 22:00
Bakulia | 113 | 21:00 | Dohazari | 110 | 21:00 | Kurigram | 66 | 20:00 | Patuakhali | 128 | 23:00 | TK | 30 | 19:30
Banani | 44 | 19:30 | Faridpur | 153 | 22:00 | Kushtia | 122 | 22:00 | Payra | 1.06 | 11:00 | Tangail | 227 | 21:00
Bangabhaban | 6 | 00:00 | Fatullah | 64 | 00:00 | Lalbag | 81 | 00:00 | Postogola | 43 | 00:00 | Thakurgaon | 80 | 22:00
Barapukuria | 52 | 22:00 | Fenchuganj | 52 | 20:00 | Lalmonirhat | 53 | 20:00 | Purbachal | 17 | 23:00 | Tongi | 100 | 00:00
Barguna | 20 | 00:00 | Feni | 96 | 23:00 | Madanganj | 88 | 00:00 | Purbasadipur | 123 | 21:00 | Ullon | 41 | 00:00
Barishal | 108 | 00:00 | GPH | 10 | 01:00 | Madaripur | 103 | 22:00 | Rahanpur_I | N/A | N/A | Uttara | 89 | 19:30
Barishal-230 | 76 | 23:00 | Ghorashal | 54 | 04:00 | Madartek | 83 | 23:00 | Rahim | 16 | 00:00 | UttaraNew | 18 | 23:00
Baroaulia | 64 | 00:00 | Goalpara | 26 | 19:30 | Madunaghat | 61 | 19:00 | Rajbari | 64 | 21:00 | Zigatola | 53 | 00:00
Baroirhat | 60 | 23:00 | Gollamari | 50 | 00:00 | Magura | 65 | 21:00 | Rajendrapur | 94 | 19:30
Bashundhara | 170 | 17:00 | Gopalganj | 107 | 23:00 | Mahasthangarh | 68 | 23:00 | Rajshahi | 139 | 22:00
BashundharaCement | 12 | 01:00 | Gulshan | 88 | 19:00 | Manikganj | 95 | 22:00 | Rajshahi-230 | 32 | 22:00
Beanibazar | 70 | 22:00 | Halishahar | 81 | 21:00 | Maniknagar | 67 | 21:00 | Ramganj | 108 | 22:00
Benapole | 60 | 21:00 | HaripurSBU | 110 | 06:00 | Matarbari | 42 | 21:00 | Rampur | 16 | 21:00
Bhaluka | 106 | 08:00 | Hasnabad | 99 | 23:00 | Matuail | 60 | 00:00 | Rangamati | 14 | 19:00
Bhandaria | 52 | 21:00 | Hathazari | 95 | 19:00 | Millgate | 64 | 12:00 | Rangpur | 119 | 19:30
Bhangura | 34 | 21:00 | Ishurdi | 69 | 19:30 | Mirpur | 129 | 19:00 | Ruppur | 3.8 | 10:00
Bheramara(GK) | 62 | 20:00 | Jaldhaka | 64 | 21:00 | Mirsorai | N/A | N/A | SSM | 4 | 17:00
Bhulta | 235 | 22:00 | Jamalpur | 143 | 21:00 | Mithapukur | 44 | 22:00 | Saidpur | 101 | 21:00
Bog-Sherpur | 54 | 08:00 | Jashore | 143 | 21:00 | Modern | 0 | 00:00 | Satkhira | 128 | 19:30
Bogura | 157 | 21:00 | Jhenaidah | 132 | 20:00 | Mogbazar | 105 | 19:00 | Satmasjid | 105 | 19:00
Borhanuddin | 42 | 00:00 | Joydebpur | 167 | 19:30 | Mongla | 34 | 00:00 | Savar | 151 | 23:00
Brahmanbaria | 176 | 21:00 | Joypurhat | 59 | 22:00 | Motijheel | 29 | 19:00 | Shahjadpur | 98 | 20:00
Cantonment | 144 | 19:30 | Juldah | 27 | 00:00 | Munshiganj | 104 | 22:00 | Shahjibazar | 114 | 22:00
Chandpur | 75 | 21:00 | KSRM | 32 | 20:00 | Mymensingh | 246 | 20:00 | Shahmirpur | 41 | 23:00
Chandraghona | 34 | 19:30 | Kabirpur | 210 | 19:30 | Naogaon | 119 | 23:00 | Shariatpur | 80 | 23:00
Chapai | 75 | 22:00 | Kachua | 74 | 20:00 | Narail | 48 | 22:00 | Sherpur | 132 | 21:00
Charsaidpur | 49 | 12:00 | Kallyanpur | 105 | 23:00 | Narinda | 52 | 00:00 | Shikalbaha | 27 | 05:00
Chauddagram | 63 | 22:00 | Kalurghat | 0 | 00:00 | Narshingdi | 189 | 23:00 | Shikalbaha-230 | N/A | N/A
Chhatak | 34 | 21:00 | Kamrangirchar | 57 | 11:00 | Natore | 126 | 21:00 | Shitalakhya | 101 | 00:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 390 | 19:30 | 376 | 01:00 | Kaliakoir | 389 | 08:00 | 382 | 02:00
| Bibiana | 408 | 06:00 | 397 | 02:00 | Payra | 416 | 18:00 | 407 | 22:00
| BIPTC | 402 | 06:00 | 397 | 11:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 409 | 06:00 | 391 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 224 | 19:30 | 215 | 15:00 | Hasnabad | 223 | 19:30 | 213 | 00:00
| AKSML | 235 | 21:00 | 221 | 11:00 | Hathazari | 236 | 19:30 | 225 | 18:30
| Aminbazar | N/A | N/A | N/A | N/A | Ishurdi | 235 | 18:00 | 226 | 21:00
| Ashuganj | 240 | 19:30 | 231 | 15:00 | Jhenaidah | 230 | 18:00 | 216 | 21:00
| Baghabari | 233 | 13:00 | 226 | 21:00 | Kaliakoir | 224 | 06:00 | 219 | 02:00
| Barapukuria | 222 | 06:00 | 211 | 21:00 | Keranigonj | 223 | 19:30 | 214 | 01:00
| Barishal | 246 | 06:00 | 237 | 22:00 | Khulna(S) | 237 | 18:00 | 224 | 21:00
| Bheramara | 232 | 18:00 | 223 | 21:00 | Maniknagar | 226 | 19:30 | 217 | 00:00
| Bhulta | 229 | 19:30 | 221 | 01:00 | Meghnaghat | 228 | 18:00 | 221 | 07:00
| Bibiana | 241 | 19:30 | 232 | 15:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 18:00 | 222 | 21:00 | Rajshahi | 234 | 18:00 | 220 | 21:00
| Bogura | 227 | 13:00 | 219 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 18:00 | 243 | 22:00 | Rampura | 226 | 21:00 | 220 | 01:00
| BSRM | 234 | 19:30 | 225 | 18:30 | Shikalbaha | 238 | 19:30 | 225 | 19:00
| Cumilla(N) | 232 | 19:30 | 223 | 02:00 | Shyampur | 224 | 19:30 | 215 | 01:00
| Fenchuganj | 242 | 07:00 | 237 | 00:00 | Siddhirganj | 225 | 06:00 | 220 | 01:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 13:00 | 227 | 21:00
| GPH | 236 | 19:30 | 23 | 22:00 | Tongi | 230 | 19:30 | 220 | 10:00
| Haripur | 225 | 19:30 | 218 | 00:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 138 | 07:00 | 134 | 00:00 | Lalbag | 138 | 19:30 | 132 | 00:00
| Agargaon | 137 | 06:00 | 132 | 14:00 | Lalmonirhat | 130 | 06:00 | 119 | 20:00
| Agrabad | 138 | 07:00 | 131 | 18:00 | Madanganj | 134 | 19:00 | 127 | 00:00
| AKS | 137 | 20:00 | 132 | 10:00 | Madaripur | 139 | 18:00 | 132 | 21:00
| Aminbazar | N/A | N/A | N/A | N/A | Madartek | 139 | 19:30 | 133 | 15:00
| Amnura | 133 | 16:00 | 121 | 21:00 | Madunaghat | 140 | 19:30 | 132 | 18:30
| Ashuganj | 137 | 19:00 | 134 | 03:00 | Magura | 140 | 13:00 | 126 | 21:00
| Bagerhat | 134 | 13:00 | 123 | 04:00 | Mahasthangarh | 136 | 16:00 | 127 | 21:00
| Bakulia | 138 | 23:00 | 131 | 18:30 | Manikganj | 136 | 13:00 | 129 | 02:00
| Banani | 133 | 06:00 | 128 | 00:00 | Maniknagar | 135 | 19:30 | 130 | 00:00
| Bangabhaban | 135 | 19:30 | 129 | 00:00 | Matarbari | 128 | 16:00 | 119 | 02:00
| Barapukuria | 136 | 06:00 | 127 | 21:00 | Matuail | 132.5 | 19:00 | 127 | 02:00
| Barguna | 136 | 18:00 | 128 | 04:00 | Millgate | 134 | 19:30 | 128 | 00:00
| Barishal | 139 | 13:00 | 127 | 15:00 | Mirpur | 132 | 19:00 | 126 | 15:00
| Barishal-230 | 140 | 06:00 | 132 | 22:00 | Mithapukur | 134 | 16:00 | 124 | 20:00
| Baroaulia | 140 | 19:00 | 131 | 18:30 | Modern | 138 | 19:00 | 134 | 16:00
| Baroirhat | 137 | 19:30 | 128 | 11:00 | Mogbazar | 139 | 08:00 | 135 | 00:00
| Bashundhara | 135 | 19:30 | 127 | 00:00 | Mongla | 133 | 18:00 | 122 | 03:00
| BashundharaCement | 134 | 19:00 | 127 | 00:00 | Motijheel | 135 | 19:30 | 129 | 00:00
| Beanibazar | 131 | 18:30 | 127 | 20:00 | Munshiganj | 133 | 23:00 | 129 | 00:00
| Benapole | 135 | 13:00 | 125 | 21:00 | Mymensingh | 131 | 18:00 | 120 | 05:00
| Bhaluka | 132 | 19:30 | 115 | 07:00 | Naogaon | 133 | 16:00 | 122 | 21:00
| Bhandaria | 140 | 18:30 | 125 | 22:00 | Narail | 137 | 13:00 | 125 | 21:00
| Bhangura | 139 | 16:00 | 133 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 13:00 | 132 | 21:00 | Narshingdi | 137 | 16:00 | 125 | 00:00
| Bheramara(GK) | 139 | 16:00 | 134 | 03:00 | Natore | 135 | 13:00 | 126 | 21:00
| Bhulta | 126 | 19:30 | 123 | 00:00 | Nawabganj | 138 | 19:30 | 130 | 00:00
| Bog-Sherpur | 137 | 16:00 | 13.4 | 06:00 | Netrakona | 133 | 23:00 | 113 | 07:00
| Bogura | 137 | 18:30 | 129 | 21:00 | New | 135 | 19:30 | 128 | 11:00
| Bogura-230 | 138 | 16:00 | 132 | 20:00 | Niamatpur | 130 | 14:00 | 119 | 21:00
| Brahmanbaria | 132 | 12:00 | 129 | 09:00 | Noapara | 136 | 18:00 | 126 | 21:00
| Cantonment | 136 | 06:00 | 130 | 03:00 | Pabna | 136 | 18:00 | 131 | 21:00
| Chandpur | 138 | 19:30 | 130 | 07:00 | Palashbari | 132 | 01:00 | 121 | 20:00
| Chandraghona | 139 | 19:30 | 132 | 18:30 | Panchagarh | 135 | 06:00 | 117 | 20:00
| Chapai | 133 | 18:00 | 120 | 21:00 | Patuakhali | 135 | 18:00 | 130 | 02:00
| Charsaidpur | 138 | 07:00 | 127 | 01:00 | Payra | 137 | 18:00 | 133 | 05:00
| Chauddagram | 137 | 19:30 | 129 | 10:00 | PHP | 136 | 19:30 | 127 | 18:30
| Chhatak | 132 | 18:00 | 126 | 21:00 | Postogola | 142 | 19:30 | 135 | 00:00
| Chowmuhani | 135 | 05:00 | 125 | 18:30 | Purbachal | 135 | 19:30 | 127 | 07:00
| Chuadanga | 134 | 13:00 | 121 | 21:00 | Purbasadipur | 131 | 00:00 | 119 | 20:00
| Coxsbazar | 126 | 07:00 | 117 | 22:00 | Rahim | 134 | 19:30 | 129 | 00:00
| Cumilla(N) | 137 | 19:30 | 130 | 10:00 | Rajbari | 135 | 18:30 | 128 | 21:00
| Cumilla(S) | 136 | 19:30 | 126 | 19:00 | Rajendrapur | 135 | 14:00 | 129 | 03:00
| Daudkandi | 132 | 19:30 | 126 | 04:00 | Rajshahi | 134 | 18:00 | 124 | 21:00
| Dhaka | 139 | 06:00 | 133 | 15:00 | Rajshahi-230 | 133 | 16:00 | 124 | 21:00
| Dhamrai | 132 | 19:30 | 127 | 00:00 | Ramganj | 134 | 00:00 | 126 | 07:00
| Dhanmondi | 134 | 19:30 | 127.5 | 00:00 | Rampur | 137 | 20:00 | 132 | 14:00
| Dohazari | 138 | 11:00 | 129 | 10:00 | Rampura | 137 | 07:00 | 134 | 00:00
| Faridpur | 135 | 06:00 | 128 | 21:00 | Rangamati | 137 | 06:00 | 131 | 18:30
| Fatullah | 135 | 19:30 | 129 | 00:00 | Rangpur | 131 | 01:00 | 120 | 19:30
| Fenchuganj | 137 | 18:00 | 133 | 15:00 | Ruppur | 137 | 16:00 | 133 | 01:00
| Feni | 138 | 19:30 | 129 | 10:00 | Saidpur | 132 | 16:00 | 119 | 20:00
| Ghorashal | 139 | 18:00 | 135 | 01:00 | Satkhira | 132 | 13:00 | 121 | 20:00
| Goalpara | 137 | 18:00 | 10.3 | 11:00 | Satmasjid | 137 | 06:00 | 131 | 15:00
| Gollamari | 136 | 18:00 | 128 | 02:00 | Savar | 134 | 19:30 | 127 | 01:00
| Gopalganj | 139 | 16:00 | 133 | 15:00 | Shahjadpur | 142 | 04:00 | 137 | 21:00
| Gopalganj_I | 140 | 06:00 | 132 | 22:00 | Shahjibazar | 135 | 23:00 | 131 | 14:00
| Gulshan | 138 | 06:00 | 133 | 01:00 | Shahmirpur | 140 | 19:30 | 134 | 10:00
| Halishahar | 139 | 19:30 | 131 | 18:30 | Shariatpur | 137 | 18:00 | 127 | 22:00
| Haripur | 134 | 19:30 | 129 | 00:00 | Sherpur | 138 | 23:00 | 112 | 07:00
| HaripurSBU | 134 | 19:30 | 128 | 00:00 | Shikalbaha | 140 | 19:30 | 131 | 18:30
| Hasnabad | 140 | 21:00 | 134 | 14:00 | Shikalbaha-230 | 140 | 19:30 | 133 | 19:00
| Hathazari | 140 | 19:30 | 132 | 18:30 | Shitalakhya | 143 | 19:30 | 133 | 02:00
| Ishurdi | 138 | 18:00 | 132 | 21:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 130 | 01:00 | 117 | 20:00 | Shyampur | 133 | 19:00 | 128 | 00:00
| Jamalpur | 140 | 23:00 | 116 | 07:00 | Shyampur-230 | 135 | 19:30 | 128 | 01:00
| Jashore | 136 | 13:00 | 124 | 21:00 | Siddhirganj | 132 | 19:00 | 128 | 01:00
| Jhenaidah | 140 | 13:00 | 130 | 21:00 | Sirajganj | 137 | 16:00 | 129 | 21:00
| Jhenaidah-230 | 140 | 13:00 | 130 | 21:00 | Sonargaon | 132 | 15:00 | 127 | 00:00
| Joydebpur | 144 | 13:00 | 140 | 00:00 | Sreemongol | 136 | 01:00 | 133 | 15:00
| Joypurhat | 134 | 16:00 | 121 | 21:00 | Srinagar | 137 | 06:00 | 131 | 01:00
| Juldah | 140 | 19:30 | 132 | 18:30 | SSM | 140 | 16:00 | 39 | 02:00
| Kabirpur | 137 | 13:00 | 124 | 01:00 | Sunamganj | 130 | 19:00 | 124 | 20:00
| Kachua | 137 | 19:30 | 129 | 09:00 | Sylhet | 133 | 00:00 | 131 | 13:00
| Kaliakoir | 137 | 12:00 | 133 | 02:00 | Tangail | 136 | 06:00 | 128 | 21:00
| Kallyanpur | 133 | 18:00 | 128 | 15:00 | Thakurgaon | 133 | 01:00 | 116 | 21:00
Page 7 of 7

## L-Curve
Date | 2022-07-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 526 | 7592 | 4388 | 11980 |  |  |  | QF-LDC-11
0:30 | 658 | 7352.5 | 4409 | 11761.5 | Date: | 2022-07-29
1:00 | 790 | 7113 | 4430 | 11543
1:30 | 760 | 7047.5 | 4415 | 11462.5
2:00 | 730 | 6982 | 4400 | 11382
2:30 | 713 | 6972.5 | 4405.5 | 11378 | [5 empty] | Gen. at Eve. Peak | 12961 | 12961 MW (21:00 )
3:00 | 696 | 6963 | 4411 | 11374 | [6 empty] | 21:00
3:30 | 692 | 6974.5 | 4374 | 11348.5 | [5 empty] | Gen. at Day Peak | 10605 | 10605 MW (12:00 )
4:00 | 688 | 6986 | 4337 | 11323 | [6 empty] | 12:00
4:30 | 702 | 6974 | 4319.5 | 11293.5 | [5 empty] | Highest Generation | 12992
5:00 | 716 | 6962 | 4302 | 11264 | [6 empty] | 22:00
5:30 | 680 | 6901 | 4241 | 11142
6:00 | 644 | 6840 | 4180 | 11020
6:30 | 631 | 6760.5 | 4081.5 | 10842
7:00 | 618 | 6681 | 3983 | 10664
7:30 | 617 | 6639 | 3953.5 | 10592.5
8:00 | 616 | 6597 | 3924 | 10521
8:30 | 611 | 6601.5 | 3918.5 | 10520
9:00 | 606 | 6606 | 3913 | 10519
9:30 | 649 | 6590.5 | 3945 | 10535.5
10:00 | 692 | 6575 | 3977 | 10552
10:30 | 681 | 6588.5 | 3973 | 10561.5
11:00 | 670 | 6602 | 3969 | 10571
11:30 | 730 | 6601 | 3987 | 10588
12:00 | 790 | 6600 | 4005 | 10605
12:30 | 766 | 6608 | 3991.5 | 10599.5
13:00 | 742 | 6616 | 3978 | 10594
13:30 | 642 | 6614 | 3933.5 | 10547.5
14:00 | 542 | 6612 | 3889 | 10501
14:30 | 615 | 6698.5 | 3894.5 | 10593
15:00 | 688 | 6785 | 3900 | 10685
15:30 | 695 | 6814 | 3945 | 10759
16:00 | 702 | 6843 | 3990 | 10833
16:30 | 761 | 6663.5 | 3973 | 10636.5
17:00 | 820 | 6484 | 3956 | 10440
17:30 | 783 | 6466 | 3848.5 | 10314.5
18:00 | 746 | 6448 | 3741 | 10189
18:30 | 609 | 6864 | 3851 | 10715
19:00 | 472 | 7280 | 3961 | 11241
19:30 | 182 | 8021 | 4219 | 12240
20:00 | 96 | 8285 | 4346 | 12631 |  |  |  | Executive Engineer
20:30 | 65 | 8434.5 | 4361.5 | 12796 |  |  |  | Network Operation Division
21:00 | 34 | 8584 | 4377 | 12961
21:30 | 126 | 8548.5 | 4428 | 12976.5
22:00 | 218 | 8513 | 4479 | 12992 |  |  |  |  | Page 6 of 7
22:30 | 324 | 8417 | 4464 | 12881
23:00 | 430 | 8321 | 4449 | 12770
23:30 | 478 | 7956.5 | 4418.5 | 12375
24:00 | 526 | 7592 | 4388 | 11980
12961 MW (21:00 )
10605 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-29 |  | Energy |  | 273068053
[13 empty] | 2022-07-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3724 | 843 | 1997 | 0 | 3069 | 1259 | 127 | 219 | 789 | 172 | 0 | 847.849
0:30 | 3704 | 869 | 1951 | 0 | 2888 | 1274 | 127.5 | 217.5 | 778 | 170 | 0 | 1095.4245 | Date: | 2022-07-29
1:00 | 3684 | 895 | 1905 | 0 | 2707 | 1289 | 128 | 216 | 767 | 168 | 0 | 1343
1:30 | 3707 | 895 | 1884 | 0 | 2633 | 1289.5 | 127.5 | 216.5 | 759.5 | 167 | 0 | 1302 | [8 empty] | Total Energy | 273.0681 | Total Energy Gen 273.068 MKWHr Energy Not Served 8.975 MKWHr Energy Requirement 282.043 MKWHr
2:00 | 3730 | 895 | 1863 | 0 | 2559 | 1290 | 127 | 217 | 752 | 166 | 0 | 1261 | [8 empty] | Energy not Served | 8.9745
2:30 | 3706.5 | 895 | 1875.5 | 0 | 2578 | 1280 | 126.5 | 217.5 | 751.5 | 165 | 0 | 1149.5 | [8 empty] | Energy Requirement | 282.0426
3:00 | 3683 | 895 | 1888 | 0 | 2597 | 1270 | 126 | 218 | 751 | 164 | 0 | 1038
3:30 | 3692.5 | 895 | 1889 | 0 | 2561 | 1270 | 125.5 | 218.5 | 752.5 | 163 | 0 | 969 | [6 empty] | Shortage
4:00 | 3702 | 895 | 1890 | 0 | 2525 | 1270 | 125 | 219 | 754 | 162 | 0 | 900
4:30 | 3706.5 | 895 | 1890 | 0 | 2505 | 1265 | 125 | 216.5 | 747 | 160 | 0 | 789
5:00 | 3711 | 895 | 1890 | 0 | 2485 | 1260 | 125 | 214 | 740 | 158 | 0 | 678
5:30 | 3680.5 | 895 | 1856 | 0 | 2477 | 1219.5 | 125.5 | 208 | 731 | 154 | 3.5 | 514
6:00 | 3650 | 895 | 1822 | 0 | 2469 | 1179 | 126 | 202 | 722 | 150 | 7 | 350
6:30 | 3611.5 | 894.5 | 1816 | 0 | 2423 | 1179 | 126 | 166 | 622.5 | 145 | 24.5 | 260.5 |  |  |  |  | Coal
7:00 | 3573 | 894 | 1810 | 0 | 2377 | 1179 | 126 | 130 | 523 | 140 | 42 | 171
7:30 | 3540 | 894.5 | 1766 | 0 | 2376.5 | 1174 | 126.5 | 130 | 502 | 139 | 74 | 135.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3507 | 895 | 1722 | 0 | 2376 | 1169 | 127 | 130 | 481 | 138 | 106 | 100
8:30 | 3513.5 | 895 | 1730 | 0 | 2372 | 1159.5 | 127 | 130 | 455.5 | 139 | 128.5 | 110.5
9:00 | 3520 | 895 | 1738 | 0 | 2368 | 1150 | 127 | 130 | 430 | 140 | 151 | 121
9:30 | 3507 | 877.5 | 1796.5 | 0 | 2336.5 | 1150 | 127.5 | 130 | 425.5 | 141 | 174 | 128.5
10:00 | 3494 | 860 | 1855 | 0 | 2305 | 1150 | 128 | 130 | 421 | 142 | 197 | 136
10:30 | 3493 | 860 | 1851.5 | 0 | 2307 | 1145 | 128 | 133.5 | 429 | 144 | 204 | 150.5
11:00 | 3492 | 860 | 1848 | 0 | 2309 | 1140 | 128 | 137 | 437 | 146 | 211 | 165
11:30 | 3462.5 | 859.5 | 1845.5 | 0 | 2342.5 | 1145 | 128 | 159 | 458.5 | 138 | 208.5 | 172.5
12:00 | 3433 | 859 | 1843 | 0 | 2376 | 1150 | 128 | 181 | 480 | 130 | 206 | 180
12:30 | 3428.5 | 859.5 | 1801.5 | 0 | 2366 | 1160 | 124.5 | 183 | 508.5 | 136 | 215 | 150.5
13:00 | 3424 | 860 | 1760 | 0 | 2356 | 1170 | 121 | 185 | 537 | 142 | 224 | 121
13:30 | 3424 | 860 | 1760 | 0 | 2356 | 1170 | 121 | 185 | 537 | 142 | 224 | 121
14:00 | 3424 | 860 | 1760 | 0 | 2356 | 1170 | 121 | 185 | 537 | 142 | 224 | 121
14:30 | 3479 | 858.5 | 1806.5 | 0 | 2377.5 | 1155 | 122.5 | 157.5 | 512.5 | 144 | 184 | 159.5
15:00 | 3534 | 857 | 1853 | 0 | 2399 | 1140 | 124 | 130 | 488 | 146 | 144 | 198
15:30 | 3542.5 | 857.5 | 1841.5 | 0 | 2482 | 1160 | 123.5 | 130 | 489 | 146 | 117 | 153
16:00 | 3551 | 858 | 1830 | 0 | 2565 | 1180 | 123 | 130 | 490 | 146 | 90 | 108
16:30 | 3508 | 857.5 | 1839.5 | 0 | 2417.5 | 1160 | 123 | 130 | 502 | 144 | 63.5 | 54
17:00 | 3508 | 857 | 1849 | 0 | 2270 | 1140 | 123 | 130 | 514 | 142 | 37 | 0
17:30 | 3487.5 | 857 | 1790 | 0 | 2263 | 1110 | 123 | 130 | 520.5 | 139 | 24.5 | 0
18:00 | 3467 | 857 | 1731 | 0 | 2256 | 1080 | 123 | 130 | 527 | 136 | 12 | 0
18:30 | 3532 | 857 | 1834.5 | 0 | 2551 | 1080 | 124 | 134.5 | 578.5 | 152 | 6 | 211.5
19:00 | 3597 | 857 | 1938 | 0 | 2846 | 1080 | 125 | 139 | 630 | 168 | 0 | 423
19:30 | 3530 | 857 | 1840 | 0 | 3816 | 1170 | 125 | 160 | 738 | 164 | 0 | 332
20:00 | 3585 | 844 | 1913 | 0 | 4015 | 1190 | 125 | 160 | 795 | 164 | 0 | 248
20:30 | 3650.5 | 844 | 1958 | 0 | 4059 | 1195 | 125.5 | 168 | 795 | 169 | 0 | 188
21:00 | 3716 | 844 | 2003 | 0 | 4103 | 1200 | 126 | 176 | 795 | 174 | 0 | 128
21:30 | 3690 | 843.5 | 1999 | 0 | 4113 | 1215 | 126.5 | 194.5 | 814.5 | 175 | 0 | 102.2454
22:00 | 3664 | 843 | 1995 | 0 | 4123 | 1230 | 127 | 213 | 834 | 176 | 0 | 76.4907
22:30 | 3687 | 843.5 | 2000 | 0 | 3982 | 1235 | 127.5 | 215 | 833 | 173 | 0 | 144.2265
23:00 | 3710 | 844 | 2005 | 0 | 3841 | 1240 | 128 | 217 | 832 | 170 | 0 | 211.9623
23:30 | 3717 | 843.5 | 2001 | 0 | 3455 | 1249.5 | 127.5 | 218 | 810.5 | 171 | 0 | 529.9056 | Max Temp. in Dhaka |  | 24.7° C | 35° C
24:00 | 3724 | 843 | 1997 | 0 | 3069 | 1259 | 127 | 219 | 789 | 172 | 0 | 847.849
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 273.068 MKWHr Energy Not Served 8.975 MKWHr Energy Requirement 282.043 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 93 | 92 | 91 | 90 | 90 | 91 | 91 | 92 | 92 | 93 | 93 | 93 | 86 | 90 | 89 | 88 | 88 | 88 |  | 90 | 90 | 90 | 91 | 92 | 93 | 92 | 2210225
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 |  | 8 | 17 | 25 | 25 | 25 | 25 | 25 | 556554
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 14 | 18 | 13 | 20 | 19 | 18 | 14 | 9 | 4 | 1 | [8 empty] | 145665
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 0 |  |  | 0 | 51 | 51 | 51 | 51 | 51 | 51 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1053950
12 | Hathazari 100 MW peaking PP | 50 | 50 | 50 | 50 | 41 | 42 | 42 | 0 | [11 empty] | 2 | 21 | 51 | 51 | 52 | 52 | 52 | 591552
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 51 | 17 |  | 19 | 85 | 75 | 103 | 105 | 87 | 87 | 2283263
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 32 | 34 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1025288
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [24 empty] | 99 | 97 | 168000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 175 | 190 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 202 | 242 |  | 247 | 260 | 265 | 278 | 278 | 275 | 248 | 4983052
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 |  | 300 | 280 | 300 | 300 | 300 | 300 | 300 | 7152355
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 35 | 32 | 35 |  | 37 | 34 | 34 | 38 | 38 | 38 | 38 | 850464
33 | Ashuganj 225 MW CCPP | 208 | 208 | 209 | 208 | 196 | 212 | 185 | 170 | 162 | 162 | 167 | 164 | 187 | 204 | 197 | 208 | 207 | 179 |  | 202 | 206 | 207 | 204 | 179 | 185 | 207 | 4666000
34 | Ashuganj 450 MW CCPP(South) | 315 | 335 | 320 | 325 | 330 | 275 | 275 | 275 | 310 | 295 | 305 | 275 | 265 | 310 | 325 | 265 | 265 | 265 |  | 310 | 275 | 285 | 330 | 325 | 260 | 300 | 7280000
| Ashuganj 450 MW CCPP(North) | 325 | 350 | 330 | 340 | 345 | 325 | 320 | 320 | 300 | 270 | 270 | 270 | 300 | 270 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 330 | 300 | 300 | 280 | 7647900
| Ashuganj 420 MW CCPP(East) | [21 empty] | 32 | 31 | 31 | 31 | 0 | 90500
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719040
36 | Chandpur 150 MW CCPP | 136 | 135 | 136 | 128 | 128 | 129 | 129 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3208320
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 407 | 411 | 412 | 412 | 409 | 409 | 408 | 408 | 410 | 408 | 405 | 400 | 407 | 408 | 402 | 406 | 411 | 410 |  | 405 | 410 | 409 | 408 | 408 | 410 | 410 | 9922550
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5058200
41 | Haripur 360MW CCPP(HPL) | 323 | 308 | 308 | 299 | 298 | 294 | 294 | 314 | 322 | 328 | 332 | 322 | 327 | 282 | 332 | 322 | 332 | 279 |  | 332 | 332 | 333 | 332 | 322 | 331 | 330 | 7598000
42 | RPCL 210MW CCPP | 104 | 104 | 104 | 104 | 104 | 106 | 105 | 105 | 97 | 92 | 81 | 80 | 72 | 71 | 71 | 98 | 98 | 98 |  | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 2225280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 26 | 39 | 48 | 45 | 35 | 55 | 39 | 46 | 10 | 4 | 1 | [8 empty] | 339280
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 43 | 43 | 44 | 43 | 43 |  | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 1026000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 41 | 41 |  | 41 | 42 | 41 | 41 | 41 | 41 | 41 | 960968
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 64 | 62 | 62 | 64 | 62 | 40 | 40 | 40 | 59 | 61 | 40 | 50 | 59 | 61 | 61 | 60 |  | 61 | 64 | 62 | 61 | 61 | 62 | 62 | 1380288
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 40 | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 846720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 220 | 220 | 220 | 220 | 221 | 221 | 220 |  | 221 | 220 | 221 | 221 | 221 | 221 | 221 | 5284140
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 32 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 30 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 747600
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 239940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 |  | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235872
55 | Fenchugonj 51 MW PP (Barakatullah) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 53 | 53 | 53 | 53 | 876000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 10 | 13 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 412566
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 325 | 325 | 325 | 325 | 280 | 280 | 260 | 285 | 310 | 315 | 320 | 270 | 260 | 320 | 300 | 280 | 270 |  | 310 | 240 | 270 | 320 | 325 | 310 | 300 | 7391500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 |  |  |  | 256647
59 | Tangail Palli Power Gen 22 MW | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 15 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 15 | 12 | 14 | 421920
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 401328
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 376380
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 452268
63 | Impoprt (Tripura) | 168 | 166 | 164 | 162 | 158 | 150 | 140 | 138 | 140 | 142 | 146 | 130 | 142 | 146 | 146 | 146 | 142 | 136 |  | 168 | 164 | 164 | 174 | 176 | 170 | 172 | 3685440
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 40 | 40 | 41 | 42 | 42 | 30 | 20 | 20 | 30 | 39 | 34 | 34 | 33 | 36 | 38 |  | 38 | 38 | 38 | 38 | 29 | 37 | 42 | 842400
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491832
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 231840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 21 | 16 | 16 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 24 | 33 | 33 | 33 | 33 | 729700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 517230
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 0 | 12 | 20 | 16 | 12 | 12 | 12 | 12 | 17 | 17 | 17 |  | 17 | 23 | 26 | 27 | 27 | 27 | 27 | 483300
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 |  | 32 | 32 | 25 | 25 | 33 | 33 | 33 | 745200
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 87 | 87 | 87 | 89 | 89 | 89 | 87 | 87 | 89 | 86 | 86 | 87 | 89 | 89 | 89 | 55 |  | 81 | 85 | 87 | 89 | 91 | 89 | 88 | 2058500
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 938220
| Chowmuhani 113 MW | 108 | 104 | 115 | 115 | 105 | 98 | 98 | 98 | 98 | 98 | 97 | 98 | 97 | 98 | 97 | 98 | 65 | 24 |  | 47 | 116 | 114 | 115 | 115 | 115 | 115 | 2418360
| Manikgonj 162MW PP(MPGL) | 82 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 162 | 54 | 54 |  | 64 | 162 | 162 | 162 | 162 | 162 | 162 | 1971360
77 | Siddhirganj 100 PP(Dutch Bangla) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 28 | 50 | 72 | 96 | 92 | 100 | 41 | 880464
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1199040
79 | Kodda 150MW PP | 98 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 73 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 64 |  | 100 | 149 | 149 | 146 | 146 | 146 | 98 | 2242080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 18 | 43 | 43 | 43 | 43 | 43 | 43 | 396811
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2473200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 36961
| Jodiac Power | 45 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 46 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1064080
| Karnaphuli Power Ltd. | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 51 | 51 |  | 58 | 90 | 102 | 110 | 110 | 110 | 110 | 2559261
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 24 | 24 | 22 | 23 | 24 | 24 | 24 | 25 | 24 | 24 | 23 | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 23 | 59 | 55 | 66 | 75 | 86 | 39 | 729600
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 32 | 17 | 17 | 17 | 17 | 35 | 35 |  | 36 | 88 | 88 | 91 | 91 | 91 | 25 | 786240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 66 | 73 | 65 | 65 | 65 | 65 | 65 | 20 | 10 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1659240
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 35 | 42 | 45 | 42 | 44 | 838800
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1188748
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 50 | 94 | 94 | 94 | 94 | 90 | 24 | 865584
95 | Patenga 50MW PP (Baraka) | 32 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 0 | 7 | 31 | 36 | 36 | 35 | 36 | 36 | 30 |  | 30 | 36 | 35 | 36 | 37 | 37 | 37 | 824160
96 | Chattogram 108 MW PP (ECPV) | 86 | 86 | 87 | 85 | 82 | 82 | 82 | 79 | 81 | 78 | 75 | 74 | 77 | 74 | 73 | 78 | 44 | 40 |  | 54 | 74 | 77 | 81 | 87 | 86 | 85 | 1841280
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 45 | 55 | 55 | 30 | 30 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 1263117
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 |  | 299893
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2598790
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 10950
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 54 | 54 | 17 | 54 | 54 | 54 | 612720
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 87 | 87 | 87 | 88 | 88 | 88 | 72 | 83 | 83 | 83 | 83 | 82 | 83 | 83 | 83 | 83 | 83 | 120 |  | 127 | 200 | 200 | 200 | 200 | 200 | 87 | 2565600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 116 | 113 | 102 | 112 | 115 | 110 | 113 | 117 | 116 | 116 | 102 | 117 | 102 | 100 | 99 | 90 | 81 | 60 |  | 68 | 85 | 97 | 97 | 97 | 97 | 99 | 2456064
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 65 |  | 72 | 90 | 90 | 90 | 90 | 90 | 21 | 835200
116 | Chandpur 200MW (Desh energy) | 113 | 50 | 50 | 50 | 50 | 50 |  |  |  |  | 1 | 46 | 50 | 50 | 50 | 50 | 68 | 68 |  | 74 | 200 | 175 | 200 | 200 | 200 | 200 | 1855680
117 | Ashuganj 150MW PP (Midland) | 129 | 125 | 125 | 133 | 136 | 141 | 132 | 125 | 127 | 134 | 130 | 132 | 130 | 128 | 125 | 132 | 130 | 135 |  | 137 | 13 | 137 | 137 | 140 | 140 | 136 | 3207253
118 | Bibiyana-III 400 MW CCPP | 397 | 402 | 403 | 402 | 403 | 402 | 364 | 365 | 367 | 404 | 404 | 402 | 365 | 363 | 403 | 404 | 366 | 365 |  | 401 | 367 | 366 | 405 | 405 | 403 | 404 | 9342000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 87 |  | 106 | 106 | 106 | 106 | 106 | 106 | 49 | 1484400
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 85 |  | 200 | 289 | 300 | 300 | 300 | 86 | 88 | 2847818
| Juldah unit-2 (Acorn) | 44 | 20 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 14 | 20 | 20 | 20 | 20 | 50 |  | 60 | 90 | 90 | 90 | 90 | 90 | 54 | 885120
| Anlima Energy Ltd. | 90 | 100 | 106 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 100 | 90 | 90 | 98 |  | 65 | 108 | 108 | 108 | 108 | 108 | 108 | 2482745
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 23 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 734040
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 7 | 15 | 14 | 30 | 34 | 34 | 35 | 23 | 9 | 20 | 10 | 1 | [8 empty] | 220274
| Chandpur 115(Doreen) | 39 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 33 | 35 | 35 | 35 | 35 | 42 | 57 | 45 | 35 |  | 31 | 35 | 30 | 35 | 20 | 18 | 18 | 835200
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 51 | 55 | 55 | 55 | 1337040
120 | Eastern Zone Total | 7113 | 6982 | 6963 | 6986 | 6962 | 6840 | 6681 | 6597 | 6606 | 6575 | 6602 | 6600 | 6616 | 6612 | 6785 | 6843 | 6484 | 6448 |  | 7280 | 8021 | 8285 | 8584 | 8513 | 8321 | 7592 | 170709264
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 81 | 67 | 81 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 34 | 35 |  | 68 | 68 | 71 | 80 | 79 | 33 | 32 | 1076160
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 38 | 38 | 38 | 38 | 38 | 38 | [11 empty] | 15 |  | 32 | 40 | 50 | 44 | 45 | 45 | 42 | 458880
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 45 | 17 |  | 35 | 82 | 82 | 70 | 70 | 70 | 35 | 1004640
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 24 | 50 | 75 | 88 | 104 | 102 | 104 | 66 | 64 | 42 | 15 | 8 | [8 empty] | 732960
131
132 | United Payra Power Ltd. | 17 | [18 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 124800
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 220 | 223 | 222 | 223 | 200 | 224 | 184 | 184 | 219 | 216 | 216 | 165 | 210 | 210 | 200 | 224 | 204 |  | 214 | 181 | 214 | 220 | 220 | 222 | 220 | 5026964
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 547488
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 60 | 63 | 60 | 60 | 61 | 55 | 60 | 58 | 60 | 60 | 60 | 60 | 52 | 60 | 60 | 60 | 60 | 60 |  | 60 | 54 | 60 | 60 | 60 | 60 | 60 | 1418000
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 30 | 29 | 28 | 26 | 26 | 23 | 22 | 22 | 19 | 24 | 26 | 26 | 24 | 23 | 22 | 21 |  | 27 | 25 | 26 | 32 | 32 | 32 | 31 | 618789
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 229875
143 | Gopalganj 100 MW Peaking PP | 55 | 55 | 55 | 55 | 55 | 55 | [11 empty] | 15 |  | 40 | 50 | 67 | 60 | 60 | 55 | 55 | 645504
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2547360
146 | Bheramara HVDC | 895 | 895 | 895 | 895 | 895 | 895 | 894 | 895 | 895 | 860 | 860 | 859 | 860 | 859 | 857 | 858 | 857 | 857 |  | 857 | 857 | 844 | 844 | 843 | 844 | 843 | 21010909
147 | Bheramara 410 MW CCPP | 160 | 155 | 155 | 155 | 165 | 165 | 165 | 170 | 170 | 165 | 160 | 155 | 155 | 155 | 145 | 160 | 160 | 160 |  | 160 | 170 | 170 | 165 | 165 | 170 | 170 | 4069440
148 | Payra 1320 MW | 1090 | 1090 | 1070 | 1070 | 1060 | 980 | 980 | 970 | 950 | 950 | 940 | 950 | 970 | 920 | 940 | 980 | 940 | 880 |  | 880 | 970 | 990 | 1000 | 1030 | 1040 | 1060 | 25806500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 4888900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 28 | 28 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 712880
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 2 | 3 | 2 | 0 | 0 | 1 | 3 | 1 | 0 | [8 empty] | 24360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 165 | 164 | 165 | 164 | 164 | 164 | 165 | 163 | 161 | 158 | 152 | 149 | 146 | 142 | 140 | 140 | 140 | 140 |  | 140 | 140 | 142 | 145 | 145 | 144 | 144 | 3854545
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 216 | 217 | 218 | 219 | 214 | 202 | 130 | 130 | 130 | 130 | 137 | 181 | 185 | 130 | 130 | 130 | 130 | 130 |  | 139 | 160 | 160 | 176 | 213 | 217 | 219 | 4319545
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 131 | 130 | 130 | 131 | 133 | 133 | 135 | 136 | 136 | 133 | 131 | 129 | 128 | 129 | 128 | 128 | 130 | 130 |  | 132 | 135 | 136 | 137 | 137 | 137 | 137 | 3416936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 283 | 289 | 306 | 318 | 319 | 322 | 285 | 251 | 250 | 310 | 298 | 290 | 290 | 285 | 285 | 303 | 306 | 305 |  | 305 | 308 | 308 | 309 | 309 | 320 | 320 | 7221163
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | [5 empty] | 0 | 5 | 15 | 20 | 20 | 27 | 27 |  | 28 | 28 | 28 | 28 | 28 | 27 | 33 | 410602
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 21 | 21 | 20 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 476880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250992
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 661100
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 676380
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 |  |  |  | 52 | 43 | 43 | 265200
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 86 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1999768
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 100 | 50 |  | 35 | 60 | 105 | 113 | 113 | 113 | 70 | 1986912
172 | Confidence Power Bogura Unit-1 113 MW | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 108 | 111 | 35 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2037888
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 95 | 98 | 85 | 84 | 83 | 85 | 78 | 79 | 85 | 85 | 85 | 85 | 56 | 55 |  | 68 | 105 | 106 | 107 | 107 | 106 | 104 | 2193436
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 5 | 5 | 6 | 5 | 5 | 6 | 4 | 2 | 1 | [8 empty] | 40409
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 90 | 90 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1602624
178