## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-01 | Monday
|  |  | Date (day): | 2022-08-01 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10933.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12700 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-07-31 | 2022-08-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 81 | 82 | 82 | 82 |  | 26 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 399 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 260 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 25 | 87 | 25 | 88 |  | 12 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 24 | 89 | 24 | 92 |  | 8 | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 94 | 24 | 94 |  | 8 | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 54 |  | 0 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 147 | 100 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55 |  |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55 |  |  | Fuel shortage
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 29 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 49 | 50 | 50
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 160 | 195 | 150 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 106 | 144 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 96 | 17 | 91 | 14 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162 |  |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 7 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 52 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2414 | 2991 | 2513 | 3197 | 1700 | 952
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 19 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 6 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 37 | 37 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 114 | 115 | 115 |  | 115 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 43 | 41 | 41 | 57 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 51 | 68 | 34 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 56 | 56 | 55 | 55 | 45 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 27 | 4 | 15
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 92 | 86 | 88 | 88 |  | 20 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 215 | 51 | 210 |  |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 36 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 92 | 92 | 92 |  | 18 | Engine problem
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 970 | 1337 | 991 | 1320 | 396 | 564
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 145 | 184 | 200 | 200
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 225 | 350 | 300 | 320
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 320 | 300 | 320
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 41 | 41 | 41 |  | 4 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 56 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 16 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 0 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 127 | 137 | 135 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 30 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 135 | 128 | 128 | 128 |  | 35 | Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 200 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 150 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 8 | 34 | 18 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 104 | 17 | 114 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 115 | 100 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 22 | 35 | 75 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1683 | 2072 | 1810 | 2114 | 579 | 85
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 71 | 100 | 65 | 65 | 137 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 88 | 144 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 77 | 45 | 105 |  | 10 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 3 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 249 | 361 | 247.6 | 388 | 137 | 42
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 53 | 33 | 33
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 43 | 30 | 30
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 40 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 81 | 20 | 20 |  |  | Gas shortage
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 33 | 34 | 33 | 33 | 17 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 16 | 24
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 280 | 300 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1353 | 1413 | 1307 | 1339 | 37 | 943
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 897 | 844 | 881 | 868
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 45 |  | 9 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 0 | 65 |  | 44 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 165 | 160 | 160 | 160 | 250 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 8 | 8 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 54 | 35 | 90 | 15 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 88 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 65 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1274 | 1284 | 1305 | 1357 | 742 | 53
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 32 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 34 | 23 | 32 |  | 8 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 | 134 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 970 | 1090 | 1110 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 212 | 220 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1281 | 1453 | 1467 | 1461 | 134 | 8
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 24 | 24 |  | 28 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 41 |  | 30 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 142 | 132 | 135 | 135 | 75 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 204 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 137 | 129 | 140 | 140 | 80 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 317 | 312 | 305 | 315 | 99 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 22 | 35 | 35 | 35 |  | 15 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52 |  |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 81 | 87 | 85 | 88 |  | 16 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 70 | 113
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 113 | 75 | 113
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1078 | 1306 | 948 | 1121 | 895 | 107
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 85 | 113 | 85 | 113
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 90 | 52 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 339 | 403 | 345 | 403 | 199 | 110
|  | Total |  |  |  |  | 22482 | 21680 | 10641 | 12620 | 10933.6 | 12700 | 4819 | 2864
| A. |  | 2022-07-31 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12628 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10641 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13800 | MW
| 3 | Day peak Generation : |  |  | 10641 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13335.23 | MW
| 4 | Evening peak Generation : |  |  | 12620 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1087 | MW
| 5 | Total Energy Generation : |  | 271.5052 | MKWHr | By Solar | 0.98757 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 131.3208 | MKWHr |  | By Oil: | 79.9271 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 31.7969 | MKWHr |  | By Hydro: | 2.7293 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4819 | MW | Dhaka | 4850.19 | 4640.19 |  | 210
|  |  |  | For Plants S/D or M/C prob = |  |  | 2864 | MW | Chittagong | 1384.21 | 1384.21 |  | 0 |  | 18:00 |  | 475
|  |  |  | Total = |  |  | 7683 | MW | Khulna | 1732 | 1532 |  | 200
| 7 | Total Gas Supplied : |  |  | 1003.7 | MMCFD |  |  | Rajshahi | 1195 | 1095 |  | 100 |  | 19:00 |  | 1582
| 8 | Fuel Cost : | i) Gas : | Taka | 151188920.852 | ii) Oil : | Taka | 1094509772.87 | Comilla | 1326 | 1116 |  | 210 |  | 19:30 |  | 1444
|  |  | iii) Coal : |  | 268407149 | Total | Taka | 1514105842.722 | Mymensingh | 1117 | 868 |  | 249 |  | 20:00 |  | 1307
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 521 | 503 |  | 18 |  | 21:00 |  | 1087
|  | ii) During Peak Demand : |  |  | 526 | MW (E to W) at | 21:00 | hrs | Barisal | 407.83 | 407.83 |  | 0 |  | 22:00 |  | 988
|  | iii) Maximum : |  |  | 442 | MW at | 19:00 | hrs | Rangpur | 802 | 702 |  | 100 |  | 23:00 |  | 955
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 13335.23 | 12248.23 |  | 1087
| B. |  | 2022-08-01 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1195 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12700 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 301.0035 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10381 | MW at | 8:00 | 350 | 130 | 170 | 160 | 135 | 115 | 45 | 0 | 90
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.0524 | MKWHr. | ii) HVDC Flow at Peak Time |  | 844 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6912 | MKWHr. | iii) Maximum HVDC Flow : |  | 898 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.98 |  | (b) Today: | 92.01 |  | (c) Rule Curve: |  | 89
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-07-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 405 | 326 |  | 0 | 225 | 0 | 24 | 0 | 0 | 0 | 0 | 62 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 33 | 51 | 80 | 81 | 33 | 17 | 28 | 0 | 0 | 0 | 0 | 340 | 207 | 175 | 136 | 41 | 56 | 0 | 43 | 0 | 40 | 43 | 19 | 10 | 33 | 20 | 150 | 104 | 0 | 20 | 0 | 43 | 41 | 53 | 45 | 110 | 0 | 63 | 81 | 0 | 220 | 0 | 33 | 10 | 310 | 8 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 116 | 0 | 21 | 126 | 127 | 400 | 49 | 88 | 87 | 0 | 87 | 36 | 110 | 17 | 107 | 35 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 24 | 47 | 0 |  | 898 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 61 | 8 | 60 | 36 | 32 | 0 | 0 | 0 | 24 | 41 | 87 | 0 | 0 | 20 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 136 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 283 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1100 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6928 | 4278 | 11206 | 3409 | 898 | 2141 | 0 | 2502 | 1300 | 116 | 213 | 690 | 150 | 0 | 1469 | 91.98
2:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 407 | 326 |  | 0 | 225 | 0 | 24 | 0 | 40 | 0 | 0 | 61 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 18 | 51 | 80 | 81 | 37 | 17 | 30 | 0 | 0 | 0 | 0 | 345 | 207 | 175 | 135 | 41 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 152 | 103 | 0 | 20 | 0 | 44 | 41 | 53 | 45 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 32 | 10 | 315 | 16 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 117 | 0 | 21 | 50 | 135 | 403 | 49 | 88 | 88 | 0 | 87 | 36 | 110 | 17 | 111 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 17 | 40 | 0 |  | 897 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 38 | 58 | 8 | 60 | 35 | 32 | 0 | 0 | 0 | 24 | 41 | 87 | 0 | 0 | 23 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 136 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 305 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 75 | 1090 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6794 | 4327 | 11121 | 3424 | 897 | 2109 | 0 | 2420 | 1290 | 116 | 213 | 713 | 152 | 0 | 1363 | 91.98
3:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 406 | 323 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 95 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 26 | 51 | 66 | 78 | 32 | 17 | 30 | 0 | 0 | 0 | 32 | 340 | 207 | 167 | 135 | 41 | 56 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 130 | 102 | 0 | 20 | 0 | 44 | 41 | 33 | 30 | 110 | 0 | 66 | 20 | 0 | 220 | 0 | 32 | 10 | 325 | 22 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 117 | 0 | 21 | 50 | 140 | 403 | 49 | 88 | 103 | 0 | 88 | 36 | 110 | 17 | 107 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 18 | 54 | 0 |  | 897 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 43 | 53 | 8 | 60 | 35 | 32 | 0 | 0 | 0 | 24 | 40 | 87 | 0 | 0 | 23 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 213 | 0 | 0 | 137 | 0 | 315 | 35 | 0 | 70 | 105 | 106 | 0 | 0 | 75 | 1090 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6840 | 4334 | 11174 | 3499 | 897 | 2084 | 0 | 2438 | 1290 | 116 | 213 | 720 | 130 | 0 | 1130 | 91.98
4:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 409 | 334 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 98 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 73 | 34 | 17 | 33 | 0 | 0 | 0 | 0 | 350 | 209 | 177 | 135 | 41 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 140 | 103 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 32 | 10 | 310 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 117 | 0 | 21 | 50 | 137 | 402 | 49 | 88 | 90 | 0 | 88 | 36 | 110 | 17 | 107 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 18 | 51 | 0 |  | 897 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 43 | 53 | 8 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 40 | 87 | 0 | 0 | 23 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 216 | 0 | 0 | 138 | 0 | 320 | 35 | 0 | 70 | 105 | 106 | 0 | 0 | 75 | 1090 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6793 | 4303 | 11096 | 3484 | 897 | 2094 | 0 | 2378 | 1290 | 116 | 216 | 697 | 140 | 0 | 1017 | 91.98
5:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 332 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 98 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 87 | 37 | 17 | 34 | 0 | 0 | 0 | 50 | 345 | 208 | 177 | 135 | 41 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 134 | 104 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 32 | 10 | 300 | 24 | 11 | 0 | 168 | 0 | 0 | 88 | 0 | 117 | 0 | 21 | 50 | 133 | 402 | 49 | 88 | 87 | 0 | 88 | 36 | 110 | 17 | 110 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 0 | 18 | 55 | 0 |  | 897 | 0 | 165 | 0 | 16 | 0 | 0 | 0 | 42 | 53 | 8 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 40 | 87 | 0 | 0 | 29 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 141 | 0 | 0 | 216 | 0 | 0 | 138 | 0 | 332 | 35 | 0 | 70 | 105 | 100 | 0 | 0 | 75 | 1070 | 223 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6847 | 4305 | 11152 | 3538 | 897 | 2098 | 0 | 2397 | 1270 | 116 | 216 | 702 | 134 | 0 | 505 | 91.98
6:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 409 | 333 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 60 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 88 | 37 | 17 | 34 | 0 | 0 | 0 | 224 | 355 | 211 | 177 | 135 | 41 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 124 | 104 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 64 | 20 | 0 | 220 | 0 | 32 | 10 | 280 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 117 | 1 | 21 | 50 | 133 | 401 | 49 | 88 | 87 | 0 | 88 | 36 | 110 | 17 | 112 | 20 | 0 | 17 | 0 | 54 | 108 | 0 | 35 | 1 | 23 | 55 | 0 |  | 897 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 26 | 16 | 0 | 0 | 0 | 24 | 0 | 87 | 0 | 0 | 31 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 190 | 0 | 0 | 140 | 0 | 337 | 37 | 0 | 70 | 105 | 100 | 0 | 0 | 75 | 1050 | 210 | 0 | 0 | 0 | 4 | 52 | 0 | 0 |  | 6969 | 4111 | 11080 | 3696 | 897 | 2065 | 0 | 2383 | 1250 | 116 | 190 | 543 | 124 | 6 | 203 | 91.98
7:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 410 | 330 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 39 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 88 | 37 | 17 | 36 | 0 | 0 | 0 | 235 | 345 | 208 | 177 | 135 | 40 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 0 | 20 | 118 | 104 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 32 | 10 | 290 | 24 | 11 | 0 | 165 | 0 | 0 | 88 | 0 | 117 | 3 | 21 | 50 | 129 | 403 | 49 | 88 | 87 | 1 | 88 | 36 | 110 | 17 | 107 | 20 | 0 | 17 | 4 | 54 | 108 | 0 | 35 | 4 | 26 | 55 | 0 |  | 897 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 25 | 16 | 0 | 0 | 0 | 24 | 0 | 87 | 0 | 0 | 31 | 8 | 22 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 333 | 37 | 0 | 70 | 88 | 100 | 0 | 0 | 75 | 1000 | 194 | 0 | 0 | 0 | 23 | 52 | 0 | 0 |  | 6921 | 4022 | 10943 | 3640 | 897 | 2050 | 0 | 2366 | 1200 | 114 | 170 | 523 | 118 | 35 | 145 | 91.99
8:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 407 | 323 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 32 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 56 | 88 | 37 | 17 | 13 | 0 | 0 | 0 | 240 | 350 | 155 | 148 | 135 | 40 | 56 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 140 | 95 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 62 | 20 | 0 | 220 | 0 | 34 | 10 | 320 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 112 | 10 | 21 | 50 | 120 | 402 | 49 | 88 | 87 | 2 | 88 | 36 | 110 | 17 | 105 | 20 | 0 | 17 | 3 | 54 | 108 | 0 | 35 | 7 | 22 | 55 | 0 |  | 897 | 0 | 165 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 32 | 8 | 22 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 170 | 0 | 0 | 139 | 0 | 321 | 35 | 0 | 70 | 88 | 85 | 0 | 1 | 76 | 990 | 194 | 0 | 0 | 0 | 58 | 52 | 0 | 0 |  | 6828 | 3988 | 10816 | 3572 | 897 | 2006 | 0 | 2315 | 1190 | 115 | 170 | 500 | 140 | 81 | 446 | 91.99
9:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 407 | 322 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 30 | 50 | 0 | 80 | 35 | 100 | 0 | 19 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 56 | 92 | 37 | 17 | 3 | 0 | 0 | 0 | 225 | 335 | 145 | 73 | 135 | 40 | 56 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 28 | 20 | 150 | 71 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 33 | 10 | 315 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 106 | 6 | 21 | 50 | 127 | 403 | 49 | 88 | 87 | 4 | 88 | 36 | 110 | 17 | 105 | 20 | 0 | 17 | 3 | 54 | 108 | 0 | 35 | 7 | 22 | 55 | 0 |  | 897 | 0 | 165 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 32 | 8 | 22 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 164 | 0 | 0 | 137 | 0 | 317 | 35 | 0 | 70 | 88 | 85 | 0 | 2 | 75 | 970 | 212 | 0 | 0 | 0 | 65 | 52 | 0 | 0 |  | 6669 | 3972 | 10641 | 3496 | 897 | 1925 | 0 | 2313 | 1170 | 115 | 164 | 488 | 150 | 87 | 792 | 91.99
10:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 403 | 322 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 16 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 55 | 87 | 37 | 17 | 5 | 0 | 0 | 0 | 240 | 350 | 147 | 63 | 135 | 40 | 30 | 0 | 43 | 0 | 24 | 8 | 19 | 10 | 22 | 20 | 154 | 71 | 0 | 20 | 0 | 44 | 41 | 33 | 30 | 110 | 0 | 63 | 20 | 0 | 220 | 0 | 33 | 10 | 330 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 106 | 18 | 21 | 50 | 130 | 402 | 49 | 88 | 87 | 6 | 88 | 36 | 110 | 17 | 105 | 20 | 0 | 17 | 1 | 54 | 108 | 0 | 35 | 13 | 32 | 55 | 0 |  | 862 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 32 | 8 | 27 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 139 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 299 | 35 | 0 | 70 | 88 | 85 | 0 | 1 | 75 | 980 | 216 | 0 | 0 | 0 | 71 | 52 | 0 | 0 |  | 6678 | 3875 | 10553 | 3487 | 862 | 1886 | 0 | 2325 | 1180 | 115 | 130 | 434 | 154 | 110 | 1057 | 91.99
11:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 322 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 16 | 42 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 14 | 0 | 50 | 66 | 87 | 37 | 17 | 5 | 0 | 0 | 0 | 240 | 345 | 200 | 63 | 136 | 40 | 10 | 0 | 43 | 0 | 26 | 8 | 19 | 10 | 16 | 20 | 158 | 71 | 0 | 20 | 0 | 44 | 41 | 33 | 30 | 110 | 0 | 61 | 20 | 0 | 220 | 0 | 33 | 10 | 300 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 105 | 20 | 21 | 50 | 127 | 403 | 49 | 88 | 87 | 6 | 88 | 36 | 110 | 17 | 97 | 20 | 0 | 36 | 7 | 54 | 90 | 0 | 35 | 14 | 57 | 55 | 0 |  | 862 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 32 | 8 | 30 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 138 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 293 | 34 | 0 | 70 | 88 | 85 | 0 | 0 | 75 | 990 | 216 | 0 | 0 | 1 | 90 | 52 | 0 | 0 |  | 6702 | 3901 | 10603 | 3532 | 862 | 1832 | 0 | 2337 | 1190 | 116 | 130 | 438 | 158 | 138 | 1287 | 91.99
12:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 401 | 322 |  | 0 | 225 | 0 | 23 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 42 | 0 | 81 | 35 | 100 | 0 | 21 | 0 | 0 | 0 | 0 |  | 15 | 0 | 50 | 66 | 78 | 37 | 17 | 10 | 0 | 0 | 0 | 230 | 330 | 194 | 63 | 135 | 40 | 10 | 0 | 43 | 0 | 32 | 8 | 19 | 10 | 24 | 20 | 164 | 67 | 0 | 20 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 20 | 0 | 220 | 0 | 33 | 10 | 330 | 24 | 11 | 0 | 160 | 0 | 0 | 87 | 0 | 104 | 18 | 21 | 50 | 124 | 368 | 49 | 70 | 105 | 2 | 88 | 36 | 110 | 17 | 107 | 20 | 0 | 34 | 12 | 54 | 90 | 0 | 35 | 15 | 58 | 55 | 0 |  | 862 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 32 | 8 | 36 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 137 | 0 | 0 | 130 | 0 | 0 | 134 | 0 | 282 | 34 | 0 | 70 | 88 | 77 | 0 | 0 | 75 | 1000 | 216 | 0 | 0 | 1 | 102 | 52 | 0 | 0 |  | 6646 | 3908 | 10554 | 3469 | 862 | 1856 | 0 | 2320 | 1200 | 116 | 130 | 416 | 164 | 151 | 1517 | 91.99
13:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 401 | 322 |  | 0 | 225 | 0 | 24 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 26 | 25 | 25 | 42 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 50 | 66 | 77 | 32 | 17 | 10 | 0 | 0 | 0 | 230 | 345 | 191 | 63 | 135 | 40 | 10 | 0 | 43 | 0 | 32 | 8 | 19 | 10 | 24 | 20 | 170 | 67 | 0 | 20 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 35 | 10 | 320 | 16 | 11 | 0 | 160 | 0 | 0 | 87 | 0 | 80 | 20 | 21 | 50 | 127 | 402 | 49 | 80 | 105 | 2 | 88 | 36 | 81 | 17 | 103 | 20 | 0 | 34 | 18 | 54 | 90 | 0 | 35 | 14 | 58 | 55 | 0 |  | 862 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 24 | 8 | 36 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 276 | 17 | 0 | 70 | 88 | 85 | 0 | 1 | 75 | 1030 | 217 | 0 | 0 | 2 | 82 | 52 | 0 | 0 |  | 6607 | 3899 | 10506 | 3493 | 862 | 1846 | 0 | 2269 | 1230 | 111 | 130 | 385 | 170 | 140 | 1331 | 91.99
14:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 400 | 322 |  | 0 | 225 | 0 | 24 | 0 | 45 | 0 | 0 | 0 | 24 | 16 | 34 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 26 | 25 | 25 | 42 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 2 | 50 | 66 | 85 | 30 | 17 | 7 | 0 | 0 | 0 | 70 | 335 | 202 | 63 | 135 | 38 | 20 | 0 | 43 | 0 | 32 | 8 | 19 | 10 | 24 | 20 | 168 | 66 | 0 | 20 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 20 | 0 | 220 | 0 | 34 | 10 | 320 | 24 | 11 | 0 | 120 | 0 | 0 | 87 | 0 | 100 | 20 | 21 | 69 | 122 | 403 | 49 | 88 | 87 | 1 | 88 | 36 | 99 | 17 | 101 | 20 | 0 | 34 | 19 | 54 | 90 | 0 | 35 | 13 | 57 | 55 | 0 |  | 861 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 25 | 16 | 0 | 0 | 0 | 0 | 5 | 81 | 0 | 0 | 24 | 8 | 35 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 133 | 0 | 0 | 130 | 0 | 0 | 128 | 0 | 270 | 17 | 0 | 70 | 88 | 85 | 0 | 1 | 75 | 1050 | 214 | 0 | 0 | 2 | 81 | 52 | 0 | 0 |  | 6456 | 3908 | 10364 | 3336 | 861 | 1843 | 0 | 2264 | 1250 | 111 | 130 | 393 | 168 | 138 | 1508 | 91.19
15:00 | 0 | 0 | 0 | 180 | 250 | 78 | 0 | 399 | 316 |  | 0 | 225 | 0 | 24 | 0 | 45 | 0 | 0 | 0 | 24 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 26 | 25 | 26 | 42 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 49 | 66 | 85 | 28 | 17 | 5 | 0 | 0 | 0 | 20 | 330 | 204 | 128 | 135 | 38 | 48 | 0 | 43 | 0 | 33 | 8 | 19 | 11 | 33 | 20 | 168 | 68 | 0 | 20 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 35 | 9 | 320 | 24 | 11 | 0 | 95 | 0 | 0 | 88 | 0 | 127 | 6 | 21 | 100 | 123 | 402 | 49 | 70 | 87 | 2 | 88 | 36 | 99 | 17 | 101 | 20 | 0 | 34 | 19 | 54 | 94 | 0 | 35 | 11 | 42 | 55 | 0 |  | 862 | 0 | 140 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 25 | 16 | 0 | 0 | 0 | 10 | 5 | 81 | 0 | 0 | 24 | 8 | 35 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 131 | 0 | 0 | 130 | 0 | 0 | 127 | 0 | 270 | 17 | 0 | 70 | 88 | 85 | 0 | 2 | 75 | 1050 | 213 | 0 | 0 | 1 | 28 | 52 | 0 | 0 |  | 6468 | 3857 | 10325 | 3235 | 862 | 1925 | 0 | 2268 | 1250 | 113 | 130 | 433 | 168 | 71 | 1636 | 91.99
16:00 | 0 | 0 | 0 | 180 | 250 | 82 | 0 | 398 | 310 |  | 0 | 225 | 0 | 21 | 0 | 45 | 0 | 0 | 0 | 24 | 16 | 34 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 26 | 25 | 18 | 42 | 0 | 78 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 50 | 66 | 84 | 22 | 17 | 5 | 0 | 0 | 0 | 20 | 330 | 203 | 128 | 135 | 38 | 53 | 0 | 43 | 0 | 38 | 8 | 19 | 11 | 33 | 14 | 172 | 68 | 0 | 20 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 35 | 9 | 320 | 24 | 11 | 0 | 95 | 0 | 0 | 88 | 0 | 99 | 6 | 21 | 100 | 128 | 403 | 49 | 88 | 87 | 3 | 88 | 36 | 92 | 17 | 102 | 20 | 0 | 34 | 15 | 140 | 108 | 0 | 35 | 9 | 44 | 34 | 0 |  | 862 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 16 | 16 | 0 | 0 | 0 | 16 | 32 | 81 | 0 | 0 | 29 | 8 | 35 | 17 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 124 | 0 | 270 | 17 | 0 | 75 | 89 | 85 | 0 | 3 | 75 | 990 | 183 | 0 | 0 | 0 | 29 | 52 | 0 | 0 |  | 6498 | 3793 | 10291 | 3186 | 862 | 1889 | 0 | 2334 | 1190 | 113 | 130 | 479 | 172 | 66 | 1483 | 92
17:00 | 0 | 0 | 0 | 180 | 250 | 82 | 0 | 401 | 310 |  | 0 | 225 | 0 | 26 | 0 | 45 | 0 | 0 | 0 | 24 | 16 | 34 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 14 | 25 | 24 | 25 | 26 | 42 | 0 | 76 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 51 | 66 | 85 | 31 | 17 | 11 | 0 | 0 | 0 | 65 | 325 | 201 | 133 | 135 | 38 | 53 | 0 | 43 | 0 | 38 | 8 | 19 | 11 | 33 | 17 | 154 | 69 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 34 | 9 | 300 | 24 | 11 | 0 | 120 | 0 | 0 | 88 | 0 | 99 | 2 | 21 | 136 | 120 | 403 | 49 | 88 | 87 | 1 | 88 | 40 | 84 | 24 | 108 | 20 | 0 | 49 | 14 | 162 | 108 | 0 | 35 | 4 | 39 | 34 | 0 |  | 862 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 14 | 16 | 0 | 0 | 0 | 24 | 36 | 81 | 0 | 0 | 32 | 8 | 35 | 17 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 126 | 0 | 287 | 27 | 0 | 111 | 88 | 105 | 0 | 3 | 113 | 980 | 183 | 0 | 0 | 0 | 27 | 52 | 0 | 0 |  | 6664 | 3921 | 10585 | 3258 | 862 | 1894 | 0 | 2580 | 1180 | 111 | 130 | 495 | 154 | 51 | 1166 | 92
18:00 | 0 | 0 | 0 | 180 | 300 | 76 | 0 | 397 | 296 |  | 0 | 225 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 24 | 25 | 27 | 50 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 51 | 66 | 79 | 33 | 0 | 7 | 0 | 0 | 0 | 135 | 330 | 203 | 125 | 129 | 38 | 53 | 0 | 43 | 0 | 38 | 8 | 19 | 11 | 33 | 17 | 162 | 69 | 0 | 22 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 20 | 0 | 220 | 0 | 36 | 9 | 320 | 24 | 11 | 0 | 230 | 0 | 0 | 143 | 0 | 115 | 0 | 21 | 200 | 125 | 404 | 76 | 88 | 94 | 0 | 88 | 54 | 92 | 114 | 113 | 20 | 0 | 90 | 2 | 162 | 108 | 0 | 35 | 2 | 42 | 34 | 0 |  | 862 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 7 | 10 | 8 | 60 | 14 | 16 | 0 | 0 | 0 | 16 | 41 | 87 | 0 | 0 | 32 | 8 | 35 | 19 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 128 | 0 | 276 | 35 | 0 | 113 | 89 | 107 | 0 | 1 | 113 | 980 | 183 | 0 | 0 | 0 | 5 | 90 | 0 | 0 |  | 7314 | 3971 | 11285 | 3386 | 862 | 1875 | 0 | 3170 | 1179 | 112 | 130 | 529 | 162 | 10 | 475 | 92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1551 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 78 | 0 | 398 | 278 |  | 0 | 225 | 0 | 45 | 0 | 45 | 0 | 0 | 0 | 48 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 28 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 68 | 66 | 82 | 37 | 17 | 17 | 0 | 0 | 0 | 230 | 330 | 202 | 125 | 128 | 39 | 55 | 0 | 43 | 0 | 47 | 16 | 19 | 11 | 33 | 20 | 168 | 85 | 0 | 22 | 0 | 44 | 41 | 33 | 30 | 110 | 0 | 61 | 20 | 0 | 220 | 0 | 36 | 9 | 325 | 24 | 11 | 0 | 195 | 0 | 0 | 143 | 0 | 149 | 0 | 90 | 200 | 130 | 400 | 77 | 105 | 105 | 0 | 205 | 54 | 92 | 114 | 113 | 52 | 0 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 41 | 34 | 0 |  | 844 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 41 | 45 | 8 | 60 | 29 | 32 | 0 | 0 | 0 | 16 | 41 | 87 | 0 | 0 | 32 | 37 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 127 | 0 | 286 | 47 | 0 | 113 | 88 | 113 | 0 | 0 | 113 | 980 | 211 | 0 | 11 | 0 | 0 | 90 | 0 | 0 |  | 7967 | 4150 | 12117 | 3522 | 844 | 1932 | 0 | 3635 | 1180 | 113 | 130 | 723 | 168 | 0 | 1582 | 92.01
19:30 | 0 | 0 | 0 | 180 | 240 | 78 | 0 | 390 | 268 |  | 0 | 225 | 0 | 77 | 0 | 55 | 0 | 0 | 0 | 60 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 28 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 34 | 67 | 55 | 86 | 37 | 17 | 19 | 0 | 0 | 0 | 265 | 330 | 208 | 125 | 129 | 39 | 55 | 0 | 43 | 0 | 47 | 34 | 19 | 11 | 33 | 20 | 154 | 97 | 0 | 22 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 40 | 78 | 0 | 220 | 0 | 34 | 9 | 260 | 24 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 135 | 0 | 90 | 200 | 128 | 353 | 77 | 105 | 105 | 0 | 210 | 54 | 92 | 114 | 113 | 100 | 0 | 96 | 0 | 162 | 108 | 0 | 35 | 0 | 36 | 34 | 0 |  | 844 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 49 | 55 | 8 | 52 | 32 | 32 | 0 | 0 | 0 | 16 | 41 | 87 | 0 | 0 | 32 | 43 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 131 | 0 | 0 | 130 | 0 | 0 | 127 | 0 | 293 | 54 | 0 | 113 | 95 | 113 | 0 | 0 | 113 | 1040 | 183 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7954 | 4229 | 12183 | 3432 | 844 | 1897 | 0 | 3763 | 1240 | 113 | 130 | 740 | 154 | 0 | 1444 | 0
20:00 | 0 | 0 | 0 | 180 | 250 | 85 | 0 | 393 | 262 |  | 0 | 225 | 0 | 75 | 0 | 55 | 0 | 0 | 0 | 88 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 28 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 37 | 67 | 56 | 86 | 37 | 17 | 24 | 0 | 0 | 0 | 360 | 320 | 183 | 78 | 128 | 40 | 54 | 0 | 43 | 0 | 38 | 34 | 19 | 11 | 33 | 20 | 156 | 100 | 0 | 22 | 0 | 43 | 41 | 53 | 40 | 110 | 0 | 40 | 81 | 0 | 220 | 0 | 34 | 9 | 260 | 24 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 135 | 0 | 90 | 200 | 130 | 351 | 77 | 105 | 105 | 0 | 213 | 54 | 92 | 114 | 113 | 100 | 0 | 94 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 37 | 0 |  | 844 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 34 | 73 | 8 | 54 | 32 | 32 | 0 | 0 | 0 | 16 | 41 | 87 | 0 | 0 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 131 | 0 | 0 | 135 | 0 | 0 | 128 | 0 | 297 | 54 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1050 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8047 | 4310 | 12357 | 3509 | 844 | 1929 | 0 | 3814 | 1250 | 113 | 135 | 742 | 156 | 0 | 1307 | 92.01
21:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 399 | 260 |  | 0 | 225 | 0 | 87 | 0 | 55 | 0 | 0 | 0 | 89 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 29 | 49 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 43 | 68 | 56 | 86 | 37 | 17 | 27 | 0 | 0 | 0 | 350 | 320 | 184 | 16 | 128 | 41 | 55 | 0 | 43 | 0 | 30 | 34 | 19 | 11 | 33 | 20 | 162 | 100 | 0 | 22 | 0 | 43 | 41 | 53 | 43 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 34 | 9 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 144 | 0 | 90 | 200 | 137 | 402 | 77 | 105 | 105 | 0 | 215 | 54 | 92 | 104 | 115 | 100 | 0 | 96 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 52 | 0 |  | 844 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 35 | 62 | 8 | 60 | 34 | 32 | 0 | 0 | 0 | 24 | 41 | 87 | 0 | 0 | 32 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 204 | 0 | 0 | 129 | 0 | 312 | 54 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1090 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8174 | 4446 | 12620 | 3644 | 844 | 1905 | 0 | 3853 | 1290 | 114 | 204 | 808 | 162 | 0 | 1087 | 92.01
22:00 | 0 | 0 | 0 | 180 | 300 | 78 | 0 | 398 | 262 |  | 0 | 225 | 0 | 89 | 0 | 55 | 0 | 0 | 0 | 90 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 25 | 16 | 42 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 43 | 68 | 56 | 95 | 37 | 17 | 33 | 0 | 0 | 0 | 320 | 320 | 186 | 8 | 128 | 41 | 56 | 0 | 43 | 0 | 30 | 34 | 19 | 11 | 33 | 20 | 164 | 105 | 0 | 22 | 0 | 43 | 41 | 53 | 43 | 110 | 0 | 64 | 81 | 0 | 220 | 0 | 34 | 9 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 149 | 0 | 90 | 200 | 139 | 401 | 77 | 105 | 105 | 0 | 213 | 54 | 92 | 114 | 115 | 100 | 0 | 97 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 55 | 0 |  | 843 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 39 | 62 | 8 | 60 | 35 | 32 | 0 | 0 | 0 | 24 | 41 | 87 | 0 | 0 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 133 | 0 | 0 | 218 | 0 | 0 | 129 | 0 | 309 | 54 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1090 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 8164 | 4464 | 12628 | 3601 | 843 | 1911 | 0 | 3877 | 1290 | 115 | 218 | 827 | 164 | 0 | 988 | 92.01
23:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 398 | 282 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 89 | 94 | 147 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 25 | 25 | 25 | 32 | 42 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 43 | 68 | 55 | 94 | 37 | 17 | 37 | 0 | 0 | 0 | 320 | 320 | 196 | 8 | 128 | 41 | 55 | 0 | 43 | 0 | 32 | 34 | 19 | 11 | 33 | 20 | 164 | 104 | 0 | 22 | 0 | 43 | 41 | 53 | 45 | 110 | 0 | 64 | 81 | 0 | 220 | 0 | 33 | 9 | 310 | 24 | 11 | 0 | 190 | 0 | 0 | 144 | 0 | 149 | 0 | 90 | 200 | 142 | 402 | 79 | 105 | 105 | 0 | 51 | 54 | 92 | 80 | 115 | 100 | 0 | 92 | 0 | 162 | 108 | 0 | 35 | 0 | 60 | 55 | 0 |  | 843 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 39 | 62 | 8 | 60 | 35 | 32 | 0 | 0 | 0 | 34 | 41 | 87 | 0 | 0 | 32 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 217 | 0 | 0 | 128 | 0 | 300 | 54 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1110 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7985 | 4479 | 12464 | 3628 | 843 | 1951 | 0 | 3615 | 1310 | 115 | 217 | 838 | 164 | 0 | 955 | 92.01
24:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 399 | 301 |  | 0 | 225 | 0 | 34 | 0 | 45 | 0 | 0 | 0 | 33 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 30 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 43 | 68 | 56 | 96 | 37 | 17 | 37 | 0 | 0 | 0 | 320 | 320 | 199 | 8 | 128 | 41 | 56 | 0 | 43 | 0 | 32 | 34 | 19 | 11 | 33 | 20 | 174 | 104 | 0 | 22 | 0 | 43 | 41 | 53 | 45 | 110 | 0 | 62 | 78 | 0 | 220 | 0 | 33 | 9 | 320 | 24 | 11 | 0 | 115 | 0 | 0 | 60 | 0 | 149 | 0 | 90 | 200 | 142 | 364 | 38 | 105 | 105 | 0 | 51 | 54 | 92 | 34 | 115 | 100 | 0 | 46 | 0 | 144 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 843 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 39 | 62 | 8 | 60 | 36 | 32 | 0 | 0 | 0 | 34 | 41 | 88 | 0 | 0 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 134 | 0 | 0 | 220 | 0 | 0 | 127 | 0 | 305 | 35 | 0 | 70 | 105 | 113 | 0 | 0 | 113 | 1110 | 163 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 7409 | 4329 | 11738 | 3597 | 843 | 1927 | 0 | 2980 | 1310 | 115 | 220 | 792 | 174 | 0 | 979 | 92.01
KWH | 0 | 0 | 0 | 4331250 | 6993909 | 1951863 | 0 | 9760770 | 7442000 |  | 0 | 5010700 | 0 | 869760 | 0 | 1201974 | 0 | 0 | 612000 | 879360 | 736848 | 2160000 | 0 | 0 | 0 | 0 | 504360 | 330829 | 265244 | 420192 | 600000 | 614880 | 586900 | 657600 | 1124482 | 0 | 1889324 | 840000 | 2300000 | 0 | 590194 | 0 | 0 | 0 | 0 |  | 437280 | 457440 | 1317662 | 1530120 | 2049600 | 838080 | 382992 | 459360 | 0 | 0 | 0 | 4199000 | 8085000 | 4707000 | 2525818 | 3186710 | 940536 | 1161120 | 0 | 1029557 | 0 | 891928 | 387874 | 448704 | 237420 | 731700 | 494160 | 3691200 | 2040960 | 0 | 465300 | 6550 | 1027000 | 959960 | 928800 | 872136 | 2632663 | 0 | 1463136 | 967680 | 0 | 5328950 | 0 | 787700 | 228780 | 7621500 | 551736 | 264000 | 0 | 3879053 | 0 | 0 | 2390400 | 0 | 2894400 | 118530 | 880320 | 2536320 | 3134690 | 9522000 | 1335600 | 2170308 | 2304181 | 32279 | 2549236 | 1054437 | 2455552 | 976980 | 2606520 | 961920 | 0 | 1040640 | 119550 | 2178720 | 2512855 | 0 | 887760 | 112789 | 908160 | 1208880 | 0 |  | 21052363 | 0 | 3924576 | 0 | 383040 | 0 | 0 | 0 | 377290 | 623104 | 194250 | 1429000 | 640086 | 565056 | 0 | 0 | 0 | 360992 | 524759 | 1971316 | 0 | 0 | 599800 | 381235 | 668000 | 449760 | 0 | 212346 | 0 | 0 | 4861000 | 0 | 0 | 3464464 | 0 | 0 | 4303255 | 0 | 0 | 3411009 | 0 | 7230364 | 853920 | 0 | 2121792 | 2326032 | 2364028 | 0 | 14556 | 2105568 | 26935900 | 5025709 | 0 | 99600 | 12360 | 570960 | 1664064 | 0 | 0 |  | 169783631 | 101721554 | 271505185 | 84355160 | 21052363 | 46965596 | 0 | 65671522 | 31796900 | 2729324 | 4303255 | 9952291 | 3691200 | 987574 | 0
Fuel Cost | 0 | 0 | 0 | 6453562.5 | 7833178.08 | 2595977.79 | 0 | 10248808.5 | 8037360 |  | 0 | 5461663 | 0 | 9723916.8 | 0 | 15926155.5 | 0 | 0 | 1071000 | 12856243.2 | 10367451.36 | 35013600 | 0 | 0 | 0 | 0 | 6415459.2 | 4466191.5 | 3556922.04 | 315144 | 450000 | 0 | 0 | 0 | 19127438.82 | 0 | 510117.48 | 226800 | 4347000 | 0 | 9649671.9 | 0 | 0 | 0 | 0 |  | 5706504 | 7630099.2 | 22426607.24 | 20671921.2 | 25988928 | 9696585.6 | 486399.84 | 1529668.8 | 0 | 0 | 0 | 4660890 | 8812650 | 5460120 | 3258305.22 | 3887786.2 | 1062805.68 | 1730068.8 | 0 | 1719360.19 | 0 | 15403596.56 | 5216905.3 | 614724.48 | 178065 | 1280475 | 370620 | 26502816 | 2224646.4 | 0 | 632808 | 104407 | 1406990 | 1267147.2 | 1616112 | 1508795.28 | 3027562.45 | 0 | 2838483.84 | 2206310.4 | 0 | 5382239.5 | 0 | 1173673 | 452984.4 | 7621500 | 413802 | 200640 | 0 | 52949073.45 | 0 | 0 | 32222592 | 0 | 40087440 | 1385615.7 | 9084902.4 | 34646131.2 | 41597336.3 | 8760240 | 16240896 | 31382653.68 | 29147889.65 | 0 | 29928030.64 | 11482818.93 | 26102517.76 | 13257618.6 | 33598042.8 | 11331417.6 | 0 | 13476288 | 1727497.5 | 27647956.8 | 28596289.9 | 0 | 11594145.6 | 1347828.55 | 13595155.2 | 15920949.6 | 0 |  | 63157089 | 0 | 4395525.12 | 0 | 3987446.4 | 0 | 0 | 0 | 6794992.9 | 11215872 | 2791372.5 | 1600480 | 1241766.84 | 6159110.4 | 0 | 0 | 0 | 6053835.84 | 9178034.91 | 30831382.24 | 0 | 0 | 10142618 | 5196233.05 | 11269160 | 931003.2 | 0 | 160745.922 | 0 | 0 | 25714690 | 0 | 0 | 4018778.24 | 0 | 0 | 75134832.3 | 0 | 0 | 3956770.44 | 0 | 7158060.36 | 11476684.8 | 0 | 25100799.36 | 33611162.4 | 30023155.6 | 0 | 160843.8 | 25561595.52 | 242692459 | 5126223.18 | 0 | 737040 | 139791.6 | 6697360.8 | 25510101.12 | 0 | 0 |  | 918138993.31 | 697927016.842 | 1616066010.152 | 94792525.942 | 63157089 | 56396394.91 | 0 | 853415141.68 | 268407149 | 736917.48 | 75134832.3 | 165959798.89 | 26502816 | 11563344.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 407 | 322 |  | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 30 | 50 | 0 | 80 | 35 | 100 | 0 | 19 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 56 | 92 | 37 | 17 | 3 | 0 | 0 | 0 | 225 | 335 | 145 | 73 | 135 | 40 | 56 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 28 | 20 | 150 | 71 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 20 | 0 | 220 | 0 | 33 | 10 | 315 | 24 | 11 | 0 | 160 | 0 | 0 | 88 | 0 | 106 | 6 | 21 | 50 | 127 | 403 | 49 | 88 | 87 | 4 | 88 | 36 | 110 | 17 | 105 | 20 | 0 | 17 | 3 | 54 | 108 | 0 | 35 | 7 | 22 | 55 | 0 |  | 897 | 0 | 165 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 32 | 8 | 22 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 142 | 0 | 0 | 164 | 0 | 0 | 137 | 0 | 317 | 35 | 0 | 70 | 88 | 85 | 0 | 2 | 75 | 970 | 212 | 0 | 0 | 0 | 65 | 52 | 0 | 0 |  | 10641 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 399 | 260 | 0 | 0 | 225 | 0 | 87 | 0 | 55 | 0 | 0 | 0 | 89 | 94 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 29 | 49 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | 68 | 56 | 86 | 37 | 17 | 27 | 0 | 0 | 0 | 350 | 320 | 184 | 16 | 128 | 41 | 55 | 0 | 43 | 0 | 30 | 34 | 19 | 11 | 33 | 20 | 162 | 100 | 0 | 22 | 0 | 43 | 41 | 53 | 43 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 34 | 9 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 144 | 0 | 90 | 200 | 137 | 402 | 77 | 105 | 105 | 0 | 215 | 54 | 92 | 104 | 115 | 100 | 0 | 96 | 0 | 162 | 108 | 0 | 35 | 0 | 35 | 52 | 0 |  | 844 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 35 | 62 | 8 | 60 | 34 | 32 | 0 | 0 | 0 | 24 | 41 | 87 | 0 | 0 | 32 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 132 | 0 | 0 | 204 | 0 | 0 | 129 | 0 | 312 | 54 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1090 | 220 | 0 | 17 | 0 | 0 | 90 | 0 | 0 |  | 12620 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 88 | 0 | 55 | 0 | 0 | 0 | 92 | 94 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 68 | 55 | 88 | 37 | 17 | 15 | 0 | 0 | 0 | 320 | 320 | 200 | 8 | 128 | 41 | 55 | 0 | 43 | 0 | 40 | 34 | 19 | 10 | 33 | 20 | 166 | 65 | 0 | 20 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 64 | 20 | 0 | 220 | 0 | 33 | 10 | 300 | 24 | 11 | 0 | 285 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 210 | 54 | 92 | 114 | 113 | 100 | 0 | 91 | 0 | 162 | 108 | 0 | 35 |  | 75 | 55 |  |  | 868 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 45 | 65 | 8 | 60 | 32 | 32 | 0 | 0 | 0 | 24 | 41 | 88 | 0 | 0 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 315 | 90 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 1100 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 51 | 55 | 88 | 37 | 17 | 4 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 128 | 41 | 55 | 0 | 43 | 0 | 40 | 8 | 19 | 10 | 33 | 20 | 143 | 65 | 0 | 20 | 1.6 | 43 | 41 | 33 | 30 | 110 | 0 | 40 | 20 | 0 | 220 | 0 | 33 | 10 | 300 | 16 | 11 | 0 | 150 | 0 | 0 | 48 | 0 | 149 | 20 | 21 | 100 | 135 | 400 | 45 | 105 | 105 | 5 | 51 | 36 | 92 | 17 | 100 | 20 | 0 | 17 | 50 | 54 | 108 | 0 | 35 | 30 | 75 | 55 |  |  | 881 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 23 | 32 | 0 | 0 | 0 | 24 | 0 | 85 | 0 | 0 | 32 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 305 | 35 | 0 | 70 | 105 | 85 | 0 | 8 | 75 | 1110 | 225 |  | 17 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 404 | 260 | 0 | 0 | 225 | 0 | 24 | 0 | 45 | 0 | 0 | 0 | 24 | 16 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 51 | 56 | 88 | 37 | 17 | 4 | 0 | 0 | 0 | 295 | 290 | 189 | 8 | 128 | 41 | 55 | 0 | 43 | 0 | 24 | 8 | 19 | 11 | 33 | 20 | 152 | 100 | 0 | 22 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 40 | 20 | 0 | 220 | 0 | 33 | 9 | 280 | 24 | 11 | 0 | 97 | 0 | 0 | 48 | 0 | 138 | 9 | 21 | 100 | 120 | 351 | 38 | 105 | 105 | 3 | 48 | 36 | 92 | 17 | 100 | 20 | 0 | 15 | 6 | 54 | 108 | 0 | 35 | 6 | 76 | 55 | 0 | 0 | 894 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 55 | 25 | 32 | 0 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 32 | 8 | 36 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 136 | 0 | 0 | 130 | 0 | 0 | 129 | 0 | 327 | 35 | 0 | 70 | 105 | 85 | 0 | 0 | 75 | 950 | 165 | 0 | 17 | 0 | 33 | 52 | 0 | 0 | 0 |  |  |  |  | 79927068 |  | 0
79927068
| Minimum Generation |  | 10641 | 9:00
| Highest Generation |  | 12628 | 22:00
| Day Peak Generation |  | 10641 | 9:00
| Evening Peak Generation |  | 12620 | 21:00
| HVDC Max Flow |  | 898 | 1:00
| HVDC EvPeak Flow |  | 844 | 21:00
| Load factor L.F |  | 89.58% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-01
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-07-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10641 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10381 | MW
Evening Peak Generation : |  | 12620 | MW Hour : | 21:00 | Available Max Generation : |  | 12700 | MW
E.P. Demand (at gen end) : |  | 13800 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12628 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 271.5052 | System Load Factor : | 89.58% | Load Shed : |  | 1195 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 442 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-01
Actual : | 92.01 | Ft.(MSL) , | Rule curve : | 89 | Ft.( MSL )
Gas Consumed : | Total = | 1003.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151188920.852
: |  | Coal : | 268407149 | Oil : | 1094509772.87 | Total : | 1514105842.722
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 210 | 5040:00 | 4483.4624 |  |  | 350 | 6.411%
Chittagong Area | 0 | 0:00 | 1269.5617 |  |  | 130 | 8.67%
Khulna Area | 200 | 4800:00 | 1675.9763 |  |  | 170 | 9.08%
Rajshahi Area | 100 | 2400:00 | 1487.6064 |  |  | 160 | 9.656%
Cumilla Area | 210 | 5040:00 | 1265.6911 |  |  | 135 | 9.323%
Mymensingh Area | 249 | 5976:00 | 1046.3563 |  |  | 115 | 9.871%
Sylhet Area | 18 | 432:00 | 467.0542 |  |  | 45 | 8.694%
Barisal Area | 0 | 0:00 | 380.6105 |  |  | 0 | 0%
Rangpur Area | 100 | 2400:00 | 825.7312 |  |  | 90 | 9.817%
Total | 1087 |  | 12902.05 |  |  | 1195
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tongi-Kabirpur 230 kV Ckt was under shut down from 10:23 to 18:43 for DFDR work.
b) Matarbari 132/33 kV T-1 transformer was under shut down from 09:21 to 09:41 for C/M.
c) Ashuganj(N) STG was synchronized at 16:55.
d) Khagrachari 132/33 kV T-2 transformer tripped at 18:09 by winding temperature high and was charged
at 21:06 and was switched on at 11:00(01/8/2022).
e) Natore 132/33 kV T-4 transformer tripped at 21:05 due to 33 kV feeder fault and was switched on at 21:21. | [5 empty] | About 08 MW power interruption occurred under
Natore S/S area from 21:05 to 21:21.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-07-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4331250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6993909 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 82 | 1951863 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9760770
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 260 | 7442000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5010700 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 87 | 869760 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1201974
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 420192
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 612000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 89 | 879360 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 736848 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 504360 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 2160000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 330829
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 265244
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1214880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 586900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 657600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1124482 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 3879053 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 2894400 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2170308
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 96 | 1040640 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2178720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 112789
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 52 | 1208880
| Dhaka area Total |  |  |  | 5847 | 2991 | 60539711
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 590194
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 118530
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 838080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 114 | 2729324 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2304181
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 457440 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1317662 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 56 | 1530120 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 880320 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 382992 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 459360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 2049600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32279
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 215 | 2549236 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1054437
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2455552 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 961920
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2512855 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1337 | 25524082
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4707000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 350 | 4199000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 8085000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 940536 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1161120
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 2525818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1029557
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 3134690 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 891928 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 128 | 3186710 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2536320
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448704
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237420
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3691200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 731700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 387874 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 494160 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 104 | 976980
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2606520
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 35 | 908160 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 2072 | 43768157
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2040960 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 465300
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 144 | 2390400
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1335600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 119550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 437280 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 361 | 6795640
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1027000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 959960 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2632663 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 928800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 872136 | Engine problem
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1463136
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 967680 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5328950
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 34 | 787700 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 551736 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7621500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9522000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 228780
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1413 | 33156041
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 844 | 21052363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 383040 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 377290 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 62 | 623104 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 3924576 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 194250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 54 | 853920 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2326032
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 570960
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1284 | 30305535
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 565056 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 640086 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1429000 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 26935900 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5025709
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 99600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1453 | 34695351
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 360992 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 524759 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 599800 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 132 | 3464464 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 204 | 4303255
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 129 | 3411009 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 312 | 7230364 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 668000 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 449760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212346
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 381235 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1971316 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2121792
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2105568
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 12360
| Rajshahi Area Total |  |  |  | 2129 | 1306 | 27817020
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4861000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2364028
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 14556
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1664064 | Engine problem
| Rangpur Area Total |  |  |  | 720 | 403 | 8903648
| Total |  |  |  | 21680 | 12620 | 271505185
| Eastern Grid Total |  |  |  | 14489 | 8174 | 169783631
| Western Grid Total |  |  |  | 7191 | 4446 | 101721554
| National Grid Total |  |  |  | 21680 | 12620 | 271505185
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-07-31
(a) ENTIRE EASTERN GRID : |  | 8511.4 | MW | (b) ENTIRE WESTERN GRID : |  | 3736.83 | MW
i) Dhaka area |  | 4640.19 | MW | i) Khulna area |  | 1532 | MW
ii) Chittagong area |  | 1384.21 | MW | ii) Rajshahi area |  | 1095 | MW
iii) Comilla area |  | 1116 | MW | iii) Barisal area |  | 407.83 | MW
iv) Mymensingh area |  | 868 | MW | iv) Rangpur area |  | 702 | MW
v) Sylhet area |  | 503 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12248.23 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 16 | 10:00 | Chowmuhani | 195 | 17:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 11 | 15:00 | Chuadanga | 88 | 18:00 | Kazla | 83 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 00:00 | Coxsbazar | 130 | 22:00 | Keranigonj | 56 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 95 | 13:00 | Cumilla(N) | 149 | 00:00 | Khagrachori | 29 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 84 | 19:00 | Cumilla(S) | 172 | 16:00 | Khulna | 92 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 49 | 06:00 | Daudkandi | 134 | 19:00 | Khulshi | 177 | 10:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 44 | 00:00 | Dhaka | 40 | 12:00 | Kishoreganj | 118 | 22:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 131 | 09:00 | Dhamrai | 110 | 22:00 | Kodda | 330 | 18:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 89 | 22:00 | Dhanmondi | 132 | 12:00 | Kulaura | 46 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 138 | 20:00 | Dohazari | 102 | 22:00 | Kurigram | 56 | 19:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 55 | 17:00 | Faridpur | 159 | 21:00 | Kushtia | 142 | 21:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 10:00 | Fatullah | 70 | 15:00 | Lalbag | 101 | 12:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 47 | 19:00 | Fenchuganj | 43 | 22:00 | Lalmonirhat | 43 | 20:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 96 | 22:00 | Madanganj | 89 | 07:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 108 | 19:00 | GPH | 88 | 11:00 | Madaripur | 109 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 78 | 19:30 | Ghorashal | 46 | 21:00 | Madartek | 86 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 74 | 23:00 | Goalpara | 26 | 13:00 | Madunaghat | 65 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 61 | 21:00 | Gollamari | 52 | 19:00 | Magura | 50 | 06:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 167 | 17:00 | Gopalganj | 105.8 | 19:30 | Mahasthangarh | 60 | 19:00 | Ramganj | 88 | 19:00
BashundharaCement | 13 | 00:00 | Gulshan | 120 | 17:00 | Manikganj | 96 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 56 | 21:00 | Halishahar | 97 | 15:00 | Maniknagar | 78 | 10:00 | Rangamati | 14 | 19:00
Benapole | 52 | 06:00 | HaripurSBU | 131 | 09:00 | Matarbari | 42 | 23:00 | Rangpur | 105 | 08:00
Bhaluka | 122 | 09:00 | Hasnabad | 136 | 14:00 | Matuail | 63 | 09:00 | Ruppur | 5 | 09:00
Bhandaria | 52 | 00:00 | Hathazari | 103 | 19:00 | Millgate | 58 | 09:00 | SSM | 3 | 05:00
Bhangura | 30 | 20:00 | Ishurdi | 64 | 03:00 | Mirpur | 137 | 20:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 52 | 19:00 | Jaldhaka | 52 | 18:00 | Mirsorai | 2.81 | 21:00 | Satkhira | 95 | 06:00
Bhulta | 241 | 09:00 | Jamalpur | 117 | 19:30 | Mithapukur | 22 | 00:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 50 | 00:00 | Jashore | 146 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 164 | 20:00 | Jhenaidah | 106 | 07:00 | Mogbazar | 126 | 14:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 01:00 | Joydebpur | 202 | 21:00 | Mongla | 34 | 10:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 140 | 19:00 | Joypurhat | 50 | 00:00 | Motijheel | 38 | 16:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 146 | 17:00 | Juldah | 23 | 00:00 | Munshiganj | 105 | 22:00 | Shariatpur | 78 | 22:00
Chandpur | 76 | 22:00 | KSRM | 9.2 | 09:00 | Mymensingh | 229 | 22:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:00 | Kabirpur | 269 | 20:00 | Naogaon | 113 | 05:00 | Shikalbaha | 28 | 19:00
Chapai | 64 | 06:00 | Kachua | 64 | 18:00 | Narail | 40 | 22:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 49 | 09:00 | Kallyanpur | 102 | 00:00 | Narinda | 74 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 51 | 00:00 | Kalurghat | 7 | 11:00 | Narshingdi | 153 | 03:00 | Sholosohor | N/A | N/A
Chhatak | 28 | 00:00 | Kamrangirchar | 61 | 19:00 | Natore | 109 | 05:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-07-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 387 | 20:00 | 357 | 17:00 | Kaliakoir | 390 | 19:00 | 371 | 17:00
| Bibiana | 408 | 19:30 | 395 | 11:00 | Payra | 412 | 08:00 | 405 | 23:00
| BIPTC | 405 | 18:00 | 398 | 00:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 403 | 10:00 | 390 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 221 | 19:30 | 206 | 12:00 | Hasnabad | 221 | 19:30 | 206 | 12:00
| AKSML | 235 | 20:00 | 221 | 05:00 | Hathazari | 236 | 19:30 | 227 | 17:00
| Aminbazar | 222 | 19:00 | 209 | 10:00 | Ishurdi | 237 | 19:30 | 228 | 05:00
| Ashuganj | 242 | 19:00 | 225 | 12:00 | Jhenaidah | 234 | 14:00 | 218 | 06:00
| Baghabari | 234 | 00:00 | 229 | 09:00 | Kaliakoir | 224 | 19:00 | 211 | 17:00
| Barapukuria | 226 | 06:00 | 221 | 13:00 | Keranigonj | 220 | 19:30 | 204 | 12:00
| Barishal | 243 | 08:00 | 235 | 22:00 | Khulna(S) | 233 | 17:00 | 222 | 07:00
| Bheramara | 233 | 19:30 | 224 | 09:00 | Maniknagar | 223 | 22:00 | 208 | 12:00
| Bhulta | 227 | 20:00 | 212 | 15:00 | Meghnaghat | 226 | 22:00 | 214 | 13:00
| Bibiana | 237 | 19:30 | 230 | 12:00 | Mirsorai | 234 | 19:30 | 227 | 23:00
| BIPTC | 235 | 19:30 | 226 | 06:00 | Rajshahi | 236 | 19:30 | 224 | 07:00
| Bogura | 230 | 19:30 | 225 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 08:00 | 241 | 23:00 | Rampura | 224 | 19:30 | 212 | 11:00
| BSRM | 234 | 19:30 | 223 | 09:00 | Shikalbaha | 238 | 19:30 | 227 | 11:00
| Cumilla(N) | 229 | 19:00 | 218 | 12:00 | Shyampur | 220 | 19:30 | 206 | 12:00
| Fenchuganj | 243 | 20:00 | 235 | 12:00 | Siddhirganj | 231 | 10:00 | 211 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 260 | 05:00 | 228 | 09:00
| GPH | 233 | 00:00 | 224 | 08:00 | Tongi | 224 | 19:00 | 209 | 17:00
| Haripur | 221 | 19:30 | 209 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 20:00 | 126 | 16:00 | Lalbag | 135 | 19:30 | 125 | 12:00
| Agargaon | 135 | 19:30 | 126 | 12:00 | Lalmonirhat | 136 | 04:00 | 127 | 08:00
| Agrabad | 138 | 19:30 | 131 | 18:00 | Madanganj | 132 | 19:30 | 123 | 12:00
| AKS | 137 | 00:00 | 130 | 11:00 | Madaripur | 136 | 10:00 | 129 | 23:00
| Aminbazar | 133 | 20:00 | 124 | 10:00 | Madartek | 136 | 06:00 | 125 | 17:00
| Amnura | 137 | 19:30 | 126 | 05:00 | Madunaghat | 140 | 20:00 | 133 | 10:00
| Ashuganj | 138 | 19:30 | 134 | 12:00 | Magura | 137 | 10:00 | 130 | 06:00
| Bagerhat | 131 | 10:00 | 121 | 07:00 | Mahasthangarh | 138 | 18:30 | 134 | 01:00
| Bakulia | 139 | 20:00 | 132 | 09:00 | Manikganj | 134 | 19:00 | 126 | 17:00
| Banani | 133 | 19:30 | 120 | 17:00 | Maniknagar | 133 | 22:00 | 123 | 12:00
| Bangabhaban | 132 | 19:30 | 123 | 17:00 | Matarbari | 134 | 15:00 | 118 | 18:00
| Barapukuria | 138 | 04:00 | 129 | 07:00 | Matuail | 131 | 20:00 | 123 | 09:00
| Barguna | 133 | 08:00 | 128 | 00:00 | Millgate | 132 | 19:30 | 121 | 17:00
| Barishal | 138 | 10:00 | 125 | 15:00 | Mirpur | 131 | 19:30 | 122 | 12:00
| Barishal-230 | 137 | 08:00 | 132 | 22:00 | Mithapukur | 137 | 04:00 | 132 | 07:00
| Baroaulia | 140 | 19:30 | 132 | 18:00 | Modern | 138 | 00:00 | 132 | 18:00
| Baroirhat | 138 | 19:30 | 127 | 05:00 | Mogbazar | 137 | 04:00 | 127 | 12:00
| Bashundhara | 131 | 23:00 | 120 | 17:00 | Mongla | 130 | 10:00 | 120 | 05:00
| BashundharaCement | 132 | 19:30 | 123 | 12:00 | Motijheel | 132 | 19:30 | 123 | 17:00
| Beanibazar | 134 | 06:00 | 130 | 01:00 | Munshiganj | 133 | 19:30 | 124 | 12:00
| Benapole | 134 | 00:00 | 125 | 06:00 | Mymensingh | 131 | 09:00 | 124 | 00:00
| Bhaluka | 134 | 10:00 | 122 | 05:00 | Naogaon | 137 | 19:30 | 128 | 04:00
| Bhandaria | 136 | 08:00 | 126 | 21:00 | Narail | 136 | 10:00 | 128 | 07:00
| Bhangura | 139 | 19:30 | 134 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 19:30 | 134 | 03:00 | Narshingdi | 136 | 19:00 | 122 | 11:00
| Bheramara(GK) | 137 | 00:00 | 134 | 15:00 | Natore | 137 | 19:30 | 131 | 06:00
| Bhulta | 125 | 19:30 | 118 | 17:00 | Nawabganj | 134 | 20:00 | 125 | 11:00
| Bog-Sherpur | 138 | 15:00 | 134 | 05:00 | Netrakona | 132 | 10:00 | 122 | 08:00
| Bogura | 139 | 17:00 | 134 | 06:00 | New | 131 | 19:00 | 121 | 17:00
| Bogura-230 | 140 | 19:30 | 135 | 01:00 | Niamatpur | 137 | 19:30 | 126 | 05:00
| Brahmanbaria | 133 | 10:00 | 130 | 13:00 | Noapara | 134 | 19:30 | 125 | 23:00
| Cantonment | 134 | 19:30 | 124 | 12:00 | Pabna | 136 | 19:30 | 132 | 03:00
| Chandpur | 138 | 19:30 | 129 | 04:00 | Palashbari | 135 | 10:00 | 130 | 00:00
| Chandraghona | 139 | 00:00 | 133 | 10:00 | Panchagarh | 136 | 19:30 | 125 | 07:00
| Chapai | 137 | 19:30 | 125 | 05:00 | Patuakhali | 134 | 07:00 | 129 | 13:00
| Charsaidpur | 133 | 20:00 | 124 | 12:00 | Payra | 136 | 04:00 | 133 | 00:00
| Chauddagram | 138 | 19:00 | 126 | 04:00 | PHP | 137 | 19:30 | 127 | 04:00
| Chhatak | 135 | 06:00 | 129 | 21:00 | Postogola | 140 | 19:30 | 127 | 12:00
| Chowmuhani | 136 | 19:30 | 125 | 03:00 | Purbachal | 132 | 19:30 | 119 | 17:00
| Chuadanga | 138 | 19:00 | 124 | 07:00 | Purbasadipur | 136 | 04:00 | 126 | 07:00
| Coxsbazar | 129 | 19:00 | 117 | 22:00 | Rahim | 132 | 19:30 | 124 | 12:00
| Cumilla(N) | 135 | 19:00 | 129 | 05:00 | Rajbari | 134 | 19:30 | 128 | 23:00
| Cumilla(S) | 136 | 19:30 | 126 | 13:00 | Rajendrapur | 136 | 19:30 | 126 | 09:00
| Daudkandi | 132 | 20:00 | 124 | 12:00 | Rajshahi | 135 | 19:30 | 127 | 05:00
| Dhaka | 137 | 19:30 | 126 | 17:00 | Rajshahi-230 | 135 | 19:30 | 127 | 07:00
| Dhamrai | 130 | 19:30 | 121 | 12:00 | Ramganj | 136 | 19:30 | 125 | 05:00
| Dhanmondi | 132 | 22:00 | 122 | 12:00 | Rampur | 138 | 19:30 | 132 | 09:00
| Dohazari | 138 | 19:00 | 128 | 18:00 | Rampura | 152 | 22:00 | 130 | 22:00
| Faridpur | 134 | 19:30 | 128 | 21:00 | Rangamati | 138 | 01:00 | 133 | 00:00
| Fatullah | 133 | 19:30 | 124 | 11:00 | Rangpur | 136 | 05:00 | 130 | 01:00
| Fenchuganj | 138 | 20:00 | 134 | 12:00 | Ruppur | 136 | 00:00 | 134 | 02:00
| Feni | 136 | 22:00 | 127 | 04:00 | Saidpur | 135 | 09:00 | 128 | 07:00
| Ghorashal | 135 | 01:00 | 130 | 12:00 | Satkhira | 130 | 10:00 | 119 | 22:00
| Goalpara | 133 | 10:00 | 125 | 06:00 | Satmasjid | 135 | 19:30 | 125 | 12:00
| Gollamari | 133 | 19:30 | 125 | 06:00 | Savar | 132 | 19:30 | 122 | 09:00
| Gopalganj | 136 | 04:00 | 131 | 07:00 | Shahjadpur | 141 | 16:00 | 137 | 11:00
| Gopalganj_I | 137 | 10:00 | 131 | 22:00 | Shahjibazar | 136 | 19:30 | 132 | 05:00
| Gulshan | 136 | 06:00 | 125 | 17:00 | Shahmirpur | 140 | 01:00 | 132 | 18:00
| Halishahar | 138 | 00:00 | 132 | 09:00 | Shariatpur | 134 | 08:00 | 126 | 22:00
| Haripur | 132 | 19:30 | 124 | 12:00 | Sherpur | 136 | 10:00 | 129 | 05:00
| HaripurSBU | 132 | 19:30 | 125 | 09:00 | Shikalbaha | 140 | 19:30 | 133 | 10:00
| Hasnabad | 140 | 20:00 | 129 | 16:00 | Shikalbaha-230 | 140 | 19:30 | 133 | 11:00
| Hathazari | 140 | 20:00 | 133 | 17:00 | Shitalakhya | 140 | 22:00 | 125 | 16:00
| Ishurdi | 138 | 19:30 | 133 | 12:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 136 | 04:00 | 126 | 08:00 | Shyampur | 132 | 19:30 | 123 | 12:00
| Jamalpur | 136 | 09:00 | 125 | 17:00 | Shyampur-230 | 133 | 19:30 | 123 | 12:00
| Jashore | 135 | 19:30 | 125 | 07:00 | Siddhirganj | 132 | 19:30 | 124 | 12:00
| Jhenaidah | 139 | 19:30 | 132 | 06:00 | Sirajganj | 137 | 16:00 | 133 | 09:00
| Jhenaidah-230 | 139 | 19:30 | 132 | 06:00 | Sonargaon | 133 | 22:00 | 125 | 10:00
| Joydebpur | 142 | 19:00 | 132 | 14:00 | Sreemongol | 137 | 19:30 | 134 | 05:00
| Joypurhat | 140 | 20:00 | 127 | 03:00 | Srinagar | 134 | 19:30 | 124 | 17:00
| Juldah | 139 | 00:00 | 132 | 18:00 | SSM | 141 | 00:00 | 130 | 20:00
| Kabirpur | 137 | 19:30 | 116 | 17:00 | Sunamganj | 134 | 07:00 | 127 | 21:00
| Kachua | 137 | 19:00 | 127 | 05:00 | Sylhet | 135 | 09:00 | 132 | 00:00
| Kaliakoir | 137 | 19:00 | 128 | 02:00 | Tangail | 137 | 13:00 | 128 | 17:00
| Kallyanpur | 132 | 19:30 | 124 | 09:00 | Thakurgaon | 134 | 01:00 | 126 | 07:00
| Kalurghat | 139 | 00:00 | 133 | 09:00 | TK | 139 | 13:00 | 132 | 18:00
| Kamrangirchar | 135 | 19:30 | 125 | 12:00 | Tongi | 133 | 23:00 | 123 | 17:00
| Kaptai | 138 | 20:00 | 133 | 16:00 | Ullon | 137 | 22:00 | 126 | 12:00
| Kazla | 132 | 19:30 | 123 | 12:00 | Uttara | 131 | 19:30 | 122 | 11:00
| Keranigonj | 136 | 22:00 | 125 | 12:00 | UttaraNew | 131 | 19:00 | 122 | 09:00
| Khagrachori | 138 | 00:00 | 132 | 09:00 | Zigatola | 135 | 20:00 | 125 | 10:00
| Khulna | 133 | 19:30 | 120 | 15:00
| Khulna(S) | 133 | 19:30 | 125 | 06:00
| Khulshi | 136 | 00:00 | 131 | 10:00
| Kishoreganj | 134 | 10:00 | 125 | 17:00
| Kodda | 142 | 19:00 | 126 | 12:00
| KSRM | 138 | 13:00 | 132 | 08:00
| Kulaura | 136 | 19:30 | 134 | 05:00
| Kurigram | 136 | 05:00 | 126 | 21:00
| Kushtia | 137 | 19:30 | 132 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-07-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 674 | 7409 | 4329 | 11738 |  |  |  | QF-LDC-11
0:30 | 750 | 7168.5 | 4303.5 | 11472 | Date: | 2022-07-31
1:00 | 826 | 6928 | 4278 | 11206
1:30 | 842 | 6861 | 4302.5 | 11163.5
2:00 | 858 | 6794 | 4327 | 11121
2:30 | 870 | 6817 | 4330.5 | 11147.5 | [5 empty] | Gen. at Eve. Peak | 12620 | 12620 MW (21:00 )
3:00 | 882 | 6840 | 4334 | 11174 | [6 empty] | 21:00
3:30 | 900 | 6816.5 | 4318.5 | 11135 | [5 empty] | Gen. at Day Peak | 10641 | 10641 MW (09:00 )
4:00 | 918 | 6793 | 4303 | 11096 | [6 empty] | 9:00
4:30 | 893 | 6820 | 4304 | 11124 | [5 empty] | Highest Generation | 12628
5:00 | 868 | 6847 | 4305 | 11152 | [6 empty] | 22:00
5:30 | 803 | 6908 | 4208 | 11116
6:00 | 738 | 6969 | 4111 | 11080
6:30 | 718 | 6945 | 4066.5 | 11011.5
7:00 | 698 | 6921 | 4022 | 10943
7:30 | 806 | 6874.5 | 4005 | 10879.5
8:00 | 914 | 6828 | 3988 | 10816
8:30 | 952 | 6748.5 | 3980 | 10728.5
9:00 | 990 | 6669 | 3972 | 10641
9:30 | 990 | 6673.5 | 3923.5 | 10597
10:00 | 990 | 6678 | 3875 | 10553
10:30 | 949 | 6690 | 3888 | 10578
11:00 | 908 | 6702 | 3901 | 10603
11:30 | 979 | 6674 | 3904.5 | 10578.5
12:00 | 1050 | 6646 | 3908 | 10554
12:30 | 934 | 6626.5 | 3903.5 | 10530
13:00 | 818 | 6607 | 3899 | 10506
13:30 | 901 | 6531.5 | 3903.5 | 10435
14:00 | 984 | 6456 | 3908 | 10364
14:30 | 957 | 6462 | 3882.5 | 10344.5
15:00 | 930 | 6468 | 3857 | 10325
15:30 | 950 | 6483 | 3825 | 10308
16:00 | 970 | 6498 | 3793 | 10291
16:30 | 986 | 6581 | 3857 | 10438
17:00 | 1002 | 6664 | 3921 | 10585
17:30 | 1036 | 6989 | 3946 | 10935
18:00 | 1070 | 7314 | 3971 | 11285
18:30 | 756 | 7640.5 | 4060.5 | 11701
19:00 | 442 | 7967 | 4150 | 12117
19:30 | 464 | 7954 | 4229 | 12183
20:00 | 542 | 8047 | 4310 | 12357 |  |  |  | Executive Engineer
20:30 | 534 | 8110.5 | 4378 | 12488.5 |  |  |  | Network Operation Division
21:00 | 526 | 8174 | 4446 | 12620
21:30 | 557 | 8169 | 4455 | 12624
22:00 | 588 | 8164 | 4464 | 12628 |  |  |  |  | Page 6 of 7
22:30 | 595 | 8074.5 | 4471.5 | 12546
23:00 | 602 | 7985 | 4479 | 12464
23:30 | 638 | 7697 | 4404 | 12101
24:00 | 674 | 7409 | 4329 | 11738
12620 MW (21:00 )
10641 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-07-31 |  | Energy |  | 271505185
[13 empty] | 2022-07-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3597 | 843 | 1927 | 0 | 2980 | 1310 | 115 | 220 | 792 | 174 | 0 | 979
0:30 | 3503 | 870.5 | 2034 | 0 | 2741 | 1305 | 115.5 | 216.5 | 741 | 162 | 0 | 1224 | Date: | 2022-07-31
1:00 | 3409 | 898 | 2141 | 0 | 2502 | 1300 | 116 | 213 | 690 | 150 | 0 | 1469
1:30 | 3416.5 | 897.5 | 2125 | 0 | 2461 | 1295 | 116 | 213 | 701.5 | 151 | 0 | 1416 | [8 empty] | Total Energy | 271.5052 | Total Energy Gen 271.505 MKWHr Energy Not Served 24.711 MKWHr Energy Requirement 296.216 MKWHr
2:00 | 3424 | 897 | 2109 | 0 | 2420 | 1290 | 116 | 213 | 713 | 152 | 0 | 1363 | [8 empty] | Energy not Served | 24.7106
2:30 | 3461.5 | 897 | 2096.5 | 0 | 2429 | 1290 | 116 | 213 | 716.5 | 141 | 0 | 1246.5 | [8 empty] | Energy Requirement | 296.2158
3:00 | 3499 | 897 | 2084 | 0 | 2438 | 1290 | 116 | 213 | 720 | 130 | 0 | 1130
3:30 | 3491.5 | 897 | 2089 | 0 | 2408 | 1290 | 116 | 214.5 | 708.5 | 135 | 0 | 1073.5 | [6 empty] | Shortage
4:00 | 3484 | 897 | 2094 | 0 | 2378 | 1290 | 116 | 216 | 697 | 140 | 0 | 1017
4:30 | 3511 | 897 | 2096 | 0 | 2387.5 | 1280 | 116 | 216 | 699.5 | 137 | 0 | 761
5:00 | 3538 | 897 | 2098 | 0 | 2397 | 1270 | 116 | 216 | 702 | 134 | 0 | 505
5:30 | 3617 | 897 | 2081.5 | 0 | 2390 | 1260 | 116 | 203 | 622.5 | 129 | 3 | 354
6:00 | 3696 | 897 | 2065 | 0 | 2383 | 1250 | 116 | 190 | 543 | 124 | 6 | 203
6:30 | 3668 | 897 | 2057.5 | 0 | 2374.5 | 1225 | 115 | 180 | 533 | 121 | 20.5 | 174 |  |  |  |  | Coal
7:00 | 3640 | 897 | 2050 | 0 | 2366 | 1200 | 114 | 170 | 523 | 118 | 35 | 145
7:30 | 3606 | 897 | 2028 | 0 | 2340.5 | 1195 | 114.5 | 170 | 511.5 | 129 | 58 | 295.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3572 | 897 | 2006 | 0 | 2315 | 1190 | 115 | 170 | 500 | 140 | 81 | 446
8:30 | 3534 | 897 | 1965.5 | 0 | 2314 | 1180 | 115 | 167 | 494 | 145 | 84 | 619
9:00 | 3496 | 897 | 1925 | 0 | 2313 | 1170 | 115 | 164 | 488 | 150 | 87 | 792
9:30 | 3491.5 | 879.5 | 1905.5 | 0 | 2319 | 1175 | 115 | 147 | 461 | 152 | 98.5 | 924.5
10:00 | 3487 | 862 | 1886 | 0 | 2325 | 1180 | 115 | 130 | 434 | 154 | 110 | 1057
10:30 | 3509.5 | 862 | 1859 | 0 | 2331 | 1185 | 115.5 | 130 | 436 | 156 | 124 | 1172
11:00 | 3532 | 862 | 1832 | 0 | 2337 | 1190 | 116 | 130 | 438 | 158 | 138 | 1287
11:30 | 3500.5 | 862 | 1844 | 0 | 2328.5 | 1195 | 116 | 130 | 427 | 161 | 144.5 | 1402
12:00 | 3469 | 862 | 1856 | 0 | 2320 | 1200 | 116 | 130 | 416 | 164 | 151 | 1517
12:30 | 3481 | 862 | 1851 | 0 | 2294.5 | 1215 | 113.5 | 130 | 400.5 | 167 | 145.5 | 1424
13:00 | 3493 | 862 | 1846 | 0 | 2269 | 1230 | 111 | 130 | 385 | 170 | 140 | 1331
13:30 | 3493 | 862 | 1846 | 0 | 2269 | 1230 | 111 | 130 | 385 | 170 | 140 | 1331
14:00 | 3493 | 862 | 1846 | 0 | 2269 | 1230 | 111 | 130 | 385 | 170 | 140 | 1331
14:30 | 3364 | 862 | 1885.5 | 0 | 2268.5 | 1240 | 112 | 130 | 409 | 169 | 105.5 | 1483.5
15:00 | 3235 | 862 | 1925 | 0 | 2268 | 1250 | 113 | 130 | 433 | 168 | 71 | 1636
15:30 | 3210.5 | 862 | 1907 | 0 | 2301 | 1220 | 113 | 130 | 456 | 170 | 68.5 | 1559.5
16:00 | 3186 | 862 | 1889 | 0 | 2334 | 1190 | 113 | 130 | 479 | 172 | 66 | 1483
16:30 | 3258 | 862 | 1891.5 | 0 | 2457 | 1185 | 112 | 130 | 487 | 163 | 58.5 | 1324.5
17:00 | 3258 | 862 | 1894 | 0 | 2580 | 1180 | 111 | 130 | 495 | 154 | 51 | 1166
17:30 | 3322 | 862 | 1884.5 | 0 | 2875 | 1179.5 | 111.5 | 130 | 512 | 158 | 30.5 | 820.5
18:00 | 3386 | 862 | 1875 | 0 | 3170 | 1179 | 112 | 130 | 529 | 162 | 10 | 475
18:30 | 3454 | 853 | 1903.5 | 0 | 3402.5 | 1179.5 | 112.5 | 130 | 626 | 165 | 5 | 1028.5
19:00 | 3522 | 844 | 1932 | 0 | 3635 | 1180 | 113 | 130 | 723 | 168 | 0 | 1582
19:30 | 3432 | 844 | 1897 | 0 | 3763 | 1240 | 113 | 130 | 740 | 154 | 0 | 1444
20:00 | 3509 | 844 | 1929 | 0 | 3814 | 1250 | 113 | 135 | 742 | 156 | 0 | 1307
20:30 | 3576.5 | 844 | 1917 | 0 | 3833.5 | 1270 | 113.5 | 169.5 | 775 | 159 | 0 | 1197
21:00 | 3644 | 844 | 1905 | 0 | 3853 | 1290 | 114 | 204 | 808 | 162 | 0 | 1087
21:30 | 3622.5 | 843.5 | 1908 | 0 | 3865 | 1290 | 114.5 | 211 | 817.5 | 163 | 0 | 1037.5
22:00 | 3601 | 843 | 1911 | 0 | 3877 | 1290 | 115 | 218 | 827 | 164 | 0 | 988
22:30 | 3614.5 | 843 | 1931 | 0 | 3746 | 1300 | 115 | 217.5 | 832.5 | 164 | 0 | 971.5
23:00 | 3628 | 843 | 1951 | 0 | 3615 | 1310 | 115 | 217 | 838 | 164 | 0 | 955
23:30 | 3612.5 | 843 | 1939 | 0 | 3297.5 | 1310 | 115 | 218.5 | 815 | 169 | 0 | 967 | Max Temp. in Dhaka |  | 24.7° C | 32.6° C
24:00 | 3597 | 843 | 1927 | 0 | 2980 | 1310 | 115 | 220 | 792 | 174 | 0 | 979
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 271.505 MKWHr Energy Not Served 24.711 MKWHr Energy Requirement 296.216 MKWHr
Note on W13: Author:

## Generation
g | 2022-07-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 81 | 81 | 81 | 81 | 81 | 79 | 80 | 80 | 80 | 81 | 81 | 76 | 76 | 78 | 78 | 76 | 77 |  | 78 | 78 | 78 | 79 | 80 | 80 | 80 | 1889324
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 | 25 | 25 | 21 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590194
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 10 | 6 | 18 | 20 | 18 | 20 | 20 | 6 | 6 | 2 | 0 | [8 empty] | 118530
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 49 | 50 | 51 | 51 |  | 68 | 67 | 67 | 68 | 68 | 68 | 68 | 1317662
12 | Hathazari 100 MW peaking PP | 33 | 18 | 26 | [10 empty] | 2 | 34 | 34 | 34 | 34 |  | 34 | 34 | 37 | 43 | 43 | 43 | 43 | 457440
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 87 | 88 | 103 | 90 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 105 | 105 | 87 | 87 | 87 | 87 | 94 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2304181
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 24 | 26 | 32 | 32 | 32 | 33 | 38 | 38 | 38 |  | 47 | 47 | 38 | 30 | 30 | 32 | 32 | 891928
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 62 | 61 | 95 | 98 | 98 | 60 | 39 | [18 empty] | 0 | 612000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 160 | 160 | 160 | 160 | 168 | 160 | 165 | 160 | 160 | 160 | 160 | 160 | 160 | 120 | 95 | 95 | 120 | 230 |  | 195 | 195 | 195 | 195 | 195 | 190 | 115 | 3879053
19 | Ashuganj 195MW PP (APSCL-United) | 175 | 175 | 167 | 177 | 177 | 177 | 177 | 148 | 73 | 63 | 63 | 63 | 63 | 63 | 128 | 128 | 133 | 125 |  | 125 | 125 | 78 | 16 | 8 | 8 | 8 | 2525818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4331250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 300 |  | 300 | 240 | 250 | 300 | 300 | 300 | 300 | 6993909
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 38 | 38 | 38 | 38 |  | 39 | 39 | 40 | 41 | 41 | 41 | 41 | 940536
33 | Ashuganj 225 MW CCPP | 207 | 207 | 207 | 209 | 208 | 211 | 208 | 155 | 145 | 147 | 200 | 194 | 191 | 202 | 204 | 203 | 201 | 203 |  | 202 | 208 | 183 | 184 | 186 | 196 | 199 | 4707000
34 | Ashuganj 450 MW CCPP(South) | 340 | 345 | 340 | 350 | 345 | 355 | 345 | 350 | 335 | 350 | 345 | 330 | 345 | 335 | 330 | 330 | 325 | 330 |  | 330 | 330 | 320 | 320 | 320 | 320 | 320 | 8085000
| Ashuganj 450 MW CCPP(North) |  |  | 32 | 0 | 50 | 224 | 235 | 240 | 225 | 240 | 240 | 230 | 230 | 70 | 20 | 20 | 65 | 135 |  | 230 | 265 | 360 | 350 | 320 | 320 | 320 | 4199000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 56 | 55 | 56 | 55 | 55 | 55 | 55 | 56 | 56 | 30 | 10 | 10 | 10 | 20 | 48 | 53 | 53 | 53 |  | 55 | 55 | 54 | 55 | 56 | 55 | 56 | 1161120
36 | Chandpur 150 MW CCPP | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 129 |  | 128 | 129 | 128 | 128 | 128 | 128 | 128 | 3186710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 407 | 406 | 409 | 410 | 409 | 410 | 407 | 407 | 403 | 407 | 401 | 401 | 400 | 399 | 398 | 401 | 397 |  | 398 | 390 | 393 | 399 | 398 | 398 | 399 | 9760770
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5010700
41 | Haripur 360MW CCPP(HPL) | 326 | 326 | 323 | 334 | 332 | 333 | 330 | 323 | 322 | 322 | 322 | 322 | 322 | 322 | 316 | 310 | 310 | 296 |  | 278 | 268 | 262 | 260 | 262 | 282 | 301 | 7442000
42 | RPCL 210MW CCPP | 104 | 103 | 102 | 103 | 104 | 104 | 104 | 95 | 71 | 71 | 71 | 67 | 67 | 66 | 68 | 68 | 69 | 69 |  | 85 | 97 | 100 | 100 | 105 | 104 | 104 | 2040960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 3 | 3 | 1 | 7 | 12 | 18 | 19 | 19 | 15 | 14 | 2 |  | 0 | [6 empty] | 119550
44 | Fenchugonj CCPP Phase-1 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1027000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 959960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 62 | 66 | 62 | 62 | 64 | 62 | 62 | 60 | 63 | 61 | 61 | 60 | 61 | 60 | 60 | 60 | 61 |  | 61 | 40 | 40 | 62 | 64 | 64 | 62 | 1463136
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 78 | 81 | 81 | 81 | 81 | 78 | 967680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5328950
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 34 | 33 | 33 | 33 | 33 | 35 | 34 | 35 | 35 | 34 | 36 |  | 36 | 34 | 34 | 34 | 34 | 33 | 33 | 787700
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 228780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 53 | 53 | 53 | 53 | 53 | 928800
56 | Shahjahanulla 25 MW PP | 8 | 16 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 551736
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 315 | 325 | 310 | 300 | 280 | 290 | 320 | 315 | 330 | 300 | 330 | 320 | 320 | 320 | 320 | 300 | 320 |  | 325 | 260 | 260 | 280 | 290 | 310 | 320 | 7621500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 0 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 |  | 0 | 265244
59 | Tangail Palli Power Gen 22 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 15 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 437280
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 382992
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 14 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 420192
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465300
63 | Impoprt (Tripura) | 150 | 152 | 130 | 140 | 134 | 124 | 118 | 140 | 150 | 154 | 158 | 164 | 170 | 168 | 168 | 172 | 154 | 162 |  | 168 | 154 | 156 | 162 | 164 | 164 | 174 | 3691200
64 | Malancha, Ctg. EPZ (United) | 28 | 30 | 30 | 33 | 34 | 34 | 36 | 13 | 3 | 5 | 5 | 10 | 10 | 7 | 5 | 5 | 11 | 7 |  | 17 | 19 | 24 | 27 | 33 | 37 | 37 | 459360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448704
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 28 | 22 | 16 | 24 | 24 | 24 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 731700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 14 | 17 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 494160
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 24 | 24 |  | 27 | 27 | 27 | 27 | 19 | 25 | 28 | 614880
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 586900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 16 | 16 | 25 | 25 | 25 | 26 | 18 | 26 | 27 |  | 28 | 28 | 28 | 29 | 16 | 32 | 30 | 657600
73 | Ghorashal 108MW PP (Regent) | 85 | 87 | 88 | 88 | 88 | 88 | 85 | 83 | 81 | 80 | 80 | 80 | 80 | 80 | 78 | 82 | 82 | 76 |  | 78 | 78 | 85 | 82 | 78 | 83 | 83 | 1951863
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 114 |  | 114 | 114 | 114 | 104 | 114 | 80 | 34 | 976980
| Chowmuhani 113 MW | 107 | 111 | 107 | 107 | 110 | 112 | 107 | 105 | 105 | 105 | 97 | 107 | 103 | 101 | 101 | 102 | 108 | 113 |  | 113 | 113 | 113 | 115 | 115 | 115 | 115 | 2606520
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 140 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 2178720
77 | Siddhirganj 100 PP(Dutch Bangla) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 48 | 60 | 88 | 89 | 90 | 89 | 33 | 879360
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 50 |  | 50 | 50 | 50 | 49 | 42 | 42 | 50 | 1124482
79 | Kodda 150MW PP | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 64 | 32 | 34 | 32 | 34 | 34 | 48 |  | 147 | 147 | 147 | 147 | 147 | 147 | 98 | 2160000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 387874
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 80 | 88 | 70 | 88 | 88 | 88 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2170308
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 6 | 6 | 2 | 2 | 1 | 2 | 3 | 1 | 0 |  | 0 | [6 empty] | 32279
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 40 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1054437
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 81 | 99 | 99 | 92 | 84 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2455552
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 24 | 24 | 23 | 24 | 24 | 24 | 21 | 26 | 30 |  | 45 | 77 | 75 | 87 | 89 | 89 | 34 | 869760
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 34 | 34 | 34 | 34 | 34 | 49 | 90 |  | 92 | 96 | 94 | 96 | 97 | 92 | 46 | 1040640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 66 | 66 | 66 | 66 | 66 | 56 | 56 | 55 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 55 | 56 | 56 | 56 | 55 | 56 | 1530120
92 | Fenchuganj 44MW (Energyprima) | 45 | 45 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 40 | 43 | 43 | 45 | 45 | 872136
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1029557
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 94 | 94 | 94 | 94 | 94 | 94 | 16 | 736848
95 | Patenga 50MW PP (Baraka) | 33 | 37 | 32 | 34 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 32 | 30 | 28 | 22 | 31 | 33 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 838080
96 | Chattogram 108 MW PP (ECPV) | 81 | 81 | 78 | 73 | 87 | 88 | 88 | 88 | 92 | 87 | 87 | 78 | 77 | 85 | 85 | 84 | 85 | 79 |  | 82 | 86 | 86 | 86 | 95 | 94 | 96 | 2049600
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 45 | 45 | 55 |  | 45 | 55 | 55 | 55 | 55 | 45 | 45 | 1201974
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 330829
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2632663
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 |  | 0 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | [8 empty] | 6550
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 504360
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 87 | 88 | 88 | 88 | 143 |  | 143 | 144 | 144 | 144 | 144 | 144 | 60 | 2390400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 116 | 117 | 117 | 117 | 117 | 117 | 117 | 112 | 106 | 106 | 105 | 104 | 80 | 100 | 127 | 99 | 99 | 115 |  | 149 | 135 | 135 | 144 | 149 | 149 | 149 | 2894400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 880320
116 | Chandpur 200MW (Desh energy) | 126 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 69 | 100 | 100 | 136 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2536320
117 | Ashuganj 150MW PP (Midland) | 127 | 135 | 140 | 137 | 133 | 133 | 129 | 120 | 127 | 130 | 127 | 124 | 127 | 122 | 123 | 128 | 120 | 125 |  | 130 | 128 | 130 | 137 | 139 | 142 | 142 | 3134690
118 | Bibiyana-III 400 MW CCPP | 400 | 403 | 403 | 402 | 402 | 401 | 403 | 402 | 403 | 402 | 403 | 368 | 402 | 403 | 402 | 403 | 403 | 404 |  | 400 | 353 | 351 | 402 | 401 | 402 | 364 | 9522000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 76 |  | 77 | 77 | 77 | 77 | 77 | 79 | 38 | 1335600
| Anwara 300 MW PP (United) | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 205 | 210 | 213 | 215 | 213 | 51 | 51 | 2549236
| Juldah unit-2 (Acorn) | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 52 | 100 | 100 | 100 | 100 | 100 | 100 | 961920
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 90 | 90 | 90 | 90 | 94 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2512855
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887760
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 7 | 7 | 13 | 14 | 15 | 14 | 13 | 11 | 9 | 4 | 2 |  | 0 | [6 empty] | 112789
| Chandpur 115(Doreen) | 24 | 17 | 18 | 18 | 18 | 23 | 26 | 22 | 22 | 32 | 57 | 58 | 58 | 57 | 42 | 44 | 39 | 42 |  | 41 | 36 | 35 | 35 | 35 | 60 | 74 | 908160
| Kanchan Purbachal Power Generation Ltd. | 47 | 40 | 54 | 51 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 34 | 34 | 34 |  | 34 | 34 | 37 | 52 | 55 | 55 | 55 | 1208880
120 | Eastern Zone Total | 6928 | 6794 | 6840 | 6793 | 6847 | 6969 | 6921 | 6828 | 6669 | 6678 | 6702 | 6646 | 6607 | 6456 | 6468 | 6498 | 6664 | 7314 |  | 7967 | 7954 | 8047 | 8174 | 8164 | 7985 | 7409 | 169783631
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 383040
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP |  | 38 | 43 | 43 | 42 | [12 empty] | 7 |  | 41 | 49 | 34 | 35 | 39 | 39 | 39 | 377290
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 35 | 35 | 35 | 34 | 34 | 17 | 17 | 17 | 17 | 27 | 35 |  | 47 | 54 | 54 | 54 | 54 | 54 | 35 | 853920
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 23 | 58 | 65 | 71 | 90 | 102 | 82 | 81 | 28 | 29 | 27 | 5 |  | 0 | [6 empty] | 570960
131
132 | United Payra Power Ltd. | [19 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 99600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 221 | 220 | 220 | 223 | 210 | 194 | 194 | 212 | 216 | 216 | 216 | 217 | 214 | 213 | 183 | 183 | 183 |  | 211 | 183 | 220 | 220 | 220 | 220 | 163 | 5025709
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 565056
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 52 | 54 | 60 | 60 | 60 | 60 | 1429000
140 | Bhola 33 MW PP (Venture) | 36 | 35 | 35 | 32 | 32 | 26 | 25 | 22 | 23 | 20 | 22 | 22 | 25 | 25 | 25 | 16 | 14 | 14 |  | 29 | 32 | 32 | 34 | 35 | 35 | 36 | 640086
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194250
143 | Gopalganj 100 MW Peaking PP | 61 | 58 | 53 | 53 | 53 | [12 empty] | 10 |  | 45 | 55 | 73 | 62 | 62 | 62 | 62 | 623104
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 89 | 88 | 89 |  | 88 | 95 | 105 | 105 | 105 | 105 | 105 | 2326032
146 | Bheramara HVDC | 898 | 897 | 897 | 897 | 897 | 897 | 897 | 897 | 897 | 862 | 862 | 862 | 862 | 861 | 862 | 862 | 862 | 862 |  | 844 | 844 | 844 | 844 | 843 | 843 | 843 | 21052363
147 | Bheramara 410 MW CCPP | 155 | 155 | 160 | 160 | 165 | 170 | 170 | 165 | 165 | 150 | 150 | 150 | 145 | 145 | 140 | 145 | 150 | 150 |  | 155 | 155 | 155 | 160 | 160 | 155 | 160 | 3924576
148 | Payra 1320 MW | 1100 | 1090 | 1090 | 1090 | 1070 | 1050 | 1000 | 990 | 970 | 980 | 990 | 1000 | 1030 | 1050 | 1050 | 990 | 980 | 980 |  | 980 | 1040 | 1050 | 1090 | 1090 | 1110 | 1110 | 26935900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4861000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [7 empty] | 10 | 16 | 24 | 16 |  | 16 | 16 | 16 | 24 | 24 | 34 | 34 | 360992
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 12360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 136 | 136 | 137 | 138 | 141 | 143 | 143 | 144 | 142 | 139 | 138 | 137 | 135 | 133 | 131 | 130 | 130 | 130 |  | 130 | 131 | 131 | 132 | 133 | 134 | 134 | 3464464
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 213 | 213 | 213 | 216 | 216 | 190 | 170 | 170 | 164 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 135 | 204 | 218 | 217 | 220 | 4303255
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 137 | 137 | 137 | 138 | 138 | 140 | 140 | 139 | 137 | 135 | 135 | 134 | 130 | 128 | 127 | 124 | 126 | 128 |  | 127 | 127 | 128 | 129 | 129 | 128 | 127 | 3411009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 283 | 305 | 315 | 320 | 332 | 337 | 333 | 321 | 317 | 299 | 293 | 282 | 276 | 270 | 270 | 270 | 287 | 276 |  | 286 | 293 | 297 | 312 | 309 | 300 | 305 | 7230364
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 41 | 41 | 40 | 40 | 40 | [8 empty] | 5 | 5 | 32 | 36 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 524759
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 |  | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 449760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212346
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 20 | 23 | 23 | 23 | 29 | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 29 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 599800
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 27 | 30 | 36 | 36 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 36 | 36 | 35 | 668000
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 37 | 43 | 52 | 52 | 52 | 52 | 8 | 381235
170 | Chapainawabganj 100 MW Peaking PP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 81 | 72 | 72 | 72 | 81 | 81 | 81 | 81 | 81 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 1971316
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 75 | 111 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2121792
172 | Confidence Power Bogura Unit-1 113 MW | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2105568
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 106 | 106 | 100 | 100 | 100 | 85 | 85 | 85 | 85 | 77 | 85 | 85 | 85 | 85 | 105 | 107 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2364028
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 1 | 1 | 2 | 3 | 3 | 1 |  | 0 | [6 empty] | 14556
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 90 | 90 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1664064
178