## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-06 | Saturday
|  |  | Date (day): | 2022-08-06 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10892.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12778 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-05 | 2022-08-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 85 | 89 | 90 | 90 |  | 18 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 412 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 332 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 80 | 8 | 50 |  | 50 | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 92 | 90 | 90 | 120 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 88 | 8 | 50 |  | 50 | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 94 | 8 | 94 |  | 8 | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 127 | 50 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 50 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 48 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 115 | 245 | 110 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 133 | 100 | 133 |  | 16 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 88 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 88 | 17 | 104 |  |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 70 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2373 | 3184 | 2474 | 3167 | 1596 | 1086
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 32 | 25 | 32 |  | 18 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 111 | 112 | 111 | 112 |  | 118 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 105 | 68 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 17 | 15 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 56 | 56 | 55 | 56 | 44 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 39 | 31 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 6 | 89 | 90 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 214 | 50 | 214 | 86 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 823 | 1236 | 859 | 1252 | 568 | 565
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 206 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 310 | 310 | 310 | 50 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 305 | 305 | 305 | 55 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 36 | 37 | 37 |  | 8 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 35 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 130 | 128 | 128 | 128 |  | 22 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 47 | 39 | 32 | 40
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 142 | 142 | 142 |  | 21 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 200 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 106 | 113 | 78 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 65 | 74 | 60 | 60 | 55 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1765 | 2106 | 1804 | 2102 | 690 | 75
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 67 | 102 | 102 | 102 | 100 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 179 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 79 | 49 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 198 | 380 | 270.6 | 381 | 100 | 86
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 54 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 33 | 53
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 49 | 49 | 30 | 49
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 61 | 61
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 81 | 10 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 32 | 32 | 31 | 32 | 18 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 8 | 16 | 9 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 290 | 290 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1376 | 1398 | 1287 | 1406 | 47 | 943
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 913 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 15 | 32 |  | 22 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 71 | 20 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 185 | 180 | 185 | 225 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 0 | 35 | 70 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1252 | 1365 | 1366 | 1381 | 772 | 61
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 32 | 16 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 31 | 23 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 88 | 88 | 88 | 106 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1040 | 1110 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 214 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1260 | 1405 | 1462 | 1470 | 106 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 32 | 24 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 34 | 34 | 34 |  | 16 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 190 | 188 | 190 | 20 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 172 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 146 | 167 | 162 | 167 | 53 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 310 | 370 | 350 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 33 | 33 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 36 | 86 | 80 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1080 | 1429 | 1054 | 1237 | 728 | 157
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 92 | 56 | 92 |  | 21 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 90 | 52 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 311 | 382 | 316 | 382 | 199 | 131
|  | Total |  |  |  |  | 22482 | 21680 | 10438 | 12885 | 10892.6 | 12778 | 4806 | 3114
| A. |  | 2022-08-05 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12951 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10438 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13450 | MW
| 3 | Day peak Generation : |  |  | 10438 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12945.39 | MW
| 4 | Evening peak Generation : |  |  | 12885 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 521 | MW
| 5 | Total Energy Generation : |  | 270.2204 | MKWHr | By Solar | 1.3813 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.3745 | MKWHr |  | By Oil: | 75.1458 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.3009 | MKWHr |  | By Hydro: | 2.6574 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4806 | MW | Dhaka | 4406.27 | 4336.27 |  | 70
|  |  |  | For Plants S/D or M/C prob = |  |  | 3114 | MW | Chittagong | 1344.25 | 1344.25 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7920 | MW | Khulna | 1621 | 1536 |  | 85
| 7 | Total Gas Supplied : |  |  | 1024.74 | MMCFD |  |  | Rajshahi | 1387 | 1302 |  | 85 |  | 19:00 |  | 476.4543
| 8 | Fuel Cost : | i) Gas : | Taka | 157364122.378 | ii) Oil : | Taka | 1043319479.92 | Comilla | 1300 | 1210 |  | 90 |  | 19:30 |  | 695.7891
|  |  | iii) Coal : |  | 254834817 | Total | Taka | 1455518419.298 | Mymensingh | 1070 | 944 |  | 126 |  | 20:00 |  | 673.6713
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 585 | 585 |  | 0 |  | 21:00 |  | 520.6899
|  | ii) During Peak Demand : |  |  | 388 | MW (E to W) at | 21:00 | hrs | Barisal | 387.87 | 387.87 |  | 0 |  | 22:00 |  | 321.6297
|  | iii) Maximum : |  |  | 274 | MW at | 22:00 | hrs | Rangpur | 844 | 779 |  | 65 |  | 23:00 |  | 394.4341
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 12945.39 | 12424.39 |  | 521
| B. |  | 2022-08-06 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 942.2963 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12778 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 287.9346 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10552 | MW at | 8:00 | 253.7441 | 100.5505 | 139.607 | 132.4836 | 108.5078 | 95.4332 | 37.1025 | 0 | 74.8676
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9956 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3648 | MKWHr. | iii) Maximum HVDC Flow : |  | 914 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 92.73 |  | (b) Today: | 93.01 |  | (c) Rule Curve: |  | 90.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 405 | 333 |  | 0 | 225 | 0 | 7 | 0 | 32 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 5 | 32 | 17 | 38 | 0 | 0 | 0 | 355 | 330 | 208 | 45 | 144 | 34 | 30 | 0 | 51 | 0 | 40 | 8 | 22 | 9 | 33 | 20 | 152 | 97 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 32 | 10 | 315 | 8 | 0 | 0 | 118 | 0 | 0 | 48 | 0 | 104 | 0 | 21 | 161 | 138 | 403 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 107 | 51 | 0 | 18 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 36 | 0 |  | 907 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 17 | 67 | 8 | 85 | 34 | 32 | 0 | 0 | 0 | 32 | 41 | 89 | 0 | 42 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 212 | 0 | 0 | 142 | 0 | 282 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1090 | 222 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6973 | 4307 | 11280 | 3751 | 907 | 2012 | 0 | 2367 | 1290 | 114 | 212 | 687 | 152 | 0 | 1585.109 | 92.63
2:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 405 | 334 |  | 0 | 225 | 0 | 8 | 0 | 32 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 5 | 27 | 17 | 39 | 0 | 0 | 0 | 345 | 320 | 208 | 45 | 144 | 34 | 55 | 0 | 51 | 0 | 48 | 8 | 22 | 9 | 33 | 20 | 108 | 98 | 0 | 20 | 0 | 43 | 41 | 53 | 48 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 320 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 96 | 0 | 21 | 100 | 132 | 403 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 107 | 20 | 0 | 18 | 0 | 162 | 96 | 0 | 35 | 0 | 75 | 37 | 0 |  | 907 | 0 | 140 | 0 | 16 | 0 | 0 | 0 | 17 | 67 | 8 | 86 | 32 | 32 | 0 | 0 | 0 | 32 | 41 | 89 | 0 | 42 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 212 | 0 | 0 | 142 | 0 | 281 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1090 | 224 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6826 | 4263 | 11089 | 3728 | 907 | 2042 | 0 | 2204 | 1290 | 115 | 212 | 695 | 108 | 0 | 1576.8148 | 92.65
3:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 406 | 333 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 5 | 32 | 17 | 40 | 0 | 0 | 0 | 320 | 335 | 200 | 8 | 143 | 34 | 56 | 0 | 51 | 0 | 48 | 8 | 22 | 9 | 33 | 20 | 100 | 98 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 330 | 8 | 0 | 0 | 112 | 0 | 0 | 48 | 0 | 98 | 0 | 21 | 100 | 137 | 399 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 102 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 36 | 0 |  | 907 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 17 | 65 | 8 | 86 | 32 | 32 | 0 | 0 | 0 | 32 | 41 | 89 | 0 | 42 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 210 | 0 | 0 | 142 | 0 | 295 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1090 | 222 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6794 | 4281 | 11075 | 3716 | 907 | 2032 | 0 | 2225 | 1290 | 114 | 210 | 691 | 100 | 0 | 1405.4019 | 92.67
4:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 403 | 333 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 50 | 0 | 33 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 6 | 32 | 17 | 40 | 0 | 0 | 0 | 320 | 335 | 187 | 8 | 142 | 34 | 56 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 122 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 32 | 10 | 320 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 98 | 0 | 21 | 100 | 132 | 402 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 102 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 20 | 0 |  | 908 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 8 | 88 | 30 | 32 | 0 | 0 | 0 | 32 | 41 | 89 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 204 | 0 | 0 | 144 | 0 | 301 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1080 | 222 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6729 | 4267 | 10996 | 3717 | 908 | 2026 | 0 | 2208 | 1280 | 68 | 204 | 667 | 122 | 0 | 1386.0488 | 92.69
5:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 404 | 333 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 26 | 33 | 33 | 50 | 0 | 53 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 6 | 32 | 17 | 41 | 0 | 0 | 0 | 310 | 335 | 178 | 8 | 144 | 34 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 128 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 32 | 10 | 325 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 102 | 0 | 21 | 100 | 135 | 401 | 49 | 105 | 81 | 0 | 16 | 36 | 55 | 17 | 107 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 19 | 0 |  | 909 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 0 | 88 | 27 | 32 | 0 | 0 | 0 | 32 | 41 | 89 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 179 | 0 | 0 | 205 | 0 | 0 | 146 | 0 | 339 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1080 | 222 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6712 | 4296 | 11008 | 3700 | 909 | 2066 | 0 | 2169 | 1280 | 88 | 205 | 668 | 128 | 0 | 1006.3599 | 92.71
6:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 410 | 333 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 50 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 6 | 32 | 17 | 42 | 0 | 0 | 0 | 260 | 305 | 186 | 8 | 144 | 34 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 118 | 101 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 310 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 97 | 0 | 21 | 100 | 142 | 400 | 49 | 105 | 80 | 0 | 16 | 36 | 55 | 17 | 107 | 20 | 0 | 17 | 1 | 54 | 108 | 0 | 35 | 1 | 75 | 19 | 0 |  | 909 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 0 | 88 | 24 | 32 | 0 | 0 | 0 | 32 | 0 | 89 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 180 | 0 | 0 | 216 | 0 | 0 | 147 | 0 | 330 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1040 | 225 | 0 | 0 | 0 | 2 | 52 | 0 | 0 |  | 6578 | 4220 | 10798 | 3637 | 909 | 2043 | 0 | 2098 | 1239 | 112 | 216 | 638 | 118 | 4 | 739.1032 | 92.73
7:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 411 | 331 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 6 | 32 | 17 | 42 | 0 | 0 | 0 | 295 | 320 | 176 | 8 | 144 | 34 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 114 | 99 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 300 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 98 | 5 | 21 | 100 | 140 | 400 | 49 | 105 | 80 | 0 | 16 | 36 | 55 | 17 | 105 | 20 | 0 | 17 | 4 | 54 | 108 | 0 | 35 | 10 | 76 | 19 | 0 |  | 909 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 56 | 0 | 88 | 25 | 32 | 0 | 0 | 0 | 32 | 0 | 89 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 216 | 0 | 0 | 149 | 0 | 332 | 0 | 0 | 50 | 105 | 56 | 0 | 1 | 55 | 970 | 223 | 0 | 0 | 0 | 11 | 52 | 0 | 0 |  | 6614 | 4147 | 10761 | 3678 | 909 | 2032 | 0 | 2095 | 1170 | 111 | 216 | 621 | 114 | 31 | 404.5714 | 92.75
8:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 410 | 331 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 6 | 32 | 17 | 42 | 0 | 0 | 0 | 300 | 325 | 183 | 8 | 143 | 34 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 108 | 80 | 0 | 20 | 1 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 50 | 0 | 220 | 0 | 32 | 10 | 305 | 8 | 0 | 0 | 112 | 0 | 0 | 48 | 0 | 88 | 0 | 21 | 100 | 132 | 402 | 48 | 105 | 68 | 0 | 50 | 36 | 55 | 17 | 106 | 20 | 0 | 17 | 26 | 54 | 108 | 0 | 35 | 7 | 75 | 17 | 0 |  | 908 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 56 | 0 | 85 | 23 | 32 | 0 | 0 | 0 | 32 | 0 | 36 | 0 | 42 | 24 | 8 | 33 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 192 | 0 | 0 | 147 | 0 | 315 | 0 | 0 | 50 | 105 | 56 | 0 | 2 | 55 | 940 | 220 | 0 | 0 | 2 | 45 | 52 | 0 | 0 |  | 6574 | 4047 | 10621 | 3669 | 908 | 1964 | 0 | 2094 | 1140 | 111 | 192 | 544 | 108 | 83 | 165 | 92.76
9:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 410 | 327 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 17 | 51 | 56 | 6 | 32 | 17 | 39 | 0 | 0 | 0 | 280 | 305 | 179 | 8 | 141 | 36 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 138 | 67 | 0 | 20 | 2 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 50 | 0 | 220 | 0 | 32 | 10 | 300 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 98 | 11 | 21 | 100 | 130 | 400 | 48 | 105 | 68 | 0 | 50 | 36 | 55 | 17 | 106 | 20 | 0 | 17 | 13 | 54 | 108 | 0 | 35 | 24 | 65 | 17 | 0 |  | 909 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 32 | 0 | 0 | 0 | 32 | 0 | 36 | 0 | 42 | 24 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 146 | 0 | 310 | 0 | 0 | 50 | 105 | 56 | 0 | 3 | 55 | 900 | 220 | 0 | 0 | 4 | 67 | 52 | 0 | 0 |  | 6535 | 3903 | 10438 | 3599 | 909 | 1945 | 0 | 2094 | 1100 | 111 | 130 | 418 | 138 | 124 | 380 | 92.77
10:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 411 | 328 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 17 | 51 | 56 | 6 | 31 | 17 | 31 | 0 | 0 | 0 | 280 | 305 | 205 | 8 | 142 | 36 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 0 | 33 | 20 | 136 | 66 | 0 | 20 | 2 | 43 | 41 | 33 | 49 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 32 | 10 | 270 | 8 | 0 | 0 | 112 | 0 | 0 | 48 | 0 | 98 | 14 | 21 | 100 | 120 | 375 | 48 | 90 | 68 | 5 | 50 | 17 | 55 | 17 | 105 | 20 | 0 | 17 | 40 | 54 | 108 | 0 | 35 | 24 | 62 | 17 | 0 |  | 909 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 32 | 0 | 0 | 0 | 32 | 0 | 36 | 0 | 42 | 24 | 8 | 12 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 280 | 0 | 0 | 50 | 105 | 56 | 0 | 4 | 55 | 900 | 218 | 0 | 0 | 4 | 88 | 52 | 0 | 0 |  | 6395 | 3877 | 10272 | 3597 | 909 | 1816 | 0 | 2025 | 1100 | 111 | 130 | 397 | 136 | 181 | 671 | 92.78
11:00 | 0 | 0 | 0 | 180 | 250 | 80 | 0 | 407 | 327 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 12 | 0 | 32 | 42 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 6 | 31 | 17 | 21 | 0 | 0 | 0 | 345 | 325 | 203 | 8 | 142 | 36 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 146 | 66 | 0 | 17 | 2 | 43 | 41 | 31 | 30 | 110 | 0 | 58 | 10 | 0 | 220 | 0 | 32 | 10 | 300 | 8 | 0 | 0 | 112 | 0 | 0 | 47 | 0 | 98 | 7 | 21 | 100 | 115 | 377 | 48 | 90 | 68 | 6 | 52 | 17 | 50 | 17 | 105 | 20 | 0 | 17 | 21 | 54 | 108 | 0 | 35 | 34 | 64 | 0 | 0 |  | 909 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 19 | 32 | 0 | 0 | 0 | 32 | 0 | 36 | 0 | 42 | 24 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 144 | 0 | 281 | 0 | 0 | 50 | 105 | 56 | 0 | 5 | 55 | 900 | 212 | 0 | 0 | 4 | 103 | 52 | 0 | 0 |  | 6354 | 3866 | 10220 | 3576 | 909 | 1800 | 0 | 2000 | 1100 | 113 | 130 | 394 | 146 | 182 | 995 | 92.79
12:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 396 | 312 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 0 | 30 | 42 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 6 | 30 | 17 | 30 | 0 | 0 | 0 | 340 | 320 | 197 | 8 | 142 | 36 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 140 | 66 | 0 | 20 | 3 | 43 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 220 | 0 | 32 | 10 | 330 | 8 | 0 | 0 | 112 | 0 | 0 | 47 | 0 | 102 | 11 | 21 | 100 | 120 | 381 | 49 | 90 | 68 | 6 | 52 | 17 | 55 | 17 | 103 | 20 | 0 | 18 | 54 | 54 | 108 | 0 | 35 | 19 | 53 | 0 | 0 |  | 908 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 23 | 32 | 0 | 0 | 0 | 32 | 5 | 36 | 0 | 42 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 181 | 0 | 0 | 159 | 0 | 0 | 144 | 0 | 268 | 0 | 0 | 50 | 105 | 56 | 0 | 6 | 55 | 920 | 213 | 0 | 0 | 4 | 107 | 52 | 0 | 0 |  | 6420 | 3909 | 10329 | 3602 | 908 | 1817 | 0 | 1992 | 1119 | 113 | 159 | 428 | 140 | 210 | 1080 | 92.79
13:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 399 | 312 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 17 | 33 | 31 | 42 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 6 | 31 | 17 | 30 | 0 | 0 | 0 | 315 | 330 | 189 | 8 | 143 | 35 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 152 | 65 | 0 | 17 | 3 | 43 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 221 | 0 | 32 | 10 | 320 | 8 | 0 | 0 | 112 | 0 | 0 | 47 | 0 | 104 | 20 | 21 | 100 | 120 | 376 | 48 | 90 | 68 | 3 | 52 | 17 | 53 | 17 | 103 | 20 | 0 | 17 | 49 | 54 | 108 | 0 | 35 | 23 | 55 | 0 | 0 |  | 909 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 25 | 32 | 0 | 0 | 0 | 32 | 5 | 36 | 0 | 42 | 29 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 201 | 0 | 0 | 143 | 0 | 265 | 0 | 0 | 50 | 105 | 56 | 0 | 6 | 55 | 940 | 212 | 0 | 0 | 4 | 64 | 52 | 0 | 0 |  | 6524 | 3938 | 10462 | 3704 | 909 | 1804 | 0 | 1993 | 1140 | 113 | 201 | 475 | 152 | 172 | 864 | 92.8
14:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 404 | 312 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 13 | 33 | 31 | 42 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 56 | 11 | 31 | 17 | 30 | 0 | 0 | 0 | 315 | 325 | 201 | 8 | 143 | 34 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 154 | 67 | 0 | 17 | 2 | 43 | 41 | 31 | 30 | 110 | 0 | 58 | 10 | 0 | 221 | 0 | 32 | 10 | 295 | 8 | 0 | 0 | 112 | 0 | 0 | 47 | 0 | 95 | 14 | 21 | 100 | 122 | 399 | 48 | 105 | 68 | 5 | 51 | 17 | 51 | 17 | 102 | 20 | 0 | 0 | 25 | 54 | 108 | 0 | 35 | 31 | 74 | 0 | 0 |  | 908 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 25 | 32 | 0 | 0 | 0 | 32 | 5 | 36 | 0 | 42 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 280 | 0 | 0 | 50 | 105 | 55 | 0 | 6 | 55 | 950 | 213 | 0 | 0 | 4 | 4 | 52 | 0 | 0 |  | 6520 | 3886 | 10406 | 3730 | 908 | 1796 | 0 | 1996 | 1150 | 114 | 199 | 467 | 154 | 91 | 824 | 92.8
15:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 396 | 318 |  | 0 | 225 | 0 | 4 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 15 | 33 | 31 | 41 | 0 | 79 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 11 | 32 | 17 | 32 | 0 | 0 | 0 | 305 | 300 | 188 | 8 | 143 | 34 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 156 | 66 | 0 | 17 | 2 | 43 | 41 | 31 | 30 | 110 | 0 | 59 | 10 | 0 | 221 | 0 | 32 | 10 | 320 | 8 | 0 | 0 | 112 | 0 | 0 | 47 | 0 | 95 | 8 | 21 | 100 | 120 | 391 | 49 | 105 | 68 | 4 | 52 | 17 | 55 | 17 | 103 | 20 | 0 | 0 | 5 | 54 | 108 | 0 | 35 | 26 | 74 | 0 | 0 |  | 909 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 25 | 32 | 0 | 0 | 0 | 32 | 5 | 36 | 0 | 42 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 179 | 0 | 0 | 180 | 0 | 0 | 141 | 0 | 275 | 0 | 0 | 50 | 105 | 55 | 0 | 5 | 55 | 950 | 213 | 0 | 0 | 2 | 83 | 90 | 0 | 0 |  | 6445 | 3977 | 10422 | 3642 | 909 | 1826 | 0 | 2043 | 1150 | 114 | 180 | 447 | 156 | 135 | 1040 | 92.81
16:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 405 | 316 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 60 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 15 | 33 | 16 | 41 | 0 | 78 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 15 | 32 | 17 | 31 | 0 | 0 | 0 | 280 | 275 | 204 | 8 | 142 | 34 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 7 | 33 | 20 | 156 | 71 | 0 | 17 | 1 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 32 | 10 | 290 | 8 | 0 | 0 | 105 | 0 | 0 | 68 | 0 | 89 | 7 | 21 | 100 | 118 | 403 | 49 | 105 | 68 | 1 | 52 | 21 | 55 | 17 | 101 | 20 | 0 | 0 | 12 | 74 | 102 | 0 | 35 | 19 | 74 | 0 | 0 |  | 912 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 87 | 24 | 16 | 0 | 0 | 0 | 32 | 6 | 36 | 0 | 42 | 24 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 130 | 0 | 0 | 142 | 0 | 300 | 0 | 0 | 50 | 105 | 65 | 0 | 4 | 55 | 920 | 200 | 0 | 0 | 0 | 51 | 90 | 0 | 0 |  | 6437 | 3877 | 10314 | 3612 | 912 | 1804 | 0 | 2104 | 1120 | 113 | 130 | 398 | 156 | 95 | 955 | 92.81
17:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 408 | 281 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 57 | 8 | 8 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 17 | 33 | 16 | 41 | 0 | 79 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 28 | 32 | 17 | 33 | 0 | 0 | 0 | 280 | 275 | 181 | 8 | 143 | 34 | 35 | 0 | 51 | 0 | 34 | 8 | 22 | 7 | 33 | 20 | 146 | 83 | 0 | 17 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 32 | 10 | 270 | 8 | 0 | 0 | 105 | 0 | 0 | 174 | 0 | 128 | 4 | 21 | 160 | 118 | 353 | 78 | 105 | 79 | 0 | 200 | 36 | 55 | 114 | 101 | 20 | 0 | 11 | 11 | 162 | 108 | 0 | 35 | 8 | 75 | 0 | 0 |  | 913 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 22 | 16 | 0 | 0 | 0 | 32 | 6 | 34 | 0 | 42 | 32 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 146 | 0 | 250 | 0 | 0 | 90 | 105 | 80 | 0 | 3 | 95 | 870 | 168 | 0 | 0 | 1 | 9 | 90 | 0 | 0 |  | 6976 | 3764 | 10740 | 3497 | 913 | 1667 | 0 | 2822 | 1070 | 114 | 130 | 475 | 146 | 36 | 194 | 92.82
18:00 | 0 | 0 | 0 | 180 | 250 | 43 | 0 | 408 | 251 |  | 0 | 225 | 0 | 5 | 0 | 30 | 0 | 0 | 37 | 8 | 8 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 17 | 33 | 33 | 41 | 0 | 77 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 10 | 66 | 32 | 17 | 33 | 0 | 0 | 0 | 280 | 260 | 207 | 8 | 143 | 31 | 35 | 0 | 10 | 0 | 34 | 8 | 22 | 8 | 33 | 20 | 134 | 83 | 0 | 19 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 40 | 10 | 0 | 206 | 0 | 31 | 10 | 270 | 8 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 119 | 0 | 21 | 200 | 118 | 333 | 78 | 105 | 101 | 0 | 213 | 36 | 55 | 88 | 106 | 20 | 0 | 18 | 3 | 162 | 108 | 0 | 35 | 2 | 70 | 0 | 0 |  | 913 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 15 | 0 | 8 | 88 | 20 | 16 | 0 | 0 | 0 | 25 | 6 | 34 | 0 | 42 | 30 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 254 | 17 | 0 | 94 | 105 | 91 | 0 | 2 | 50 | 700 | 164 | 0 | 0 | 0 | 8 | 90 | 0 | 0 |  | 6916 | 3609 | 10525 | 3391 | 913 | 1554 | 0 | 2992 | 900 | 112 | 130 | 514 | 134 | 15 | 0 | 92.83
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 408 | 310 |  | 0 | 225 | 0 | 42 | 0 | 30 | 0 | 0 | 95 | 24 | 58 | 130 | 0 | 0 | 0 | 0 | 40 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 46 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 75 | 32 | 17 | 35 | 0 | 0 | 0 | 335 | 325 | 203 | 8 | 142 | 34 | 55 | 0 | 32 | 0 | 40 | 20 | 22 | 8 | 33 | 20 | 160 | 99 | 0 | 19 | 0 | 43 | 41 | 53 | 48 | 110 | 0 | 60 | 81 | 0 | 220 | 0 | 32 | 10 | 290 | 12 | 0 | 0 | 243 | 0 | 0 | 178 | 0 | 136 | 0 | 90 | 200 | 122 | 403 | 78 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 112 | 40 | 0 | 50 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 0 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 44 | 30 | 8 | 88 | 30 | 16 | 0 | 0 | 0 | 25 | 19 | 86 | 0 | 42 | 30 | 46 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 158 | 0 | 0 | 137 | 0 | 260 | 25 | 0 | 94 | 105 | 91 | 0 | 0 | 60 | 740 | 208 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7949 | 3934 | 11883 | 3794 | 913 | 1891 | 0 | 3401 | 940 | 114 | 158 | 670 | 160 | 0 | 476.4543 | 92.86
19:30 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 411 | 332 |  | 0 | 225 | 0 | 78 | 0 | 30 | 0 | 0 | 53 | 89 | 64 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 50 | 0 | 79 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 82 | 32 | 17 | 35 | 0 | 0 | 0 | 280 | 275 | 200 | 8 | 142 | 36 | 55 | 0 | 35 | 0 | 35 | 43 | 22 | 8 | 33 | 20 | 152 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 250 | 16 | 0 | 0 | 243 | 0 | 0 | 179 | 0 | 136 | 0 | 90 | 200 | 123 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 72 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 0 | 0 |  | 913 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 38 | 37 | 8 | 88 | 31 | 16 | 0 | 0 | 0 | 25 | 25 | 86 | 0 | 42 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 150 | 0 | 0 | 154 | 0 | 250 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1010 | 208 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8023 | 4322 | 12345 | 3732 | 913 | 1872 | 0 | 3685 | 1210 | 114 | 150 | 667 | 152 | 0 | 695.7891 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 409 | 332 |  | 0 | 225 | 0 | 73 | 0 | 30 | 0 | 0 | 52 | 76 | 94 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 50 | 0 | 77 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 84 | 32 | 17 | 29 | 0 | 0 | 0 | 280 | 275 | 207 | 8 | 143 | 36 | 54 | 0 | 51 | 0 | 42 | 43 | 22 | 8 | 33 | 20 | 154 | 101 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 260 | 16 | 11 | 0 | 243 | 0 | 0 | 179 | 0 | 135 | 0 | 76 | 200 | 123 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 112 | 100 | 0 | 90 | 0 | 162 | 108 | 0 | 35 | 0 | 66 | 0 | 0 |  | 913 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 38 | 76 | 8 | 88 | 29 | 32 | 0 | 0 | 0 | 32 | 30 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 130 | 0 | 0 | 159 | 0 | 254 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1020 | 214 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8083 | 4386 | 12469 | 3757 | 913 | 1901 | 0 | 3708 | 1220 | 112 | 130 | 704 | 154 | 0 | 673.6713 | 92.85
21:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 412 | 332 |  | 0 | 225 | 0 | 80 | 0 | 30 | 0 | 0 | 92 | 88 | 94 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 15 | 51 | 56 | 89 | 32 | 17 | 31 | 0 | 0 | 0 | 310 | 305 | 206 | 8 | 142 | 36 | 55 | 0 | 51 | 0 | 39 | 43 | 22 | 10 | 33 | 20 | 162 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 9 | 270 | 16 | 11 | 0 | 245 | 0 | 0 | 179 | 0 | 133 | 0 | 90 | 200 | 128 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 88 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 913 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 71 | 8 | 88 | 31 | 32 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 172 | 0 | 0 | 167 | 0 | 370 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1040 | 214 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8304 | 4581 | 12885 | 3877 | 913 | 2031 | 0 | 3820 | 1240 | 112 | 172 | 730 | 162 | 0 | 520.6899 | 92.86
22:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 410 | 333 |  | 0 | 225 | 0 | 79 | 0 | 30 | 0 | 0 | 97 | 81 | 94 | 112 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 25 | 33 | 48 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 18 | 51 | 56 | 90 | 32 | 17 | 39 | 0 | 0 | 0 | 330 | 330 | 205 | 8 | 142 | 34 | 55 | 0 | 51 | 0 | 34 | 43 | 22 | 10 | 33 | 20 | 172 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 32 | 9 | 290 | 24 | 11 | 0 | 258 | 0 | 0 | 180 | 0 | 135 | 0 | 90 | 200 | 135 | 404 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 91 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 70 | 8 | 86 | 32 | 32 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 160 | 0 | 0 | 163 | 0 | 360 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1040 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8391 | 4560 | 12951 | 3916 | 913 | 2057 | 0 | 3840 | 1240 | 112 | 160 | 701 | 172 | 0 | 321.6297 | 92.87
23:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 409 | 333 |  | 0 | 225 | 0 | 75 | 0 | 30 | 0 | 0 | 97 | 84 | 32 | 112 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 25 | 33 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 45 | 89 | 32 | 17 | 30 | 0 | 0 | 0 | 345 | 330 | 204 | 8 | 142 | 34 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 166 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 31 | 10 | 310 | 24 | 11 | 0 | 260 | 0 | 0 | 47 | 0 | 135 | 0 | 90 | 200 | 135 | 405 | 49 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 112 | 100 | 0 | 79 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 913 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 68 | 8 | 85 | 32 | 32 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 199 | 0 | 0 | 163 | 0 | 363 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1040 | 221 | 0 | 0 | 0 | 0 | 91 | 0 | 0 |  | 8173 | 4599 | 12772 | 3920 | 913 | 2073 | 0 | 3595 | 1240 | 113 | 199 | 752 | 166 | 0 | 394.4341 | 92.88
24:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 404 | 332 |  | 0 | 225 | 0 | 15 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 25 | 33 | 42 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 89 | 19 | 17 | 42 | 0 | 0 | 0 | 310 | 310 | 210 | 8 | 142 | 36 | 55 | 0 | 51 | 0 | 32 | 43 | 22 | 10 | 33 | 20 | 168 | 102 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 31 | 10 | 300 | 8 | 11 | 0 | 205 | 0 | 0 | 47 | 0 | 101 | 0 | 90 | 181 | 138 | 401 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 98 | 90 | 0 | 23 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 32 | 56 | 8 | 87 | 31 | 32 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 34 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 192 | 0 | 0 | 209 | 0 | 0 | 160 | 0 | 352 | 0 | 0 | 50 | 105 | 73 | 0 | 0 | 55 | 1100 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7233 | 4461 | 11694 | 3847 | 914 | 1950 | 0 | 2724 | 1300 | 113 | 209 | 678 | 168 | 0 | 1019.262 | 92.89
KWH | 0 | 0 | 0 | 4378500 | 7018845 | 1952909 | 0 | 9887750 | 7708000 |  | 0 | 5035400 | 0 | 499200 | 0 | 853556 | 0 | 0 | 966000 | 522240 | 495216 | 1669920 | 0 | 0 | 0 | 0 | 870120 | 1330984 | 954209 | 392184 | 600000 | 489240 | 686160 | 718400 | 1122720 | 0 | 1813440 | 844000 | 2300000 | 0 | 580883 | 0 | 0 | 0 | 0 |  | 0 | 552048 | 1201626 | 1309080 | 731520 | 740640 | 375456 | 869760 | 0 | 0 | 0 | 7763000 | 7594000 | 4728000 | 284363 | 3402030 | 831024 | 1100640 | 0 | 1175026 | 0 | 1057560 | 404381 | 502416 | 201240 | 807900 | 493360 | 3364800 | 2030400 | 0 | 408528 | 15450 | 1024000 | 956624 | 1069800 | 1069800 | 2591263 | 0 | 1416480 | 1261440 | 0 | 5246580 | 0 | 749480 | 236880 | 7427500 | 233024 | 55000 | 0 | 3748580 | 0 | 0 | 1900800 | 0 | 2607696 | 112455 | 862080 | 3254880 | 3082836 | 9387000 | 1342800 | 2466000 | 2043227 | 23641 | 2029855 | 776329 | 1317267 | 1061340 | 2550240 | 954240 | 0 | 650880 | 286310 | 2760480 | 2589382 | 0 | 887760 | 249991 | 1710720 | 458640 | 0 |  | 21995636 | 0 | 3989376 | 0 | 375360 | 0 | 0 | 0 | 292320 | 854528 | 143250 | 2076507 | 634351 | 724032 | 0 | 0 | 0 | 740640 | 409440 | 1474800 | 0 | 924528 | 558750 | 384000 | 528870 | 457460 | 0 | 264474 | 0 | 0 | 4886100 | 0 | 0 | 4495045 | 0 | 0 | 4534573 | 0 | 0 | 3801964 | 0 | 7170981 | 175200 | 0 | 1630656 | 2562192 | 1601011 | 0 | 48532 | 1588224 | 25414800 | 5058955 | 0 | 0 | 35760 | 609120 | 1691520 | 0 | 0 |  | 168087424 | 102132955 | 270220379 | 89520507 | 21995636 | 45854008 | 0 | 61270754 | 30300900 | 2657440 | 4534573 | 9340502 | 3364800 | 1381259 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 7861106.4 | 2597368.97 | 0 | 10382137.5 | 8324640 |  | 0 | 5488586 | 0 | 5581056 | 0 | 11309617 | 0 | 0 | 1690500 | 7635148.8 | 6967689.12 | 27069403.2 | 0 | 0 | 0 | 0 | 11067926.4 | 17968284 | 12795942.69 | 294138 | 450000 | 0 | 0 | 0 | 19097467.2 | 0 | 489628.8 | 227880 | 4347000 | 0 | 9497437.05 | 0 | 0 | 0 | 0 |  | 0 | 9208160.64 | 20451674.52 | 17685670.8 | 9275673.6 | 8569204.8 | 476829.12 | 2896300.8 | 0 | 0 | 0 | 8616930 | 8277460 | 5484480 | 366828.27 | 4150476.6 | 939057.12 | 1639953.6 | 0 | 1962293.42 | 0 | 18264061.2 | 5438924.45 | 688309.92 | 150930 | 1413825 | 370020 | 24159264 | 2213136 | 0 | 555598.08 | 246273 | 1402880 | 1262743.68 | 1861452 | 1850754 | 2979952.45 | 0 | 2747971.2 | 2876083.2 | 0 | 5299045.8 | 0 | 1116725.2 | 469022.4 | 7427500 | 174768 | 41800 | 0 | 51168117 | 0 | 0 | 25622784 | 0 | 36116589.6 | 1314598.95 | 8896665.6 | 44461660.8 | 40909233.72 | 8636040 | 16328448 | 35658360 | 25846821.55 | 0 | 23830497.7 | 8454222.81 | 14002548.21 | 14402383.8 | 32872593.6 | 11240947.2 | 0 | 8428896 | 4137179.5 | 35030491.2 | 29467167.16 | 0 | 11594145.6 | 2987392.45 | 25609478.4 | 6040288.8 | 0 |  | 65986908 | 0 | 4468101.12 | 0 | 3907497.6 | 0 | 0 | 0 | 5264683.2 | 15381504 | 2058502.5 | 2325687.84 | 1230640.94 | 7891948.8 | 0 | 0 | 0 | 12420532.8 | 7161105.6 | 23065872 | 0 | 15310183.68 | 9448462.5 | 5233920 | 8922036.9 | 946942.2 | 0 | 200206.818 | 0 | 0 | 25847469 | 0 | 0 | 5214252.2 | 0 | 0 | 79173644.58 | 0 | 0 | 4410278.24 | 0 | 7099271.19 | 2354688 | 0 | 19290660.48 | 37023674.4 | 20332839.7 | 0 | 536278.6 | 19281039.36 | 228987348 | 5160134.1 | 0 | 0 | 404445.6 | 7144977.6 | 25931001.6 | 0 | 0 |  | 883736506.65 | 679416739.148 | 1563153245.798 | 101069673.638 | 65986908 | 56294448.74 | 0 | 807488338.78 | 254834817 | 717508.8 | 79173644.58 | 156657496.56 | 24159264 | 16771145.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 410 | 327 |  | 0 | 225 | 0 | 7 | 0 | 40 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 17 | 51 | 56 | 6 | 32 | 17 | 39 | 0 | 0 | 0 | 280 | 305 | 179 | 8 | 141 | 36 | 35 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 138 | 67 | 0 | 20 | 2 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 50 | 0 | 220 | 0 | 32 | 10 | 300 | 8 | 0 | 0 | 115 | 0 | 0 | 48 | 0 | 98 | 11 | 21 | 100 | 130 | 400 | 48 | 105 | 68 | 0 | 50 | 36 | 55 | 17 | 106 | 20 | 0 | 17 | 13 | 54 | 108 | 0 | 35 | 24 | 65 | 17 | 0 |  | 909 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 32 | 0 | 0 | 0 | 32 | 0 | 36 | 0 | 42 | 24 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 146 | 0 | 310 | 0 | 0 | 50 | 105 | 56 | 0 | 3 | 55 | 900 | 220 | 0 | 0 | 4 | 67 | 52 | 0 | 0 |  | 10438 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 412 | 332 | 0 | 0 | 225 | 0 | 80 | 0 | 30 | 0 | 0 | 92 | 88 | 94 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 51 | 56 | 89 | 32 | 17 | 31 | 0 | 0 | 0 | 310 | 305 | 206 | 8 | 142 | 36 | 55 | 0 | 51 | 0 | 39 | 43 | 22 | 10 | 33 | 20 | 162 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 9 | 270 | 16 | 11 | 0 | 245 | 0 | 0 | 179 | 0 | 133 | 0 | 90 | 200 | 128 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 88 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 913 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 71 | 8 | 88 | 31 | 32 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 172 | 0 | 0 | 167 | 0 | 370 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1040 | 214 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 12885 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 90 | 50 | 94 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 51 | 56 | 95 | 32 | 17 | 30 | 0 | 0 | 0 | 310 | 305 | 210 | 8 | 142 | 37 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 166 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 290 | 16 | 0 | 0 | 275 | 0 | 0 | 180 | 0 | 133 | 0 | 90 | 200 | 128 | 400 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 |  | 60 | 55 |  |  | 930 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 70 | 8 | 88 | 30 | 32 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 34 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 350 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1100 | 220 |  | 0 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 90 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 17 | 55 | 90 | 25 | 17 | 10 | 0 | 0 | 0 | 310 | 305 | 210 | 8 | 142 | 37 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 143 | 102 | 0 | 20 | 1.6 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 31 | 10 | 290 | 8 | 0 | 0 | 110 | 0 | 0 | 48 | 0 | 100 | 20 | 21 | 100 | 128 | 400 | 49 | 88 | 68 | 5 | 50 | 36 | 55 | 17 | 78 | 20 | 0 | 17 | 50 | 70 | 108 | 0 | 35 | 30 | 60 | 55 |  |  | 930 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 15 | 20 | 0 | 88 | 23 | 16 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 34 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 350 | 0 | 0 | 50 | 105 | 56 | 0 | 8 | 55 | 1110 | 225 |  | 0 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 303 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 17 | 56 | 89 | 25 | 17 | 13 | 0 | 0 | 0 | 310 | 305 | 211 | 8 | 142 | 37 | 56 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 124 | 104 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 65 | 10 | 0 | 221 | 0 | 31 | 10 | 280 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 68 | 128 | 363 | 49 | 88 | 68 | 2 | 16 | 36 | 55 | 17 | 78 | 20 | 0 | 18 | 1 | 54 | 108 | 0 | 35 | 1 | 58 | 55 | 0 | 0 | 913 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 88 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 34 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 340 | 0 | 0 | 50 | 105 | 56 | 0 | 2 | 55 | 960 | 223 | 0 | 0 | 0 | 16 | 52 | 0 | 0 | 0 |  |  |  |  | 75145829 |  | 0
75145829
| Minimum Generation |  | 10438 | 9:00
| Highest Generation |  | 12951 | 22:00
| Day Peak Generation |  | 10438 | 9:00
| Evening Peak Generation |  | 12885 | 21:00
| HVDC Max Flow |  | 914 | 24:00
| HVDC EvPeak Flow |  | 913 | 21:00
| Load factor L.F |  | 86.94% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-06
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10438 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10552 | MW
Evening Peak Generation : |  | 12885 | MW Hour : | 21:00 | Available Max Generation : |  | 12778 | MW
E.P. Demand (at gen end) : |  | 13450 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 12951 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 270.2204 | System Load Factor : | 86.94% | Load Shed : |  | 942.2963 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 274 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-06
Actual : | 93.01 | Ft.(MSL) , | Rule curve : | 90.6 | Ft.( MSL )
Gas Consumed : | Total = | 1024.74 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157364122.378
: |  | Coal : | 254834817 | Oil : | 1043319479.92 | Total : | 1455518419.298
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 70 | 1680:00 | 4419.4129 |  |  | 253.7441 | 5.742%
Chittagong Area | 0 | 0:00 | 1251.4251 |  |  | 100.5505 | 8.035%
Khulna Area | 85 | 2040:00 | 1652.0338 |  |  | 139.607 | 8.451%
Rajshahi Area | 85 | 2040:00 | 1466.3548 |  |  | 132.4836 | 9.035%
Cumilla Area | 90 | 2160:00 | 1247.6098 |  |  | 108.5078 | 8.697%
Mymensingh Area | 126 | 3024:00 | 1031.4083 |  |  | 95.4332 | 9.253%
Sylhet Area | 0 | 0:00 | 460.382 |  |  | 37.1025 | 8.059%
Barisal Area | 0 | 0:00 | 375.1732 |  |  | 0 | 0%
Rangpur Area | 65 | 1560:00 | 813.935 |  |  | 74.8676 | 9.198%
Total | 521 |  | 12717.735 |  |  | 942.2963
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Halishahar-Khulshi 132 kV Ckt-3 tripped at 08:29 showing Dist. Z1, B-phase relay at Halishahar end & Dist.
Z1, C-phase relay at Khulshi end and was switched on at 08:55.
b) Mymensing-Kishoreganj 132 kV Ckt-2 tripped at 09:01 showing Dist. Z1, C-phase relay at Mymensing end &
Dist. Z1, C-phase relay at Kishoreganj end and was switched on at 10:55.
c) Sonargaon 132/33 kV T-1 transformer was under shut down from 10:35 to 12:30 for D/W.
d) Sonargaon 132/33 kV T-2 transformer was under shut down from 12:32 to 13:14 for D/W.
e) Sonargaon-Sonargaon Orion P/P 132 kV Ckt was under shut down from 14:04 to 14:44 for D/W.
f) Niamatpur 132/33 kV T-1 transformer was under shut down from 17:25 to 18:48 due to R/H maintenance. | [5 empty] | About 24 MW power interruption occurred under
Niamatpur S/S area from 17:25 to 18:48.
g) Siddhirganj 210 MW GT-1 was synchronized at 12:14.
h) Dohazari-Sikalbaha 132 kV Ckt-1 tripped at 19:24 from both end showing Dist. Z1, B-phase relays and
was switched on at 19:51.
i) Cumilla(N)-Daudkandi 132 kV Ckt-1 tripped at 04:28(06-08-2022) from both end showing, O/C, Dist. Z1,
A-phase relays and was switched on at 04:33(06-08-2022).
j) Shahjibazar 132/33 kV T-4 transformer was under shut down from 06:36(06/08/22) to 07:10(06/08/22) for C/M. | [5 empty] | About 40 MW power interruption occurred under
Shahjibazar S/S area from 06:36(06/08/22) to 07:10
k) Mymensing-Netrokona 132 kV Ckt-1 tripped at 05:51(06-08-22) showing Dist. Z1, A-phase relay at Mymensing
end & Dist. Z1, 3-phase relay at Netrokona end and was switched on at 06:49(06-08-2022).
l) Purbasadipur 132/33 kV T-4 transformer was shut down at 05:20(06/08/22) due to 33 kV Bus maintenance by | [5 empty] | About 40 MW power interruption occurred under
NESCO. | [5 empty] | Purbasadipur S/S area from 05:20(06/08/22) to till.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7018845 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 89 | 1952909 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9887750
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7708000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5035400 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 80 | 499200 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 853556 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 392184
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 92 | 966000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 88 | 522240 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 495216 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 870120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 127 | 1669920 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1330984
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 954209
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1089240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 686160
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 718400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1122720 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 3748580 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2607696 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2466000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 88 | 650880 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2760480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 249991
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 458640
| Dhaka area Total |  |  |  | 5847 | 3184 | 61093820
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 580883
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 112455
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 740640 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 112 | 2657440 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2043227
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 552048 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1201626 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 56 | 1309080 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 862080 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 375456 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 869760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 731520 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23641
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 2029855 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 776329 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1317267 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 954240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2589382 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1236 | 22026929
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4728000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7763000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7594000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 831024 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1100640
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 284363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1175026
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 3082836 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 1057560 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 3402030 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3254880
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502416
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 201240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3364800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 807900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 404381 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 493360 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1061340
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2550240
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 1710720 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 2106 | 46257516
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 2030400 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 408528
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15450
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 179 | 1900800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1342800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 286310
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 380 | 5984288
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 956624 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2591263 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1069800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 1069800
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 55000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1416480
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1261440 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5246580
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 32 | 749480 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 233024 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7427500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9387000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 236880
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1398 | 32724871
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 21995636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 375360 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 292320 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 71 | 854528 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 185 | 3989376 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 143250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 175200 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2562192
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 609120
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1365 | 30996982
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 724032 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 634351 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2076507 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1040 | 25414800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 214 | 5058955
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1405 | 33908645
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 740640 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 409440 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 924528 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 558750 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4495045 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4534573
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 167 | 3801964 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 7170981 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 528870 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 457460
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 264474
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 384000
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 1474800 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1630656 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1588224 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35760
| Rajshahi Area Total |  |  |  | 2129 | 1429 | 29000165
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4886100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1601011 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48532
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1691520 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 382 | 8227163
| Total |  |  |  | 21680 | 12885 | 270220379
| Eastern Grid Total |  |  |  | 14489 | 8304 | 168087424
| Western Grid Total |  |  |  | 7191 | 4581 | 102132955
| National Grid Total |  |  |  | 21680 | 12885 | 270220379
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-05
(a) ENTIRE EASTERN GRID : |  | 8419.52 | MW | (b) ENTIRE WESTERN GRID : |  | 4004.87 | MW
i) Dhaka area |  | 4336.27 | MW | i) Khulna area |  | 1536 | MW
ii) Chittagong area |  | 1344.25 | MW | ii) Rajshahi area |  | 1302 | MW
iii) Comilla area |  | 1210 | MW | iii) Barisal area |  | 387.87 | MW
iv) Mymensingh area |  | 944 | MW | iv) Rangpur area |  | 779 | MW
v) Sylhet area |  | 585 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12424.39 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 18 | 05:00 | Chowmuhani | 187 | 17:00 | Kaptai | 4.5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 20 | 15:00 | Chuadanga | 93 | 21:00 | Kazla | 85 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 19:30 | Coxsbazar | 118 | 22:00 | Keranigonj | 56 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 79 | 19:00 | Cumilla(N) | 154 | 19:00 | Khagrachori | 26 | 18:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 62 | 00:00 | Cumilla(S) | 172 | 22:00 | Khulna | 90 | 20:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 52 | 22:00 | Daudkandi | 134 | 21:00 | Khulshi | 169 | 19:30 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 43 | 00:00 | Dhaka | 20 | 00:00 | Kishoreganj | 118 | 20:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 143 | 19:00 | Dhamrai | 92 | 21:00 | Kodda | 268 | 08:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 89 | 23:00 | Dhanmondi | 124 | 19:00 | Kulaura | 54 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 92 | 21:00 | Dohazari | 92 | 20:00 | Kurigram | 66 | 19:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 47 | 19:30 | Faridpur | 150 | 22:00 | Kushtia | 132 | 22:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 6 | 10:00 | Fatullah | 63 | 02:00 | Lalbag | 80 | 01:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 50 | 22:00 | Fenchuganj | 49 | 20:00 | Lalmonirhat | 46 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 22 | 23:00 | Feni | 95 | 17:00 | Madanganj | 65 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 101 | 23:00 | GPH | 91 | 06:00 | Madaripur | 113 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 74 | 00:00 | Ghorashal | 44 | 22:00 | Madartek | 85 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 73 | 21:00 | Goalpara | 25 | 22:00 | Madunaghat | 69 | 19:30 | Rajshahi | 132 | 22:00
Baroirhat | 63 | 19:30 | Gollamari | 48 | 20:00 | Magura | 50 | 07:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 154 | 16:00 | Gopalganj | 105.4 | 19:30 | Mahasthangarh | 62 | 04:00 | Ramganj | 88 | 19:00
BashundharaCement | 6 | 00:00 | Gulshan | 92 | 19:00 | Manikganj | 95 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 72 | 22:00 | Halishahar | 65 | 19:00 | Maniknagar | 50 | 00:00 | Rangamati | 14 | 19:00
Benapole | 48 | 19:00 | HaripurSBU | 131 | 00:00 | Matarbari | 42 | 20:00 | Rangpur | 105 | 08:00
Bhaluka | 104 | 18:00 | Hasnabad | 89 | 22:00 | Matuail | 54 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 00:00 | Hathazari | 97 | 19:30 | Millgate | 44 | 00:00 | SSM | 3 | 05:00
Bhangura | 30 | 22:00 | Ishurdi | 70 | 22:00 | Mirpur | 126 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 55 | 19:00 | Jaldhaka | 54 | 08:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 247 | 03:00 | Jamalpur | 128 | 17:00 | Mithapukur | 26 | 03:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 56 | 19:30 | Jashore | 126 | 23:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 157 | 22:00 | Jhenaidah | 110 | 22:00 | Mogbazar | 104 | 16:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 00:00 | Joydebpur | 173 | 20:00 | Mongla | 22 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 176 | 19:30 | Joypurhat | 56 | 21:00 | Motijheel | 30 | 19:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 138 | 19:00 | Juldah | 28 | 04:00 | Munshiganj | 104 | 21:00 | Shariatpur | 78 | 22:00
Chandpur | 66 | 21:00 | KSRM | 23 | 05:00 | Mymensingh | 215 | 18:30 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:00 | Kabirpur | 185 | 02:00 | Naogaon | 108 | 19:00 | Shikalbaha | 28 | 19:00
Chapai | 61 | 22:00 | Kachua | 68 | 21:00 | Narail | 48 | 22:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 43 | 00:00 | Kallyanpur | 102 | 23:00 | Narinda | 41 | 00:00 | Shitalakhya | 114 | 12:00
Chauddagram | 55 | 20:00 | Kalurghat | 22 | 04:00 | Narshingdi | 195 | 21:00 | Sholosohor | N/A | N/A
Chhatak | 35 | 22:00 | Kamrangirchar | 52 | 01:00 | Natore | 134 | 19:30 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 389 | 19:30 | 369 | 12:00 | Kaliakoir | 391 | 18:00 | 380 | 00:00
| Bibiana | 407 | 19:00 | 397 | 12:00 | Payra | 417 | 18:00 | 406 | 23:00
| BIPTC | 402 | 06:00 | 395 | 14:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 410 | 18:00 | 390 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 221 | 19:30 | 210 | 12:00 | Hasnabad | 220 | 19:30 | 212 | 09:00
| AKSML | 232 | 18:00 | 218 | 07:00 | Hathazari | 236 | 19:30 | 225 | 11:00
| Aminbazar | 221 | 18:00 | 216 | 10:00 | Ishurdi | 236 | 18:00 | 227 | 04:00
| Ashuganj | 238 | 19:30 | 230 | 12:00 | Jhenaidah | 230 | 18:00 | 215 | 23:00
| Baghabari | 234 | 17:00 | 227 | 07:00 | Kaliakoir | 234 | 17:00 | 210 | 20:00
| Barapukuria | 224 | 16:00 | 212 | 07:00 | Keranigonj | 220 | 19:30 | 210 | 12:00
| Barishal | 245 | 18:00 | 235 | 23:00 | Khulna(S) | 239 | 18:30 | 219 | 23:00
| Bheramara | 233 | 18:00 | 223 | 04:00 | Maniknagar | 223 | 19:30 | 214 | 12:00
| Bhulta | 227 | 20:00 | 217 | 12:00 | Meghnaghat | 228 | 19:00 | 217 | 13:00
| Bibiana | 238 | 19:30 | 232 | 02:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 18:00 | 223 | 23:00 | Rajshahi | 235 | 18:00 | 223 | 05:00
| Bogura | 229 | 18:00 | 219 | 04:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 18:00 | 242 | 23:00 | Rampura | 224 | 19:30 | 216 | 12:00
| BSRM | 234 | 19:30 | 223 | 05:00 | Shikalbaha | 236 | 20:00 | 223 | 08:00
| Cumilla(N) | 229 | 19:30 | 221 | 12:00 | Shyampur | 221 | 19:30 | 211 | 12:00
| Fenchuganj | 242 | 19:30 | 236 | 04:00 | Siddhirganj | 228 | 16:00 | 217 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 15:00 | 228 | 03:00
| GPH | 235 | 19:30 | 223 | 07:00 | Tongi | 226 | 20:00 | 215 | 12:00
| Haripur | 222 | 20:00 | 214 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 20:00 | 130 | 12:00 | Lalbag | 136 | 18:00 | 129 | 12:00
| Agargaon | 136 | 18:00 | 130 | 13:00 | Lalmonirhat | 130 | 16:00 | 117 | 07:00
| Agrabad | 138 | 18:00 | 131 | 10:00 | Madanganj | 133 | 19:30 | 129 | 07:00
| AKS | 137 | 20:00 | 128 | 07:00 | Madaripur | 139 | 18:00 | 129 | 22:00
| Aminbazar | 133 | 18:00 | 126 | 15:00 | Madartek | 135 | 18:00 | 129 | 12:00
| Amnura | 132 | 18:00 | 126 | 04:00 | Madunaghat | 139 | 20:00 | 131 | 12:00
| Ashuganj | 138 | 09:00 | 134 | 12:00 | Magura | 138 | 18:00 | 126 | 23:00
| Bagerhat | 133 | 18:00 | 119 | 23:00 | Mahasthangarh | 136 | 18:00 | 125 | 08:00
| Bakulia | 139 | 19:00 | 132 | 07:00 | Manikganj | 134 | 18:00 | 128 | 16:00
| Banani | 133 | 18:30 | 125 | 12:00 | Maniknagar | 130 | 18:00 | 128 | 17:00
| Bangabhaban | 131 | 20:00 | 124 | 12:00 | Matarbari | 132 | 05:00 | 116 | 19:30
| Barapukuria | 137 | 16:00 | 128 | 05:00 | Matuail | 132.6 | 20:00 | 126.1 | 12:00
| Barguna | 138 | 09:00 | 128 | 23:00 | Millgate | 132 | 18:00 | 126 | 12:00
| Barishal | 140 | 18:00 | 128 | 23:00 | Mirpur | 130 | 01:00 | 124 | 14:00
| Barishal-230 | 139 | 18:00 | 131 | 23:00 | Mithapukur | 134 | 16:00 | 123 | 07:00
| Baroaulia | 138 | 19:30 | 132 | 07:00 | Modern | 138 | 00:00 | 132 | 09:00
| Baroirhat | 136 | 00:00 | 128 | 07:00 | Mogbazar | 136 | 20:00 | 130 | 12:00
| Bashundhara | 133 | 18:00 | 126 | 12:00 | Mongla | 132 | 18:00 | 120 | 06:00
| BashundharaCement | 133 | 19:30 | 125 | 12:00 | Motijheel | 131 | 20:00 | 124 | 12:00
| Beanibazar | 133 | 09:00 | 127 | 20:00 | Munshiganj | 134 | 19:30 | 127 | 00:00
| Benapole | 136 | 18:00 | 123 | 23:00 | Mymensingh | 132 | 10:00 | 117 | 07:00
| Bhaluka | 132 | 10:00 | 117 | 07:00 | Naogaon | 135 | 18:00 | 126 | 04:00
| Bhandaria | 139 | 18:00 | 127 | 22:00 | Narail | 136 | 18:30 | 125 | 22:00
| Bhangura | 139 | 18:00 | 134 | 05:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 18:00 | 132 | 22:00 | Narshingdi | 136 | 08:00 | 125 | 00:00
| Bheramara(GK) | 138 | 18:00 | 132 | 22:00 | Natore | 136 | 18:00 | 128 | 07:00
| Bhulta | 126 | 20:00 | 119 | 00:00 | Nawabganj | 136 | 18:00 | 129 | 12:00
| Bog-Sherpur | 137 | 16:00 | 129 | 05:00 | Netrakona | 134 | 09:00 | 118 | 12:00
| Bogura | 138 | 18:00 | 129 | 08:00 | New | 134 | 19:30 | 127 | 12:00
| Bogura-230 | 139 | 18:00 | 130 | 04:00 | Niamatpur | 132 | 16:00 | 123 | 05:00
| Brahmanbaria | 132 | 10:00 | 129 | 12:00 | Noapara | 136 | 18:00 | 123 | 23:00
| Cantonment | 134 | 18:00 | 127 | 12:00 | Pabna | 136 | 18:00 | 130 | 04:00
| Chandpur | 139 | 00:00 | 134 | 01:00 | Palashbari | 132 | 16:00 | 121 | 23:00
| Chandraghona | 139 | 20:00 | 132 | 11:00 | Panchagarh | 135 | 15:00 | 117 | 08:00
| Chapai | 132 | 18:00 | 125 | 07:00 | Patuakhali | 137 | 09:00 | 129 | 23:00
| Charsaidpur | 135 | 19:30 | 126 | 12:00 | Payra | 139 | 18:00 | 133 | 12:00
| Chauddagram | 135 | 19:30 | 127 | 04:00 | PHP | 136 | 19:30 | 128 | 04:00
| Chhatak | 132 | 09:00 | 127 | 20:00 | Postogola | 138 | 19:30 | 130 | 12:00
| Chowmuhani | 135 | 00:00 | 128 | 04:00 | Purbachal | 133 | 18:00 | 125 | 12:00
| Chuadanga | 135 | 18:00 | 122 | 23:00 | Purbasadipur | 134 | 15:00 | 116 | 08:00
| Coxsbazar | 129 | 15:00 | 113 | 19:30 | Rahim | 133 | 19:30 | 127 | 12:00
| Cumilla(N) | 135 | 19:30 | 129 | 04:00 | Rajbari | 135 | 18:00 | 127 | 22:00
| Cumilla(S) | 135 | 19:30 | 125 | 19:00 | Rajendrapur | 135 | 18:30 | 127 | 04:00
| Daudkandi | 132 | 19:30 | 126 | 12:00 | Rajshahi | 133 | 16:00 | 127 | 04:00
| Dhaka | 136 | 19:30 | 130 | 12:00 | Rajshahi-230 | 134 | 18:00 | 127 | 05:00
| Dhamrai | 131 | 18:00 | 124 | 12:00 | Ramganj | 136 | 00:00 | 130 | 06:00
| Dhanmondi | 132 | 21:00 | 124 | 12:00 | Rampur | 137 | 19:00 | 131 | 08:00
| Dohazari | 136 | 00:00 | 128 | 14:00 | Rampura | 135 | 20:00 | 129 | 12:00
| Faridpur | 135 | 18:00 | 127 | 22:00 | Rangamati | 138 | 20:00 | 132 | 04:00
| Fatullah | 135 | 19:30 | 128 | 12:00 | Rangpur | 131 | 15:00 | 118 | 08:00
| Fenchuganj | 137 | 23:00 | 134 | 05:00 | Ruppur | 135 | 02:00 | 132 | 22:00
| Feni | 136 | 19:00 | 130 | 04:00 | Saidpur | 133 | 15:00 | 120 | 08:00
| Ghorashal | 137 | 16:00 | 134 | 01:00 | Satkhira | 157 | 10:00 | 117 | 22:00
| Goalpara | 136 | 18:00 | 124 | 23:00 | Satmasjid | 135 | 18:00 | 129 | 12:00
| Gollamari | 136 | 18:00 | 124 | 23:00 | Savar | 132 | 18:00 | 125 | 12:00
| Gopalganj | 139 | 18:00 | 131 | 21:00 | Shahjadpur | 141 | 18:30 | 135 | 22:00
| Gopalganj_I | 140 | 18:00 | 131 | 22:00 | Shahjibazar | 135 | 02:00 | 132 | 12:00
| Gulshan | 135 | 18:00 | 129 | 12:00 | Shahmirpur | 139 | 19:30 | 131 | 10:00
| Halishahar | 139 | 20:00 | 131 | 14:00 | Shariatpur | 136 | 18:00 | 127 | 22:00
| Haripur | 133 | 20:00 | 127 | 12:00 | Sherpur | 135 | 10:00 | 114 | 07:00
| HaripurSBU | 133 | 20:00 | 128 | 00:00 | Shikalbaha | 140 | 01:00 | 131 | 10:00
| Hasnabad | 137 | 20:00 | 130 | 12:00 | Shikalbaha-230 | 139 | 18:00 | 132 | 08:00
| Hathazari | 140 | 20:00 | 133 | 11:00 | Shitalakhya | 138 | 20:00 | 129 | 12:00
| Ishurdi | 138 | 18:00 | 132 | 05:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 132 | 15:00 | 116 | 08:00 | Shyampur | 133 | 18:30 | 124 | 12:00
| Jamalpur | 138 | 10:00 | 116 | 07:00 | Shyampur-230 | 134 | 00:00 | 128 | 12:00
| Jashore | 136 | 18:00 | 124 | 22:00 | Siddhirganj | 133 | 20:00 | 126 | 12:00
| Jhenaidah | 139 | 16:00 | 130 | 22:00 | Sirajganj | 137 | 18:30 | 130 | 07:00
| Jhenaidah-230 | 140 | 18:00 | 130 | 23:00 | Sonargaon | 134 | 19:30 | 126 | 00:00
| Joydebpur | 140 | 07:00 | 135 | 12:00 | Sreemongol | 136 | 09:00 | 134 | 14:00
| Joypurhat | 136 | 18:00 | 125 | 03:00 | Srinagar | 135 | 19:30 | 128 | 12:00
| Juldah | 139 | 18:00 | 131 | 11:00 | SSM | 139 | 19:30 | 134 | 14:00
| Kabirpur | 137 | 18:30 | 124 | 01:00 | Sunamganj | 132 | 09:00 | 124 | 20:00
| Kachua | 136 | 19:00 | 130 | 03:00 | Sylhet | 134 | 09:00 | 131 | 14:00
| Kaliakoir | 137 | 15:00 | 132 | 14:00 | Tangail | 134 | 18:30 | 126 | 21:00
| Kallyanpur | 132 | 06:00 | 125 | 12:00 | Thakurgaon | 132 | 00:00 | 113 | 08:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 590 | 7233 | 4461 | 11694 |  |  |  | QF-LDC-11
0:30 | 669 | 7103 | 4384 | 11487 | Date: | 2022-08-05
1:00 | 748 | 6973 | 4307 | 11280
1:30 | 748 | 6899.5 | 4285 | 11184.5
2:00 | 748 | 6826 | 4263 | 11089
2:30 | 739 | 6810 | 4272 | 11082 | [5 empty] | Gen. at Eve. Peak | 12885 | 12885 MW (21:00 )
3:00 | 730 | 6794 | 4281 | 11075 | [6 empty] | 21:00
3:30 | 724 | 6761.5 | 4274 | 11035.5 | [5 empty] | Gen. at Day Peak | 10438 | 10438 MW (09:00 )
4:00 | 718 | 6729 | 4267 | 10996 | [6 empty] | 9:00
4:30 | 727 | 6720.5 | 4281.5 | 11002 | [5 empty] | Highest Generation | 12951
5:00 | 736 | 6712 | 4296 | 11008 | [6 empty] | 22:00
5:30 | 720 | 6645 | 4258 | 10903
6:00 | 704 | 6578 | 4220 | 10798
6:30 | 654 | 6596 | 4183.5 | 10779.5
7:00 | 604 | 6614 | 4147 | 10761
7:30 | 595 | 6594 | 4097 | 10691
8:00 | 586 | 6574 | 4047 | 10621
8:30 | 578 | 6554.5 | 3975 | 10529.5
9:00 | 570 | 6535 | 3903 | 10438
9:30 | 587 | 6465 | 3890 | 10355
10:00 | 604 | 6395 | 3877 | 10272
10:30 | 629 | 6374.5 | 3871.5 | 10246
11:00 | 654 | 6354 | 3866 | 10220
11:30 | 758 | 6387 | 3887.5 | 10274.5
12:00 | 862 | 6420 | 3909 | 10329
12:30 | 783 | 6472 | 3923.5 | 10395.5
13:00 | 704 | 6524 | 3938 | 10462
13:30 | 723 | 6522 | 3912 | 10434
14:00 | 742 | 6520 | 3886 | 10406
14:30 | 803 | 6482.5 | 3931.5 | 10414
15:00 | 864 | 6445 | 3977 | 10422
15:30 | 835 | 6441 | 3927 | 10368
16:00 | 806 | 6437 | 3877 | 10314
16:30 | 658 | 6706.5 | 3820.5 | 10527
17:00 | 510 | 6976 | 3764 | 10740
17:30 | 488 | 6946 | 3686.5 | 10632.5
18:00 | 466 | 6916 | 3609 | 10525
18:30 | 413 | 7432.5 | 3771.5 | 11204
19:00 | 360 | 7949 | 3934 | 11883
19:30 | 296 | 8023 | 4322 | 12345
20:00 | 320 | 8083 | 4386 | 12469 |  |  |  | Executive Engineer
20:30 | 354 | 8193.5 | 4483.5 | 12677 |  |  |  | Network Operation Division
21:00 | 388 | 8304 | 4581 | 12885
21:30 | 331 | 8347.5 | 4570.5 | 12918
22:00 | 274 | 8391 | 4560 | 12951 |  |  |  |  | Page 6 of 7
22:30 | 303 | 8282 | 4579.5 | 12861.5
23:00 | 332 | 8173 | 4599 | 12772
23:30 | 461 | 7703 | 4530 | 12233
24:00 | 590 | 7233 | 4461 | 11694
12885 MW (21:00 )
10438 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-05 |  | Energy |  | 270220379
[13 empty] | 2022-08-05 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3847 | 914 | 1950 | 0 | 2724 | 1300 | 113 | 209 | 678 | 168 | 0 | 1019.262
0:30 | 3799 | 910.5 | 1981 | 0 | 2545.5 | 1295 | 113.5 | 210.5 | 682.5 | 160 | 0 | 1302.1855 | Date: | 2022-08-05
1:00 | 3751 | 907 | 2012 | 0 | 2367 | 1290 | 114 | 212 | 687 | 152 | 0 | 1585.109
1:30 | 3739.5 | 907 | 2027 | 0 | 2285.5 | 1290 | 114.5 | 212 | 691 | 130 | 0 | 1580.9619 | [7 empty] | Total Energy | 270.2204 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3728 | 907 | 2042 | 0 | 2204 | 1290 | 115 | 212 | 695 | 108 | 0 | 1576.8148 | [7 empty] | Energy not Served | 18.516
2:30 | 3722 | 907 | 2037 | 0 | 2214.5 | 1290 | 114.5 | 211 | 693 | 104 | 0 | 1491.1083 | [7 empty] | Energy Requirement | 288.7364
3:00 | 3716 | 907 | 2032 | 0 | 2225 | 1290 | 114 | 210 | 691 | 100 | 0 | 1405.4019
3:30 | 3716.5 | 907.5 | 2029 | 0 | 2216.5 | 1285 | 91 | 207 | 679 | 111 | 0 | 1395.7253 | [5 empty] | Shortage
4:00 | 3717 | 908 | 2026 | 0 | 2208 | 1280 | 68 | 204 | 667 | 122 | 0 | 1386.0488
4:30 | 3708.5 | 908.5 | 2046 | 0 | 2188.5 | 1280 | 78 | 204.5 | 667.5 | 125 | 0 | 1196.2043
5:00 | 3700 | 909 | 2066 | 0 | 2169 | 1280 | 88 | 205 | 668 | 128 | 0 | 1006.3599
5:30 | 3668.5 | 909 | 2054.5 | 0 | 2133.5 | 1259.5 | 100 | 210.5 | 653 | 123 | 2 | 872.7315
6:00 | 3637 | 909 | 2043 | 0 | 2098 | 1239 | 112 | 216 | 638 | 118 | 4 | 739.1032
6:30 | 3657.5 | 909 | 2037.5 | 0 | 2096.5 | 1204.5 | 111.5 | 216 | 629.5 | 116 | 17.5 | 571.8373 |  |  |  | Coal
7:00 | 3678 | 909 | 2032 | 0 | 2095 | 1170 | 111 | 216 | 621 | 114 | 31 | 404.5714
7:30 | 3673.5 | 908.5 | 1998 | 0 | 2094.5 | 1155 | 111 | 204 | 582.5 | 111 | 57 | 284.7857 |  |  | Oil |  |  |  | ,
8:00 | 3669 | 908 | 1964 | 0 | 2094 | 1140 | 111 | 192 | 544 | 108 | 83 | 165
8:30 | 3634 | 908.5 | 1954.5 | 0 | 2094 | 1120 | 111 | 161 | 481 | 123 | 103.5 | 272.5
9:00 | 3599 | 909 | 1945 | 0 | 2094 | 1100 | 111 | 130 | 418 | 138 | 124 | 380
9:30 | 3598 | 909 | 1880.5 | 0 | 2059.5 | 1100 | 111 | 130 | 407.5 | 137 | 152.5 | 525.5
10:00 | 3597 | 909 | 1816 | 0 | 2025 | 1100 | 111 | 130 | 397 | 136 | 181 | 671
10:30 | 3586.5 | 909 | 1808 | 0 | 2012.5 | 1100 | 112 | 130 | 395.5 | 141 | 181.5 | 833
11:00 | 3576 | 909 | 1800 | 0 | 2000 | 1100 | 113 | 130 | 394 | 146 | 182 | 995
11:30 | 3589 | 908.5 | 1808.5 | 0 | 1996 | 1109.5 | 113 | 144.5 | 411 | 143 | 196 | 1037.5
12:00 | 3602 | 908 | 1817 | 0 | 1992 | 1119 | 113 | 159 | 428 | 140 | 210 | 1080
12:30 | 3653 | 908.5 | 1810.5 | 0 | 1992.5 | 1129.5 | 113 | 180 | 451.5 | 146 | 191 | 972
13:00 | 3704 | 909 | 1804 | 0 | 1993 | 1140 | 113 | 201 | 475 | 152 | 172 | 864
13:30 | 3704 | 909 | 1804 | 0 | 1993 | 1140 | 113 | 201 | 475 | 152 | 172 | 864
14:00 | 3704 | 909 | 1804 | 0 | 1993 | 1140 | 113 | 201 | 475 | 152 | 172 | 864
14:30 | 3673 | 909 | 1815 | 0 | 2018 | 1145 | 113.5 | 190.5 | 461 | 154 | 153.5 | 952
15:00 | 3642 | 909 | 1826 | 0 | 2043 | 1150 | 114 | 180 | 447 | 156 | 135 | 1040
15:30 | 3627 | 910.5 | 1815 | 0 | 2073.5 | 1135 | 113.5 | 155 | 422.5 | 156 | 115 | 997.5
16:00 | 3612 | 912 | 1804 | 0 | 2104 | 1120 | 113 | 130 | 398 | 156 | 95 | 955
16:30 | 3497 | 912.5 | 1735.5 | 0 | 2463 | 1095 | 113.5 | 130 | 436.5 | 151 | 65.5 | 574.5
17:00 | 3497 | 913 | 1667 | 0 | 2822 | 1070 | 114 | 130 | 475 | 146 | 36 | 194
17:30 | 3444 | 913 | 1610.5 | 0 | 2907 | 985 | 113 | 130 | 494.5 | 140 | 25.5 | 97
18:00 | 3391 | 913 | 1554 | 0 | 2992 | 900 | 112 | 130 | 514 | 134 | 15 | 0
18:30 | 3592.5 | 913 | 1722.5 | 0 | 3196.5 | 920 | 113 | 144 | 592 | 147 | 7.5 | 238.2271
19:00 | 3794 | 913 | 1891 | 0 | 3401 | 940 | 114 | 158 | 670 | 160 | 0 | 476.4543
19:30 | 3732 | 913 | 1872 | 0 | 3685 | 1210 | 114 | 150 | 667 | 152 | 0 | 695.7891
20:00 | 3757 | 913 | 1901 | 0 | 3708 | 1220 | 112 | 130 | 704 | 154 | 0 | 673.6713
20:30 | 3817 | 913 | 1966 | 0 | 3764 | 1230 | 112 | 151 | 717 | 158 | 0 | 597.1806
21:00 | 3877 | 913 | 2031 | 0 | 3820 | 1240 | 112 | 172 | 730 | 162 | 0 | 520.6899
21:30 | 3896.5 | 913 | 2044 | 0 | 3830 | 1240 | 112 | 166 | 715.5 | 167 | 0 | 421.1598
22:00 | 3916 | 913 | 2057 | 0 | 3840 | 1240 | 112 | 160 | 701 | 172 | 0 | 321.6297
22:30 | 3918 | 913 | 2065 | 0 | 3717.5 | 1240 | 112.5 | 179.5 | 726.5 | 169 | 0 | 358.0319
23:00 | 3920 | 913 | 2073 | 0 | 3595 | 1240 | 113 | 199 | 752 | 166 | 0 | 394.4341
23:30 | 3883.5 | 913.5 | 2011.5 | 0 | 3159.5 | 1270 | 113 | 204 | 715 | 167 | 0 | 706.848 | Max Temp. in Dhaka |  | 35.4° C
24:00 | 3847 | 914 | 1950 | 0 | 2724 | 1300 | 113 | 209 | 678 | 168 | 0 | 1019.262
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 79 | 80 | 79 | 33 | 53 | 77 | 76 | 76 | 76 | 76 | 78 | 78 | 78 | 79 | 79 | 78 | 79 | 77 |  | 79 | 79 | 77 | 77 | 77 | 78 | 78 | 1813440
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 16 | 16 | 25 | 25 | 25 | 25 | 580883
| Teknaf 20MW PP (Solartech) | [6 empty] | 5 | 0 | 11 | 14 | 7 | 11 | 20 | 14 | 8 | 7 | 4 | 0 | [8 empty] | 112455
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1201626
12 | Hathazari 100 MW peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 26 | 26 | 26 | 25 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 15 | 18 | 26 | 26 | 552048
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 87 | 87 | 87 | 87 | 81 | 80 | 80 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 79 | 101 |  | 105 | 105 | 105 | 105 | 105 | 105 | 87 | 2043227
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 40 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 34 | 34 |  | 40 | 35 | 42 | 39 | 34 | 40 | 32 | 1057560
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [12 empty] | 94 | 94 | 92 | 60 | 57 | 37 |  | 95 | 53 | 52 | 92 | 97 | 97 | 94 | 966000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 118 | 115 | 112 | 115 | 115 | 115 | 115 | 112 | 115 | 112 | 112 | 112 | 112 | 112 | 112 | 105 | 105 | 250 |  | 243 | 243 | 243 | 245 | 258 | 260 | 205 | 3748580
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 284363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 250 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7018845
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 36 | 36 | 36 | 35 | 34 | 34 | 34 | 34 | 31 |  | 34 | 36 | 36 | 36 | 34 | 34 | 36 | 831024
33 | Ashuganj 225 MW CCPP | 208 | 208 | 200 | 187 | 178 | 186 | 176 | 183 | 179 | 205 | 203 | 197 | 189 | 201 | 188 | 204 | 181 | 207 |  | 203 | 200 | 207 | 206 | 205 | 204 | 210 | 4728000
34 | Ashuganj 450 MW CCPP(South) | 330 | 320 | 335 | 335 | 335 | 305 | 320 | 325 | 305 | 305 | 325 | 320 | 330 | 325 | 300 | 275 | 275 | 260 |  | 325 | 275 | 275 | 305 | 330 | 330 | 310 | 7594000
| Ashuganj 450 MW CCPP(North) | 355 | 345 | 320 | 320 | 310 | 260 | 295 | 300 | 280 | 280 | 345 | 340 | 315 | 315 | 305 | 280 | 280 | 280 |  | 335 | 280 | 280 | 310 | 330 | 345 | 310 | 7763000
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 30 | 55 | 56 | 56 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 54 | 55 | 55 | 55 | 55 | 1100640
36 | Chandpur 150 MW CCPP | 144 | 144 | 143 | 142 | 144 | 144 | 144 | 143 | 141 | 142 | 142 | 142 | 143 | 143 | 143 | 142 | 143 | 143 |  | 142 | 142 | 143 | 142 | 142 | 142 | 142 | 3402030
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 405 | 406 | 403 | 404 | 410 | 411 | 410 | 410 | 411 | 407 | 396 | 399 | 404 | 396 | 405 | 408 | 408 |  | 408 | 411 | 409 | 412 | 410 | 409 | 404 | 9887750
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5035400
41 | Haripur 360MW CCPP(HPL) | 333 | 334 | 333 | 333 | 333 | 333 | 331 | 331 | 327 | 328 | 327 | 312 | 312 | 312 | 318 | 316 | 281 | 251 |  | 310 | 332 | 332 | 332 | 333 | 333 | 332 | 7708000
42 | RPCL 210MW CCPP | 97 | 98 | 98 | 100 | 100 | 101 | 99 | 80 | 67 | 66 | 66 | 66 | 65 | 67 | 66 | 71 | 83 | 83 |  | 99 | 102 | 101 | 102 | 100 | 100 | 102 | 2030400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 4 | 26 | 13 | 40 | 21 | 54 | 49 | 25 | 5 | 12 | 11 | 3 |  | 0 | [6 empty] | 286310
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 956624
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 61 | 61 | 60 | 60 | 61 | 61 | 60 | 60 | 60 | 58 | 55 | 55 | 58 | 59 | 61 | 61 | 40 |  | 60 | 61 | 61 | 61 | 60 | 60 | 61 | 1416480
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 10 | 1261440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 220 | 220 | 220 | 220 | 220 | 221 | 221 | 221 | 220 | 221 | 206 |  | 220 | 220 | 220 | 220 | 221 | 221 | 221 | 5246580
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 |  | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 749480
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 236880
54 | Hobiganj 11MW PP Cofidence-E | [21 empty] | 11 | 11 | 11 | 11 | 11 | 55000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 33 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 53 | 53 | 53 | 53 | 53 | 53 | 31 | 1069800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 12 | 16 | 16 | 16 | 24 | 24 | 8 | 233024
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 320 | 330 | 320 | 325 | 310 | 300 | 305 | 300 | 270 | 300 | 330 | 320 | 295 | 320 | 290 | 270 | 270 |  | 290 | 250 | 260 | 270 | 290 | 310 | 300 | 7427500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 954209
59 | Tangail Palli Power Gen 22 MW | [26 empty] | 0
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 375456
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 0 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 392184
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 19 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 408528
63 | Impoprt (Tripura) | 152 | 108 | 100 | 122 | 128 | 118 | 114 | 108 | 138 | 136 | 146 | 140 | 152 | 154 | 156 | 156 | 146 | 134 |  | 160 | 152 | 154 | 162 | 172 | 166 | 168 | 3364800
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 40 | 40 | 41 | 42 | 42 | 42 | 39 | 31 | 21 | 30 | 30 | 30 | 32 | 31 | 33 | 33 |  | 35 | 35 | 29 | 31 | 39 | 30 | 42 | 869760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502416
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 8 |  | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 201240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 493360
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 20 | 20 | 12 | 20 | 17 | 13 | 15 | 15 | 17 | 17 |  | 19 | 23 | 25 | 25 | 25 | 18 | 19 | 489240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 686160
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 31 | 31 | 31 | 16 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 718400
73 | Ghorashal 108MW PP (Regent) | 80 | 80 | 83 | 83 | 83 | 83 | 83 | 85 | 85 | 85 | 80 | 82 | 81 | 82 | 84 | 84 | 84 | 43 |  | 85 | 87 | 89 | 89 | 89 | 90 | 90 | 1952909
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 114 | 88 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 1061340
| Chowmuhani 113 MW | 107 | 107 | 102 | 102 | 107 | 107 | 105 | 106 | 106 | 105 | 105 | 103 | 103 | 102 | 103 | 101 | 101 | 106 |  | 112 | 113 | 112 | 113 | 113 | 112 | 98 | 2550240
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 74 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2760480
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 89 | 76 | 88 | 81 | 84 | 8 | 522240
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 |  | 46 | 50 | 50 | 48 | 48 | 50 | 42 | 1122720
79 | Kodda 150MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 132 | 132 |  | 130 | 130 | 130 | 127 | 112 | 112 | 48 | 1669920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 20 | 43 | 43 | 43 | 43 | 43 | 43 | 404381
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2466000
| Kaptai 7 MW Solar PP | [5 empty] | 0 |  |  | 0 | 5 | 6 | 6 | 3 | 5 | 4 | 1 | 0 | [9 empty] | 23641
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 776329
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 53 | 51 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1317267
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 7 | 0 | 4 | 8 | 7 | 5 |  | 42 | 78 | 73 | 80 | 79 | 75 | 15 | 499200
| Meghnaghat 104 MW PP (OPCL) | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 0 |  | 0 | 11 | 18 |  | 50 | 72 | 90 | 88 | 91 | 79 | 23 | 650880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 10 |  | 56 | 56 | 56 | 56 | 56 | 45 | 56 | 1309080
92 | Fenchuganj 44MW (Energyprima) | 49 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 48 | 49 | 49 | 49 | 49 | 49 | 30 | 1069800
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 |  | 32 | 35 | 51 | 51 | 51 | 51 | 51 | 1175026
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 58 | 64 | 94 | 94 | 94 | 32 | 8 | 495216
95 | Patenga 50MW PP (Baraka) | 32 | 27 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 30 | 31 | 31 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 19 | 740640
96 | Chattogram 108 MW PP (ECPV) | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 11 | 11 | 15 | 28 | 66 |  | 75 | 82 | 84 | 89 | 90 | 89 | 89 | 731520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 853556
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1330984
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2591263
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15450
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 |  | 40 | 54 | 54 | 54 | 54 | 54 | 35 | 870120
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 68 | 174 | 175 |  | 178 | 179 | 179 | 179 | 180 | 47 | 47 | 1900800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 104 | 96 | 98 | 98 | 102 | 97 | 98 | 88 | 98 | 98 | 98 | 102 | 104 | 95 | 95 | 89 | 128 | 119 |  | 136 | 136 | 135 | 133 | 135 | 135 | 101 | 2607696
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 90 | 90 | 76 | 90 | 90 | 90 | 90 | 862080
116 | Chandpur 200MW (Desh energy) | 161 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 160 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 181 | 3254880
117 | Ashuganj 150MW PP (Midland) | 138 | 132 | 137 | 132 | 135 | 142 | 140 | 132 | 130 | 120 | 115 | 120 | 120 | 122 | 120 | 118 | 118 | 118 |  | 122 | 123 | 123 | 128 | 135 | 135 | 138 | 3082836
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 399 | 402 | 401 | 400 | 400 | 402 | 400 | 375 | 377 | 381 | 376 | 399 | 391 | 403 | 353 | 333 |  | 403 | 402 | 402 | 402 | 404 | 405 | 401 | 9387000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 49 | 48 | 48 | 49 | 49 | 78 | 78 |  | 78 | 79 | 79 | 79 | 79 | 49 | 49 | 1342800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 50 | 50 | 52 | 52 | 52 | 51 | 52 | 52 | 200 | 213 |  | 214 | 214 | 214 | 214 | 214 | 214 | 16 | 2029855
| Juldah unit-2 (Acorn) | 51 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 40 | 100 | 100 | 100 | 100 | 100 | 90 | 954240
| Anlima Energy Ltd. | 108 | 96 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 102 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2589382
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887760
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 10 | 7 | 24 | 24 | 34 | 19 | 23 | 31 | 26 | 19 | 8 | 2 |  | 0 | [6 empty] | 249991
| Chandpur 115(Doreen) | 76 | 75 | 75 | 75 | 75 | 75 | 76 | 75 | 65 | 62 | 64 | 53 | 55 | 74 | 74 | 74 | 75 | 70 |  | 67 | 67 | 66 | 74 | 75 | 76 | 75 | 1710720
| Kanchan Purbachal Power Generation Ltd. | 36 | 37 | 36 | 20 | 19 | 19 | 19 | 17 | 17 | 17 | 0 | [11 empty] | 55 | 55 | 55 | 55 | 458640
120 | Eastern Zone Total | 6973 | 6826 | 6794 | 6729 | 6712 | 6578 | 6614 | 6574 | 6535 | 6395 | 6354 | 6420 | 6524 | 6520 | 6445 | 6437 | 6976 | 6916 |  | 7949 | 8023 | 8083 | 8304 | 8391 | 8173 | 7233 | 168087424
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 375360
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 15 |  | 44 | 38 | 38 | 32 | 32 | 32 | 32 | 292320
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 17 |  | 25 | 35 | 35 | 35 | 35 | 35 |  | 175200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 11 | 45 | 67 | 88 | 103 | 107 | 64 | 4 | 83 | 51 | 9 | 8 | [8 empty] | 609120
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 224 | 222 | 222 | 222 | 225 | 223 | 220 | 220 | 218 | 212 | 213 | 212 | 213 | 213 | 200 | 168 | 164 |  | 208 | 208 | 214 | 214 | 220 | 221 | 220 | 5058955
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 |  | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 724032
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 86 | 86 | 88 | 88 | 88 | 88 | 85 | 86 | 87 | 84 | 83 | 84 | 83 | 84 | 87 | 85 | 88 |  | 88 | 88 | 88 | 88 | 86 | 85 | 87 | 2076507
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 32 | 30 | 27 | 24 | 25 | 23 | 22 | 22 | 19 | 23 | 25 | 25 | 25 | 24 | 22 | 20 |  | 30 | 31 | 29 | 31 | 32 | 32 | 31 | 634351
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 143250
143 | Gopalganj 100 MW Peaking PP | 67 | 67 | 65 | 56 | 56 | 56 | 56 | 56 | 0 | [10 empty] | 30 | 37 | 76 | 71 | 70 | 68 | 56 | 854528
144 | Bheramara GTPP Unit-3 |  |  |  |  | 0 | 0 | 0
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2562192
146 | Bheramara HVDC | 907 | 907 | 907 | 908 | 909 | 909 | 909 | 908 | 909 | 909 | 909 | 908 | 909 | 908 | 909 | 912 | 913 | 913 |  | 913 | 913 | 913 | 913 | 913 | 913 | 914 | 21995636
147 | Bheramara 410 MW CCPP | 145 | 140 | 150 | 160 | 160 | 160 | 160 | 160 | 155 | 160 | 150 | 145 | 150 | 145 | 145 | 150 | 155 | 160 |  | 170 | 180 | 180 | 185 | 185 | 185 | 180 | 3989376
148 | Payra 1320 MW | 1090 | 1090 | 1090 | 1080 | 1080 | 1040 | 970 | 940 | 900 | 900 | 900 | 920 | 940 | 950 | 950 | 920 | 870 | 700 |  | 740 | 1010 | 1020 | 1040 | 1040 | 1040 | 1100 | 25414800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4886100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 |  | 25 | 25 | 32 | 32 | 32 | 32 | 32 | 740640
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 2 |  | 1 | 0 | [8 empty] | 35760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 182 | 181 | 181 | 181 | 179 | 180 | 180 | 180 | 180 | 180 | 180 | 181 | 181 | 180 | 179 | 176 | 130 | 130 |  | 140 | 184 | 187 | 190 | 190 | 188 | 192 | 4495045
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 212 | 212 | 210 | 204 | 205 | 216 | 216 | 192 | 130 | 130 | 130 | 159 | 201 | 199 | 180 | 130 | 130 | 130 |  | 158 | 150 | 130 | 172 | 160 | 199 | 209 | 4534573
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 142 | 142 | 142 | 144 | 146 | 147 | 149 | 147 | 146 | 145 | 144 | 144 | 143 | 141 | 141 | 142 | 146 | 130 |  | 137 | 154 | 159 | 167 | 163 | 163 | 160 | 3801964
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 282 | 281 | 295 | 301 | 339 | 330 | 332 | 315 | 310 | 280 | 281 | 268 | 265 | 280 | 275 | 300 | 250 | 254 |  | 260 | 250 | 254 | 370 | 360 | 363 | 352 | 7170981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | [6 empty] | 5 | 5 | 5 | 5 | 6 | 6 | 6 |  | 19 | 25 | 30 | 40 | 41 | 41 | 41 | 409440
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 19 |  | 19 | 21 | 21 | 21 | 21 | 21 | 22 | 457460
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264474
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 34 | 34 | 34 | 34 | 34 | 924528
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29 | 24 | 24 | 24 | 32 | 30 |  | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 558750
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 12 | 0 | [6 empty] | 33 |  | 33 | 34 | 33 | 33 | 33 | 33 | 33 | 528870
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 46 | 52 | 52 | 52 | 52 | 52 | 8 | 384000
170 | Chapainawabganj 100 MW Peaking PP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 34 | 34 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1474800
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1630656
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 50 |  | 60 | 95 | 95 | 95 | 95 | 95 | 55 | 1588224
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 65 | 80 | 91 |  | 91 | 92 | 92 | 92 | 92 | 92 | 73 | 1601011
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 6 | 6 | 5 | 4 | 3 | 2 | [8 empty] | 48532
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 1691520
178